## About
2000-F00-LST-PP-10003 Control Valve List Rev 0
Tables only, from the original XLSX (Every sheet of the original except the cover page, rebuilt from the cell values). Cover page, logos, sign off names and file metadata removed. Built by tools/build_sources.py.
Sheet | Rows | Columns | Hidden in the original
Control Valve SoW | 126 | 6
Control Valve List | 837 | 54
Valve Detail | 86 | 7
Control Panel List | 830 | 10
Control Valve Type | 7 | 5
Control Panel Count | 96 | 3
Materials of construction | 31 | 5
Tubing change to 12mm | 120 | 9
Pressure ratings | 21 | 2
Emerson data | 166 | 8
Valve GAs | 152 | 5
Control Panel DRGS | 88 | 4
Area Codes - Do Not Print | 145 | 2 | Yes
Pivot Ref - Do Not Print | 841 | 7 | Yes
Pivot Table - Do Not Print | 80 | 5 | Yes

## Control Valve SoW
LIST
KCGM GROWTH PROJECT
Primero Project Number: | 23517
List Title: | Control Valve List
Document Number: | 2000-F00-DSH-PP-11007
Client Company Name: | Northern Star Resources Limited
DATE | REVISION | STATUS | PREPARED | REVIEWED | APPROVED
2025-08-15 | 0 | Issued for Use | [name removed] | [name removed] | [name removed]
PROCUREMENT PACKAGE: |  | PP007
PRIMERO PROJECT NO. |  | 23517
Description: |  | Control Valves and Valve Control Panels throughout the plant
Reference Specifications: |  | SPEC-00-G-05 - Technical Specification for Protective Coating
2000-F00-PID-PR-10007 - Piping and Instrumentation Diagram - Legend Sheet 7
2000-F00-SKT-IC-10101 - Conceptual Termination Diagram Layout 1
2000-F00-SKT-IC-10102 - Conceptual Termination Diagram Layout 2
2000-F00-STS-GE-10001 - Packing and Shipping Specification
2000-F00-STS-GE-10002 - Site Specific Information
2000-F00-STS-EL-10001 - Electrical Equipment for Mechanical Packages Specification
2000-F00-STS-EL-10008 - Electrical Enclosures Specification
2000-F00-STS-EL-10014 - Preferred Equipment Suppliers for Electrical, Instrumentation and Controls Specification
2000-F00-STS-PP-10001 - Piping Materials and Valves (Appendix B - Valve Datasheets)
2000-MEP-PP007-SCH1 - Vendor Document Schedule
SCOPE OF WORK
Work Included
Design, manufacture and assembly of control valves including, but not limited to:
· Valve as specified on the control valve list and valve datasheet
o Vendor to confirm valve sizing for modulating control valves
· Pneumatic actuator as specified on control valve list, with 316SS quick connect push-in fittings
· Positioner as specified on the control valve list, mounted onto valve actuator
· Valve position feedback via positioner feedback transmitter or position limit switches as specified on control valve list.
· All valve mounted instruments to be pre-terminated to local junction box mounted on valve body
o Junction box to be 316SS, Enclosure rating IP65
o Cable glands shall be IP66/68 nickel plated brass with metric threads to AS/NZS 60079, with PVC shrouds
o Cables to valve mounted instruments shall be installed within flexible anaconda
· Valve Control Panels. Panels shall include:
o Material of Construction to be 316SS with hinged door and mounting brackets. Enclosure rating of IP65
o Air supply pressure of 400 - 1,000 kPag
o Labelling of control panel tag number and associated valve tag numbers and solenoid valve tag numbers for easy identification
▪ All external labelling to be 316SS fixed with screws to control panel door
o Pneumatic filter regulator complete with pressure gauge and normally closed automatic drain
▪ The filter regulator automatic drain shall be piped to outside the enclosure
o Solenoid valve as per control valve list, with opening adjustment for valve opening and closing speed (for open/closed valves)
o Isolation valve with bleed and silencers
▪ One for each solenoid mounted in panel, and one for the entire control panel
o Pneumatic fittings to be 316SS, quick connect push-in tube fittings
o Tubing penetrations shall be standard bulkhead fittings
o Vendor to specify required air tubing size and ports, size to be common across a number of valve sizes
▪ Tubing to be DIN73378 PA12 Blue Nylon pneumatic tubing
o Pneumatic Schematic Drawing installed inside panel
o Termination strips for valve instrumentation, complete with required fixing hardware such as endplates and end clamps.
o All vendor wired cables to come equipped with bootlaces and ferrules labelled as per Primero termination diagrams/naming convention
o Gland plate cable entry
o All controller and transmitter signals to be 4-20 mA, solenoid and position switch signals to be 24Vdc
· All ancillary items and special tools normally supplied with, or required to adjust and maintain all components associated with the equipment.
Specifications:
· All equipment to be supplied in accordance with the above referenced specifications.
· Any non-conformances with the specifications shall be clarified with the Principal for approval.
Documentation / Quality:
· Vendor data and documentation in accordance with 2000-MEP-PP007-SCH1.
· Shop assembly and testing to the greatest extent possible with accompanying documentation including but not limited to:
o Dimensional checks
o Testing of control devices
o Calibration of instruments
o Operation of manual, pneumatic or electric actuators
o Testing of all other auxilliaries to confirm functionality
· Performance guarantees and testing (state extents).
Shipping:
· Packaging suitable for transport as per 2000-F00-STS-GE-10001.
· Delivery as nominated in the commercial documentation.
Work Excluded
Excluded from this scope of works shall be the following:
· Hold-down bolts, nuts, and washers at structural steel.
· Supply of all power, control, and instrumentation cabling outside battery limits.
· Lubricants and greases, other than initial fill quantities applied during shop assembly and /or preparation for shipment.
· Spare parts.
· Offloading the equipment at site.
· Installation and commissioning at site.
Battery Limits
The works covered by this datasheet extend up to, and include the following battery limits:
· Inlet and outlet connection of valve body
· Pneuamatic inlet and outlet connection of actuator
· Control Valve Instrument Junction Box Cable Entry
· Pneumatic Inlet and outlet connections of Valve Control Panel
· Valve Control Panel Gland Plate
Design Requirements
General
· Equipment will be operating in a harsh, outdoors environment and handling various solutions, thus, materials and surface treatments must be suitably selected to guarantee the longevity of the components for each individual pump.
· Design and materials for seals/glands to be suitable for the specified water quality.
· The equipment may be in contact with process water and slurry which contains reagents, components shall not contain any brass, bronze, or aluminium alloys.
Guards
· All guards shall be capable of being removed without disturbing other parts of the equipment.
· Where guards interfere with access to lubrication points, stainless steel tubing and fixed remote grease nipples shall be provided so that lubrication can be undertaken without removing the guard and while the equipment is operating.
· Guards shall have sufficient space for drive and component adjustment.
DUTY SPECIFICATION | UOM | PRIMERO DATA | SUPPLIER DATA |  | NOTES
Site Data
Site Location | - | Kalgoorlie, WA |  |  | 1
Site Data | - | Refer to 2000-F00-STS-GE-10002 – Site Specific Information |  |  | 1
Application Data
Duty | - | Continuous |  |  | 1
Location | - | Outdoors |  |  | 1
Operating Hours per Day | hr/day | 24 |  |  | 1
Operating Days per Week | days/week | 7 |  |  | 1
Operating Weeks per Year | weeks/year | 52 |  |  | 1
Utilisation | % | >95 |  |  | 1
Design Life | years | 30 years minimum |  |  | 1
Expected Ambient Operating Temperature Range | °C | 1.7 to 37.2 |  |  | 1
Design for -5°C to 50°C

## Control Valve List
CONTROL VALVE LIST
Last Revised | Valve Type | Area Number | Sequential Number | Valve TAG | Valve Size | Valve Class | Control Valve Code | Location Description | Piping Line Number | P&ID | Air P&ID | Stage | Brownfield / Greenfield | Service Fluid | Line Spec. | Line Size | Flowrate (m3/h) Min | Flowrate (m3/h) Max | Inlet Pressure (kPag) | Valve Pressure Drop (kPa) @ Min Flow | Valve Pressure Drop (kPa) @ Max Flow | Solids P50 (µm) | Solids P80 (µm) | % Solids (w/w) | Fluid SG | Max. Pressure kPa(g) | Closing Time (sec) | Detail | Power Failure FC / FO / FL | Actuator Type | Solenoid Type | Solenoid Tag | Positioner Yes/No | Position Feedback | Special Requirements | Pneumatic Control Panel / HPU Tag Number | Control Panel General Arrangement Drawing | Valve Package | Pneumatic Control Panel Package | Comments | Valve Manufacturer | Valve Model No. | Valve Drawing | Actuator Manufacturer | Actuator Model | Limit/proximity Switches/Positoner Model | System | Sub-System | Valve Tag | Valve Class | Fluid Service | Table
0 | HV | 12 | 262 | HV 12262 | 80 | VBFD1S1 | 80VBFD1S1-Manual | Primary Crusher 2 Cooling Water Pump 1 Suction Manual Valve | 12-1606-COW-SS1-80 | 2000-F12-PID-PR-10003 | N/A | Stage 1 | Greenfield | COW | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 3 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10027 | Emerson | Manual Lever | 2000043108 TVF-M2WGNMM | F12.20 | F12.20.14 | HV12262 | VBF | Cooling Water | AS2129 Table D
0 | HV | 12 | 263 | HV 12263 | 50 | VB03S1 | 50VB03S1-Manual | Primary Crusher 2 Cooling Water Pump 1 Discharge Manual Valve | 12-1607-COW-SS3-50 | 2000-F12-PID-PR-10003 | N/A | Stage 1 | Greenfield | COW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 2 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | K-BALL F182 | 2000-PP007-B02-10009 | Emerson | Manual Lever | SWIT TOP TVF-M2WGNMM | F12.20 | F12.20.14 | HV12263 | VB0 | Cooling Water | AS2129 Table E
0 | HV | 12 | 264 | HV 12264 | 80 | VBFD1S1 | 80VBFD1S1-Manual | Primary Crusher 2 Cooling Water Pump 2 Suction Manual Valve | 12-1646-COW-SS1-80 | 2000-F12-PID-PR-10003 | N/A | Stage 1 | Greenfield | COW | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 3 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10027 | Emerson | Manual Lever | 2000043108 TVF-M2WGNMM | F12.20 | F12.20.14 | HV12264 | VBF | Cooling Water | AS2129 Table D
0 | HV | 12 | 265 | HV 12265 | 50 | VB03S1 | 50VB03S1-Manual | Primary Crusher 2 Cooling Water Pump 2 Discharge Manual Valve | 12-1647-COW-SS3-50 | 2000-F12-PID-PR-10003 | N/A | Stage 1 | Greenfield | COW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 2 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | K-BALL F182 | 2000-PP007-B02-10009 | Emerson | Manual Lever | SWIT TOP TVF-M2WGNMM | F12.20 | F12.20.14 | HV12265 | VB0 | Cooling Water | AS2129 Table E
0 | PRV | 12 | 390 | PRV 12390 | 32 | N/A |  | Primary Crushing 2 Air Receiver Pressure Release Valve |  | 2000-F24-PID-PR-10012 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME024 | N/A | Vendor Supply Set Pressure @ 1,000 kPag | NUOVA General Industrial | F32 OT |  |  |  |  | F12.10 | F12.10.05 | PRV12390 | N/A | #N/A | #N/A
0 | SV | 12 | 220 | SV 12220 | 25 | SV | 25SV-Solenoid-FC | Primary Crusher 2 Discharge Chamber Spray Water | 12-0003-BW-SS3-25 | 2000-F12-PID-PR-10001 | N/A | Stage 1 | Greenfield | BW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F12.10 | F12.10.19 | SV12220 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 12 | 550 | SV 12550 | 25 | SV | 25SV-Solenoid-FC | Stockpile Feed Conveyor Tail End Spray Water | 12-0004-BW-SS3-25 | 2000-F12-PID-PR-10002 | N/A | Stage 1 | Greenfield | BW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F12.10 | F12.10.19 | SV12550 | SV | Hypersaline Water | AS2129 Table E
1 | SV | 12 | 584 | SV 12584 | 25 | SV | 25SV-Solenoid-FC | Stockpile Feed Conveyor Spillage Tray Spray Bar 1 | 12-2601-BW-SS3-25 | 2000-F12-PID-PR-10002 | N/A | Stage 1 | Greenfield | BW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F12.10 | F12.10.19 | SV12584 | SV | Hypersaline Water | AS2129 Table E
1 | SV | 12 | 585 | SV 12585 | 25 | SV | 25SV-Solenoid-FC | Stockpile Feed Conveyor Spillage Tray Spray Bar 2 | 12-2603-BW-SS3-25 | 2000-F12-PID-PR-10002 | N/A | Stage 1 | Greenfield | BW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F12.10 | F12.10.19
1 | SV | 12 | 586 | SV 12586 | 25 | SV | 25SV-Solenoid-FC | Stockpile Feed Conveyor Spillage Tray Spray Bar 3 | 12-2605-BW-SS3-25 | 2000-F12-PID-PR-10002 | N/A | Stage 1 | Greenfield | BW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F12.10 | F12.10.19
1 | SV | 12 | 587 | SV 12587 | 25 | SV | 25SV-Solenoid-FC | Stockpile Feed Conveyor Spillage Tray Spray Bar 4 | 12-2607-BW-SS3-25 | 2000-F12-PID-PR-10002 | N/A | Stage 1 | Greenfield | BW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F12.10 | F12.10.19
1 | SV | 12 | 588 | SV 12588 | 25 | SV | 25SV-Solenoid-FC | Stockpile Feed Conveyor Spillage Tray Spray Bar 5 | 12-2609-BW-SS3-25 | 2000-F12-PID-PR-10002 | N/A | Stage 1 | Greenfield | BW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F12.10 | F12.10.19
1 | SV | 12 | 589 | SV 12589 | 25 | SV | 25SV-Solenoid-FC | Stockpile Feed Conveyor Spillage Tray Spray Bar 6 | 12-2611-BW-SS3-25 | 2000-F12-PID-PR-10002 | N/A | Stage 1 | Greenfield | BW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F12.10 | F12.10.19
1 | SV | 12 | 590 | SV 12590 | 25 | SV | 25SV-Solenoid-FC | Stockpile Feed Conveyor Spillage Tray Spray Bar 7 | 12-2613-BW-SS3-25 | 2000-F12-PID-PR-10002 | N/A | Stage 1 | Greenfield | BW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F12.10 | F12.10.19
1 | SV | 12 | 591 | SV 12591 | 25 | SV | 25SV-Solenoid-FC | Stockpile Feed Conveyor Spillage Tray Spray Bar 8 | 12-2615-BW-SS3-25 | 2000-F12-PID-PR-10002 | N/A | Stage 1 | Greenfield | BW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F12.10 | F12.10.19
0 | TCV | 12 | 127 | TCV 12127 | 50 | VTWD1C1 | 50VTWD1C1-Double Acting-Positioner-Pattern 3 | Primary Crusher 2 Oil Chiller Temperature Control Valve | 12-0159-COW-SS3-50-TI | 2000-F12-PID-PR-10001 | 2000-F24-PID-PR-10012 | Stage 1 | Greenfield | COW | SS3 | 50-TI | 0 | 20 | 400 | 400 | 50 | N/A | N/A | N/A | 1 | 1400 | 2 | Detail 1 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | No | Pattern 3 | N/A | N/A | PP007 | N/A | No pneumatic panel to be provided. Valve model KTM-MB11 T-Port with Flow Plan F - Pattern 3. |  |  | 2000-PP007-B02-10127 |  |  |  | F12.20 | F12.20.14 | TCV12127 | VTW | Cooling Water | AS2129 Table E
0 | XV | 12 | 5 | XV 12005 | 80 | VBFE1S1 | 80VBFE1S1-Double Acting-Solenoid on Valve | ROM Bin Spray Water | 12-0002-PSW-SS1-80 | 2000-F12-PID-PR-10001 | 2000-F24-PID-PR-10012 | Stage 1 | Greenfield | PSW | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 3 | Detail 7 | FC | Double Acting | Single Acting | SV12005 | No | Position Switches | Solenoid on Valve | Solenoid on Valve | N/A | PP007 | N/A | Solenoids to be installed on Valve | Emerson | GRW | 2000-PP007-B02-10113 | Emerson | KEYSTONE F89-004 | 2000043108 TVF-M2WGNMM | F12.10 | F12.10.34 | XV12005 | VBF | Process Scheme Water | AS2129 Table D
0 | XV | 12 | 6 | XV 12006 | 80 | VBFD1S1 | 80VBFD1S1-Double Acting-Solenoid on Valve | ROM Apron Feeder Spray Water | 12-1082-BW-SS1-80 | 2000-F12-PID-PR-10001 | 2000-F24-PID-PR-10012 | Stage 1 | Greenfield | BW | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 7 | FC | Double Acting | Single Acting |  | No | Position Switches | Solenoid on Valve | Solenoid on Valve | N/A | PP007 | N/A | Solenoids to be installed on Valve | Emerson | GRW | 2000-PP007-B02-10154 | Emerson | KEYSTONE F89-004 | 2000043108 TVF-M2WGNMM | F12.10 | F12.10.19 | XV12006 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 12 | 259 | XV 12259 | 50 | VB03S1 | 50VB03S1-Double Acting-Solenoid on Valve | Primary Crusher 2 Cooling Water Tank Scheme Water Inlet Valve | 12-0046-PSW-MSG3-50 | 2000-F12-PID-PR-10003 | 2000-F24-PID-PR-10012 | Stage 1 | Greenfield | PSW | MSG3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV12259 | No | Position Switches | Solenoid on Valve | Solenoid on Valve | N/A | PP007 | N/A | Solenoids to be installed on Valve | Emerson | K-BALL F182 | 2000-PP007-B02-10107 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F12.10 | F12.10.34 | XV12259 | VB0 | Process Scheme Water | AS2129 Table E
0 | XV | 12 | 551 | XV 12551 | 80 | VBFE1S1 | 80VBFE1S1-Double Acting-Solenoid on Valve | Stockpile Feed Conveyor Head End Spray Water | 12-0005-BW-SS2-80 | 2000-F12-PID-PR-10002 | 2000-F24-PID-PR-10012 | Stage 1 | Greenfield | BW | SS2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 7 | FC | Double Acting | Single Acting | SV12551 | No | Position Switches | Solenoid on Valve | Solenoid on Valve | N/A | PP007 | N/A | Solenoids to be installed on Valve | Emerson | GRW | 2000-PP007-B02-10113 | Emerson | KEYSTONE F89-004 | 2000043108 TVF-M2WGNMM | F12.10 | F12.10.19 | XV12551 | VBF | Hypersaline Water | AS2129 Table E
0 | FCV | 13 | 71 | FCV 13071 | 150 | VBFE1S1 | 150VBFE1S1-Double Acting-Positioner | SAG Mill Discharge Screen Process Water Flow Control Valve | 13-0018-PW-SS2-200 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | PW | SS2 | 200 | 160 | 240 | 540 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 6 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F13-CP-409 | 2000-PP007-B02-10308 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10060 | Emerson | KEYSTONE F89-014 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.01 | FCV13071 | VBF | Hypersaline Water | AS2129 Table E
0 | FCV | 13 | 121 | FCV 13121 | 300 | VBFD1S1 | 300VBFD1S1-Double Acting-Positioner | SAG Mill Feed Box Process Water | 13-0032-PW-SS1-300 | 2000-F13-PID-PR-10003 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | PW | SS1 | 300 | 440 | 660 | 165 | VTA | VTA | N/A | N/A | N/A | 1.07 | 700 | 12 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F13-CP-407 | 2000-PP007-B02-10306 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10078 | Emerson | KEYSTONE F89-085 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.07 | FCV13121 | VBF | Hypersaline Water | AS2129 Table D
0 | FCV | 13 | 123 | FCV 13123 | 150 | VBFE1S1 | 150VBFE1S1-Double Acting-Positioner | SAG Mill Trommel Spray Water Flow Control Valve | 13-0092-PW-SS2-200 | 2000-F13-PID-PR-10003 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | PW | SS2 | 200 | 120 | 180 | 540 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 6 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F13-CP-409 | 2000-PP007-B02-10308 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10060 | Emerson | KEYSTONE F89-014 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.01 | FCV13123 | VBF | Hypersaline Water | AS2129 Table E
0 | FCV | 13 | 125 | FCV 13125 | 80 | VBFD1L1 | 80VBFD1L1-Double Acting-Positioner | SAG Mill VSD Cooling System Cooling Water Flow Control Valve | 13-0096-COW-MSG1-100-TI | 2000-F13-PID-PR-10009 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | COW | MSG1 | 100-TI | 64 | 96 | 250 | VTA | VTA | N/A | N/A | N/A | 1 | 700 | 3 | Detail 1 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F13-CP-405 | 2000-PP007-B02-10304 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10152 | Emerson | KEYSTONE F89-004 | SMC IP8100 031 J (4-20mA) | F13.10 | F13.10.55 | FCV13125 | VBF | Cooling Water | AS2129 Table D
0 | FCV | 13 | 126 | FCV 13126 | 80 | VBFD1L1 | 80VBFD1L1-Double Acting-Positioner | Ball Mill VSD Cooling System Cooling Water Flow Control Valve | 13-0097-COW-MSG1-100-TI | 2000-F13-PID-PR-10009 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | COW | MSG1 | 100-TI | 64 | 96 | 250 | VTA | VTA | N/A | N/A | N/A | 1 | 700 | 3 | Detail 1 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F13-CP-405 | 2000-PP007-B02-10304 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10152 | Emerson | KEYSTONE F89-004 | SMC IP8100 031 J (4-20mA) | F13.10 | F13.10.55 | FCV13126 | VBF | Cooling Water | AS2129 Table D
0 | FCV | 13 | 127 | FCV 13127 | 50 | VBD1C1 | 50VBD1C1-Double Acting-Positioner | Cyclone Feed Pump VSD Cooling System Cooling Water Flow Control Valve | 13-0366-COW-MSG1-80-TI | 2000-F13-PID-PR-10009 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | COW | MSG1 | 80-TI | 40 | 60 | 250 | VTA | VTA | N/A | N/A | N/A | 1 | 700 | 2 | Detail 1 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F13-CP-405 | 2000-PP007-B02-10304 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10111 | Emerson | KEYSTONE F89-004 | Positioner SMC IP8100 031 J X318 | F13.10 | F13.10.55 | FCV13127 | VBD | Cooling Water | AS2129 Table D
0 | FCV | 13 | 141 | FCV 13141 | 250 | VBFD1S1 | 250VBFD1S1-Double Acting-Positioner | Ball Mill Feed Chute Process Water | 13-0051-PW-SS1-300 | 2000-F13-PID-PR-10004 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | PW | SS1 | 300 | 120 | 600 | 165 | VTA | VTA | N/A | N/A | N/A | 1.07 | 700 | 10 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F13-CP-407 | 2000-PP007-B02-10306 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10072 | Emerson | KEYSTONE F89-051 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.07 | FCV13141 | VBF | Hypersaline Water | AS2129 Table D
0 | FCV | 13 | 143 | FCV 13143 | 150 | VBFE1S1 | 150VBFE1S1-Double Acting-Positioner | Ball Mill Trommel Spray Water Valve | 13-0048-PW-SS2-200 | 2000-F13-PID-PR-10004 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | PW | SS2 | 200 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 6 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F13-CP-409 | 2000-PP007-B02-10308 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10060 | Emerson | KEYSTONE F89-014 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.01 | FCV13143 | VBF | Hypersaline Water | AS2129 Table E
0 | FCV | 13 | 075A | FCV 13075A | 300 | VBD1S4 | 300VBD1S4-Double Acting-Positioner | Primary Cyclone Feed Hopper Process Water 1 | 13-0021-PW-SS1-600 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | PW | SS1 | 600 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 12 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F13-CP-403 | 2000-PP007-B02-10302 | PP039 | PP007 | [7 empty] | F24.20 | F24.20.07 | FCV13075A | VBD | Hypersaline Water | AS2129 Table D
0 | FCV | 13 | 075B | FCV 13075B | 300 | VBD1S4 | 300VBD1S4-Double Acting-Positioner | Primary Cyclone Feed Hopper Process Water 2 | 13-0022-PW-SS1-450 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | PW | SS1 | 450 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 12 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F13-CP-403 | 2000-PP007-B02-10302 | PP039 | PP007 | [7 empty] | F24.20 | F24.20.07 | FCV13075B | VBD | Hypersaline Water | AS2129 Table D
0 | HV | 13 | 422 | HV 13422 | 300 | VBFD1L1 | 300VBFD1L1-Manual | Cooling Water Mill Pump 1 Suction Manual Valve | 13-0106-COW-MSG1-300-TI | 2000-F13-PID-PR-10012 | N/A | Stage 1 | Greenfield | COW | MSG1 | 300-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 12 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10077 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.58 | HV13422 | VBF | Cooling Water | AS2129 Table D
0 | HV | 13 | 423 | HV 13423 | 250 | VBFD1L1 | 250VBFD1L1-Manual | Cooling Water Mill Pump 1 Discharge Manual Valve | 13-1381-COW-MSG1-250-TI | 2000-F13-PID-PR-10012 | N/A | Stage 1 | Greenfield | COW | MSG1 | 250-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 10 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10071 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.58 | HV13423 | VBF | Cooling Water | AS2129 Table D
0 | HV | 13 | 424 | HV 13424 | 300 | VBFD1L1 | 300VBFD1L1-Manual | Cooling Water Mill Pump 2 Suction Manual Valve | 13-0108-COW-MSG1-300-TI | 2000-F13-PID-PR-10012 | N/A | Stage 1 | Greenfield | COW | MSG1 | 300-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 12 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10077 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.58 | HV13424 | VBF | Cooling Water | AS2129 Table D
0 | HV | 13 | 425 | HV 13425 | 250 | VBFD1L1 | 250VBFD1L1-Manual | Cooling Water Mill Pump 2 Discharge Manual Valve | 13-0109-COW-MSG1-250-TI | 2000-F13-PID-PR-10012 | N/A | Stage 1 | Greenfield | COW | MSG1 | 250-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 10 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10071 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.58 | HV13425 | VBF | Cooling Water | AS2129 Table D
0 | HV | 13 | 431 | HV 13431 | 300 | VBFD1L1 | 300VBFD1L1-Manual | Chiller Recirculating Water Pump 1 Suction Manual Valve | 13-0118-PSW-MSG1-300-TI | 2000-F13-PID-PR-10012 | N/A | Stage 1 | Greenfield | PSW | MSG1 | 300-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 12 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10077 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.56 | HV13431 | VBF | Process Scheme Water | AS2129 Table D
0 | HV | 13 | 432 | HV 13432 | 250 | VBFD1L1 | 250VBFD1L1-Manual | Chiller Recirculating Water Pump 1 Discharge Manual Valve | 13-0119-PSW-MSG1-250-TI | 2000-F13-PID-PR-10012 | N/A | Stage 1 | Greenfield | PSW | MSG1 | 250-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 10 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10071 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.57 | HV13432 | VBF | Process Scheme Water | AS2129 Table D
0 | HV | 13 | 433 | HV 13433 | 300 | VBFD1L1 | 300VBFD1L1-Manual | Chiller Recirculating Water Pump 2 Suction Manual Valve | 13-0120-PSW-MSG1-300-TI | 2000-F13-PID-PR-10012 | N/A | Stage 1 | Greenfield | PSW | MSG1 | 300-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 12 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10077 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.56 | HV13433 | VBF | Process Scheme Water | AS2129 Table D
0 | HV | 13 | 434 | HV 13434 | 250 | VBFD1L1 | 250VBFD1L1-Manual | Chiller Recirculating Water Pump 2 Discharge Manual Valve | 13-0121-PSW-MSG1-250-TI | 2000-F13-PID-PR-10012 | N/A | Stage 1 | Greenfield | PSW | MSG1 | 250-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 10 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10071 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.57 | HV13434 | VBF | Process Scheme Water | AS2129 Table D
0 | HV | 13 | 442 | HV 13442 | 150 | VBFD1L1 | 150VBFD1L1-Manual | Chiller 1 Discharge Manual Valve | 13-0128-COW-MSG1-150-TI | 2000-F13-PID-PR-10012 | N/A | Stage 1 | Greenfield | COW | MSG1 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 6 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10054 | Emerson | Manual Lever | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.57 | HV13442 | VBF | Cooling Water | AS2129 Table D
0 | HV | 13 | 444 | HV 13444 | 150 | VBFD1L1 | 150VBFD1L1-Manual | Chiller 2 Discharge Manual Valve | 13-0129-COW-MSG1-150-TI | 2000-F13-PID-PR-10012 | N/A | Stage 1 | Greenfield | COW | MSG1 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 6 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10054 | Emerson | Manual Lever | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.57 | HV13444 | VBF | Cooling Water | AS2129 Table D
0 | HV | 13 | 446 | HV 13446 | 150 | VBFD1L1 | 150VBFD1L1-Manual | Chiller 3 Discharge Manual Valve | 13-0157-COW-MSG1-150-TI | 2000-F13-PID-PR-10012 | N/A | Stage 1 | Greenfield | COW | MSG1 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 6 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10054 | Emerson | Manual Lever | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.57 | HV13446 | VBF | Cooling Water | AS2129 Table D
0 | HV | 13 | 448 | HV 13448 | 150 | VBFD1L1 | 150VBFD1L1-Manual | Chiller 4 Discharge Manual Valve | 13-0127-COW-MSG1-250-TI | 2000-F13-PID-PR-10012 | N/A | Stage 1 | Greenfield | COW | MSG1 | 250-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 6 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRW | 2000-PP007-B02-10054 | Emerson | Manual Lever | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.57 | HV13448 | VBF | Cooling Water | AS2129 Table D
0 | PCV | 13 | 186 | PCV 13186 | 25 | PCV | 25PCV-N/A-Water | Recycle Crusher C Scheme Water Pressure Control Valve | 13-1435-PSW-SS3-25 | 2000-F13-PID-PR-10006 | N/A | Stage 1 | Greenfield | PSW | SS3 | 25 | 0 | 50 | 200 | 200 | 100 | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Water | N/A | N/A | PP007 | N/A | Set Pressure @ 100 kPag | Calorex Pty Ltd | Roma Fig. 514 | 2000-PP007-B02-10402 | N/A | N/A | N/A | F24.70 | F24.70.01 | PCV13186 | PCV | Process Scheme Water | AS2129 Table E
0 | PCV | 13 | 293 | PCV 13293 | 25 | PCV | 25PCV-N/A-Water | Recycle Crusher D Scheme Water Pressure Control Valve | 13-0770-PSW-SS3-25 | 2000-F13-PID-PR-10006 | N/A | Stage 1 | Greenfield | PSW | SS3 | 25 | 0 | 50 | 200 | 200 | 100 | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Water | N/A | N/A | PP007 | N/A | Set Pressure @ 100 kPag | Calorex Pty Ltd | Roma Fig. 514 | 2000-PP007-B02-10402 | N/A | N/A | N/A | F24.70 | F24.70.01 | PCV13293 | PCV | Process Scheme Water | AS2129 Table E
0 | PRV | 13 | 235 | PRV 13235 |  | N/A |  | Vendor Package Lube Oil Pressure Relief Valves |  | 2000-F13-PID-PR-10006 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME001.6 | N/A | Vendor Supply | [6 empty] | F13.40 | F13.40.15 | PRV13235 | N/A | #N/A | #N/A
0 | PRV | 13 | 285 | PRV 13285 |  | N/A |  | Vendor Package Lube Oil Pressure Relief Valves |  | 2000-F13-PID-PR-10006 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME001.6 | N/A | Vendor Supply | [6 empty] | F13.40 | F13.40.16 | PRV13285 | N/A | #N/A | #N/A
0 | PRV | 13 | 450 | PRV 13450 | 32 | N/A |  | Mill Air Receiver Pressure Release Valve |  | 2000-F24-PID-PR-10011 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME024 | N/A | Vendor Supply Set Pressure @ 1000 kPag | NUOVA General Industrial | F32 OT |  |  |  |  | F13.10 | F13.10.74 | PRV13450 | N/A | #N/A | #N/A
0 | PRV | 13 | 452 | PRV 13452 | 32 | N/A |  | Classificatoin Air Receiver Pressure Release Valve |  | 2000-F24-PID-PR-10025 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME024 | N/A | Vendor Supply Set Pressure @ 1000 kPag | NUOVA General Industrial | F32 OT |  |  |  |  | F13.10 | F13.10.75 | PRV13452 | N/A | #N/A | #N/A
0 | PRV | 13 | 454 | PRV 13454 | 32 | N/A |  | Recycle Crushing/COS Vault Air Receiver Pressure Release Valve |  | 2000-F24-PID-PR-10012 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME024 | N/A | Vendor Supply Set Pressure @ 1000 kPag | NUOVA General Industrial | F32 OT |  |  |  |  | F13.10 | F13.10.42 | PRV13454 | N/A | #N/A | #N/A
0 | SV | 13 | 61 | SV 13061 | 25 | SV | 25SV-Solenoid-FC | SAG Mill Feed Conveyor Spray Water 1 | 13-0012-BW-SS3-25 | 2000-F13-PID-PR-10001 | N/A | Stage 1 | Greenfield | BW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F24.40 | F24.40.04 | SV13061 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 13 | 62 | SV 13062 | 25 | SV | 25SV-Solenoid-FC | SAG Mill Feed Conveyor Spray Water 2 | 13-0013-BW-SS3-25 | 2000-F13-PID-PR-10001 | N/A | Stage 1 | Greenfield | BW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F24.40 | F24.40.04 | SV13062 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 13 | 63 | SV 13063 | 25 | SV | 25SV-Solenoid-FC | SAG Mill Feed Conveyor Spray Water 3 | 13-0014-BW-SS3-25 | 2000-F13-PID-PR-10001 | N/A | Stage 1 | Greenfield | BW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F24.40 | F24.40.04 | SV13063 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 13 | 185 | SV 13185 | 25 | SV | 25SV-Solenoid-FO | Recycle Crusher C Scheme Water Solenoid Valve | 13-1435-PSW-SS3-25 | 2000-F13-PID-PR-10006 | N/A | Stage 1 | Greenfield | PSW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F24.70 | F24.70.01 | SV13185 | SV | Process Scheme Water | AS2129 Table E
0 | SV | 13 | 292 | SV 13292 | 25 | SV | 25SV-Solenoid-FO | Recycle Crusher C Scheme Water Solenoid Valve | 13-0770-PSW-SS3-25 | 2000-F13-PID-PR-10006 | N/A | Stage 1 | Greenfield | PSW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F24.70 | F24.70.01 | SV13292 | SV | Process Scheme Water | AS2129 Table E
0 | SV | 13 | 344 | SV 13344 | 25 | SV | 25SV-Solenoid-FC | Recycle Crusher Discharge Conveyor Raw Water Solenoid Valve 1 | 13-2046-BW-SS3-50 | 2000-F13-PID-PR-10006 | N/A | Stage 1 | Greenfield | BW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F24.40 | F24.40.04 | SV13344 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 13 | 345 | SV 13345 | 25 | SV | 25SV-Solenoid-FC | Recycle Crusher Discharge Conveyor Raw Water Solenoid Valve 2 | 13-2047-BW-SS3-50 | 2000-F13-PID-PR-10006 | N/A | Stage 1 | Greenfield | BW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F24.40 | F24.40.04 | SV13345 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 13 | 464 | SV 13464 | 25 | SV | 25SV-Solenoid-FO | TRASH DEWATERING SCREEN UNDERFLOW PUMP GLAND WATER | 13-0821-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F13.50 | F13.50.11 | SV13464 | SV | Hypersaline Water | AS2129 Table E
0 | TCV | 13 | 129 | TCV 13129 | 80 | VTWD1C1 | 80VTWD1C1-Double Acting-Positioner-Pattern 3 | Cyclone Feed Pump Motor Cooling Water Temperature Control Valve | 13-0203-COW-MSG1-80-TI | 2000-F13-PID-PR-10009 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | COW | MSG1 | 80-TI | 40 | 60 | 250 | VTA | VTA | N/A | N/A | N/A | 1 | 700 | 3 | Detail 1 | FL | Double Acting | Manual Isolation | Manual Isolation | Yes | No | Pattern 3 | F13-CP-404 | 2000-PP007-B02-10303 | PP007 | PP007 | No pneumatic panel to be provided. Valve model KTM-MB11 T-Port with Flow Plan F - Pattern 3. | Emerson | KTM MB11 T Port | 2000-PP007-B02-10035 | Emerson | KTM AGN13 | SMC IP8100-031-J Included | F13.10 | F13.10.55 | TCV13129 | VTW | Cooling Water | AS2129 Table D
0 | TCV | 13 | 410 | TCV 13410 | 100 | VTWD1C1 | 100VTWD1C1-Double Acting-Positioner-Pattern 2 | SAG Mill Motor 1 Cooling Water Temperature Control Valve | 13-0112-COW-MSG1-100-TI | 2000-F13-PID-PR-10010 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | COW | MSG1 | 100-TI | 64 | 96 | 250 | VTA | VTA | N/A | N/A | N/A | 1 | 700 | 4 | Detail 1 | FL | Double Acting | Manual Isolation | Manual Isolation | Yes | No | Pattern 2 | F13-CP-409 | 2000-PP007-B02-10308 | PP007 | PP007 | No pneumatic panel to be provided. Valve model KTM-MB11 T-Port with Flow Plan G - Pattern 2. | Emerson | KTM MB11 T Port | 2000-PP007-B02-10048 | Emerson | KTM AWN13 | SMC IP8100-031-J Included | F13.10 | F13.10.55 | TCV13410 | VTW | Cooling Water | AS2129 Table D
0 | TCV | 13 | 412 | TCV 13412 | 100 | VTWD1C1 | 100VTWD1C1-Double Acting-Positioner-Pattern 3 | SAG Mill Motor 2 Cooling Water Temperature Control Valve | 13-0113-COW-MSG1-100-TI | 2000-F13-PID-PR-10010 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | COW | MSG1 | 100-TI | 64 | 96 | 250 | VTA | VTA | N/A | N/A | N/A | 1 | 700 | 4 | Detail 1 | FL | Double Acting | Manual Isolation | Manual Isolation | Yes | No | Pattern 3 | F13-CP-409 | 2000-PP007-B02-10308 | PP007 | PP007 | No pneumatic panel to be provided. Valve model KTM-MB11 T-Port with Flow Plan F - Pattern 3. | Emerson | KTM MB11 T Port | 2000-PP007-B02-10048 | Emerson | KTM AWN13 | SMC IP8100-031-J Included | F13.10 | F13.10.55 | TCV13412 | VTW | Cooling Water | AS2129 Table D
0 | TCV | 13 | 414 | TCV 13414 | 100 | VTWD1C1 | 100VTWD1C1-Double Acting-Positioner-Pattern 2 | Ball Mill Motor 1 Cooling Water Temperature Control Valve | 13-0114-COW-MSG1-100-TI | 2000-F13-PID-PR-10011 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | COW | MSG1 | 100-TI | 64 | 96 | 250 | VTA | VTA | N/A | N/A | N/A | 1 | 700 | 4 | Detail 1 | FL | Double Acting | Manual Isolation | Manual Isolation | Yes | No | Pattern 2 | F13-CP-409 | 2000-PP007-B02-10308 | PP007 | PP007 | No pneumatic panel to be provided. Valve model KTM-MB11 T-Port with Flow Plan G - Pattern 2. | Emerson | KTM MB11 T Port | 2000-PP007-B02-10048 | Emerson | KTM AWN13 | SMC IP8100-031-J Included | F13.10 | F13.10.55 | TCV13414 | VTW | Cooling Water | AS2129 Table D
0 | TCV | 13 | 416 | TCV 13416 | 100 | VTWD1C1 | 100VTWD1C1-Double Acting-Positioner-Pattern 2 | Ball Mill Motor 2 Cooling Water Temperature Control Valve | 13-0115-COW-MSG1-100-TI | 2000-F13-PID-PR-10011 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | COW | MSG1 | 100-TI | 64 | 96 | 250 | VTA | VTA | N/A | N/A | N/A | 1 | 700 | 4 | Detail 1 | FL | Double Acting | Manual Isolation | Manual Isolation | Yes | No | Pattern 2 | F13-CP-409 | 2000-PP007-B02-10308 | PP007 | PP007 | No pneumatic panel to be provided. Valve model KTM-MB11 T-Port with Flow Plan G - Pattern 2. | Emerson | KTM MB11 T Port | 2000-PP007-B02-10048 | Emerson | KTM AWN13 | SMC IP8100-031-J Included | F13.10 | F13.10.55 | TCV13416 | VTW | Cooling Water | AS2129 Table D
0 | XV | 13 | 69 | XV 13069 | 50 | VB03S1 | 50VB03S1-Electric 24VDC | Emergency Feed Bin Stockpile Spray Water Valve | 13-0323-BW-PE8-63 | 2000-F13-PID-PR-10001 | N/A | Stage 1 | Greenfield | BW | PE8 | 63 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 15 | Detail 15 | FC | Electric 24VDC | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Electric Actuator Keystone EPI 2 Model 063 (8 step) 24VDC energise to open, de-energise to close, no position feedback. | Emerson | K-BALL F182 | 2000-PP007-B02-10136 | Emerson | Keystone EPI 2 Model 063 (8 step) 24VDC energise to open, de-energise to close, no position feedback | None | F13.20 | F13.20.06 | XV13069 | VB0 | Hypersaline Water | AS2129 Table D PN10
0 | XV | 13 | 74 | XV 13074 | 150 | VKGE1C1 | 150VKGE1C1-Double Acting | Cyclone Feed Pump Suction Flushing Water | 13-1380-PW-SS2-150 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | PW | SS2 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 6 | Detail 4 | FC | Double Acting | Single Acting | SV13074 | No | Position Switches | - | F13-CP-404 | 2000-PP007-B02-10303 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10064 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F13.30 | F13.30.48 | XV13074 | VKG | Hypersaline Water | AS2129 Table E
0 | XV | 13 | 77 | XV 13077 | 300 | VKGD1L1 | 300VKGD1L1-Double Acting | Primary Cyclone Feed Hopper Drain | 13-0344-MS-PE10-315 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | MS | PE10 | 315 | N/A | N/A | N/A | N/A | N/A | 306 | 757 | 0.62 | 1.76 | 700 | 12 | Detail 4 | FO | Double Acting | Single Acting | SV13077 | No | Position Switches | - | F13-CP-404 | 2000-PP007-B02-10303 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10080 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F13.30 | F13.30.48 | XV13077 | VKG | Mill Slurry | AS2129 Table D PN10
0 | XV | 13 | 81 | XV 13081 | 300 | VKGD1C1 | 300VKGD1C1-Double Acting | Cyclone Feed Pump Suction Drain | 13-0343-MS-PE10-315 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | MS | PE10 | 315 | N/A | N/A | N/A | N/A | N/A | 306 | 757 | 0.62 | 1.76 | 700 | 12 | Detail 4 | FO | Double Acting | Single Acting | SV13081 | No | Position Switches | - | F13-CP-404 | 2000-PP007-B02-10303 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10079 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F13.30 | F13.30.48 | XV13081 | VKG | Mill Slurry | AS2129 Table D PN10
0 | XV | 13 | 82 | XV 13082 | 1200 | VKGD1L2 | 1200VKGD1L2-Double Acting | Cyclone Feed Pump Suction Valve | MECH-1200-CERAMIC | 2000-F13-PID-PR-10002 | N/A | Stage 1 | Greenfield | MS | CERAMIC | 1200 | N/A | N/A | N/A | N/A | N/A | 306 | 757 | 0.62 | 1.76 | 300 | 48 | Detail 5 | FL | Double Acting | Double Acting | SVO/SVC13082 | No | Position Switches | - | F13-HU-407 | 2000-PP007-B02-10202 | PP007 | PP007 | Hydraulically actuated valve | Emerson | Clarkson KGA+ | 2000-PP007-B02-10105 | Emerson | Hydraulic cylinder | SWI LMT PXM P+F NCB5-18GM40-N0 5-24VDC | F13.30 | F13.30.48 | XV13082 | VKG | Mill Slurry | AS2129 Table D
0 | XV | 13 | 83 | XV 13083 | 400 | VKGE1C1 | 400VKGE1C1-Double Acting | Cyclone Feed Pump Suction Process Water | 13-0055-PW-SS2-400 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | PW | SS2 | 400 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 16 | Detail 4 | FC | Double Acting | Single Acting | SV13083 | No | Position Switches | - | F13-CP-404 | 2000-PP007-B02-10303 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10090 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F13.30 | F13.30.48 | XV13083 | VKG | Hypersaline Water | AS2129 Table E
0 | XV | 13 | 84 | XV 13084 | 500 | VKGE1C1 | 500VKGE1C1-Double Acting | Cyclone Feed Pump Discharge Drain | 13-0893-MS-PE10-500 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | MS | PE10 | 500 | N/A | N/A | N/A | N/A | N/A | 306 | 757 | 0.62 | 1.76 | 700 | 20 | Detail 4 | FO | Double Acting | Single Acting | SV13084 | No | Position Switches | - | F13-CP-404 | 2000-PP007-B02-10303 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10120 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F13.30 | F13.30.48 | XV13084 | VKG | Mill Slurry | AS2129 Table D PN10
0 | XV | 13 | 88 | XV 13088 | 80 | VKGE1C1 | 80VKGE1C1-Double Acting | Gravity Cyclone 1 HP Process Water | 13-1604-PW-SS2-80 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | PW | SS2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 3 | Detail 4 | FC | Double Acting | Single Acting | SV13088 | No | Position Switches | - | F13-CP-412 | 2000-PP007-B02-10311 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10034 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F24.20 | F24.20.01 | XV13088 | VKG | Hypersaline Water | AS2129 Table E
0 | XV | 13 | 89 | XV 13089 | 80 | VKGE1C1 | 80VKGE1C1-Double Acting | Gravity Cyclone 2 HP Process Water | 13-1605-PW-SS2-80 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | PW | SS2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 3 | Detail 4 | FC | Double Acting | Single Acting | SV13089 | No | Position Switches | - | F13-CP-412 | 2000-PP007-B02-10311 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10034 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F24.20 | F24.20.01 | XV13089 | VKG | Hypersaline Water | AS2129 Table E
0 | XV | 13 | 94 | XV 13094 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13094 | No | Position Switches | - | F13CY401-CP02 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13094 | N/A | #N/A | #N/A
0 | XV | 13 | 95 | XV 13095 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13095 | No | Position Switches | - | F13CY401-CP02 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13095 | N/A | #N/A | #N/A
0 | XV | 13 | 96 | XV 13096 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13096 | No | Position Switches | - | F13CY401-CP02 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13096 | N/A | #N/A | #N/A
0 | XV | 13 | 97 | XV 13097 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13097 | No | Position Switches | - | F13CY401-CP02 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13097 | N/A | #N/A | #N/A
0 | XV | 13 | 98 | XV 13098 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13098 | No | Position Switches | - | F13CY401-CP02 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13098 | N/A | #N/A | #N/A
0 | XV | 13 | 99 | XV 13099 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13099 | No | Position Switches | - | F13CY401-CP02 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13099 | N/A | #N/A | #N/A
0 | XV | 13 | 100 | XV 13100 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13100 | No | Position Switches | - | F13CY401-CP02 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13100 | N/A | #N/A | #N/A
0 | XV | 13 | 101 | XV 13101 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13101 | No | Position Switches | - | F13CY401-CP02 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13101 | N/A | #N/A | #N/A
0 | XV | 13 | 102 | XV 13102 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13102 | No | Position Switches | - | F13CY401-CP02 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13102 | N/A | #N/A | #N/A
0 | XV | 13 | 103 | XV 13103 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13103 | No | Position Switches | - | F13CY401-CP03 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13103 | N/A | #N/A | #N/A
0 | XV | 13 | 104 | XV 13104 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13104 | No | Position Switches | - | F13CY401-CP03 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13104 | N/A | #N/A | #N/A
0 | XV | 13 | 105 | XV 13105 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13105 | No | Position Switches | - | F13CY401-CP03 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13105 | N/A | #N/A | #N/A
0 | XV | 13 | 106 | XV 13106 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13106 | No | Position Switches | - | F13CY401-CP03 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13106 | N/A | #N/A | #N/A
0 | XV | 13 | 107 | XV 13107 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13107 | No | Position Switches | - | F13CY401-CP03 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13107 | N/A | #N/A | #N/A
0 | XV | 13 | 108 | XV 13108 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves |  | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13108 | No | Position Switches | - | F13CY401-CP03 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13108 | N/A | #N/A | #N/A
0 | XV | 13 | 110 | XV 13110 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves | 13-0077-MS-RL3-400 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | MS | RL3 | 400 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13110 | No | Position Switches | - | F13-CP-412 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13110 | N/A | Mill Slurry | AS2129 Table D
0 | XV | 13 | 111 | XV 13111 |  | N/A |  | Vendor Package Actuated Cyclone Feed Valves | 13-0078-MS-RL3-400 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | MS | RL3 | 400 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13111 | No | Position Switches | - | F13-CP-412 | N/A | ME005A | ME005A | Vendor Supply | [6 empty] | F13.30 | F13.30.49 | XV13111 | N/A | Mill Slurry | AS2129 Table D
0 | XV | 13 | 114 | XV 13114 | 750 | VKGD1C1 | 750VKGD1C1-Double Acting | Cyclone Underflow Boil Box to Ball Mill Feed Box 1 Line 1 | 13-1213-MS-RL3-750 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | MS | RL3 | 750 | N/A | N/A | N/A | N/A | N/A | 300 | 850 | 0.784 | 2.1 | 700 | 30 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13114 | No | Position Switches | - | F13-CP-407 | 2000-PP007-B02-10306 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10103 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F13.30 | F13.30.49 | XV13114 | VKG | Mill Slurry | AS2129 Table D
0 | XV | 13 | 115 | XV 13115 | 750 | VKGD1C1 | 750VKGD1C1-Double Acting | Cyclone Underflow Boil Box to Ball Mill Feed Box 1 Line 2 | 13-1212-MS-RL3-750 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | MS | RL3 | 750 | N/A | N/A | N/A | N/A | N/A | 300 | 850 | 0.784 | 2.1 | 700 | 30 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13115 | No | Position Switches | - | F13-CP-407 | 2000-PP007-B02-10306 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10103 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F13.30 | F13.30.49 | XV13115 | VKG | Mill Slurry | AS2129 Table D
0 | XV | 13 | 116 | XV 13116 | 750 | VKGD1C1 | 750VKGD1C1-Double Acting | Cyclone Underflow Boil Box to Sag Mill Feed Box | 13-1211-MS-RL3-750 | 2000-F13-PID-PR-10002 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | MS | RL3 | 750 | N/A | N/A | N/A | N/A | N/A | 300 | 850 | 0.784 | 2.1 | 700 | 30 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13116 | No | Position Switches | - | F13-CP-407 | 2000-PP007-B02-10306 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10103 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F13.30 | F13.30.49 | XV13116 | VKG | Mill Slurry | AS2129 Table D
0 | XV | 13 | 173 | XV 13173 |  | N/A |  | Flotation Feed Sampler Upstream Flush Valve | MECH | 2000-F13-PID-PR-10008 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FC | Double Acting | Double Acting | SVO/SVC13173 | No | Position Switches | - | F16SA401-CP | N/A | ME074 | ME074 | Vendor Supply | [6 empty] | F16.20 | F16.20.19 | XV13173 | N/A | #N/A | #N/A
0 | XV | 13 | 174 | XV 13174 |  | N/A |  | Flotation Feed Sampler Downstream Flush Valve | MECH | 2000-F13-PID-PR-10008 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FC | Double Acting | Double Acting | SVO/SVC13174 | No | Position Switches | - | F16SA401-CP | N/A | ME074 | ME074 | Vendor Supply | [6 empty] | F16.20 | F16.20.19 | XV13174 | N/A | #N/A | #N/A
0 | XV | 13 | 175 | XV 13175 |  | N/A |  | Flotation Feed Sampler Cutter | MECH | 2000-F13-PID-PR-10008 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13175 | No | Position Switches | - | F16SA401-CP | N/A | ME074 | ME074 | Vendor Supply | [6 empty] | F16.20 | F16.20.19 | XV13175 | N/A | #N/A | #N/A
0 | XV | 13 | 220 | XV 13220 |  | N/A |  | Recycle Crusher Bypass Gate | MECH | 2000-F13-PID-PR-10006 | 2000-F24-PID-PR-10012 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13220 | No | Position Switches | - | XV13220_CP | N/A | ME090 | ME090 | Actuated Gate | [6 empty] | F13.40 | F13.40.10 | XV13220 | N/A | #N/A | #N/A
0 | XV | 13 | 360 | XV 13360 | 200 | VBFE1S1 | 200VBFE1S1-Double Acting | Trash Screen Final Collection Box Process Water | 13-0382-PW-SS2-250 | 2000-F13-PID-PR-10008 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS2 | 250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 8 | Detail 7 | FC | Double Acting | Single Acting | SV13360 | No | Position Switches | - | F13-CP-408 | 2000-PP007-B02-10307 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10068 | Emerson | KEYSTONE F89-032 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.01 | XV13360 | VBF | Hypersaline Water | AS2129 Table E
0 | XV | 13 | 361 | XV 13361 | 100 | VBFE1S1 | 100VBFE1S1-Double Acting | Trash Screen 1 Spray Water | 13-0065-PW-SS2-100 | 2000-F13-PID-PR-10007 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS2 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 4 | Detail 7 | FC | Double Acting | Single Acting | SV13361 | No | Position Switches | - | F13-CP-402 | 2000-PP007-B02-10301 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10044 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.01 | XV13361 | VBF | Hypersaline Water | AS2129 Table E
0 | XV | 13 | 371 | XV 13371 | 100 | VBFE1S1 | 100VBFE1S1-Double Acting | Trash Screen 2 Spray Water | 13-0069-PW-SS2-100 | 2000-F13-PID-PR-10007 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS2 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 4 | Detail 7 | FC | Double Acting | Single Acting | SV13371 | No | Position Switches | - | F13-CP-402 | 2000-PP007-B02-10301 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10044 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.01 | XV13371 | VBF | Hypersaline Water | AS2129 Table E
0 | XV | 13 | 374 | XV 13374 | 80 | VBFE1S1 | 80VBFE1S1-Double Acting | Trash Dewatering Screen Spray Water | 13-1277-PW-SS2-80 | 2000-F13-PID-PR-10007 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 3 | Detail 7 | FC | Double Acting | Single Acting | SV13374 | No | Position Switches | - | F13-CP-406 | 2000-PP007-B02-10305 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10032 | Emerson | KEYSTONE F89-004 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.01 | XV13374 | VBF | Hypersaline Water | AS2129 Table E
0 | XV | 13 | 382 | XV 13382 | 250 | VKGD1L1 | 250VKGD1L1-Double Acting | Trash Dewatering Screen Underflow Pump Suction Valve | 250-MECH-RL1 | 2000-F13-PID-PR-10007 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | MECH | 250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 10 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13382 | No | Position Switches | - | F16-CP-401 | 2000-PP007-B02-10314 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10075 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F13.50 | F13.50.10 | XV13382 | VKG | Hypersaline Water | 0
0 | XV | 13 | 383 | XV 13383 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Trash Dewatering Screen Underflow Pump Suction Drain Valve | 250-MECH-RL1 | 2000-F13-PID-PR-10007 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | MECH | 250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13383 | No | Position Switches | - | F16-CP-401 | 2000-PP007-B02-10314 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F13.50 | F13.50.10 | XV13383 | VKG | Hypersaline Water | 0
0 | XV | 13 | 384 | XV 13384 | 500 | VKGD1L1 | 500VKGD1L1-Double Acting | Trash Dewatering Screen Bypass | 13-1303-PW-PE8-500 | 2000-F13-PID-PR-10007 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | PE8 | 500 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 20 | Detail 4 | FO | Double Acting | Single Acting | SV13384 | No | Position Switches | - | F13-CP-406 | 2000-PP007-B02-10305 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10098 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F13.50 | F13.50.10 | XV13384 | VKG | Hypersaline Water | AS2129 Table D PN10
0 | XV | 13 | 386 | XV 13386 |  | N/A |  | Trash Screen 1 Feed Gate | MECH | 2000-F13-PID-PR-10007 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | FS | MECH |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13386 | No | Position Switches | - | F13GA421-CP01 | N/A | ME093 | ME093 | Actuated Gate | [6 empty] | F13.50 | F13.50.04 | XV13386 | N/A | Flotation Slurry | 0
0 | XV | 13 | 387 | XV 13387 |  | N/A |  | Trash Screen 2 Feed Gate | MECH | 2000-F13-PID-PR-10007 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | FS | MECH |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13387 | No | Position Switches | - | F13GA421-CP01 | N/A | ME093 | ME093 | Actuated Gate | [6 empty] | F13.50 | F13.50.04 | XV13387 | N/A | Flotation Slurry | 0
0 | XV | 13 | 388 | XV 13388 |  | N/A |  | Trash Screen 3 Feed Gate | MECH | 2000-F13-PID-PR-10007 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | FS | MECH |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13388 | No | Position Switches | - | F13GA421-CP01 | N/A | ME093 | ME093 | Actuated Gate | [6 empty] | F13.50 | F13.50.04 | XV13388 | N/A | Flotation Slurry | 0
0 | XV | 13 | 389 | XV 13389 |  | N/A |  | Trash Screen 4 Feed Gate | MECH | 2000-F13-PID-PR-10007 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | FS | MECH |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC13389 | No | Position Switches | - | F13GA421-CP01 | N/A | ME093 | ME093 | Actuated Gate | [6 empty] | F13.50 | F13.50.04 | XV13389 | N/A | Flotation Slurry | 0
0 | XV | 13 | 391 | XV 13391 | 100 | VBFE1S1 | 100VBFE1S1-Double Acting | Trash Screen 4 Spray Water | 13-0170-PW-SS2-100 | 2000-F13-PID-PR-10008 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS2 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 4 | Detail 7 | FC | Double Acting | Single Acting | SV13391 | No | Position Switches | - | F13-CP-402 | 2000-PP007-B02-10301 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10044 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.01 | XV13391 | VBF | Hypersaline Water | AS2129 Table E
0 | XV | 13 | 401 | XV 13401 | 100 | VBFE1S1 | 100VBFE1S1-Double Acting | Trash Screen 3 Spray Water | 13-0073-PW-SS2-100 | 2000-F13-PID-PR-10008 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS2 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 4 | Detail 7 | FC | Double Acting | Single Acting | SV13401 | No | Position Switches | - | F13-CP-402 | 2000-PP007-B02-10301 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10044 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.01 | XV13401 | VBF | Hypersaline Water | AS2129 Table E
0 | XV | 13 | 418 | XV 13418 | 50 | VB03S1 | 50VB03S1-Double Acting | Cooling Water Tank 2 Valve | 13-0043-PSW-SS3-50 | 2000-F13-PID-PR-10012 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PSW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 2 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC13418 | No | Position Switches | - | F13-CP-411 | 2000-PP007-B02-10310 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10008 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F24.70 | F24.70.01 | XV13418 | VB0 | Process Scheme Water | AS2129 Table E
0 | XV | 13 | 419 | XV 13419 | 50 | VB03S1 | 50VB03S1-Double Acting | Chiller Tank Valve | 13-0105-PSW-SS3-50 | 2000-F13-PID-PR-10012 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PSW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 2 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC13419 | No | Position Switches | - | F13-CP-410 | 2000-PP007-B02-10309 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10008 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F24.70 | F24.70.01 | XV13419 | VB0 | Process Scheme Water | AS2129 Table E
0 | XV | 13 | 441 | XV 13441 | 150 | VBFD1L1 | 150VBFD1L1-Double Acting | Chiller 1 Feed Valve | 13-0156-PSW-MSG1-150-TI | 2000-F13-PID-PR-10012 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PSW | MSG1 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 6 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC13441 | No | Position Switches | - | F13-CP-410 | 2000-PP007-B02-10309 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10053 | Emerson | KEYSTONE F89-014 | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.55 | XV13441 | VBF | Process Scheme Water | AS2129 Table D
0 | XV | 13 | 443 | XV 13443 | 150 | VBFD1L1 | 150VBFD1L1-Double Acting | Chiller 2 Feed Valve | 13-0126-PSW-MSG1-150-TI | 2000-F13-PID-PR-10012 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PSW | MSG1 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 6 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC13443 | No | Position Switches | - | F13-CP-410 | 2000-PP007-B02-10309 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10053 | Emerson | KEYSTONE F89-014 | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.55 | XV13443 | VBF | Process Scheme Water | AS2129 Table D
0 | XV | 13 | 445 | XV 13445 | 150 | VBFD1L1 | 150VBFD1L1-Double Acting | Chiller 3 Feed Valve | 13-0125-PSW-MSG1-150-TI | 2000-F13-PID-PR-10012 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PSW | MSG1 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 6 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC13445 | No | Position Switches | - | F13-CP-410 | 2000-PP007-B02-10309 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10053 | Emerson | KEYSTONE F89-014 | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.55 | XV13445 | VBF | Process Scheme Water | AS2129 Table D
0 | XV | 13 | 447 | XV 13447 | 150 | VBFD1L1 | 150VBFD1L1-Double Acting | Chiller 4 Feed Valve | 13-0119-PSW-MSG1-250-TI | 2000-F13-PID-PR-10012 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PSW | MSG1 | 250-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 6 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC13447 | No | Position Switches | - | F13-CP-410 | 2000-PP007-B02-10309 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10053 | Emerson | KEYSTONE F89-014 | 2000043108 TVF-M2WGNMM | F13.10 | F13.10.55 | XV13447 | VBF | Process Scheme Water | AS2129 Table D
0 | XV | 13 | 460 | XV 13460 | 40 | VB03S1 | 40VB03S1-Spring Return | CYCLONE FEED PUMP GLAND WATER | 13-0357-GW-SS3-40 | 2000-F24-PID-PR-10004 | 2000-F24-PID-PR-10011 | Stage 1 | Greenfield | GW | SS3 | 40 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 8 | FO | Spring Return | Single Acting | SV13460 | No | Position Switches | - | F13-CP-404 | 2000-PP007-B02-10303 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10006 | Emerson | KEYSTONE F89-014 | SWIT TOP TVF-M2WGNMM | F13.30 | F13.30.47 | XV13460 | VB0 | Hypersaline Water | AS2129 Table E
0 | FCV | 14 | 1 | FCV 14001 | 150 | VBFE1S1 | 150VBFE1S1-Double Acting-Positioner | Gravity Screen 1 Feed Box Process Water | 14-0182-PW-SS2-200 | 2000-F14-PID-PR-10001 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | PW | SS2 | 200 | 130 | 400 | 320 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 6 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F14-CP-402 | 2000-PP007-B02-10313 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10060 | Emerson | KEYSTONE F89-014 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.01 | FCV14001 | VBF | Hypersaline Water | AS2129 Table E
0 | FCV | 14 | 2 | FCV 14002 | 150 | VBFE1S1 | 150VBFE1S1-Double Acting-Positioner | Gravity Screen 2 Feed Box Process Water | 14-0184-PW-SS2-200 | 2000-F14-PID-PR-10001 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | PW | SS2 | 200 | 130 | 400 | 320 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 6 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F14-CP-402 | 2000-PP007-B02-10313 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10060 | Emerson | KEYSTONE F89-014 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.01 | FCV14002 | VBF | Hypersaline Water | AS2129 Table E
0 | FCV | 14 | 33 | FCV 14033 | 100 | N/A |  | Gravity Concentrator 1 Fluidising Water Flow Control Valve | 14-0211-BW-SS1-150 | 2000-F14-PID-PR-10001 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | BW | SS1 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | Solenoid on Valve | Solenoid on Valve | N/A | ME015 | ME015 | Vendor Supply | [6 empty] | F14.20 | F14.20.03 | FCV14033 | N/A | Hypersaline Water | AS2129 Table D
0 | FCV | 14 | 43 | FCV 14043 | 100 | N/A |  | Gravity Concentrator 2 Fluidising Water Flow Control Valve | 14-0210-BW-SS1-150 | 2000-F14-PID-PR-10001 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | BW | SS1 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | Solenoid on Valve | Solenoid on Valve | N/A | ME015 | ME015 | Vendor Supply | [6 empty] | F14.20 | F14.20.06 | FCV14043 | N/A | Hypersaline Water | AS2129 Table D
0 | SV | 14 | 118 | SV 14118 | 25 | SV | 25SV-Solenoid-FO | INTENSIVE CYANIDE LEACH REACTOR TRANSFER PUMP GLAND WATER | 14-0240-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F14.20 | F14.20.07 | SV14118 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 14 | 125 | SV 14125 | 25 | SV | 25SV-Solenoid-FO | Leach Aid Screw Feeder Air Line Valve | N/A | 2000-ME053-E02-10001 | N/A | Stage 1 | Greenfield | IA | MSG3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AIR | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A | Valve to be retrofitted to the screw feeder F14-FS-420 inside package ME053 | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F14.20 | F14.20.07 | SV14125 | SV | Instrument Air | AS2129 Table E
0 | XV | 14 | 12 | XV 14012 | 100 | VBFE1S1 | 100VBFE1S1-Double Acting | Gravity Screen 1 Spray Water Flow Control Valve | 14-0188-PW-SS2-150 | 2000-F14-PID-PR-10001 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | PW | SS2 | 150 | 82 | 250 | 320 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 4 | Detail 7 | FC | Double Acting | Single Acting | SV14012 | No | Position Switches | - | F14-CP-402 | 2000-PP007-B02-10313 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10044 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.01 | XV14012 | VBF | Hypersaline Water | AS2129 Table E
0 | XV | 14 | 14 | XV 14014 | 100 | VBFE1S1 | 100VBFE1S1-Double Acting | Gravity Screen 2 Spray Water Flow Control Valve | 14-0192-PW-SS2-150 | 2000-F14-PID-PR-10001 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | PW | SS2 | 150 | 82 | 250 | 320 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 4 | Detail 7 | FC | Double Acting | Single Acting | SV14014 | No | Position Switches | - | F14-CP-402 | 2000-PP007-B02-10313 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10044 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.01 | XV14014 | VBF | Hypersaline Water | AS2129 Table E
0 | XV | 14 | 31 | XV 14031 | 400 | VKGD1C1 | 400VKGD1C1-Double Acting | Gravity Concentrator 1 Feed Valve | 14-1235-MS-RL3-400 | 2000-F14-PID-PR-10001 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | MS | RL3 | 400 | N/A | N/A | N/A | N/A | N/A | 300 | 850 | 0.6 | 1.72 | 700 | 16 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC14031 | No | Position Switches | - | F14-CP-401 | 2000-PP007-B02-10312 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10088 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F14.20 | F14.20.02 | XV14031 | VKG | Mill Slurry | AS2129 Table D
0 | XV | 14 | 41 | XV 14041 | 400 | VKGD1C1 | 400VKGD1C1-Double Acting | Gravity Concentrator 2 Feed Valve | 14-1239-MS-RL3-400 | 2000-F14-PID-PR-10001 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | MS | RL3 | 400 | N/A | N/A | N/A | N/A | N/A | 300 | 850 | 0.6 | 1.72 | 700 | 16 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC14041 | No | Position Switches | - | F14-CP-401 | 2000-PP007-B02-10312 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10088 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F14.20 | F14.20.05 | XV14041 | VKG | Mill Slurry | AS2129 Table D
0 | XV | 14 | 51 | XV 14051 | 400 | VKGD1C1 | 400VKGD1C1-Double Acting | Gravity Concentrator 1 Feed Bypass to Tails Launder Valve | 14-1234-MS-RL3-400 | 2000-F14-PID-PR-10001 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | MS | RL3 | 400 | N/A | N/A | N/A | N/A | N/A | 300 | 850 | 0.6 | 1.72 | 700 | 16 | Detail 4 | FO | Double Acting | Single Acting | SV14051 | No | Position Switches | - | F14-CP-401 | 2000-PP007-B02-10312 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10088 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F14.20 | F14.20.02 | XV14051 | VKG | Mill Slurry | AS2129 Table D
0 | XV | 14 | 52 | XV 14052 | 400 | VKGD1C1 | 400VKGD1C1-Double Acting | Gravity Concentrator 2 Feed Bypass to Tails Launder Valve | 14-1238-MS-RL3-400 | 2000-F14-PID-PR-10001 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | MS | RL3 | 400 | N/A | N/A | N/A | N/A | N/A | 300 | 850 | 0.6 | 1.72 | 700 | 16 | Detail 4 | FO | Double Acting | Single Acting | SV14052 | No | Position Switches | - | F14-CP-401 | 2000-PP007-B02-10312 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10088 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F14.20 | F14.20.05 | XV14052 | VKG | Mill Slurry | AS2129 Table D
0 | XV | 14 | 61 | XV 14061 | 100 | VBFE1S1 | 100VBFE1S1-Double Acting | Gravity Screen Oversize Chutes Process Water | 14-0041-PW-SS2-100 | 2000-F14-PID-PR-10001 | 2000-F24-PID-PR-10025 | Stage 1 | Greenfield | PW | SS2 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 4 | Detail 7 | FC | Double Acting | Single Acting | SV14061 | No | Position Switches | - | F14-CP-402 | 2000-PP007-B02-10313 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10044 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.01 | XV14061 | VBF | Hypersaline Water | AS2129 Table E
0 | FCV | 16 | 1 | FCV 16001 | 200 | VBFE1S1 | 200VBFE1S1-Double Acting-Positioner | Rougher Flotation Cell 1 Procees Water Flow Control Valve | 16-0248-PW-SS2-250 | 2000-F16-PID-PR-10001 | 2000-F24-PID-PR-10008 | Stage 1 | Greenfield | PW | SS2 | 250 | 104 | 700 | 390 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 8 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F16-CP-403 | 2000-PP007-B02-10315 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10114 | Emerson | KEYSTONE F89-032 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.01 | FCV16001 | VBF | Hypersaline Water | AS2129 Table E
0 | FCV | 16 | 11 | FCV 16011 |  | N/A |  | Rougher Flotation Cell 1 Low Pressure Air Flow Control Valve |  | 2000-F16-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.15 | FCV16011 | N/A | #N/A | #N/A
0 | FCV | 16 | 51 | FCV 16051 |  | N/A |  | Rougher Flotation Cell 2 Low Pressure Air Flow Control Valve |  | 2000-F16-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.15 | FCV16051 | N/A | #N/A | #N/A
0 | FCV | 16 | 61 | FCV 16061 |  | N/A |  | Rougher Flotation Cell 3 Low Pressure Air Flow Control Valve |  | 2000-F16-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.15 | FCV16061 | N/A | #N/A | #N/A
0 | FCV | 16 | 81 | FCV 16081 |  | N/A |  | Scavenger Flotation Cell 1 Low Pressure Air Flow Control Valve |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.15 | FCV16081 | N/A | #N/A | #N/A
0 | FCV | 16 | 91 | FCV 16091 |  | N/A |  | Scavenger Flotation Cell 2 Low Pressure Air Flow Control Valve |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.15 | FCV16091 | N/A | #N/A | #N/A
0 | FCV | 16 | 101 | FCV 16101 |  | N/A |  | Scavenger Flotation Cell 3 Low Pressure Air Flow Control Valve |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.15 | FCV16101 | N/A | #N/A | #N/A
0 | FCV | 16 | 111 | FCV 16111 |  | N/A |  | Scavenger Flotation Cell 4 Low Pressure Air Flow Control Valve |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.15 | FCV16111 | N/A | #N/A | #N/A
0 | LCV | 16 | 013A | LCV 16013A |  | N/A |  | Rougher Flotation Cell 2 Level Control Valve A |  | 2000-F16-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.01 | LCV16013A | N/A | #N/A | #N/A
0 | LCV | 16 | 013B | LCV 16013B |  | N/A |  | Rougher Flotation Cell 2 Level Control Valve B |  | 2000-F16-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.01 | LCV16013B | N/A | #N/A | #N/A
0 | LCV | 16 | 053A | LCV 16053A |  | N/A |  | Rougher Flotation Cell 3 Level Control Valve A |  | 2000-F16-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.01 | LCV16053A | N/A | #N/A | #N/A
0 | LCV | 16 | 053B | LCV 16053B |  | N/A |  | Rougher Flotation Cell 3 Level Control Valve B |  | 2000-F16-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.01 | LCV16053B | N/A | #N/A | #N/A
0 | LCV | 16 | 063A | LCV 16063A |  | N/A |  | Scavenger Flotation Cell 1 Level Control Valve A |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.02 | LCV16063A | N/A | #N/A | #N/A
0 | LCV | 16 | 063B | LCV 16063B |  | N/A |  | Scavenger Flotation Cell 1 Level Control Valve B |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.02 | LCV16063B | N/A | #N/A | #N/A
0 | LCV | 16 | 083A | LCV 16083A |  | N/A |  | Scavenger Flotation Cell 2 Level Control Valve A |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.02 | LCV16083A | N/A | #N/A | #N/A
0 | LCV | 16 | 083B | LCV 16083B |  | N/A |  | Scavenger Flotation Cell 2 Level Control Valve B |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.02 | LCV16083B | N/A | #N/A | #N/A
0 | LCV | 16 | 093A | LCV 16093A |  | N/A |  | Scavenger Flotation Cell 3 Level Control Valve A |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.02 | LCV16093A | N/A | #N/A | #N/A
0 | LCV | 16 | 093B | LCV 16093B |  | N/A |  | Scavenger Flotation Cell 3 Level Control Valve B |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.02 | LCV16093B | N/A | #N/A | #N/A
0 | LCV | 16 | 103A | LCV 16103A |  | N/A |  | Scavenger Flotation Cell 4 Level Control Valve A |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.02 | LCV16103A | N/A | #N/A | #N/A
0 | LCV | 16 | 103B | LCV 16103B |  | N/A |  | Scavenger Flotation Cell 4 Level Control Valve B |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.02 | LCV16103B | N/A | #N/A | #N/A
0 | LCV | 16 | 113A | LCV 16113A |  | N/A |  | Flotation Discharge Box Level Control Valve A |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.02 | LCV16113A | N/A | #N/A | #N/A
0 | LCV | 16 | 113B | LCV 16113B |  | N/A |  | Flotation Discharge Box Level Control Valve B |  | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME001.4 | ME001.4 | Vendor Supply | [6 empty] | F16.20 | F16.20.02 | LCV16113B | N/A | #N/A | #N/A
0 | PRV | 16 | 180 | PRV 16180 | 32 | N/A |  | Flotation/Thickener Air Receiver Pressure Release Valve |  | 2000-F24-PID-PR-10008 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME024 | N/A | Vendor Supply Set Pressure @ 1000 kPag | NUOVA General Industrial | F32 OT |  |  |  |  | F16.10 | F16.10.01 | PRV16180 | N/A | #N/A | #N/A
0 | SV | 16 | 155 | SV 16155 | 25 | SV | 25SV-Solenoid-FO | SAMPLE RETURN PUMP 1 GLAND WATER | 16-0820-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F16.20 | F16.20.10 | SV16155 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 16 | 165 | SV 16165 | 25 | SV | 25SV-Solenoid-FO | SAMPLE RETURN PUMP 2 GLAND WATER | 16-0819-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F16.20 | F16.20.10 | SV16165 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 16 | 357 | SV 16357 | 25 | SV | 25SV-Solenoid-FO | FLOATATION CELLS DRAIN PUMP GLAND WATER | 16-1557-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F16.20 | F16.20.14 | SV16357 | SV | Hypersaline Water | AS2129 Table E
0 | XV | 16 | 25 | XV 16025 |  | N/A |  | Rougher 1 Concentrate Cleaner Launder Gate |  | 2000-F16-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC16025 | No | Position Switches | - | F16GA425-CP01 | N/A | ME093 | ME093 | Actuated Gate | [6 empty] | F16.20 | F16.20.01 | XV16025 | N/A | #N/A | #N/A
0 | XV | 16 | 26 | XV 16026 |  | N/A |  | Rougher 1 Final Concentrate Launder Gate |  | 2000-F16-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC16026 | No | Position Switches | - | F16GA425-CP01 | N/A | ME093 | ME093 | Actuated Gate | [6 empty] | F16.20 | F16.20.01 | XV16026 | N/A | #N/A | #N/A
1 | XV | 16 | 80 | XV 16080 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Flotation Discharge Box Drain Valve | 16-0371-FS-PE10-160 | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | PE10 | 160 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.285 | 1.24 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC16080 | No | Position Switches | - | F17-CP-404 | 2000-PP007-B02-10319 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F16.20 | F16.20.02 | XV16080 | VKG | Flotation Slurry | AS2129 Table D PN10
0 | XV | 16 | 122 | XV 16122 | 300 | VKGD1L1 | 300VKGD1L1-Double Acting | Flotation Cells Drain Pump Isolation Valve | 16-1287-FS-RL1-300 | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.285 | 1.24 | 700 | 12 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC16122 | No | Position Switches | - | F17-CP-404 | 2000-PP007-B02-10319 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10080 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F16.20 | F16.20.14 | XV16122 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 16 | 123 | XV 16123 | 100 | VKGD1L1 | 100VKGD1L1-Double Acting | Flotation Cells Drain Pump Drain Valve | 16-1287-FS-RL1-300 | 2000-F16-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.285 | 1.24 | 700 | 4 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC16123 | No | Position Switches | - | F17-CP-404 | 2000-PP007-B02-10319 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10046 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F16.20 | F16.20.14 | XV16123 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 16 | 152 | XV 16152 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Sample Return Pump 1 Sunction Valve | 150-MECH-RL1 | 2000-F16-PID-PR-10005 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | FS | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.285 | 1.24 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC16152 | No | Position Switches | - | F16-CP-401 | 2000-PP007-B02-10314 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F16.20 | F16.20.10 | XV16152 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 16 | 153 | XV 16153 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | Sample Return Pump 1 Drain Valve | 150-MECH-RL1 | 2000-F16-PID-PR-10005 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | FS | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.285 | 1.24 | 700 | 2 | Detail 4 | FO | Double Acting | Single Acting | SV16153 | No | Position Switches | - | F16-CP-401 | 2000-PP007-B02-10314 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F16.20 | F16.20.10 | XV16153 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 16 | 162 | XV 16162 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Sample Return Pump 2 Sunction Valve | 150-MECH-RL1 | 2000-F16-PID-PR-10005 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | FS | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.285 | 1.24 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC16162 | No | Position Switches | - | F16-CP-401 | 2000-PP007-B02-10314 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F16.20 | F16.20.10
0 | XV | 16 | 163 | XV 16163 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | Sample Return Pump 2 Drain Valve | 150-MECH-RL1 | 2000-F16-PID-PR-10005 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | FS | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.285 | 1.24 | 700 | 2 | Detail 4 | FO | Double Acting | Single Acting | SV16163 | No | Position Switches | - | F16-CP-401 | 2000-PP007-B02-10314 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F16.20 | F16.20.10 | XV16163 | VKG | Flotation Slurry | AS2129 Table D
0 | FCV | 17 | 1 | FCV 17001 | 150 | VBFD1S1 | 150VBFD1S1-Double Acting-Positioner | Flotation Tailings Thickener Flocculant In-Line Mixer Process Water Flow Control Valve | 17-0361-PW-SS1-200 | 2000-F17-PID-PR-10001 | 2000-F24-PID-PR-10008 | Stage 1 | Greenfield | PW | SS1 | 200 | 77 | 400 | 600 | VTA | VTA | N/A | N/A | N/A | 1.07 | 700 | 6 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F17-CP-407 | 2000-PP007-B02-10322 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10057 | Emerson | KEYSTONE F89-014 | SMC IP8100 031 J (4-20mA) | F17.20 | F24.20.07 | FCV17001 | VBF | Hypersaline Water | AS2129 Table D
0 | FCV | 17 | 127 | FCV 17127 | 350 | VPID1L1 | 350VPID1L1-Double Acting-Positioner | Flotation Tailings Thickener Underflow Pumps CIL 2 Feed Box Valve | 17-1064-FS-RL1-600 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FS | RL1 | 600 | 775 | 1500 | 225 | VTA | VTA | 70 | 180 | 0.56 | 1.65 | 700 | 14 | Detail 2 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | Transmitter | - | F17-CP-405 | 2000-PP007-B02-10320 | PP007 | PP007 |  | Jindex | CMR06OT-MYY58-TD40XX | 2000-PP007-B02-10085 | Jindex | Pneu DA Internal positioner mechanism | Positioner Siemens PS2 4-20mA with position feed back 4-20mA and fail last circuit | F17.20 | F17.20.04 | FCV17127 | VPI | Flotation Slurry | AS2129 Table D
0 | FCV | 17 | 128 | FCV 17128 | 350 | VPID1L1 | 350VPID1L1-Double Acting-Positioner | Flotation Tailings Thickener Underflow Pumps CIL 3 Feed Box Valve | 17-1065-FS-RL1-350 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FS | RL1 | 350 | 775 | 1500 | 225 | VTA | VTA | 70 | 180 | 0.56 | 1.65 | 700 | 14 | Detail 2 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | Transmitter | - | F17-CP-405 | 2000-PP007-B02-10320 | PP007 | PP007 |  | Jindex | CMR06OT-MYY58-TD40XX | 2000-PP007-B02-10085 | Jindex | Pneu DA Internal positioner mechanism | Positioner Siemens PS2 4-20mA with position feed back 4-20mA and fail last circuit | F17.20 | F17.20.04 | FCV17128 | VPI | Flotation Slurry | AS2129 Table D
0 | FCV | 17 | 130 | FCV 17130 | 400 | VPID1L1 | 400VPID1L1-Double Acting-Positioner | Flotation Tailings Thickener Underflow Pumps to Final Tails Tank Pinch Valve | 17-0376-CON-PE10-500 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | CON | PE10 | 500 | 1190 | 1900 | 225 | VTA | VTA | 70 | 180 | 0.56 | 1.65 | 700 | 16 | Detail 2 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | Transmitter | - | F17-CP-406 | 2000-PP007-B02-10321 | PP007 | PP007 |  | Jindex | CMR06OT-MYY58-TD40XX | 2000-PP007-B02-10091 | Jindex | Pneu DA Internal positioner mechanism | Positioner Siemens PS2 4-20mA with position feed back 4-20mA and fail last circuit | F17.20 | F17.20.04 | FCV17130 | VPI | Concentrate Slurry | AS2129 Table D PN10
0 | SV | 17 | 104 | SV 17104 | 25 | SV | 25SV-Solenoid-FO | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 1 GLAND WATER | 17-0867-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F17.20 | F17.20.04 | SV17104 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 17 | 114 | SV 17114 | 25 | SV | 25SV-Solenoid-FO | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 2 GLAND WATER | 17-0868-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F17.20 | F17.20.04 | SV17114 | SV | Hypersaline Water | AS2129 Table E
0 | SVO | 17 | 19 | SVO 17019 | 15 | SV | 15SV-Solenoid-FC | Flotation Tailings Thickener Turbidity Element Air Flushing Solenoid Valve | MECH | 2000-F17-PID-PR-10001 | 2000-F24-PID-PR-10008 | Stage 1 | Greenfield | IA | N/A | N/A | 0 | 1200 | 700 | 0 | 650 | N/A | N/A | N/A | AIR | 1000 | 0 | Detail 11 | FC | Solenoid | Single Acting | SV17019 | No | No | FC | F17-CP-407 | 2000-PP007-B02-10322 | PP007 | PP007 | This is an additional solenoid valve to be located in pneaumatic valve panel. No control valve required. | SMC | VXZ242GZ2A 24VDC | 2000-PP007-B02-10501 | N/A | N/A | N/A | F17.20 | F17.20.01 | SVO17019 | SV | Instrument Air | #N/A
0 | XV | 17 | 5 | XV 17005 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Final Tails Sample Pump Suction Valve | 16-0660-FS-RL1-80 | 2000-F17-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.3333 | 1.13 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC17005 | No | Position Switches | - | F17-CP-404 | 2000-PP007-B02-10319 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.02 | XV17005 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 17 | 6 | XV 17006 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | Final Tails Sample Pump Suction Drain | 16-1515-FS-SS3-50 | 2000-F17-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.3333 | 1.13 | 700 | 2 | Detail 4 | FO | Double Acting | Single Acting | SV17006 | No | Position Switches | - | F17-CP-404 | 2000-PP007-B02-10319 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F16.10 | F16.10.13 | XV17006 | VKG | Flotation Slurry | AS2129 Table E
0 | XV | 17 | 7 | XV 17007 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | Final Tails Sample Pump Discharge Drain | 16-1448-FS-SS3-50 | 2000-F17-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.3333 | 1.13 | 700 | 2 | Detail 4 | FO | Double Acting | Single Acting | SV17007 | No | Position Switches | - | F17-CP-404 | 2000-PP007-B02-10319 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F16.10 | F16.10.13 | XV17007 | VKG | Flotation Slurry | AS2129 Table E
0 | XV | 17 | 9 | XV 17009 | 1200 | VKGD1L2 | 1200VKGD1L2-Double Acting | Flotation Tailings Thickener Recirculation Feed Box Isolation Valve | 17-1742-FS-RL1-1200 | 2000-F17-PID-PR-10001 | N/A | Stage 1 | Greenfield | FS | RL1 | 1200 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 300 | 48 | Detail 5 | FL | Double Acting | Double Acting | SVO/SVC17009 | No | Position Switches | - | F17-HU-422 | 2000-PP007-B02-10202 | PP007 | PP007 | Hydraulically actuated valve | Emerson | Clarkson KGA+ | 2000-PP007-B02-10105 | Emerson | Hydraulic cylinder | SWI LMT PXM P+F NCB5-18GM40-N0 5-24VDC | F17.20 | F17.20.01 | XV17009 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 17 | 85 | XV 17085 |  | N/A |  | Flotation Tailings Feed Sampler Upstream Flush Valve |  | 2000-F17-PID-PR-10001 | 2000-F24-PID-PR-10008 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FC | Double Acting | Double Acting | SVO/SVC17085 | No | Position Switches | - | F17SA416-CP | N/A | ME074 | ME074 | Vendor Supply | [6 empty] | F17.20 | F17.20.02 | XV17085 | N/A | #N/A | #N/A
0 | XV | 17 | 86 | XV 17086 |  | N/A |  | Flotation Tailings Feed Sampler Down Steam Flush Valve |  | 2000-F17-PID-PR-10001 | 2000-F24-PID-PR-10008 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FC | Double Acting | Double Acting | SVO/SVC17086 | No | Position Switches | - | F17SA416-CP | N/A | ME074 | ME074 | Vendor Supply | [6 empty] | F17.20 | F17.20.02 | XV17086 | N/A | #N/A | #N/A
0 | XV | 17 | 87 | XV 17087 |  | N/A |  | Flotation Tailings Feed Sampler Sample Valve |  | 2000-F17-PID-PR-10001 | 2000-F24-PID-PR-10008 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC17087 | No | Position Switches | - | F17SA416-CP | N/A | ME074 | ME074 | Vendor Supply | [6 empty] | F17.20 | F17.20.02 | XV17087 | N/A | #N/A | #N/A
0 | XV | 17 | 91 | XV 17091 | 600 | VKGD1L1 | 600VKGD1L1-Double Acting-Drain Plate | Flotation Tailings Thickener Underflow Cone Discharge Valve 1 | 17-0364-CON-RL1-600 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 24 | Detail 4 | FC | Double Acting | Single Acting | SV17091 | No | Position Switches | Drain Plate | F17-CP-401 | 2000-PP007-B02-10316 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGD | 2000-PP007-B02-10119 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.01 | XV17091 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 92 | XV 17092 | 600 | VKGD1L1 | 600VKGD1L1-Double Acting-Drain Plate | Flotation Tailings Thickener Underflow Cone Discharge Valve 2 | 17-0365-CON-RL1-600 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 24 | Detail 4 | FC | Double Acting | Single Acting | SV17092 | No | Position Switches | Drain Plate | F17-CP-401 | 2000-PP007-B02-10316 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGD | 2000-PP007-B02-10119 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.01 | XV17092 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 93 | XV 17093 | 600 | VKGD1L1 | 600VKGD1L1-Double Acting-Drain Plate | Flotation Tailings Thickener Underflow Cone Discharge Valve 3 | 17-0374-CON-RL1-600 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 24 | Detail 4 | FC | Double Acting | Single Acting | SV17093 | No | Position Switches | Drain Plate | F17-CP-401 | 2000-PP007-B02-10316 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGD | 2000-PP007-B02-10119 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.01 | XV17093 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 94 | XV 17094 | 600 | VKGD1L1 | 600VKGD1L1-Double Acting-Drain Plate | Flotation Tailings Thickener Underflow Cone Discharge Valve 4 | 17-0377-CON-RL1-600 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 24 | Detail 4 | FC | Double Acting | Single Acting | SV17094 | No | Position Switches | Drain Plate | F17-CP-401 | 2000-PP007-B02-10316 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGD | 2000-PP007-B02-10119 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17094 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 95 | XV 17095 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | Flotation Tailings Thickener Underflow Pump 1 Suction Flushing Valve | 17-0628-CON-RL1-750 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 750 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC17095 | No | Position Switches | - | F17-CP-401 | 2000-PP007-B02-10316 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17095 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 96 | XV 17096 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | Flotation Tailings Thickener Underflow Pump 2 Suction Flushing Valve | 17-0629-CON-RL1-750 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 750 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC17096 | No | Position Switches | - | F17-CP-401 | 2000-PP007-B02-10316 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17096 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 101 | XV 17101 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | Flotation Tailings Thickener Underflow Pump 1 Discharge Flushing Valve | 17-0380-CON-RL1-750 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 750 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC17101 | No | Position Switches | - | F17-CP-402 | 2000-PP007-B02-10317 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17101 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 102 | XV 17102 | 300 | VKGD1L1 | 300VKGD1L1-Double Acting | Flotation Tailings Thickener Underflow Pump 1 Discharge Drain Valve | 17-0628-CON-RL1-750 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 750 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 12 | Detail 4 | FO | Double Acting | Single Acting | SV17102 | No | Position Switches | - | F17-CP-402 | 2000-PP007-B02-10317 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10080 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17102 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 103 | XV 17103 | 750 | VKGD1L2 | 750VKGD1L2-Double Acting | Flotation Tailings Thickener Underflow Pump 1 Discharge Valve | 17-0380-CON-RL1-750 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 750 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 30 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC17103 | No | Position Switches | - | F17-CP-402 | 2000-PP007-B02-10317 | PP007 | PP007 |  | Emerson | Clarkson KGA+ | 2000-PP007-B02-10104 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17103 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 111 | XV 17111 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | Flotation Tailings Thickener Underflow Pump 2 Discharge Flushing Valve | 17-0381-CON-RL1-750 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 750 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC17111 | No | Position Switches | - | F17-CP-402 | 2000-PP007-B02-10317 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17111 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 112 | XV 17112 | 300 | VKGD1L1 | 300VKGD1L1-Double Acting | Flotation Thickener Underflow Pump 2 Discharge Drain Valve | 17-0629-CON-RL1-750 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 750 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 12 | Detail 4 | FO | Double Acting | Single Acting | SV17112 | No | Position Switches | - | F17-CP-402 | 2000-PP007-B02-10317 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10080 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17112 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 113 | XV 17113 | 750 | VKGD1L2 | 750VKGD1L2-Double Acting | Flotation Thickener Underflow Pump 2 Discharge Valve | 17-0381-CON-RL1-750 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 750 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 30 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC17113 | No | Position Switches | - | F17-CP-402 | 2000-PP007-B02-10317 | PP007 | PP007 |  | Emerson | Clarkson KGA+ | 2000-PP007-B02-10104 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17113 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 123 | XV 17123 | 750 | VKGD1L2 | 750VKGD1L2-Double Acting | Flotation Tailings Thickener Underflow Discharge Header Valve | 17-0380-CON-RL1-750 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 750 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 30 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC17123 | No | Position Switches | - | F17-CP-403 | 2000-PP007-B02-10318 | PP007 | PP007 |  | Emerson | Clarkson KGA+ | 2000-PP007-B02-10104 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17123 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 124 | XV 17124 | 250 | VKGD1L1 | 250VKGD1L1-Double Acting | Flotation Tailings Thickener Underflow Pumps Discharge Header Drain Valve | 17-0380-CON-RL1-750 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 750 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 10 | Detail 4 | FO | Double Acting | Single Acting | SV17124 | No | Position Switches | - | F17-CP-403 | 2000-PP007-B02-10318 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10075 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17124 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 125 | XV 17125 | 500 | VKGD1L1 | 500VKGD1L1-Double Acting | Flotation Tailings Thickener Underflow Pumps Flotation Tailings Thickener Recirculation Bypass Valve | 17-0543-CON-RL1-500 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 500 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 20 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC17125 | No | Position Switches | - | F17-CP-403 | 2000-PP007-B02-10318 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10098 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17125 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 126 | XV 17126 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Flotation Tailings Thickener Underflow Pumps Flotation Tailings Thickener Recirculation Bypass Drain Valve | 17-0543-CON-RL1-500 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 500 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC17126 | No | Position Switches | - | F17-CP-403 | 2000-PP007-B02-10318 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17126 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 131 | XV 17131 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting | Flotation Tailings Thickener Underflow Pumps Discharge Header Flushing Valve | 17-0380-CON-RL1-750 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | CON | RL1 | 750 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 16 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC17131 | No | Position Switches | - | F17-CP-403 | 2000-PP007-B02-10318 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10089 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17131 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 17 | 132 | XV 17132 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting-Drain Plate | Flotation Tailings Thickener Underflow Pumps to Final Tails Tank Isolation Valve | 17-0376-CON-PE10-500 | 2000-F17-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | CON | PE10 | 500 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.56 | 1.65 | 700 | 16 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC17132 | No | Position Switches | Drain Plate | F17-CP-406 | 2000-PP007-B02-10321 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGD | 2000-PP007-B02-10118 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F17.20 | F17.20.04 | XV17132 | VKG | Concentrate Slurry | AS2129 Table D PN10
0 | FCV | 18 | 56 | FCV 18056 |  | N/A |  | Cleaner Flotation Cell Air Flow Control Valve |  | 2000-F18-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | - | F18-CP-401 | N/A | ME073 | PP007 | Vendor Supply | [6 empty] | F18.20 | F18.20.05 | FCV18056 | N/A | #N/A | #N/A
0 | FCV | 18 | 57 | FCV 18057 |  | N/A |  | Cleaner Flotation Cell Wash Water Flow Flow Control Valve | 18-0430-PW-PE16-225 | 2000-F18-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | PW | PE16 | 225 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | - | F18-CP-401 | N/A | ME073 | PP007 | Vendor Supply | [6 empty] | F24.20 | F24.20.01 | FCV18057 | N/A | Hypersaline Water | AS2129 Table E PN16
0 | FCV | 18 | 256 | FCV 18256 |  | N/A |  | Cleaner-Scavenger Flotation Cell Air Flow Control Valve |  | 2000-F18-PID-PR-10004 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | - | F18-CP-402 | N/A | ME073 | PP007 | Vendor Supply | [6 empty] | F18.20 | F18.20.06 | FCV18256 | N/A | #N/A | #N/A
0 | FCV | 18 | 257 | FCV 18257 |  | N/A |  | Cleaner-Scavenger Flotation Cell High Pressure Water Flow Control Valve | 18-2054-PW-SS1-150 | 2000-F18-PID-PR-10004 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | PW | SS1 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | - | F18-CP-402 | N/A | ME073 | PP007 | Vendor Supply | [6 empty] | F24.20 | F24.20.01 | FCV18257 | N/A | Hypersaline Water | AS2129 Table D
0 | LCV | 18 | 1 | LCV 18001 | 100 | VBFD1S1 | 100VBFD1S1-Double Acting-Positioner | Final Concentrate Hopper Process Water Level Control Valve | 18-0611-PW-SS1-150 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | PW | SS1 | 150 | 90 | 220 | 300 | VTA | VTA | N/A | N/A | N/A | 1.07 | 700 | 4 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F18-CP-410 | 2000-PP007-B02-10332 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10041 | Emerson | KEYSTONE F89-006 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.07 | LCV18001 | VBF | Hypersaline Water | AS2129 Table D
0 | LCV | 18 | 51 | LCV 18051 | 500 | N/A |  | Cleaner Flotation Cell Tank Slurry Level Control Valve | 18-0941-FS-RL3-500 | 2000-F18-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL3 | 500 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 20 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | - | F18-CP-401 | N/A | ME073 | PP007 | Vendor Supply | [6 empty] | F18.20 | F18.20.05 | LCV18051 | N/A | Flotation Slurry | AS2129 Table D
0 | LCV | 18 | 211 | LCV 18211 | 150 | VBFD1S1 | 150VBFD1S1-Double Acting-Positioner | Cleaner Scavenger Flotation Cell Tails Hopper Process Water Level Control Valve | 18-0817-PW-SS1-200 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | PW | SS1 | 200 | 250 | 450 | 300 | VTA | VTA | N/A | N/A | N/A | 1.07 | 700 | 6 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F18-CP-404 | 2000-PP007-B02-10326 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10057 | Emerson | KEYSTONE F89-014 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.07 | LCV18211 | VBF | Hypersaline Water | AS2129 Table D
0 | LCV | 18 | 251 | LCV 18251 | 500 | N/A |  | Cleaner-Scavenger Flotation Cell Tank Slurry Level Control Valve | 18-0795-FS-RL3-500 | 2000-F18-PID-PR-10004 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL3 | 500 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 20 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | - | F18-CP-402 | N/A | ME073 | PP007 | Vendor Supply | [6 empty] | F18.20 | F18.20.06 | LCV18251 | N/A | Flotation Slurry | AS2129 Table D
0 | LCV | 18 | 011A | LCV 18011A | 100 | VBFD1S1 | 100VBFD1S1-Double Acting-Positioner | Cleaner Flotation Cell Feed Hopper Process Water Level Control Valve | 18-0611-PW-SS1-150 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | PW | SS1 | 150 | 150 | 220 | 300 | VTA | VTA | N/A | N/A | N/A | 1.07 | 700 | 4 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F18-CP-410 | 2000-PP007-B02-10332 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10041 | Emerson | KEYSTONE F89-006 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.07 | LCV18011A | VBF | Hypersaline Water | AS2129 Table D
0 | LCV | 18 | 011B | LCV 18011B | 500 | N/A |  | Cleaner Flotation Cell Feed Hopper Recycle Level Control Valve | 18-0942-FS-RL3-500 | 2000-F18-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL3 | 500 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 20 | Detail 2 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | Transmitter | - | F18-CP-401 | N/A | ME073 | PP007 | Vendor Supply | [6 empty] | F18.20 | F18.20.05 | LCV18011B | N/A | Flotation Slurry | AS2129 Table D
0 | LCV | 18 | 201A | LCV 18201A | 100 | VBFD1S1 | 100VBFD1S1-Double Acting-Positioner | Cleaner Scavenger Flotation Cell Feed Hopper Process Water Level Control Valve | 18-0466-PW-SS1-150 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | PW | SS1 | 150 | 150 | 220 | 300 | VTA | VTA | N/A | N/A | N/A | 1.07 | 700 | 4 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F18-CP-408 | 2000-PP007-B02-10330 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10041 | Emerson | KEYSTONE F89-006 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.07 | LCV18201A | VBF | Hypersaline Water | AS2129 Table D
0 | LCV | 18 | 201B | LCV 18201B | 500 | N/A |  | Cleaner Scavenger Recycle Level Control Valve | 18-0796-FS-RL3-500 | 2000-F18-PID-PR-10004 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL3 | 500 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 20 | Detail 2 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | Transmitter | - | F18-CP-402 | N/A | ME073 | PP007 | Vendor Supply | [6 empty] | F18.20 | F18.20.06 | LCV18201B | N/A | Flotation Slurry | AS2129 Table D
0 | SV | 18 | 500 | SV 18500 | 25 | SV | 25SV-Solenoid-FO | Final Concentrate Pump 1 Gland Water | 18-0882-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F18.20 | F18.20.01 | SV18500 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 18 | 504 | SV 18504 | 25 | SV | 25SV-Solenoid-FO | Final Concentrate Pump 2 Gland Water | 18-0881-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F18.20 | F18.20.01 | SV18504 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 18 | 508 | SV 18508 | 25 | SV | 25SV-Solenoid-FO | Cleaner Flotation Cell Recirculation Pump 1 Gland Water | 18-0880-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F18.20 | F18.20.02 | SV18508 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 18 | 512 | SV 18512 | 25 | SV | 25SV-Solenoid-FO | Cleaner Flotation Cell Recirculation Pump 2 Gland Water | 18-0879-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F18.20 | F18.20.02 | SV18512 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 18 | 524 | SV 18524 | 25 | SV | 25SV-Solenoid-FO | Cleaner-Scavenger Flotation Cell Recirculation Pump 1 Gland Water | 18-0878-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F18.20 | F18.20.03 | SV18524 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 18 | 528 | SV 18528 | 25 | SV | 25SV-Solenoid-FO | Cleaner-Scavenger Flotation Cell Recirculation Pump 2 Gland Water | 18-0877-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F18.20 | F18.20.03 | SV18528 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 18 | 532 | SV 18532 | 25 | SV | 25SV-Solenoid-FO | Cleaner-Scavenger Flotation Cell Tails Pump 1 Gland Water | 18-0823-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F18.20 | F18.20.04 | SV18532 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 18 | 536 | SV 18536 | 25 | SV | 25SV-Solenoid-FO | Cleaner-Scavenger Flotation Cell Tails Pump 2 Gland Water | 18-0822-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F18.20 | F18.20.04 | SV18536 | SV | Hypersaline Water | AS2129 Table E
0 | XV | 18 | 12 | XV 18012 | 150 | VBFD1S2 | 150VBFD1S2-Double Acting | Final Concentrate Hopper Process Water Isolation Valve | 18-0611-PW-SS1-150 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | PW | SS1 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 6 | Detail 7 | FC | Double Acting | Single Acting | SV18012 | No | Position Switches | - | F18-CP-410 | 2000-PP007-B02-10332 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10058 | Emerson | KEYSTONE F89-014 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.07 | XV18012 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 18 | 13 | XV 18013 | 150 | VBFD1S2 | 150VBFD1S2-Double Acting | Cleaner Flotation Cell Feed Hopper Process Water Isolation Valve | 18-0783-PW-SS1-150 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | PW | SS1 | 150 | N/A | N/A | N/A | VTA | VTA | N/A | N/A | N/A | 1.07 | 700 | 6 | Detail 7 | FC | Double Acting | Single Acting | SV18013 | No | Position Switches | - | F18-CP-410 | 2000-PP007-B02-10332 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10058 | Emerson | KEYSTONE F89-014 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.07 | XV18013 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 18 | 14 | XV 18014 | 150 | VBFD1S2 | 150VBFD1S2-Double Acting | Cleaner Scavenger Flotation Cell Feed Hopper Process Water Isolation Valve | 18-0466-PW-SS1-150 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | PW | SS1 | 150 | N/A | N/A | N/A | VTA | VTA | N/A | N/A | N/A | 1.07 | 700 | 6 | Detail 7 | FC | Double Acting | Single Acting | SV18014 | No | Position Switches | - | F18-CP-408 | 2000-PP007-B02-10330 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10058 | Emerson | KEYSTONE F89-014 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.07 | XV18014 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 18 | 15 | XV 18015 | 200 | VBFD1S2 | 200VBFD1S2-Double Acting | Cleaner Scavenger Flotation Cell Tails Hopper Process Water Isolation Valve | 18-0817-PW-SS1-200 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | PW | SS1 | 200 | N/A | N/A | N/A | VTA | VTA | N/A | N/A | N/A | 1.07 | 700 | 8 | Detail 7 | FC | Double Acting | Single Acting | SV18015 | No | Position Switches | - | F18-CP-404 | 2000-PP007-B02-10326 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10067 | Emerson | KEYSTONE F89-032 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.07 | XV18015 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 18 | 21 | XV 18021 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting | Final Concentrate Pump 1 Suction Valve | 400-MECH-RL1 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 0.221 | 1.28 | 700 | 16 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18021 | No | Position Switches | - | F18-CP-406 | 2000-PP007-B02-10328 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10089 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.01 | XV18021 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 22 | XV 18022 | 100 | VKGD1L1 | 100VKGD1L1-Double Acting | Final Concentrate Pump 1 Drain Valve | 400-MECH-RL1 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 0.221 | 1.28 | 700 | 4 | Detail 4 | FO | Double Acting | Single Acting | SV18022 | No | Position Switches | - | F18-CP-406 | 2000-PP007-B02-10328 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10046 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.01 | XV18022 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 23 | XV 18023 | 250 | VKGD1L1 | 250VKGD1L1-Double Acting-Drain Plate | Final Concentrate Pump 1 Discharge Valve | 18-0926-FS-RL1-250 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 250 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 0.221 | 1.28 | 700 | 10 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18023 | No | Position Switches | Drain Plate | F18-CP-406 | 2000-PP007-B02-10328 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGD | 2000-PP007-B02-10116 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.01 | XV18023 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 24 | XV 18024 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting | Final Concentrate Pump 2 Suction Valve | 400-MECH-RL1 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 0.221 | 1.28 | 700 | 16 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18024 | No | Position Switches | - | F18-CP-406 | 2000-PP007-B02-10328 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10089 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.01 | XV18024 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 25 | XV 18025 | 100 | VKGD1L1 | 100VKGD1L1-Double Acting | Final Concentrate Pump 2 Drain Valve | 400-MECH-RL1 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 0.221 | 1.28 | 700 | 4 | Detail 4 | FO | Double Acting | Single Acting | SV18025 | No | Position Switches | - | F18-CP-406 | 2000-PP007-B02-10328 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10046 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.01 | XV18025 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 26 | XV 18026 | 250 | VKGD1L1 | 250VKGD1L1-Double Acting-Drain Plate | Final Concentrate Pump 2 Discharge Valve | 18-0927-FS-RL1-250 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 250 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 0.221 | 1.28 | 700 | 10 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18026 | No | Position Switches | Drain Plate | F18-CP-406 | 2000-PP007-B02-10328 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGD | 2000-PP007-B02-10116 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.01 | XV18026 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 28 | XV 18028 | 50 | VDD1L1 | 50VDD1L1-Double Acting | Final Concentrate Sampler Discharge Valve | 18-0378-FS-RL1-50 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 50 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.285 | 1.24 | 700 |  | Detail 7 | FC | Double Acting | Single Acting | SV18028 | No | Position Switches | - | F18-CP-406 | 2000-PP007-B02-10328 | PP007 | PP007 |  | KDV | Series 37 Straight Through (ST) | 2000-PP007-B02-10017 | KDV | Pneumatic cylinder | IMTEX Std Box Mech on/off Sw KDV/Linear Drive +2 Terminal | F24.20 | F24.20.07 | XV18028 | VDD | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 29 | XV 18029 | 50 | VB03S1 | 50VB03S1-Double Acting | Final Concentrate Sampler Discharge Process Water Valve | 18-0349-PW-PE8-63 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | PW | PE8 | 63 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 |  | Detail 7 | FC | Double Acting | Single Acting | SV18029 | No | Position Switches | - | F18-CP-406 | 2000-PP007-B02-10328 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10008 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F16.10 | F16.10.13 | XV18029 | VB0 | Hypersaline Water | AS2129 Table D PN10
0 | XV | 18 | 31 | XV 18031 | 600 | VKGD1L1 | 600VKGD1L1-Double Acting | Cleaner Flotation Cell Recirculation Pump 1 Suction Valve | 600-MECH-RL1 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 15.7 | 1.19 | 700 | 24 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18031 | No | Position Switches | - | F18-CP-407 | 2000-PP007-B02-10329 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10100 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.02 | XV18031 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 32 | XV 18032 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Cleaner Flotation Cell Recirculation Pump 1 Drain Valve | 600-MECH-RL1 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 15.7 | 1.19 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV18032 | No | Position Switches | - | F18-CP-407 | 2000-PP007-B02-10329 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.02 | XV18032 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 33 | XV 18033 | 500 | VKGD1C1 | 500VKGD1C1-Double Acting | Cleaner Flotation Cell Recirculation Pump 1 Discharge Valve | 18-0956-FS-RL1-500 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 500 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 15.7 | 1.19 | 700 | 20 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18033 | No | Position Switches | - | F18-CP-407 | 2000-PP007-B02-10329 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10097 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.02 | XV18033 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 34 | XV 18034 | 600 | VKGD1L1 | 600VKGD1L1-Double Acting | Cleaner Flotation Cell Recirculation Pump 2 Suction Valve | 600-MECH-RL1 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 15.7 | 1.19 | 700 | 24 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18034 | No | Position Switches | - | F18-CP-407 | 2000-PP007-B02-10329 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10100 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.02 | XV18034 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 35 | XV 18035 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Cleaner Flotation Cell Recirculation Pump 2 Drain Valve | 600-MECH-RL1 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 15.7 | 1.19 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV18035 | No | Position Switches | - | F18-CP-407 | 2000-PP007-B02-10329 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.02 | XV18035 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 36 | XV 18036 | 500 | VKGD1C1 | 500VKGD1C1-Double Acting | Cleaner Flotation Cell Recirculation Pump 2 Discharge Valve | 18-0923-FS-RL1-500 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 500 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 15.7 | 1.19 | 700 | 20 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18036 | No | Position Switches | - | F18-CP-407 | 2000-PP007-B02-10329 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10097 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.02 | XV18036 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 38 | XV 18038 | 50 | VDD1L1 | 50VDD1L1-Double Acting | Cleaner Feed Sampler Discharge Valve | 18-0955-FS-RL1-50 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 50 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.25 | 1.26 | 700 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV18038 | No | Position Switches | - | F18-CP-410 | 2000-PP007-B02-10332 | PP007 | PP007 |  | KDV | Series 37 Straight Through (ST) | 2000-PP007-B02-10017 | KDV | Pneumatic cylinder | IMTEX Std Box Mech on/off Sw KDV/Linear Drive +2 Terminal | F16.10 | F16.10.13 | XV18038 | VDD | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 39 | XV 18039 | 50 | VB03S1 | 50VB03S1-Double Acting | Cleaner Feed Discharge Process Water Valve | 18-1116-PW-PE8-63 | 2000-F18-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | PW | PE8 | 63 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV18039 | No | Position Switches | - | F18-CP-410 | 2000-PP007-B02-10332 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10008 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F24.20 | F24.20.07 | XV18039 | VB0 | Hypersaline Water | AS2129 Table D PN10
0 | XV | 18 | 221 | XV 18221 | 600 | VKGD1L1 | 600VKGD1L1-Double Acting | Cleaner Scavenger Flotation Cell Recirculation Pump 1 Suction Valve | 600-MECH-RL1 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.9 | 1.21 | 700 | 24 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18221 | No | Position Switches | - | F18-CP-403 | 2000-PP007-B02-10325 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10100 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.03 | XV18221 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 222 | XV 18222 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Cleaner Scavenger Flotation Cell Recirculation Pump 1 Drain Valve | 600-MECH-RL1 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.9 | 1.21 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV18222 | No | Position Switches | - | F18-CP-403 | 2000-PP007-B02-10325 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.03 | XV18222 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 223 | XV 18223 | 500 | VKGD1C1 | 500VKGD1C1-Double Acting | Cleaner Scavenger Flotation Cell Recirculation Pump 1 Discharge Valve | 18-0709-FS-RL1-500 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 500 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.9 | 1.21 | 700 | 20 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18223 | No | Position Switches | - | F18-CP-403 | 2000-PP007-B02-10325 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10097 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.03 | XV18223 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 224 | XV 18224 | 600 | VKGD1L1 | 600VKGD1L1-Double Acting | Cleaner Scavenger Flotation Cell Recirculation Pump 2 Suction Valve | 600-MECH-RL1 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.9 | 1.21 | 700 | 24 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18224 | No | Position Switches | - | F18-CP-403 | 2000-PP007-B02-10325 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10100 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.03 | XV18224 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 225 | XV 18225 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Cleaner Scavenger Flotation Cell Recirculation Pump 2 Drain Valve | 600-MECH-RL1 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.9 | 1.21 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV18225 | No | Position Switches | - | F18-CP-403 | 2000-PP007-B02-10325 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.03 | XV18225 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 226 | XV 18226 | 500 | VKGD1C1 | 500VKGD1C1-Double Acting | Cleaner Scavenger Flotation Cell Recirculation Pump 2 Discharge Valve | 18-0710-FS-RL1-500 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 500 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.9 | 1.21 | 700 | 20 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18226 | No | Position Switches | - | F18-CP-403 | 2000-PP007-B02-10325 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10097 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.03 | XV18226 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 229 | XV 18229 | 50 | VB03S1 | 50VB03S1-Double Acting | Cleaner Scavenger Tails Sample Discharge Flushing Valve | 18-0345-PW-PE8-63 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | PW | PE8 | 63 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV18229 | No | Position Switches | - | F18-CP-409 | 2000-PP007-B02-10331 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10008 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F24.20 | F24.20.07 | XV18229 | VB0 | Hypersaline Water | AS2129 Table D PN10
0 | XV | 18 | 231 | XV 18231 | 450 | VKGD1L1 | 450VKGD1L1-Double Acting | Cleaner Scavenger Flotation Cell Tails Pump 1 Suction Valve | 450-MECH-RL1 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 450 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.8 | 1.21 | 700 | 18 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18231 | No | Position Switches | - | F18-CP-405 | 2000-PP007-B02-10327 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10094 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.04 | XV18231 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 232 | XV 18232 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Cleaner Scavenger Flotation Cell Tails Pump 1 Drain Valve | 450-MECH-RL1 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 450 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.8 | 1.21 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV18232 | No | Position Switches | - | F18-CP-405 | 2000-PP007-B02-10327 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.04 | XV18232 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 233 | XV 18233 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting-Drain Plate | Cleaner Scavenger Flotation Cell Tails Pump 1 Discharge Valve | 18-0713-FS-RL1-400 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.8 | 1.21 | 700 | 16 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18233 | No | Position Switches | Drain Plate | F18-CP-405 | 2000-PP007-B02-10327 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGD | 2000-PP007-B02-10118 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.04 | XV18233 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 234 | XV 18234 | 450 | VKGD1L1 | 450VKGD1L1-Double Acting | Cleaner Scavenger Flotation Cell Tails Pump 2 Suction Valve | 450-MECH-RL1 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 450 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.8 | 1.21 | 700 | 18 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18234 | No | Position Switches | - | F18-CP-405 | 2000-PP007-B02-10327 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10094 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.04 | XV18234 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 235 | XV 18235 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Cleaner Scavenger Flotation Cell Tails Pump 2 Drain Valve | 450-MECH-RL1 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 450 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.8 | 1.21 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV18235 | No | Position Switches | - | F18-CP-405 | 2000-PP007-B02-10327 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.04 | XV18235 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 236 | XV 18236 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting-Drain Plate | Cleaner Scavenger Flotation Cell Tails Pump 2 Discharge Valve | 18-0714-FS-RL1-400 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.8 | 1.21 | 700 | 16 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18236 | No | Position Switches | Drain Plate | F18-CP-405 | 2000-PP007-B02-10327 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGD | 2000-PP007-B02-10118 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.04 | XV18236 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 239 | XV 18239 | 50 | VDD1L1 | 50VDD1L1-Double Acting | Cleaner Scavenger Tails Sample Discharge Valve | 18-0346-FS-RL1-50 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 50 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.285 | 1.24 | 700 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV18239 | No | Position Switches | - | F18-CP-409 | 2000-PP007-B02-10331 | PP007 | PP007 |  | KDV | Series 37 Straight Through (ST) | 2000-PP007-B02-10017 | KDV | Pneumatic cylinder | IMTEX Std Box Mech on/off Sw KDV/Linear Drive +2 Terminal | F18.20 | F18.20.04 | XV18239 | VDD | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 241 | XV 18241 | 400 | VKGD1C1 | 400VKGD1C1-Double Acting | Cleaner Scavenger Tails Discharge to Flotation Discharge Box Valve | 18-0858-FS-RL1-400 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.8 | 1.21 | 700 | 16 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18241 | No | Position Switches | - | F18-CP-409 | 2000-PP007-B02-10331 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10088 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.04 | XV18241 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 242 | XV 18242 | 400 | VKGD1C1 | 400VKGD1C1-Double Acting | Cleaner Scavenger Tails Discharge to Scavenger Flotation Cell 1 Valve | 18-0857-FS-RL1-400 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.8 | 1.21 | 700 | 16 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC18242 | No | Position Switches | - | F18-CP-409 | 2000-PP007-B02-10331 | PP007 | PP007 |  | Emerson | Clarkson KS1 | 2000-PP007-B02-10088 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.04 | XV18242 | VKG | Flotation Slurry | AS2129 Table D
0 | XV | 18 | 243 | XV 18243 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Cleaner Scavenger Tails Discharge to Flotation Discharge Box Drain Valve | 18-1258-FS-PE10-160 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | PE10 | 160 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.8 | 1.21 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV18243 | No | Position Switches | - | F18-CP-409 | 2000-PP007-B02-10331 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.04 | XV18243 | VKG | Flotation Slurry | AS2129 Table D PN10
0 | XV | 18 | 244 | XV 18244 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Cleaner Scavenger Tails Discharge to Scavenger Flotation Cell 1 Drain Valve | 18-1259-FS-PE10-160 | 2000-F18-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 1 | Greenfield | FS | PE10 | 160 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 18.8 | 1.21 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV18244 | No | Position Switches | - | F18-CP-409 | 2000-PP007-B02-10331 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.04 | XV18244 | VKG | Flotation Slurry | AS2129 Table D PN10
1 | FCV | 21 | 2 | FCV 21002 | 25 | VDE1L2 | 25VDE1L2-Double Acting-Positioner | CIL 4 Feed Distribution Box Cyanide Inlet Flow Control Valve | 21-0423-CN-MS2-25 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CN | MS2 | 25 | 0 | 5 | 200 | 200 | 50 | N/A | N/A | N/A | 1.1 | 700 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F21-CP-401 | 2000-PP007-B02-10356 | PP007 | PP007 |  | KDV | Weir Type series 35 | 2000-PP007-B02-10004 | KDV | Pneumatic actuator | SMC Smart Linear Positioner IP8001-032 I-P 4-20mA IN/OUT + 2 Alarms | F21.20 | F21.20.02 | FCV21002 | VDE | Cyanide Solution | AS2129 Table E
1 | FCV | 21 | 3 | FCV 21003 | 25 | VDE1L2 | 25VDE1L2-Double Acting-Positioner | CIL 4 Tank 1 Cyanide Inlet Flow Control Valve | 21-0424-CN-MS2-25 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CN | MS2 | 25 | 0 | 5 | 200 | 200 | 50 | N/A | N/A | N/A | 1.1 | 700 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F21-CP-401 | 2000-PP007-B02-10356 | PP007 | PP007 |  | KDV | Weir Type series 35 | 2000-PP007-B02-10004 | KDV | Pneumatic actuator | SMC Smart Linear Positioner IP8001-032 I-P 4-20mA IN/OUT + 2 Alarms | F21.20 | F21.20.01 | FCV21003 | VDE | Cyanide Solution | AS2129 Table E
1 | FCV | 21 | 4 | FCV 21004 | 25 | VDE1L2 | 25VDE1L2-Double Acting-Positioner | CIL 4 Tank 2 Cyanide Inlet Flow Control Valve | 21-0425-CN-MS2-25 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CN | MS2 | 25 | 0 | 5 | 200 | 200 | 50 | N/A | N/A | N/A | 1.1 | 700 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F21-CP-401 | 2000-PP007-B02-10356 | PP007 | PP007 |  | KDV | Weir Type series 35 | 2000-PP007-B02-10004 | KDV | Pneumatic actuator | SMC Smart Linear Positioner IP8001-032 I-P 4-20mA IN/OUT + 2 Alarms | F21.20 | F21.20.01 | FCV21004 | VDE | Cyanide Solution | AS2129 Table E
1 | FCV | 21 | 5 | FCV 21005 | 25 | VDE1L2 | 25VDE1L2-Double Acting-Positioner | CIL 4 Tank 3 Cyanide Inlet Flow Control Valve | 21-0426-CN-MS2-25 | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CN | MS2 | 25 | 0 | 5 | 200 | 200 | 50 | N/A | N/A | N/A | 1.1 | 700 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F21-CP-401 | 2000-PP007-B02-10356 | PP007 | PP007 |  | KDV | Weir Type series 35 | 2000-PP007-B02-10004 | KDV | Pneumatic actuator | SMC Smart Linear Positioner IP8001-032 I-P 4-20mA IN/OUT + 2 Alarms | F72.80 | F72.80.02 | FCV21005 | VDE | Cyanide Solution | AS2129 Table E
0 | FCV | 21 | 347 | FCV 21347 | 25 | VGLE1S1 | 25VGLE1S1-Double Acting-Positioner | CIL 4 Tank 1 Oxygen Injection 1 Flow Control Valve | 21-0415-OXY-SS6-25 | 2000-F72-PID-PR-10011 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | OXY | SS6 | 25 | 0 | 75 | 700 | 700 | 150 | N/A | N/A | N/A | OXYGEN | 1400 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F21-CP-402 | 2000-PP007-B02-10357 | PP007 | PP007 |  | Emerson | FISHER 025 24000SVF | 2000-PP007-B02-10005 | Emerson | Pneumatic actuator | DVC2000,HART Communicating-HC 4-20mA | F72.50 | F72.50.02 | FCV21347 | VGL | Oxygen | AS2129 Table E
0 | FCV | 21 | 349 | FCV 21349 | 25 | VGLE1S1 | 25VGLE1S1-Double Acting-Positioner | CIL 4 Tank 1 Oxygen Injection 2 Flow Control Valve | 21-0417-OXY-SS6-25 | 2000-F72-PID-PR-10011 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | OXY | SS6 | 25 | 0 | 75 | 700 | 700 | 150 | N/A | N/A | N/A | OXYGEN | 1400 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F21-CP-402 | 2000-PP007-B02-10357 | PP007 | PP007 |  | Emerson | FISHER 025 24000SVF | 2000-PP007-B02-10005 | Emerson | Pneumatic actuator | DVC2000,HART Communicating-HC 4-20mA | F72.50 | F72.50.02 | FCV21349 | VGL | Oxygen | AS2129 Table E
0 | FCV | 21 | 356 | FCV 21356 | 25 | VGLE1S1 | 25VGLE1S1-Double Acting-Positioner | CIL 4 Tank 2 Oxygen Injection 1 Flow Control Valve | 21-0418-OXY-SS6-25 | 2000-F72-PID-PR-10011 | 2000-F24-PID-PR-10007 | Stage 2 | Greenfield | OXY | SS6 | 25 | 0 | 75 | 700 | 700 | 150 | N/A | N/A | N/A | OXYGEN | 1400 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F21-CP-403 | 2000-PP007-B02-10358 | PP007 | PP007 |  | Emerson | FISHER 025 24000SVF | 2000-PP007-B02-10005 | Emerson | Pneumatic actuator | DVC2000,HART Communicating-HC 4-20mA | F72.50 | F72.50.02 | FCV21356 | VGL | Oxygen | AS2129 Table E
0 | FCV | 21 | 358 | FCV 21358 | 25 | VGLE1S1 | 25VGLE1S1-Double Acting-Positioner | CIL 4 Tank 2 Oxygen Injection 2 Flow Control Valve | 21-0419-OXY-SS6-25 | 2000-F72-PID-PR-10011 | 2000-F24-PID-PR-10007 | Stage 2 | Greenfield | OXY | SS6 | 25 | 0 | 75 | 700 | 700 | 150 | N/A | N/A | N/A | OXYGEN | 1400 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F21-CP-403 | 2000-PP007-B02-10358 | PP007 | PP007 |  | Emerson | FISHER 025 24000SVF | 2000-PP007-B02-10005 | Emerson | Pneumatic actuator | DVC2000,HART Communicating-HC 4-20mA | F72.50 | F72.50.02 | FCV21358 | VGL | Oxygen | AS2129 Table E
1 | PCV | 21 | 339 | PCV 21339 | 50 | PCV | 50PCV-N/A-Oxygen | Oxygen Plant Discharge Pressure Regulating Valve | 21-2120-OXY-SS6-100 | 2000-F72-PID-PR-10011 | N/A | Stage 2 | Greenfield | OXY | SS6 | 100 | 1520 | 2042 | 850 | 50 | 50 | N/A | N/A | N/A | OXYGEN | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Oxygen | N/A | N/A | PP007 | N/A | Set Pressure @ 800 kPag | Fisher | 1098-EGR | 2000-PP007-B02-10420 | Fisher | Size 40 | N/A | F72.50 | F72.50.02 | PCV21339 | PCV | Oxygen | AS2129 Table E
0 | PCV | 21 | 346 | PCV 21346 | 25 | PCV | 25PCV-N/A-Oxygen | CIL 4 Tank 1 Oxygen Injection Header Pressure Regulating Valve | 21-0415-OXY-SS6-50 | 2000-F72-PID-PR-10011 | N/A | Stage 2 | Greenfield | OXY | SS6 | 50 | 150 | 180 | 800 | 80 | 80 | N/A | N/A | N/A | OXYGEN | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Oxygen | N/A | N/A | PP007 | N/A | Set Pressure @ 720 kPag | Fisher | MR95H-3063-2995955 | 2000-PP007-B02-10418 | N/A | N/A | N/A | F72.50 | F72.50.02 | PCV21346 | PCV | Oxygen | AS2129 Table E
0 | PCV | 21 | 355 | PCV 21355 | 25 | PCV | 25PCV-N/A-Oxygen | CIL 4 Tank 2 Oxygen Injection Header Pressure Regulating Valve | 21-0418-OXY-SS6-50 | 2000-F72-PID-PR-10011 | N/A | Stage 2 | Greenfield | OXY | SS6 | 50 | 150 | 180 | 800 | 80 | 80 | N/A | N/A | N/A | OXYGEN | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Oxygen | N/A | N/A | PP007 | N/A | Set Pressure @ 720 kPag | Fisher | MR95H-3063-2995955 | 2000-PP007-B02-10418 | N/A | N/A | N/A | F72.50 | F72.50.02 | PCV21355 | PCV | Oxygen | AS2129 Table E
1 | PRV | 21 | 330 | PRV 21330 | 32 | N/A |  | CIL 4 / Elution Air Receiver |  | 2000-F24-PID-PR-10016 | N/A | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME024 | N/A | Vendor Supply Set Pressure @ 1000 kPag | NUOVA General Industrial | F32 OT |  |  |  |  | F21.10 | F21.10.01 | PRV21330 | N/A | #N/A | #N/A
0 | SV | 21 | 305 | SV 21305 |  | N/A |  | CIL 4 Secondary Tails Sampler Spray Water Solenoid | 21-2020-BW-SS3-25 | 2000-F21-PID-PR-10005 | N/A | Stage 2 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | No | Check Detail | - | N/A | N/A | ME027B | ME027B | Vendor Supply | [6 empty] | F21.20 | F21.20.04 | SV21305 | N/A | Hypersaline Water | AS2129 Table E
0 | SV | 21 | 308 | SV 21308 |  | N/A |  | CIL 4 Tails Tertiary Sampler Spray Water Solenoid | 21-2021-BW-SS3-25 | 2000-F21-PID-PR-10005 | N/A | Stage 2 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | No | Check Detail | - | N/A | N/A | ME027B | ME027B | Vendor Supply | [6 empty] | F21.20 | F21.20.04 | SV21308 | N/A | Hypersaline Water | AS2129 Table E
0 | SV | 21 | 311 | SV 21311 |  | N/A |  | CIL 4 Primary Tails Sampler Spray Water Solenoid | 21-1527-BW-SS3-25 | 2000-F21-PID-PR-10005 | N/A | Stage 2 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | No | Check Detail | - | N/A | N/A | ME027B | ME027B | Vendor Supply | [6 empty] | F21.20 | F21.20.04 | SV21311 | N/A | Hypersaline Water | AS2129 Table E
0 | SV | 21 | 317 | SV 21317 |  | N/A |  | CIL 4 Tails Final Sample Dewatering Module Instrument Air Solenoid | 21-2022-IA-MSG3-25 | 2000-F21-PID-PR-10005 | N/A | Stage 2 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | No | Check Detail | - | N/A | N/A | ME027B | ME027B | Vendor Supply | [6 empty] | F21.20 | F21.20.04 | SV21317 | N/A | Hypersaline Water | AS2129 Table E
0 | SV | 21 | 320 | SV 21320 | 25 | SV | 25SV-Solenoid-FO | CIL 4 Tank 1 Oxygen Injection Pump Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Greenfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F21.20 | F21.20.09 | SV21320 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 21 | 324 | SV 21324 | 25 | SV | 25SV-Solenoid-FO | CIL 4 Tank 2 Oxygen Injection Pump Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Greenfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F21.20 | F21.20.09 | SV21324 | SV | Hypersaline Water | AS2129 Table E
0 | XV | 21 | 1 | XV 21001 | 50 | VBE1C1 | 50VBE1C1-Double Acting | CIL 4 Tanks Cyanide Distribution Valve | 21-0422-CN-MS2-50 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CN | MS2 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 2 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC21001 | No | Position Switches | - | F21-CP-401 | 2000-PP007-B02-10356 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10140 |  |  |  | F72.80 | F72.80.02 | XV21001 | VBE | Cyanide Solution | AS2129 Table E
0 | XV | 21 | 11 | XV 21011 | 100 | VKGD1L1 | 100VKGD1L1-Double Acting | Milk Of Lime Ringmain Drain Valve 1 | 21-1251-LS-PE10-110 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10007 | Stage 2 | Greenfield | LS | PE10 | 110 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 4 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21011 | No | Position Switches | - | F17-CP-405 | 2000-PP007-B02-10320 | PP007 | PP007 | Actuated via Manual 4-Way Valve located in control panel | Emerson | Clarkson KGD | 2000-PP007-B02-10046 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F72.110 | F72.110.03 | XV21011 | VKG | Lime Slurry | AS2129 Table D PN10
0 | XV | 21 | 12 | XV 21012 | 100 | VKGD1L1 | 100VKGD1L1-Double Acting | Milk Of Lime to CIL 4 Feed Distribution Box Supply Valve | 21-1045-LS-PE10-110 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | LS | PE10 | 110 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 4 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC21012 | No | Position Switches | - | F21-CP-401 | 2000-PP007-B02-10356 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10046 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F72.110 | F72.110.03 | XV21012 | VKG | Lime Slurry | AS2129 Table D PN10
0 | XV | 21 | 51 | XV 21051 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting | CIL 4 Tank 1 Oxygen Injection Pump Suction Valve | 21-0411-CON-RL1-400 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CON | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 16 | Detail 4 | FC | Double Acting | Single Acting | SV21051 | No | Position Switches | - | F21-CP-402 | 2000-PP007-B02-10357 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10089 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F21.20 | F21.20.09 | XV21051 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 21 | 52 | XV 21052 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | CIL 4 Tank 1 Oxygen Injection Pump Suction Drain Valve | 21-0411-CON-RL1-400 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CON | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV21052 | No | Position Switches | - | F21-CP-402 | 2000-PP007-B02-10357 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F21.20 | F21.20.09 | XV21052 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 21 | 53 | XV 21053 | 350 | VKGD1L1 | 350VKGD1L1-Double Acting | CIL 4 Tank 1 Oxygen Injection Pump Discharge Valve | 21-0412-CON-RL1-300 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 14 | Detail 4 | FC | Double Acting | Single Acting | SV21053 | No | Position Switches | - | F21-CP-402 | 2000-PP007-B02-10357 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10084 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F21.20 | F21.20.09 | XV21053 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 21 | 56 | XV 21056 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | CIL 4 Tank 1 Oxygen Injection Pump Discharge Drain Valve | 21-0412-CON-RL1-300 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV21056 | No | Position Switches | - | F21-CP-402 | 2000-PP007-B02-10357 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F21.20 | F21.20.09 | XV21056 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 21 | 91 | XV 21091 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting | CIL 4 Tank 2 Oxygen Injection Pump Suction Valve | 21-0413-CON-RL1-400 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10007 | Stage 2 | Greenfield | CON | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 16 | Detail 4 | FC | Double Acting | Single Acting | SV21091 | No | Position Switches | - | F21-CP-403 | 2000-PP007-B02-10358 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10089 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F21.20 | F21.20.09 | XV21091 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 21 | 92 | XV 21092 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | CIL 4 Tank 2 Oxygen Injection Pump Suction Drain Valve | 21-0413-CON-RL1-400 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10007 | Stage 2 | Greenfield | CON | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV21092 | No | Position Switches | - | F21-CP-403 | 2000-PP007-B02-10358 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F21.20 | F21.20.09 | XV21092 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 21 | 93 | XV 21093 | 350 | VKGD1L1 | 350VKGD1L1-Double Acting | CIL 4 Tank 2 Oxygen Injection Pump Discharge Valve | 21-0414-CON-RL1-300 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10007 | Stage 2 | Greenfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 14 | Detail 4 | FC | Double Acting | Single Acting | SV21093 | No | Position Switches | - | F21-CP-403 | 2000-PP007-B02-10358 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10084 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F21.20 | F21.20.09 | XV21093 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 21 | 96 | XV 21096 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | CIL 4 Tank 2 Oxygen Injection Pump Discharge Drain Valve | 21-0414-CON-RL1-300 | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10007 | Stage 2 | Greenfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV21096 | No | Position Switches | - | F21-CP-403 | 2000-PP007-B02-10358 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F21.20 | F21.20.09 | XV21096 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 21 | 136 | XV 21136 | 50 | VB03S1 | 50VB03S1-Double Acting | CIL 4 Loaded Carbon Screen Spray Water Valve | 21-0421-BW-SS3-50 | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | BW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV21136 | No | Position Switches | - | F22-CP-401 | 2000-PP007-B02-10359 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10008 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F24.40 | F24.40.11 | XV21136 | VB0 | Hypersaline Water | AS2129 Table E
1 | XV | 21 | 280 | XV 21280 | 50 | VB03S1 | 50VB03S1-Double Acting-Solenoid on Valve | CIL 4 Carbon Sizing Screen Spray Water Valve | 21-0456-BW-SS3-50 | 2000-F21-PID-PR-10003 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | BW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV21280 | No | Position Switches | Solenoid on Valve | F21-CP-005 | N/A | PP007 | ME007 | Solenoid to be removed from valve on site and a new solenoid added to F21-CP-005. | Emerson | K-BALL F182 | 2000-PP007-B02-10107 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F24.40 | F24.40.11 | XV21280 | VB0 | Hypersaline Water | AS2129 Table E
0 | XV | 21 | 013A | XV 21013A |  | N/A |  | CIL 4 Feed Distribution Box Isolation Gate 1 |  | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21013A | No | Position Switches | - | F21-CP-001 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21013A | N/A | #N/A | #N/A
0 | XV | 21 | 013B | XV 21013B |  | N/A |  | CIL 4 Feed Distribution Box Isolation Gate 2 |  | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21013B | No | Position Switches | - | F21-CP-001 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21013B | N/A | #N/A | #N/A
0 | XV | 21 | 014A | XV 21014A |  | N/A |  | CIL 4 Feed Distribution Box Isolation Gate 3 |  | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21014A | No | Position Switches | - | F21-CP-001 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21014A | N/A | #N/A | #N/A
0 | XV | 21 | 014B | XV 21014B |  | N/A |  | CIL 4 Feed Distribution Box Isolation Gate 4 |  | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21014B | No | Position Switches | - | F21-CP-001 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21014B | N/A | #N/A | #N/A
0 | XV | 21 | 081A | XV 21081A |  | N/A |  | CIL 4 Tank 1 Discharge Launder Isolation Gate 1 |  | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21081A | No | Position Switches | - | F21-CP-001 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21081A | N/A | #N/A | #N/A
0 | XV | 21 | 081B | XV 21081B |  | N/A |  | CIL 4 Tank 1 Discharge Launder Isolation Gate 2 |  | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21081B | No | Position Switches | - | F21-CP-001 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21081B | N/A | #N/A | #N/A
0 | XV | 21 | 082A | XV 21082A |  | N/A |  | CIL 4 Tank 1 Discharge Launder Isolation Gate 3 |  | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21082A | No | Position Switches | - | F21-CP-001 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21082A | N/A | #N/A | #N/A
0 | XV | 21 | 082B | XV 21082B |  | N/A |  | CIL 4 Tank 1 Discharge Launder Isolation Gate 4 |  | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21082B | No | Position Switches | - | F21-CP-001 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21082B | N/A | #N/A | #N/A
0 | XV | 21 | 121A | XV 21121A |  | N/A |  | CIL 4 Tank 2 Discharge Launder Isolation Gate 1 |  | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21121A | No | Position Switches | - | F21-CP-002 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21121A | N/A | #N/A | #N/A
0 | XV | 21 | 121B | XV 21121B |  | N/A |  | CIL 4 Tank 2 Discharge Launder Isolation Gate 2 |  | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21121B | No | Position Switches | - | F21-CP-002 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21121B | N/A | #N/A | #N/A
0 | XV | 21 | 122A | XV 21122A |  | N/A |  | CIL 4 Tank 2 Discharge Launder Isolation Gate 3 |  | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21122A | No | Position Switches | - | F21-CP-002 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21122A | N/A | #N/A | #N/A
0 | XV | 21 | 122B | XV 21122B |  | N/A |  | CIL 4 Tank 2 Discharge Launder Isolation Gate 4 |  | 2000-F21-PID-PR-10001 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21122B | No | Position Switches | - | F21-CP-002 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21122B | N/A | #N/A | #N/A
0 | XV | 21 | 161A | XV 21161A |  | N/A |  | CIL 4 Tank 3 Discharge Launder Isolation Gate 1 |  | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21161A | No | Position Switches | - | F21-CP-002 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21161A | N/A | #N/A | #N/A
0 | XV | 21 | 161B | XV 21161B |  | N/A |  | CIL 4 Tank 3 Discharge Launder Isolation Gate 2 |  | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21161B | No | Position Switches | - | F21-CP-002 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21161B | N/A | #N/A | #N/A
0 | XV | 21 | 162A | XV 21162A |  | N/A |  | CIL 4 Tank 3 Discharge Launder Isolation Gate 3 |  | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21162A | No | Position Switches | - | F21-CP-002 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21162A | N/A | #N/A | #N/A
0 | XV | 21 | 162B | XV 21162B |  | N/A |  | CIL 4 Tank 3 Discharge Launder Isolation Gate 4 |  | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21162B | No | Position Switches | - | F21-CP-002 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21162B | N/A | #N/A | #N/A
0 | XV | 21 | 181A | XV 21181A |  | N/A |  | CIL 4 Tank 4 Discharge Launder Isolation Gate 1 |  | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21181A | No | Position Switches | - | F21-CP-003 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21181A | N/A | #N/A | #N/A
0 | XV | 21 | 181B | XV 21181B |  | N/A |  | CIL 4 Tank 4 Discharge Launder Isolation Gate 2 |  | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21181B | No | Position Switches | - | F21-CP-003 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21181B | N/A | #N/A | #N/A
0 | XV | 21 | 182A | XV 21182A |  | N/A |  | CIL 4 Tank 4 Discharge Launder Isolation Gate 3 |  | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21182A | No | Position Switches | - | F21-CP-003 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21182A | N/A | #N/A | #N/A
0 | XV | 21 | 182B | XV 21182B |  | N/A |  | CIL 4 Tank 4 Discharge Launder Isolation Gate 4 |  | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21182B | No | Position Switches | - | F21-CP-003 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.01 | XV21182B | N/A | #N/A | #N/A
0 | XV | 21 | 201A | XV 21201A |  | N/A |  | CIL 4 Tank 5 Discharge Launder Isolation Gate 1 |  | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21201A | No | Position Switches | - | F21-CP-003 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21201A | N/A | #N/A | #N/A
0 | XV | 21 | 201B | XV 21201B |  | N/A |  | CIL 4 Tank 5 Discharge Launder Isolation Gate 2 |  | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21201B | No | Position Switches | - | F21-CP-003 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21201B | N/A | #N/A | #N/A
0 | XV | 21 | 202A | XV 21202A |  | N/A |  | CIL 4 Tank 5 Discharge Launder Isolation Gate 3 |  | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21202A | No | Position Switches | - | F21-CP-003 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21202A | N/A | #N/A | #N/A
0 | XV | 21 | 202B | XV 21202B |  | N/A |  | CIL 4 Tank 5 Discharge Launder Isolation Gate 4 |  | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21202B | No | Position Switches | - | F21-CP-003 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21202B | N/A | #N/A | #N/A
0 | XV | 21 | 241A | XV 21241A |  | N/A |  | CIL 4 Tank 6 Discharge Launder Isolation Gate 1 |  | 2000-F21-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21241A | No | Position Switches | - | F21-CP-004 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21241A | N/A | #N/A | #N/A
0 | XV | 21 | 241B | XV 21241B |  | N/A |  | CIL 4 Tank 6 Discharge Launder Isolation Gate 2 |  | 2000-F21-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21241B | No | Position Switches | - | F21-CP-004 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21241B | N/A | #N/A | #N/A
0 | XV | 21 | 242A | XV 21242A |  | N/A |  | CIL 4 Tank 6 Discharge Launder Isolation Gate 3 |  | 2000-F21-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21242A | No | Position Switches | - | F21-CP-004 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21242A | N/A | #N/A | #N/A
0 | XV | 21 | 242B | XV 21242B |  | N/A |  | CIL 4 Tank 6 Discharge Launder Isolation Gate 4 |  | 2000-F21-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21242B | No | Position Switches | - | F21-CP-004 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21242B | N/A | #N/A | #N/A
0 | XV | 21 | 261A | XV 21261A |  | N/A |  | CIL 4 Tank 7 Discharge Launder Isolation Gate 1 |  | 2000-F21-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21261A | No | Position Switches | - | F21-CP-004 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21261A | N/A | #N/A | #N/A
0 | XV | 21 | 261B | XV 21261B |  | N/A |  | CIL 4 Tank 7 Discharge Launder Isolation Gate 2 |  | 2000-F21-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21261B | No | Position Switches | - | F21-CP-004 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21261B | N/A | #N/A | #N/A
0 | XV | 21 | 262A | XV 21262A |  | N/A |  | CIL 4 Tank 7 Discharge Launder Isolation Gate 3 |  | 2000-F21-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21262A | No | Position Switches | - | F21-CP-004 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21262A | N/A | #N/A | #N/A
0 | XV | 21 | 262B | XV 21262B |  | N/A |  | CIL 4 Tank 7 Discharge Launder Isolation Gate 4 |  | 2000-F21-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21262B | No | Position Switches | - | F21-CP-004 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21262B | N/A | #N/A | #N/A
0 | XV | 21 | 271A | XV 21271A |  | N/A |  | CIL 4 Tank 8 Discharge Launder Isolation Gate 1 |  | 2000-F21-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21271A | No | Position Switches | - | F21-CP-005 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21271A | N/A | #N/A | #N/A
0 | XV | 21 | 271B | XV 21271B |  | N/A |  | CIL 4 Tank 8 Discharge Launder Isolation Gate 2 |  | 2000-F21-PID-PR-10003 | 2000-F24-PID-PR-10024 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV21271B | No | Position Switches | - | F21-CP-005 | N/A | ME007 | ME007 | Launder Gate | [6 empty] | F21.20 | F21.20.03 | XV21271B | N/A | #N/A | #N/A
0 | HV | 22 | 244 | HV 22244 | 150 | VBFD1L2 | 150VBFD1L2-Manual | Kiln Abatement System Cooling Water Pump 1 Suction Manual Valve | 24-2050-COW-MSG1-150 | 2000-F22-PID-PR-10008 | N/A | Stage 2 | Greenfield | COW | MSG1 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 6 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10055 | Emerson | Manual Lever | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.01 | HV22244 | VBF | Cooling Water | AS2129 Table D
0 | HV | 22 | 245 | HV 22245 | 100 | VBFD1L2 | 100VBFD1L2-Manual | Kiln Abatement System Cooling Water Pump 1 Discharge Manual Valve | 24-2051-COW-MSG1-100 | 2000-F22-PID-PR-10008 | N/A | Stage 2 | Greenfield | COW | MSG1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 4 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10039 | Emerson | Manual Lever | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.01 | HV22245 | VBF | Cooling Water | AS2129 Table D
0 | HV | 22 | 246 | HV 22246 | 150 | VBFD1L2 | 150VBFD1L2-Manual | Kiln Abatement System Cooling Water Pump 2 Suction Manual Valve | 24-2052-COW-MSG1-150 | 2000-F22-PID-PR-10008 | N/A | Stage 2 | Greenfield | COW | MSG1 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 6 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10055 | Emerson | Manual Lever | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.01 | HV22246 | VBF | Cooling Water | AS2129 Table D
0 | HV | 22 | 247 | HV 22247 | 100 | VBFD1L2 | 100VBFD1L2-Manual | Kiln Abatement System Cooling Water Pump 2 Discharge Manual Valve | 24-2053-COW-MSG1-100 | 2000-F22-PID-PR-10008 | N/A | Stage 2 | Greenfield | COW | MSG1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 4 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10039 | Emerson | Manual Lever | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.01 | HV22247 | VBF | Cooling Water | AS2129 Table D
0 | PCV | 22 | 121 | PCV 22121 | 100 | VDE1S2 | 100VDE1S2-Double Acting-Positioner | CIL 4 Elution Recovery Heat Exchanger To Eluate Tanks Pressure Control Valve | 22-0500-PE-SS2-100-TI | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PE | SS2 | 100-TI | 0 | 96 | 430 | 430 | 430 | N/A | N/A | N/A | 1.1 | 1400 | 4 | Detail 1 | FO | Double Acting | Manual Isolation | No Solenoid | Yes | No | - | F22-CP-402 | 2000-PP007-B02-10360 | PP007 | PP007 | Set Pressure @ 430kPag at 100°C | KDV | SERIES 2AHRT | 2000-PP007-B02-10155 | N/A | N/A |  | F22.20 | F22.20.03 | PCV22121 | VDE | Pregnant Eluate | AS2129 Table E
0 | PRV | 22 | 35 | PRV 22035 | 32 | N/A |  | Elution Air Receiver |  | 2000-F24-PID-PR-10031 | N/A | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME024 | N/A | Vendor Supply Set Pressure @ 1000 kPag | NUOVA General Industrial | F32 OT |  |  |  |  | F22.10 | F22.10.30 | PRV22035 | N/A | #N/A | #N/A
0 | PRV | 22 | 41 | PRV 22041 | 80 | PRV | 80PRV-N/A-Reagent | CIL 4 Elution & Acid Wash Column Pressure Relief Valve | 22-0472-HPE-SS7-80 | 2000-F22-PID-PR-10001 | N/A | Stage 2 | Greenfield | HPE | SS7 | 80 | N/A | 120 | 500 | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 500 kPag | Calorex Pty Ltd | Roma Fig-161 | 2000-PP007-B02-10415 | N/A | N/A | N/A | F22.20 | F22.20.02 | PRV22041 | PRV | Hydrochloric Acid / Pregnant Eluate | AS2129 Table E
0 | PRV | 22 | 148 | PRV 22148 | 100 | PRV | 100PRV-N/A-Reagent | CIL 4 Elution Pumps Pressure Relief Valve | 22-1531-PE-SS2-100-TI | 2000-F22-PID-PR-10002 | N/A | Stage 2 | Greenfield | PE | SS2 | 100-TI | N/A | 77.4 | 900 | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 900 kPag | Calorex Pty Ltd | Roma Fig-161 | 2000-PP007-B02-10413 | N/A | N/A | N/A | F22.20 | F22.20.03 | PRV22148 | PRV | Pregnant Eluate | AS2129 Table E
0 | SV | 22 | 260 | SV 22260 | 25 | SV | 25SV-Solenoid-FO | CIL 4 Barren Carbon Pump Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Greenfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F22.20 | F22.20.06 | SV22260 | SV | Hypersaline Water | AS2129 Table E
0 | TCV | 22 | 228 | TCV 22228 | 100 | VTWD1C1 | 100VTWD1C1-Double Acting-Positioner-Pattern 3 | Kiln Mercury Abatement Cooling Water Temperature Control Valve | 22-1550-COW-MSG1-100-TI | 2000-F22-PID-PR-10007 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | COW | MSG1 | 100-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 4 | Detail 1 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | No | Pattern 3 | F22-CP-405 | 2000-PP007-B02-10363 | PP007 | PP007 | No pneumatic panel to be provided. Valve model KTM-MB11 T-Port with Flow Plan F - Pattern 3. | Emerson | KTM MB11 T Port | 2000-PP007-B02-10048 | Emerson | KTM AWN13 | SMC IP8100-031-J Included | F22.20 | F22.20.08 | TCV22228 | VTW | Cooling Water | AS2129 Table D
0 | XV | 22 | 11 | XV 22011 | 200 | VBE1N1 | 200VBE1N1-Spring Return | Loaded Carbon to CIL 4 Elution & Acid Wash Column Valve | 22-0471-SC-MS2-200 | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | SC | MS2 | 200 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 1400 | 8 | Detail 8 | FC | Spring Return | Single Acting | SV22011 | No | Position Switches | - | F22-CP-401 | 2000-PP007-B02-10359 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10066 | Emerson | KEYSTONE F89-240 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.02 | XV22011 | VBE | Carbon Slurry | AS2129 Table E
0 | XV | 22 | 16 | XV 22016 | 150 | VBE1N1 | 150VBE1N1-Spring Return | CIL 4 Elution & Acid Wash Column to CIL 4 Elution Filter Valve | 22-1809-HPE-SS7-150-TI | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | HPE | SS7 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 6 | Detail 8 | FC | Spring Return | Single Acting | SV22016 | No | Position Switches | - | F22-CP-401 | 2000-PP007-B02-10359 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10051 | Emerson | KEYSTONE F89-140 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.02 | XV22016 | VBE | Hydrochloric Acid / Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 21 | XV 22021 | 150 | VBFE1L2 | 150VBFE1L2-Double Acting | CIL 4 Carbon Eductor Pump Scheme Water Valve | 22-0486-PSW-MS2-150 | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PSW | MS2 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 6 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC22021 | No | Position Switches | - | F22-CP-407 | 2000-PP007-B02-10365 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10059 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.12 | XV22021 | VBF | Process Scheme Water | AS2129 Table E
0 | XV | 22 | 22 | XV 22022 | 100 | VBE1N1 | 100VBE1N1-Spring Return | CIL 4 Carbon Eductor Pump to CIL 4 Elution & Acid Wash Column Valve | 22-0488-PSW-MS2-100 | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PSW | MS2 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 4 | Detail 8 | FC | Spring Return | Single Acting | SV22022 | No | Position Switches | - | F22-CP-402 | 2000-PP007-B02-10360 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10037 | Emerson | KEYSTONE F89-052 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.12 | XV22022 | VBE | Process Scheme Water | AS2129 Table E
0 | XV | 22 | 24 | XV 22024 | 100 | VBE1N1 | 100VBE1N1-Spring Return | CIL 4 Elution & Acid Wash Column Dilute Hydrochloric Acid Inlet Valve | 22-0547-HCL-SS7-100 | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | HCL | SS7 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 8 | FC | Spring Return | Single Acting | SV22024 | No | Position Switches | - | F22-CP-402 | 2000-PP007-B02-10360 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10037 | Emerson | KEYSTONE F89-052 | TOPWORX TVF-M2WGNMM | F72.70 | F72.70.03 | XV22024 | VBE | Hydrochloric Acid | AS2129 Table E
0 | XV | 22 | 26 | XV 22026 | 100 | VBE1N1 | 100VBE1N1-Spring Return | CIL 4 Carbon Eductor Pump Outlets To Screens Valve | 22-0487-PSW-MS2-150 | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PSW | MS2 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 4 | Detail 8 | FC | Spring Return | Single Acting | SV22026 | No | Position Switches | - | F22-CP-402 | 2000-PP007-B02-10360 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10037 | Emerson | KEYSTONE F89-052 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.12 | XV22026 | VBE | Process Scheme Water | AS2129 Table E
0 | XV | 22 | 30 | XV 22030 | 150 | VBE1N1 | 150VBE1N1-Spring Return | CIL 4 Elution & Acid Wash Column Pregnant Eluate Inlet Valve | 22-0510-PE-SS2-150-TI | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PE | SS2 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 6 | Detail 8 | FO | Spring Return | Single Acting | SV22030 | No | Position Switches | - | F22-CP-402 | 2000-PP007-B02-10360 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10051 | Emerson | KEYSTONE F89-140 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.02 | XV22030 | VBE | Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 34 | XV 22034 | 150 | VBE1N1 | 150VBE1N1-Spring Return | CIL 4 Elution & Acid Wash Column Inlet Drain Valve | 22-0495-HPE-SS7-150 | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | HPE | SS7 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 6 | Detail 8 | FC | Spring Return | Single Acting | SV22034 | No | Position Switches | - | F22-CP-402 | 2000-PP007-B02-10360 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10051 | Emerson | KEYSTONE F89-140 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.02 | XV22034 | VBE | Hydrochloric Acid / Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 51 | XV 22051 | 150 | VBE1N1 | 150VBE1N1-Spring Return | CIL 4 Elution Filters Acid Rinse Water to Final Collection Box Valve | 22-0676-HPE-SS7-150-TI | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | HPE | SS7 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 6 | Detail 8 | FC | Spring Return | Single Acting | SV22051 | No | Position Switches | - | F22-CP-401 | 2000-PP007-B02-10359 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10051 | Emerson | KEYSTONE F89-140 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.02 | XV22051 | VBE | Hydrochloric Acid / Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 54 | XV 22054 | 150 | VBE1N1 | 150VBE1N1-Spring Return | CIL 4 Elution Filters Pregnant Eluate to CIL 4 Elution Recovery Heat Exchanger Valve | 22-0676-HPE-SS7-150-TI | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | HPE | SS7 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 6 | Detail 8 | FC | Spring Return | Single Acting | SV22054 | No | Position Switches | - | F22-CP-401 | 2000-PP007-B02-10359 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10051 | Emerson | KEYSTONE F89-140 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.02 | XV22054 | VBE | Hydrochloric Acid / Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 57 | XV 22057 | 150 | VBE1N1 | 150VBE1N1-Spring Return | CIL 4 Elution & Acid Wash Column Drain to Screens Valve | 22-0491-SC-SS7-150 | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | SC | SS7 | 150 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 1400 | 6 | Detail 8 | FC | Spring Return | Single Acting | SV22057 | No | Position Switches | - | F22-CP-402 | 2000-PP007-B02-10360 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10051 | Emerson | KEYSTONE F89-140 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.02 | XV22057 | VBE | Carbon Slurry | AS2129 Table E
0 | XV | 22 | 61 | XV 22061 | 150 | VKGE1L1 | 150VKGE1L1-Double Acting | CIL 4 Elution & Acid Wash Column Drain to CIL 4 Regen Kiln Dewatering Screen Feed Box Valve | 22-0491-SC-SS7-150 | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | SC | SS7 | 150 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 1400 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC22061 | No | Position Switches | - | F22-CP-403 | 2000-PP007-B02-10361 | PP007 | PP007 |  | Emerson | Clarkson KGA+ | 2000-PP007-B02-10065 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F22.20 | F22.20.12 | XV22061 | VKG | Carbon Slurry | AS2129 Table E
0 | XV | 22 | 62 | XV 22062 | 150 | VKGE1L1 | 150VKGE1L1-Double Acting | CIL 4 Elution & Acid Wash Column Drain to CIL 4 Carbon Sizing Screen Feed Box Valve | 22-0492-SC-SS7-150 | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | SC | SS7 | 150 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 1400 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC22062 | No | Position Switches | - | F22-CP-403 | 2000-PP007-B02-10361 | PP007 | PP007 |  | Emerson | Clarkson KGA+ | 2000-PP007-B02-10065 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F22.20 | F22.20.12 | XV22062 | VKG | Carbon Slurry | AS2129 Table E
0 | XV | 22 | 72 | XV 22072 | 150 | VBFD1L5 | 150VBFD1L5-Spring Return | CIL 4 Elution Area Sump Pump To CIL 4 Feed Distribution Box Valve | 22-0482-FD-PE10-160 | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | FD | PE10 | 160 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 6 | Detail 8 | FC | Spring Return | Single Acting | SV22072 | No | Position Switches | - | F22-CP-403 | 2000-PP007-B02-10361 | PP007 | PP007 |  | Emerson | F990 | 2000-PP007-B02-10056 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM | F22.10 | F22.10.21 | XV22072 | VBF | Floor Drainage | AS2129 Table D PN10
0 | XV | 22 | 73 | XV 22073 | 100 | VBFD1L5 | 100VBFD1L5-Double Acting | CIL 4 Elution Area Sump Pump To Final Tails Collection Box Valve | 22-0680-FD-PE10-110 | 2000-F22-PID-PR-10001 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | FD | PE10 | 110 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 4 | Detail 7 | FO | Double Acting | Single Acting | SV22073 | No | Position Switches | - | F22-CP-403 | 2000-PP007-B02-10361 | PP007 | PP007 |  | Emerson | F990 | 2000-PP007-B02-10040 | Emerson | KEYSTONE F89-006 | TOPWORX TVF-M2WGNMM | F22.10 | F22.10.21 | XV22073 | VBF | Floor Drainage | AS2129 Table D PN10
0 | XV | 22 | 124 | XV 22124 | 100 | VBE1S1 | 100VBE1S1-Spring Return | CIL 4 Elution Recovery Heat Exchanger To CIL 4 Eluate Circulation Tank Valve | 22-0500-PE-SS2-100-TI | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PE | SS2 | 100-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 4 | Detail 8 | FC | Spring Return | Single Acting | SV22124 | No | Position Switches | - | F22-CP-402 | 2000-PP007-B02-10360 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10151 |  |  |  | F22.20 | F22.20.03 | XV22124 | VBE | Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 138 | XV 22138 | 50 | VB03S1 | 50VB03S1-Spring Return | CIL 4 Loaded Carbon Transfer Vessel Scheme Water Inlet Valve | 22-1525-PSW-MS2-50 | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PSW | MS2 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 2 | Detail 8 | FC | Spring Return | Single Acting | SV22138 | No | Position Switches | - | F22-CP-401 | 2000-PP007-B02-10359 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10010 | Emerson | KEYSTONE F89-009 | TOPWORX TVF-M2WGNMM | F24.70 | F24.70.02 | XV22138 | VB0 | Process Scheme Water | AS2129 Table E
0 | XV | 22 | 139 | XV 22139 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | CIL 4 Loaded Carbon Transfer Vessel Drain Valve | 22-0471-SC-PE10-225 | 2000-F21-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | FT | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 8 | Detail 4 | FC | Double Acting | Single Acting | SV22139 | No | Position Switches | - | F22-CP-401 | 2000-PP007-B02-10359 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F22.20 | F22.20.11 | XV22139 | VKG | Final Tailings | AS2129 Table D
0 | XV | 22 | 141 | XV 22141 | 100 | VBFE1S4 | 100VBFE1S4-Spring Return | CIL 4 Lean Eluate Tank Pregnant Eluate Inlet Valve | 22-0501-PE-SS2-100-TI | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PE | SS2 | 100-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 4 | Detail 8 | FC | Spring Return | Single Acting | SV22141 | No | Position Switches | - | F22-CP-402 | 2000-PP007-B02-10360 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10045 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.03 | XV22141 | VBF | Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 142 | XV 22142 | 100 | VBFE1L2 | 100VBFE1L2-Spring Return | CIL 4 Lean Eluate Tank Scheme Water Inlet Valve | 22-0513-PSW-MS2-100 | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PSW | MS2 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 4 | Detail 8 | FC | Spring Return | Single Acting | SV22142 | No | Position Switches | - | F22-CP-407 | 2000-PP007-B02-10365 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10043 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.09 | XV22142 | VBF | Process Scheme Water | AS2129 Table E
0 | XV | 22 | 144 | XV 22144 | 150 | VBFE1S4 | 150VBFE1S4-Spring Return | CIL 4 Lean Eluate Tank Discharge Valve | 22-0503-PE-SS2-150-TI | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PE | SS2 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 6 | Detail 8 | FC | Spring Return | Single Acting | SV22144 | No | Position Switches | - | F22-CP-404 | 2000-PP007-B02-10362 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10061 | Emerson | KEYSTONE F89-032 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.09 | XV22144 | VBF | Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 145 | XV 22145 | 100 | VBFE1S4 | 100VBFE1S4-Spring Return | CIL 4 Eluate Expansion Tank Pregnant Eluate Inlet Valve | 22-1266-PE-SS2-100-TI | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PE | SS2 | 100-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 4 | Detail 8 | FC | Spring Return | Single Acting | SV22145 | No | Position Switches | - | F22-CP-402 | 2000-PP007-B02-10360 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10045 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.03 | XV22145 | VBF | Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 147 | XV 22147 | 150 | VBFE1S4 | 150VBFE1S4-Spring Return | CIL 4 Eluate Expansion Tank Discharge Valve | 22-1264-PE-SS2-150-TI | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PE | SS2 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 6 | Detail 8 | FC | Spring Return | Single Acting | SV22147 | No | Position Switches | - | F22-CP-404 | 2000-PP007-B02-10362 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10061 | Emerson | KEYSTONE F89-032 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.09 | XV22147 | VBF | Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 151 | XV 22151 | 100 | VBFE1L2 | 100VBFE1L2-Spring Return | CIL 4 Elution Water Tank Scheme Water Inlet Valve | 22-0512-PSW-MS2-100 | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PSW | MS2 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 4 | Detail 8 | FC | Spring Return | Single Acting | SV22151 | No | Position Switches | - | F22-CP-407 | 2000-PP007-B02-10365 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10043 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.09 | XV22151 | VBF | Process Scheme Water | AS2129 Table E
0 | XV | 22 | 153 | XV 22153 | 150 | VBFE1S4 | 150VBFE1S4-Spring Return | CIL 4 Elution Water Tank Discharge Valve | 22-0505-PE-SS2-150-TI | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PE | SS2 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 6 | Detail 8 | FC | Spring Return | Single Acting | SV22153 | No | Position Switches | - | F22-CP-404 | 2000-PP007-B02-10362 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10061 | Emerson | KEYSTONE F89-032 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.09 | XV22153 | VBF | Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 161 | XV 22161 | 150 | VBE1S1 | 150VBE1S1-Double Acting | CIL 4 Elution Pump 1 Suction Valve | 22-0505-PE-SS2-150-TI | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PE | SS2 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 6 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC22161 | No | Position Switches | - | F22-CP-404 | 2000-PP007-B02-10362 | PP007 | PP007 |  | Emerson | K-BALL F194 | 2000-PP007-B02-10052 | Emerson | KEYSTONE F89-051 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.09 | XV22161 | VBE | Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 162 | XV 22162 | 100 | VBE1S1 | 100VBE1S1-Double Acting | CIL 4 Elution Pump 1 Discharge Valve | 22-0507-PE-SS2-100-TI | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PE | SS2 | 100-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 4 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC22162 | No | Position Switches | - | F22-CP-404 | 2000-PP007-B02-10362 | PP007 | PP007 |  | Emerson | K-BALL F194 | 2000-PP007-B02-10038 | Emerson | KEYSTONE F89-020 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.09 | XV22162 | VBE | Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 163 | XV 22163 | 150 | VBE1S1 | 150VBE1S1-Double Acting | CIL 4 Elution Pump 2 Suction Valve | 22-0506-PE-SS2-150-TI | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PE | SS2 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 6 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC22163 | No | Position Switches | - | F22-CP-404 | 2000-PP007-B02-10362 | PP007 | PP007 |  | Emerson | K-BALL F194 | 2000-PP007-B02-10052 | Emerson | KEYSTONE F89-051 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.09 | XV22163 | VBE | Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 164 | XV 22164 | 100 | VBE1S1 | 100VBE1S1-Double Acting | CIL 4 Elution Pump 2 Discharge Valve | 22-0508-PE-SS2-100-TI | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PE | SS2 | 100-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 4 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC22164 | No | Position Switches | - | F22-CP-404 | 2000-PP007-B02-10362 | PP007 | PP007 |  | Emerson | K-BALL F194 | 2000-PP007-B02-10038 | Emerson | KEYSTONE F89-020 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.09 | XV22164 | VBE | Pregnant Eluate | AS2129 Table E
0 | XV | 22 | 181 | XV 22181 | 50 | VBE1C1 | 50VBE1C1-Spring Return | Cyanide to CIL Elution Pumps Valve | 22-0489-CN-MS2-50 | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | CN | MS2 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 2 | Detail 8 | FC | Spring Return | Single Acting | SV22181 | No | Position Switches | - | F22-CP-407 | 2000-PP007-B02-10365 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10014 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.09 | XV22181 | VBE | Cyanide Solution | AS2129 Table E
0 | XV | 22 | 191 | XV 22191 | 40 | VBD1C1 | 40VBD1C1-Spring Return | Caustic to CIL Elution Pumps Valve | 22-0490-NS-MS1-40 | 2000-F22-PID-PR-10002 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | NS | MS1 | 40 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 1 | Detail 8 | FC | Spring Return | Single Acting | SV22191 | No | Position Switches | - | F22-CP-407 | 2000-PP007-B02-10365 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10007 | Emerson | KEYSTONE F89-009 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.09 | XV22191 | VBD | Caustic Soda | AS2129 Table D
0 | XV | 22 | 194 | XV 22194 | 80 | VBFD1S2 | 80VBFD1S2-Double Acting | CIL 4 Barren Carbon Pump Suction Valve | 22-0524-BW-SS1-80 | 2000-F22-PID-PR-10005 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | BW | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 7 | FO | Double Acting | Single Acting | SV22194 | No | Position Switches | - | F22-CP-405 | 2000-PP007-B02-10363 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10028 | Emerson | KEYSTONE F89-004 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.06 | XV22194 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 22 | 201 | XV 22201 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | CIL 4 Carbon Quench Hopper to CIL 4 Barren Carbon Pump Valve | 22-0519-SC-SS1-150 | 2000-F22-PID-PR-10005 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | SC | SS1 | 150 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 6 | Detail 4 | FC | Double Acting | Single Acting | SV22201 | No | Position Switches | - | F22-CP-405 | 2000-PP007-B02-10363 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F22.20 | F22.20.05 | XV22201 | VKG | Carbon Slurry | AS2129 Table D
0 | XV | 22 | 202 | XV 22202 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | CIL 4 Barren Carbon Pump Suction Drain Valve | 22-0519-SC-SS1-150 | 2000-F22-PID-PR-10005 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | SC | SS1 | 150 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC22202 | No | Position Switches | - | F22-CP-405 | 2000-PP007-B02-10363 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F22.20 | F22.20.06 | XV22202 | VKG | Carbon Slurry | AS2129 Table D
0 | XV | 22 | 207 | XV 22207 | 80 | VBFE1L1 | 80VBFE1L1-Double Acting | CIL 4 Carbon Quench Hopper Water Inlet Valve | 22-0527-PSW-MS2-80 | 2000-F22-PID-PR-10005 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PSW | MS2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 3 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC22207 | No | Position Switches | - | F22-CP-405 | 2000-PP007-B02-10363 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10030 | Emerson | KEYSTONE F89-004 | TOPWORX TVF-M2WGNMM | F22.20 | F22.20.05 | XV22207 | VBF | Process Scheme Water | AS2129 Table E
0 | XV | 22 | 231 | XV 22231 | 100 | VBFD1L1 | 100VBFD1L1-Double Acting | Kiln Mercury Abatement Off-Gas Cooler Cooling Water Inlet TCV Bypass Valve | 22-2475-COW-MSG1-100-TI | 2000-F22-PID-PR-10007 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | COW | MSG1 | 100-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 4 | Detail 7 | FO | Double Acting | Single Acting | SV22231 | No | Position Switches | - | F22-CP-405 | 2000-PP007-B02-10363 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10148 | Emerson | KEYSTONE F89-004 | SMC IP8100 031 J (4-20mA) | F22.20 | F22.20.08 | XV22231 | VBF | Cooling Water | AS2129 Table D
0 | XV | 22 | 241 | XV 22241 | 50 | VB03S1 | 50VB03S1-Double Acting | Kiln Abatement System Cooling Water Tank Scheme Water Valve | 22-2035-PSW-MSG3-50 | 2000-F22-PID-PR-10008 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | PSW | MSG3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV22241 | No | Position Switches | - | F22-CP-406 | 2000-PP007-B02-10364 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10008 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F22.20 | F22.20.01 | XV22241 | VB0 | Process Scheme Water | AS2129 Table E
0 | XV | 22 | 251 | XV 22251 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | CIL 4 Carbon Regeneration Kiln Feed Hopper Discharge Valve | 22-2275-SC-PE10-225 | 2000-F22-PID-PR-10005 | 2000-F24-PID-PR-10031 | Stage 2 | Greenfield | SC | PE10 | 225 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 8 | Detail 4 | FC | Double Acting | Single Acting | SV22251 | No | Position Switches | - | F22-CP-405 | 2000-PP007-B02-10363 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F22.20 | F22.20.05 | XV22251 | VKG | Carbon Slurry | AS2129 Table D PN10
0 | FCV | 23 | 405 | FCV 23405 | 350 | VBFD1S1 | 350VBFD1S1-Double Acting-Positioner | Final Tails Tank Saline Water Feed Flow Control Valve |  | 2000-F23-PID-PR-10001 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 350 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 14 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F23-CP-402 | 2000-PP007-B02-10334 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10082 | Emerson | KEYSTONE F89-085 | SMC IP8100 031 J (4-20mA) | F24.50 | F24.50.01 | FCV23405 | VBF | Hypersaline Water | AS2129 Table D
0 | FCV | 23 | 456 | FCV 23456 | 350 | VBFE1S1 | 350VBFE1S1-Double Acting-Positioner | FIM 1 Valve Station Feed Flow Control Valve | 23-2537-PW-PE16-355 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | PW | PE16 | 355 | 0 | 700 | 550 | 550 | 10 | N/A | N/A | N/A | 1.07 | 1400 | 14 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F23-CP-405 | 2000-PP007-B02-10388 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10128 |  |  |  | F24.20 | F24.20.01 | FCV23456 | VBF | Hypersaline Water | AS2129 Table E PN16
0 | HV | 23 | 420 | HV 23420 | 600 | VKGE1L1 | 600VKGE1L1-Manual-Chain Wheel | Final Tails Slurry Line D Isolation Manual Valve | 23-0545-FT-PE16-630 | 2000-F23-PID-PR-10002 | N/A | Stage 1 | Greenfield | FT | PE16 | 630 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 24 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | Chain Wheel | N/A | N/A | PP007 | N/A | Manual Valve with positioner feedback and chain wheel | Emerson | Clarkson KGA+ | 2000-PP007-B02-10121 | Emerson | Bevel gear with chainwheel | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.01 | HV23420 | VKG | Final Tailings | AS2129 Table E PN16
0 | HV | 23 | 433 | HV 23433 | 600 | VKGE1L1 | 600VKGE1L1-Manual-Chain Wheel | Final Tails Slurry Line B Isolation Manual Valve | 23-0584-FT-PE16-630 | 2000-F23-PID-PR-10002 | N/A | Stage 1 | Greenfield | FT | PE16 | 630 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 24 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | Chain Wheel | N/A | N/A | PP007 | N/A | Manual Valve with positioner feedback and chain wheel | Emerson | Clarkson KGA+ | 2000-PP007-B02-10121 | Emerson | Bevel gear with chainwheel | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.02 | HV23433 | VKG | Final Tailings | AS2129 Table E PN16
0 | HV | 23 | 444 | HV 23444 | 600 | VKGE1L1 | 600VKGE1L1-Manual-Chain Wheel | Final Tails Slurry Line A Isolation Manual Valve | 23-0585-FT-PE16-630 | 2000-F23-PID-PR-10002 | N/A | Stage 1 | Greenfield | FT | PE16 | 630 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 24 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | Chain Wheel | N/A | N/A | PP007 | N/A | Manual Valve with positioner feedback and chain wheel | Emerson | Clarkson KGA+ | 2000-PP007-B02-10121 | Emerson | Bevel gear with chainwheel | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.03 | HV23444 | VKG | Final Tailings | AS2129 Table E PN16
0 | HV | 23 | 455 | HV 23455 | 600 | VKGE1L1 | 600VKGE1L1-Manual-Chain Wheel | Final Tails Slurry Line C Isolation Manual Valve | 23-0657-FT-PE16-630 | 2000-F23-PID-PR-10002 | N/A | Stage 1 | Greenfield | FT | PE16 | 630 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 24 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | Chain Wheel | N/A | N/A | PP007 | N/A | Manual Valve with positioner feedback and chain wheel | Emerson | Clarkson KGA+ | 2000-PP007-B02-10121 | Emerson | Bevel gear with chainwheel | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.04 | HV23455 | VKG | Final Tailings | AS2129 Table E PN16
0 | PCV | 23 | 410 | PCV 23410 | 400 | VBFD1S1 | 400VBFD1S1-Double Acting-Positioner | Final Tails Pump 1 Upstream Flushing Valve | 23-0066-BW-SS1-400 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 400 | 0 | 900 | 370 | 370 | 10 | N/A | N/A | N/A | 1.07 | 700 | 16 | Detail 1 | FC | Double Acting | Manual Isolation | No Solenoid | Yes | No | - | F23-CP-402 | 2000-PP007-B02-10334 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10086 | Emerson | KEYSTONE F89-085 | SMC IP8100 031 J (4-20mA) | F23.20 | F23.20.05 | PCV23410 | VBF | Hypersaline Water | AS2129 Table D
0 | PCV | 23 | 423 | PCV 23423 | 400 | VBFD1S1 | 400VBFD1S1-Double Acting-Positioner | Final Tails Pump 2 Upstream Flushing Valve | 23-0085-BW-SS1-400 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 400 | 0 | 900 | 370 | 370 | 10 | N/A | N/A | N/A | 1.07 | 700 | 16 | Detail 1 | FC | Double Acting | Manual Isolation | No Solenoid | Yes | No | - | F23-CP-402 | 2000-PP007-B02-10334 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10086 | Emerson | KEYSTONE F89-085 | SMC IP8100 031 J (4-20mA) | F23.20 | F23.20.05 | PCV23423 | VBF | Hypersaline Water | AS2129 Table D
0 | PCV | 23 | 434 | PCV 23434 | 400 | VBFD1S1 | 400VBFD1S1-Double Acting-Positioner | Final Tails Pump 3 Upstream Flushing Valve | 23-0535-BW-SS1-400 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 400 | 0 | 900 | 370 | 370 | 10 | N/A | N/A | N/A | 1.07 | 700 | 16 | Detail 1 | FC | Double Acting | Manual Isolation | No Solenoid | Yes | No | - | F23-CP-404 | 2000-PP007-B02-10336 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10086 | Emerson | KEYSTONE F89-085 | SMC IP8100 031 J (4-20mA) | F23.20 | F23.20.05 | PCV23434 | VBF | Hypersaline Water | AS2129 Table D
0 | PCV | 23 | 445 | PCV 23445 | 400 | VBFD1S1 | 400VBFD1S1-Double Acting-Positioner | Final Tails Pump 4 Upstream Flushing Valve | 23-0652-BW-SS1-400 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 400 | 0 | 900 | 370 | 370 | 10 | N/A | N/A | N/A | 1.07 | 700 | 16 | Detail 1 | FC | Double Acting | Manual Isolation | No Solenoid | Yes | No | - | F23-CP-404 | 2000-PP007-B02-10336 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10086 | Emerson | KEYSTONE F89-085 | SMC IP8100 031 J (4-20mA) | F23.20 | F23.20.05 | PCV23445 | VBF | Hypersaline Water | AS2129 Table D
0 | SV | 23 | 480 | SV 23480 | 25 | SV | 25SV-Solenoid-FO | FINAL TAILS PUMP 1 GLAND WATER | 23-0847-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F23.20 | F23.20.01 | SV23480 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 23 | 484 | SV 23484 | 25 | SV | 25SV-Solenoid-FO | FINAL TAILS PUMP 2 GLAND WATER | 23-0848-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F23.20 | F23.20.02 | SV23484 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 23 | 488 | SV 23488 | 25 | SV | 25SV-Solenoid-FO | FINAL TAILS PUMP 3 GLAND WATER | 23-0849-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F23.20 | F23.20.03 | SV23488 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 23 | 492 | SV 23492 | 25 | SV | 25SV-Solenoid-FO | FINAL TAILS PUMP 4 GLAND WATER | 23-0850-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F23.20 | F23.20.04 | SV23492 | SV | Hypersaline Water | AS2129 Table E
0 | XV | 23 | 402 | XV 23402 | 250 | VKGD1L1 | 250VKGD1L1-Double Acting | Final Tails Tank Drain Valve | 23-0249-FT-PE10-280 | 2000-F23-PID-PR-10001 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FT | - | - | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 10 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC23402 | No | Position Switches | - | F23-CP-403 | 2000-PP007-B02-10335 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10075 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.05 | XV23402 | VKG | Final Tailings | #N/A
0 | XV | 23 | 411 | XV 23411 | 600 | VKGD1L1 | 600VKGD1L1-Double Acting | Final Tails Pump 1 Suction Valve | 600-MECH-RL1 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FT | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 24 | Detail 4 | FC | Double Acting | Single Acting | SV23411 | No | Position Switches | - | F23-CP-401 | 2000-PP007-B02-10333 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10100 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.05 | XV23411 | VKG | Final Tailings | AS2129 Table D
0 | XV | 23 | 412 | XV 23412 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting | Final Tails Pump 1 Suction Flushing Water Valve | 23-0066-BW-SS1-400 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 400 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 16 | Detail 4 | FC | Double Acting | Single Acting | SV23412 | No | Position Switches | - | F23-CP-401 | 2000-PP007-B02-10333 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10089 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.05 | XV23412 | VKG | Hypersaline Water | AS2129 Table D
0 | XV | 23 | 413 | XV 23413 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | Final Tails Pump 1 Suction Drain Valve | 600-MECH-RL1 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FT | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 8 | Detail 4 | FO | Double Acting | Single Acting | SV23413 | No | Position Switches | - | F23-CP-401 | 2000-PP007-B02-10333 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.05 | XV23413 | VKG | Final Tailings | AS2129 Table D
0 | XV | 23 | 414 | XV 23414 | 600 | VKGE1L1 | 600VKGE1L1-Double Acting-Drain Plate | Final Tails Pump 1 Discharge Valve | 22-0843-FT-RL2-600 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FT | RL2 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 1400 | 24 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC23414 | No | Position Switches | Drain Plate | F23-CP-402 | 2000-PP007-B02-10334 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGA+ | 2000-PP007-B02-10101 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.01 | XV23414 | VKG | Final Tailings | AS2129 Table E
0 | XV | 23 | 415 | XV 23415 | 300 | VKGE1L1 | 300VKGE1L1-Double Acting-Drain Plate | Final Tails Pump 1 Discharge Flushing Water Valve | 23-1240-PW-SS2-300 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | PW | SS2 | 300 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 12 | Detail 4 | FC | Double Acting | Single Acting | SV23415 | No | Position Switches | Drain Plate | F23-CP-402 | 2000-PP007-B02-10334 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGA+ | 2000-PP007-B02-10081 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.01 | XV23415 | VKG | Hypersaline Water | AS2129 Table E
0 | XV | 23 | 424 | XV 23424 | 600 | VKGD1L1 | 600VKGD1L1-Double Acting | Final Tails Pump 2 Suction Valve | 600-MECH-RL1 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FT | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 24 | Detail 4 | FC | Double Acting | Single Acting | SV23424 | No | Position Switches | - | F23-CP-401 | 2000-PP007-B02-10333 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10100 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.05 | XV23424 | VKG | Final Tailings | AS2129 Table D
0 | XV | 23 | 425 | XV 23425 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting | Final Tails Pump 2 Suction Flushing Water Valve | 23-0085-BW-SS1-400 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 400 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 16 | Detail 4 | FC | Double Acting | Single Acting | SV23425 | No | Position Switches | - | F23-CP-401 | 2000-PP007-B02-10333 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10089 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.05 | XV23425 | VKG | Hypersaline Water | AS2129 Table D
0 | XV | 23 | 426 | XV 23426 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | Final Tails Pump 2 Suction Drain Valve | 600-MECH-RL1 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FT | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 8 | Detail 4 | FO | Double Acting | Single Acting | SV23426 | No | Position Switches | - | F23-CP-401 | 2000-PP007-B02-10333 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.05 | XV23426 | VKG | Final Tailings | AS2129 Table D
0 | XV | 23 | 427 | XV 23427 | 600 | VKGE1L1 | 600VKGE1L1-Double Acting-Drain Plate | Final Tails Pump 2 Discharge Valve | 23-0844-FT-RL2-600 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FT | RL2 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 1400 | 24 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC23427 | No | Position Switches | Drain Plate | F23-CP-402 | 2000-PP007-B02-10334 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGA+ | 2000-PP007-B02-10101 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.02 | XV23427 | VKG | Final Tailings | AS2129 Table E
0 | XV | 23 | 428 | XV 23428 | 300 | VKGE1L1 | 300VKGE1L1-Double Acting-Drain Plate | Final Tails Pump 2 Discharge Flushing Water Valve | 23-1241-PW-SS2-300 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | PW | SS2 | 300 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 12 | Detail 4 | FC | Double Acting | Single Acting | SV23428 | No | Position Switches | Drain Plate | F23-CP-402 | 2000-PP007-B02-10334 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGA+ | 2000-PP007-B02-10081 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.02 | XV23428 | VKG | Hypersaline Water | AS2129 Table E
0 | XV | 23 | 435 | XV 23435 | 600 | VKGD1L1 | 600VKGD1L1-Double Acting | Final Tails Pump 3 Suction Valve | 600-MECH-RL1 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FT | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 24 | Detail 4 | FC | Double Acting | Single Acting | SV23435 | No | Position Switches | - | F23-CP-403 | 2000-PP007-B02-10335 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10100 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.05 | XV23435 | VKG | Final Tailings | AS2129 Table D
0 | XV | 23 | 436 | XV 23436 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting | Final Tails Pump 3 Suction Flushing Water Valve | 23-0535-BW-SS1-400 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 400 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 16 | Detail 4 | FC | Double Acting | Single Acting | SV23436 | No | Position Switches | - | F23-CP-403 | 2000-PP007-B02-10335 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10089 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.05 | XV23436 | VKG | Hypersaline Water | AS2129 Table D
0 | XV | 23 | 437 | XV 23437 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | Final Tails Pump 3 Suction Drain Valve | 600-MECH-RL1 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FT | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 8 | Detail 4 | FO | Double Acting | Single Acting | SV23437 | No | Position Switches | - | F23-CP-403 | 2000-PP007-B02-10335 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.05 | XV23437 | VKG | Final Tailings | AS2129 Table D
0 | XV | 23 | 438 | XV 23438 | 600 | VKGE1L1 | 600VKGE1L1-Double Acting-Drain Plate | Final Tails Pump 3 Discharge Valve | 23-0845-FT-RL2-600 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FT | RL2 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 1400 | 24 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC23438 | No | Position Switches | Drain Plate | F23-CP-404 | 2000-PP007-B02-10336 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGA+ | 2000-PP007-B02-10101 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.03 | XV23438 | VKG | Final Tailings | AS2129 Table E
0 | XV | 23 | 439 | XV 23439 | 300 | VKGE1L1 | 300VKGE1L1-Double Acting-Drain Plate | Final Tails Pump 3 Discharge Flushing Water Valve | 23-1242-PW-SS2-300 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | PW | SS2 | 300 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 12 | Detail 4 | FC | Double Acting | Single Acting | SV23439 | No | Position Switches | Drain Plate | F23-CP-404 | 2000-PP007-B02-10336 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGA+ | 2000-PP007-B02-10081 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.03 | XV23439 | VKG | Hypersaline Water | AS2129 Table E
0 | XV | 23 | 446 | XV 23446 | 600 | VKGD1L1 | 600VKGD1L1-Double Acting | Final Tails Pump 4 Suction Valve | 600-MECH-RL1 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FT | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 24 | Detail 4 | FC | Double Acting | Single Acting | SV23446 | No | Position Switches | - | F23-CP-403 | 2000-PP007-B02-10335 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10100 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.05 | XV23446 | VKG | Final Tailings | AS2129 Table D
0 | XV | 23 | 447 | XV 23447 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting | Final Tails Pump 4 Suction Flushing Water Valve | 23-0652-BW-SS1-400 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 400 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 16 | Detail 4 | FC | Double Acting | Single Acting | SV23447 | No | Position Switches | - | F23-CP-403 | 2000-PP007-B02-10335 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10089 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.05 | XV23447 | VKG | Hypersaline Water | AS2129 Table D
0 | XV | 23 | 448 | XV 23448 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | Final Tails Pump 4 Suction Drain Valve | 600-MECH-RL1 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FT | RL1 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 700 | 8 | Detail 4 | FO | Double Acting | Single Acting | SV23448 | No | Position Switches | - | F23-CP-403 | 2000-PP007-B02-10335 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.05 | XV23448 | VKG | Final Tailings | AS2129 Table D
0 | XV | 23 | 449 | XV 23449 | 600 | VKGE1L1 | 600VKGE1L1-Double Acting-Drain Plate | Final Tails Pump 4 Discharge Valve | 23-0846-FT-RL2-600 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | FT | RL2 | 600 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 1400 | 24 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC23449 | No | Position Switches | Drain Plate | F23-CP-404 | 2000-PP007-B02-10336 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGA+ | 2000-PP007-B02-10101 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.04 | XV23449 | VKG | Final Tailings | AS2129 Table E
0 | XV | 23 | 450 | XV 23450 | 300 | VKGE1L1 | 300VKGE1L1-Double Acting-Drain Plate | Final Tails Pump 4 Discharge Flushing Water Valve | 23-1243-PW-SS2-300 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | PW | SS2 | 300 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 12 | Detail 4 | FC | Double Acting | Single Acting | SV23450 | No | Position Switches | Drain Plate | F23-CP-404 | 2000-PP007-B02-10336 | PP007 | PP007 | Splash Guard Required | Emerson | Clarkson KGA+ | 2000-PP007-B02-10081 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F23.20 | F23.20.04 | XV23450 | VKG | Hypersaline Water | AS2129 Table E
0 | XV | 23 | 457 | XV 23457 | 350 | VKGE1L1 | 350VKGE1L1-Double Acting | FIM 1 Valve Station Feed Valve 1 | 23-2537-PW-PE16-355 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | PW | PE16 | 355 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 14 | Detail 4 | FC | Double Acting | Single Acting | SV23457 | No | Position Switches | - | F23-CP-405 | 2000-PP007-B02-10388 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10129 |  |  |  | F24.20 | F24.20.01 | XV23457 | VKG | Hypersaline Water | AS2129 Table E PN16
0 | XV | 23 | 458 | XV 23458 | 250 | VKGE1L1 | 250VKGE1L1-Double Acting | FIM 1 Valve Station Feed Valve 2 | 23-2538-PW-PE16-280 | 2000-F23-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | PW | PE16 | 280 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 10 | Detail 4 | FC | Double Acting | Single Acting | SV23458 | No | Position Switches | - | F23-CP-405 | 2000-PP007-B02-10388 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10130 |  |  |  | F24.20 | F24.20.01
0 | HV | 24 | 507 | HV 24507 | 250 | VBFD1S2 | 250VBFD1S2-Manual | Raw Water Feed Booster Pumps to Raw Water Tank Manual Valve | 24-0103-BW-SS1-250 | 2000-F24-PID-PR-10017 | N/A | Stage 1 | Greenfield | BW | SS1 | 250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 10 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10074 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F24.40 | F24.40.03 | HV24507 | VBF | Hypersaline Water | AS2129 Table D
0 | HV | 24 | 508 | HV 24508 | 250 | VBFD1S2 | 250VBFD1S2-Manual | Saline Water Pumps to Raw Water Tank Manual Valve | 24-0286-BW-PE8-280 | 2000-F24-PID-PR-10017 | N/A | Stage 1 | Greenfield | BW | PE8 | 280 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 10 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10074 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F24.50 | F24.50.01 | HV24508 | VBF | Hypersaline Water | AS2129 Table D PN10
0 | LCV | 24 | 401 | LCV 24401 | 450 | VBFD1S1 | 450VBFD1S1-Double Acting-Positioner | Process Water Tank Level Control Valve | 24-0581-BW-SS1-500 | 2000-F24-PID-PR-10001 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | BW | SS1 | 500 | 1000 | 3000 | 145 | VTA | VTA | N/A | N/A | N/A | 1.07 | 700 | 18 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F24-CP-401 | 2000-PP007-B02-10337 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10092 | Emerson | KEYSTONE F89-140 | SMC IP8100 031 J (4-20mA) | F24.50 | F24.50.01 | LCV24401 | VBF | Hypersaline Water | AS2129 Table D
0 | LCV | 24 | 431 | LCV 24431 | 250 | VBFD1S1 | 250VBFD1S1-Double Acting-Positioner | Raw Water Tank Level Control Valve | 24-0103-BW-SS1-250 | 2000-F24-PID-PR-10002 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 250 | 220 | 500 | 100 | VTA | VTA | N/A | N/A | N/A | 1.07 | 700 | 10 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | N/A | N/A | PP007 | N/A | Air to valve | Emerson | GRW | 2000-PP007-B02-10072 | Emerson | KEYSTONE F89-051 | SMC IP8100 031 J (4-20mA) | F24.40 | F24.40.03 | LCV24431 | VBF | Hypersaline Water | AS2129 Table D
0 | LCV | 24 | 456 | LCV 24456 | 200 | VBFE1S1 | 200VBFE1S1-Double Acting-Positioner | Raw Water Booster Tank Level Control Valve | 24-1221-BW-SS2-200 | 2000-F24-PID-PR-10020 | 2000-F24-PID-PR-10012 | Stage 1 | Greenfield | BW | SS2 | 200 | 1000 | 3000 | 145 | VTA | VTA | N/A | N/A | N/A | 1.07 | 700 | 8 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | N/A | N/A | PP007 | N/A | Manual isolation on valve | Emerson | GRW | 2000-PP007-B02-10114 | Emerson | KEYSTONE F89-032 | SMC IP8100 031 J (4-20mA) | F24.40 | F24.40.12 | LCV24456 | VBF | Hypersaline Water | AS2129 Table E
0 | PCV | 24 | 452 | PCV 24452 | 50 | PCV | 50PCV-N/A-Water | LP Gland Water Back Pressure Regulating Valve 2 | 24-0070-GW-SS3-50 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 50 | 0 | 41 | 850 | 850 | 200 | N/A | N/A | N/A | 1.07 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Water | N/A | N/A | PP007 | N/A | Set Pressure @ 650 kPag | Calorex Pty Ltd | Roma Fig. A72 | 2000-PP007-B02-10405 | N/A | N/A | N/A | F24.30 | F24.30.01 | PCV24452 | PCV | Hypersaline Water | AS2129 Table E
0 | PCV | 24 | 453 | PCV 24453 | 50 | PCV | 50PCV-N/A-Water | LP Gland Water Back Pressure Regulating Valve 1 | 24-0335-GW-SS3-50 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 50 | 0 | 41 | 850 | 850 | 200 | N/A | N/A | N/A | 1.07 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Water | N/A | N/A | PP007 | N/A | Set Pressure @ 650 kPag | Calorex Pty Ltd | Roma Fig. A72 | 2000-PP007-B02-10405 | N/A | N/A | N/A | F24.30 | F24.30.01 | PCV24453 | PCV | Hypersaline Water | AS2129 Table E
0 | PCV | 24 | 462 | PCV 24462 | 50 | PCV | 50PCV-N/A-Water | HP Gland Water Back Pressure Regulating Valve 1 | 24-0354-GW-SS3-50 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 50 | 0 | 51 | 1325 | 1325 | 25 | N/A | N/A | N/A | 1.07 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Water | N/A | N/A | PP007 | N/A | Set Pressure @ 1300 kPag | Calorex Pty Ltd | Roma Fig. A72 | 2000-PP007-B02-10405 | N/A | N/A | N/A | F24.30 | F24.30.03 | PCV24462 | PCV | Hypersaline Water | AS2129 Table E
0 | PCV | 24 | 463 | PCV 24463 | 50 | PCV | 50PCV-N/A-Water | HP Gland Water Back Pressure Regulating Valve 2 | 24-0068-GW-SS3-50 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 50 | 0 | 51 | 1325 | 1325 | 25 | N/A | N/A | N/A | 1.07 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Water | N/A | N/A | PP007 | N/A | Set Pressure @ 1300 kPag | Calorex Pty Ltd | Roma Fig. A72 | 2000-PP007-B02-10405 | N/A | N/A | N/A | F24.30 | F24.30.03 | PCV24463 | PCV | Hypersaline Water | AS2129 Table E
0 | PCV | 24 | 672 | PCV 24672 | 150 | PCV | 150PCV-N/A-Fire Water | Fire Water Pressure Regulating Valve - Elution Heater Oil System | 22-1806-FW-MSG2-150 | 2000-F24-PID-PR-10026 | N/A | Stage 2 | Greenfield | FW | MSG2 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 6 | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Fire Water | N/A | N/A | PP024 | N/A | Set Pressure @ 300 kPag | [6 empty] | F24.90 | F24.90.02 | PCV24672 | PCV | Fire Water | #N/A
0 | PCV | 24 | 721 | PCV 24721 | 150 | PCV | 150PCV-N/A-Fire Water | Fire Water Pressure Regulating Valve - Brownfields Tie In Point | 75-0549-FW-MSG2-200 | 2000-F24-PID-PR-10023 | N/A | Stage 1 | Greenfield | FW | MSG2 | 200 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Fire Water | N/A | N/A | PP024 | N/A | Set Pressure @ 700 kPag | [6 empty] | F24.90 | F24.90.01 | PCV24721 | PCV | Fire Water | #N/A
0 | PRV | 24 | 481 | PRV 24481 | 38 | N/A |  | Plant Air Receiver Pressure Release Valve 1 |  | 2000-F24-PID-PR-10007 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME024 | N/A | Vendor Supply Set Pressure @ 1000 kPag | NUOVA General Industrial | F32 OT |  |  |  |  | F24.60 | F24.60.01 | PRV24481 | N/A | #N/A | #N/A
0 | PRV | 24 | 483 | PRV 24483 | 38 | N/A |  | Plant Air Receiver Pressure Release Valve 2 |  | 2000-F24-PID-PR-10007 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME024 | N/A | Vendor Supply Set Pressure @ 1000 kPag | NUOVA General Industrial | B38 OT |  |  |  |  | F24.60 | F24.60.01 | PRV24483 | N/A | #N/A | #N/A
0 | PRV | 24 | 635 | PRV 24635 | 32 | N/A |  | Process Water/Reagents/Trash Screens Air Receiver Pressure Release Valve |  | 2000-F24-PID-PR-10013 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME024 | N/A | Vendor Supply Set Pressure @ 1000 kPag | NUOVA General Industrial | F32 OT |  |  |  |  | F24.60 | F24.60.03 | PRV24635 | N/A | #N/A | #N/A
1 | PRV | 24 | 652 | PRV 24652 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 17-0271-FW-MSG2-80 | 2000-F24-PID-PR-10009 | N/A | Stage 1 | Greenfield | FW | MSG2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F24.90 | F24.90.01 | PRV24652 | PRV | Fire Water | #N/A
1 | PRV | 24 | 654 | PRV 24654 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 72-0994-FW-MSG2-80 | 2000-F24-PID-PR-10009 | N/A | Stage 1 | Greenfield | FW | MSG2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F24.90 | F24.90.01 | PRV24654 | PRV | Fire Water | #N/A
1 | PRV | 24 | 657 | PRV 24657 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 13-1404-FW-MSG2-80 | 2000-F24-PID-PR-10009 | N/A | Stage 1 | Greenfield | FW | MSG2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F13.10 | F13.10.14 | PRV24657 | PRV | Fire Water | #N/A
1 | PRV | 24 | 663 | PRV 24663 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 13-0563-FW-MSG2-80 | 2000-F24-PID-PR-10009 | N/A | Stage 1 | Greenfield | FW | MSG2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F13.10 | F13.10.14 | PRV24663 | PRV | Fire Water | #N/A
1 | PRV | 24 | 675 | PRV 24675 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 28-1419-FW-MSG2-80 | 2000-F24-PID-PR-10015 | N/A | Stage 1 | Brownfields | FW | MSG2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F28.10 | F28.10.07 | PRV24675 | PRV | Fire Water | #N/A
1 | PRV | 24 | 682 | PRV 24682 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 12-0202-FW-MSG2-150 | 2000-F24-PID-PR-10022 | N/A | Stage 1 | Greenfield | FW | MSG2 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F12.10 | F12.10.24 | PRV24682 | PRV | Fire Water | #N/A
1 | PRV | 24 | 684 | PRV 24684 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 12-0634-FW-MSG2-80 | 2000-F24-PID-PR-10022 | N/A | Stage 1 | Greenfield | FW | MSG2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F12.10 | F12.10.24 | PRV24684 | PRV | Fire Water | #N/A
1 | PRV | 24 | 687 | PRV 24687 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 12-0201-FW-MSG2-80 | 2000-F24-PID-PR-10022 | N/A | Stage 1 | Greenfield | FW | MSG2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F12.10 | F12.10.24 | PRV24687 | PRV | Fire Water | #N/A
0 | PRV | 24 | 689 | PRV 24689 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 22-1806-FW-MSG2-150 | 2000-F24-PID-PR-10026 | N/A | Stage 2 | Greenfield | FW | MSG2 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F24.90 | F24.90.02 | PRV24689 | PRV | Fire Water | #N/A
1 | PRV | 24 | 694 | PRV 24694 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 12-0273-FW-MSG3-50 | 2000-F24-PID-PR-10022 | N/A | Stage 1 | Greenfield | FW | MSG3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F12.10 | F12.10.24 | PRV24694 | PRV | Fire Water | AS2129 Table E
1 | PRV | 24 | 702 | PRV 24702 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 13-0550-FW-MSG2-80 | 2000-F24-PID-PR-10023 | N/A | Stage 1 | Greenfield | FW | MSG2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F24.90 | F24.90.01 | PRV24702 | PRV | Fire Water | #N/A
1 | PRV | 24 | 707 | PRV 24707 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 13-0551-FW-MSG2-80 | 2000-F24-PID-PR-10023 | N/A | Stage 1 | Greenfield | FW | MSG2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F24.90 | F24.90.01 | PRV24707 | PRV | Fire Water | #N/A
1 | PRV | 24 | 712 | PRV 24712 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 13-0571-FW-MSG2-80 | 2000-F24-PID-PR-10023 | N/A | Stage 1 | Greenfield | FW | MSG2 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F24.90 | F24.90.01 | PRV24712 | PRV | Fire Water | #N/A
1 | PRV | 24 | 716 | PRV 24716 | 15 | PRV | 15PRV-N/A | Firewater Thermal Expansion Valve | 13-0562-FW-MSG2-150 | 2000-F24-PID-PR-10023 | N/A | Stage 1 | Greenfield | FW | MSG2 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | PP024 | N/A | Set Pressure @ 1200 kPag | [6 empty] | F24.90 | F24.90.01 | PRV24716 | PRV | Fire Water | #N/A
0 | PRV | 24 | 722 | PRV 24722 | 80 | PRV | 80PRV-N/A-Fire Water | Fire Water Pressure Relief Valve - Brownfields Tie In Point | 75-0549-FW-MSG2-200 | 2000-F24-PID-PR-10023 | N/A | Stage 1 | Greenfield | FW | MSG2 | 200 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Fire Water | N/A | N/A | PP024 | N/A | Set Pressure @ 700 kPag | [6 empty] | F24.90 | F24.90.01 | PRV24722 | PRV | Fire Water | #N/A
0 | SV | 24 | 512 | SV 24512 | 25 | SV | 25SV-Solenoid-FO | MILL WATER PUMP 1 GLAND WATER | 24-1282-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F24.20 | F24.20.07 | SV24512 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 24 | 515 | SV 24515 | 25 | SV | 25SV-Solenoid-FO | MILL WATER PUMP 2 GLAND WATER | 24-1281-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F24.20 | F24.20.07 | SV24515 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 24 | 518 | SV 24518 | 25 | SV | 25SV-Solenoid-FO | HIGH PRESSURE PROCESS WATER PUMP 1 GLAND WATER | 24-1286-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F24.20 | F24.20.01 | SV24518 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 24 | 521 | SV 24521 | 25 | SV | 25SV-Solenoid-FO | HIGH PRESSURE PROCESS WATER PUMP 2 GLAND WATER | 24-1285-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F24.20 | F24.20.01 | SV24521 | SV | Hypersaline Water | AS2129 Table E
0 | XV | 24 | 402 | XV 24402 | 500 | VBFD1S1 | 500VBFD1S1-Double Acting | Process Water Tank Saline Water Feed Valve | 24-0580-BW-SS1-500 | 2000-F24-PID-PR-10001 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | BW | SS1 | 500 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 20 | Detail 7 | FC | Double Acting | Single Acting | SV24402 | No | Position Switches | - | F24-CP-401 | 2000-PP007-B02-10337 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10095 | Emerson | KEYSTONE F89-140 | 2000043108 TVF-M2WGNMM | F24.50 | F24.50.01 | XV24402 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 24 | 411 | XV 24411 | 750 | VBFD1L6 | 750VBFD1L6-Double Acting | Mill Water Pump 1 Suction Valve | 24-0590-PW-SS1-750 | 2000-F24-PID-PR-10001 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS1 | 750 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 30 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC24411 | No | Position Switches | - | F24-CP-402 | 2000-PP007-B02-10338 | PP007 | PP007 |  | Emerson | GRF | 2000-PP007-B02-10102 | Emerson | KTM AW20 CD | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.08 | XV24411 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 24 | 412 | XV 24412 | 750 | VBFD1L6 | 750VBFD1L6-Double Acting | Mill Water Pump 1 Discharge Valve | 24-0593-PW-SS1-750 | 2000-F24-PID-PR-10001 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS1 | 750 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 30 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC24412 | No | Position Switches | - | F24-CP-402 | 2000-PP007-B02-10338 | PP007 | PP007 |  | Emerson | GRF | 2000-PP007-B02-10102 | Emerson | KTM AW20 CD | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.07 | XV24412 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 24 | 413 | XV 24413 | 750 | VBFD1L6 | 750VBFD1L6-Double Acting | Mill Water Pump 2 Suction Valve | 24-0591-PW-SS1-750 | 2000-F24-PID-PR-10001 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS1 | 750 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 30 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC24413 | No | Position Switches | - | F24-CP-402 | 2000-PP007-B02-10338 | PP007 | PP007 |  | Emerson | GRF | 2000-PP007-B02-10102 | Emerson | KTM AW20 CD | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.08 | XV24413 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 24 | 414 | XV 24414 | 750 | VBFD1L6 | 750VBFD1L6-Double Acting | Mill Water Pump 2 Discharge Valve | 24-0592-PW-SS1-750 | 2000-F24-PID-PR-10001 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS1 | 750 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 30 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC24414 | No | Position Switches | - | F24-CP-402 | 2000-PP007-B02-10338 | PP007 | PP007 |  | Emerson | GRF | 2000-PP007-B02-10102 | Emerson | KTM AW20 CD | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.07 | XV24414 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 24 | 421 | XV 24421 | 600 | VBFD1L2 | 600VBFD1L2-Double Acting | High Pressure Process Water Pump 1 Suction Valve | 24-0586-PW-SS1-600 | 2000-F24-PID-PR-10001 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS1 | 600 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 24 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC24421 | No | Position Switches | - | F24-CP-403 | 2000-PP007-B02-10339 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10099 | Emerson | KEYSTONE F89-240 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.08 | XV24421 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 24 | 422 | XV 24422 | 500 | VBFE1L2 | 500VBFE1L2-Double Acting | High Pressure Process Water Pump 1 Discharge Valve | 24-0589-PW-SS2-500 | 2000-F24-PID-PR-10001 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS2 | 500 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 20 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC24422 | No | Position Switches | - | F24-CP-403 | 2000-PP007-B02-10339 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10096 | Emerson | KEYSTONE F89-140 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.01 | XV24422 | VBF | Hypersaline Water | AS2129 Table E
0 | XV | 24 | 423 | XV 24423 | 600 | VBFD1L2 | 600VBFD1L2-Double Acting | High Pressure Process Water Pump 2 Suction Valve | 24-0587-PW-SS1-600 | 2000-F24-PID-PR-10001 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS1 | 600 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 24 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC24423 | No | Position Switches | - | F24-CP-403 | 2000-PP007-B02-10339 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10099 | Emerson | KEYSTONE F89-240 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.08 | XV24423 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 24 | 424 | XV 24424 | 500 | VBFE1L2 | 500VBFE1L2-Double Acting | High Pressure Process Water Pump 2 Discharge Valve | 24-0588-PW-SS2-500 | 2000-F24-PID-PR-10001 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PW | SS2 | 500 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 20 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC24424 | No | Position Switches | - | F24-CP-403 | 2000-PP007-B02-10339 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10096 | Emerson | KEYSTONE F89-140 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.01 | XV24424 | VBF | Hypersaline Water | AS2129 Table E
0 | XV | 24 | 501 | XV 24501 | 350 | VBFD1S2 | 350VBFD1S2-Double Acting | Raw Water Feed Booster Pump 1 Suction Valve | 24-1473-BW-SS1-350 | 2000-F24-PID-PR-10017 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 350 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 14 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC24501 | No | Position Switches | - | F24-CP-404 | 2000-PP007-B02-10340 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10083 | Emerson | KEYSTONE F89-085 | 2000043108 TVF-M2WGNMM | F24.40 | F24.40.03 | XV24501 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 24 | 502 | XV 24502 | 250 | VBFD1S2 | 250VBFD1S2-Double Acting | Raw Water Feed Booster Pump 1 Discharge Valve | 24-0219-BW-SS1-250 | 2000-F24-PID-PR-10017 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 10 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC24502 | No | Position Switches | - | F24-CP-404 | 2000-PP007-B02-10340 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10073 | Emerson | KEYSTONE F89-051 | 2000043108 TVF-M2WGNMM | F24.40 | F24.40.03 | XV24502 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 24 | 503 | XV 24503 | 350 | VBFD1S2 | 350VBFD1S2-Double Acting | Raw Water Feed Booster Pump 2 Suction Valve | 24-1475-BW-SS1-350 | 2000-F24-PID-PR-10017 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 350 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 14 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC24503 | No | Position Switches | - | F24-CP-404 | 2000-PP007-B02-10340 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10083 | Emerson | KEYSTONE F89-085 | 2000043108 TVF-M2WGNMM | F24.40 | F24.40.03 | XV24503 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 24 | 504 | XV 24504 | 250 | VBFD1S2 | 250VBFD1S2-Double Acting | Raw Water Feed Booster Pump 2 Discharge Valve | 24-1476-BW-SS1-250 | 2000-F24-PID-PR-10017 | 2000-F24-PID-PR-10007 | Stage 1 | Greenfield | BW | SS1 | 250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 10 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC24504 | No | Position Switches | - | F24-CP-404 | 2000-PP007-B02-10340 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10073 | Emerson | KEYSTONE F89-051 | 2000043108 TVF-M2WGNMM | F24.40 | F24.40.03 | XV24504 | VBF | Hypersaline Water | AS2129 Table D
0 | DCV | 28 | 91 | DCV 28091 | 50 | VB03S1 | 50VB03S1-Double Acting-Positioner | UFG Mill 2 Discharge Hopper Process Water Density Control Valve | 28-0729-PW-SS3-50 | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | PW | SS3 | 50 | 16 | 24 | 600 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 2 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F28-CP-406 | 2000-PP007-B02-10345 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10106 | Emerson | KEYSTONE F89-009 | BIPO NON PST SMC IP8100 031 J X318 | F24.20 | F24.20.01 | DCV28091 | VB0 | Hypersaline Water | AS2129 Table E
0 | DCV | 28 | 281 | DCV 28281 | 50 | VB03S1 | 50VB03S1-Double Acting-Positioner | UFG Mill 3 Discharge Hopper Process Water Density Control Valve | 28-0516-PW-SS3-50 | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | PW | SS3 | 50 | 16 | 24 | 600 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 2 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F28-CP-401 | 2000-PP007-B02-10341 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10106 | Emerson | KEYSTONE F89-009 | BIPO NON PST SMC IP8100 031 J X318 | F24.20 | F24.20.11 | DCV28281 | VB0 | Hypersaline Water | AS2129 Table E
0 | FCV | 28 | 21 | FCV 28021 | 80 | VBFE1S1 | 80VBFE1S1-Double Acting-Positioner | UFG Mill 2 Feed Hopper HP Process Water Flow Control Valve 2 | 28-1247-PW-SS2-80 | 2000-F28-PID-PR-10001 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | PW | SS2 | 80 | 16 | 50 | 600 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 3 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F28-CP-404 | 2000-PP007-B02-10344 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10112 | Emerson | KEYSTONE F89-004 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.01 | FCV28021 | VBF | Hypersaline Water | AS2129 Table E
0 | FCV | 28 | 23 | FCV 28023 | 150 | VBFE1S1 | 150VBFE1S1-Double Acting-Positioner | UFG Mill 2 Feed Hopper HP Process Water Flow Control Valve 1 | 28-0758-PW-SS2-200 | 2000-F28-PID-PR-10001 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | PW | SS2 | 200 | 256 | 384 | 600 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 6 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F28-CP-404 | 2000-PP007-B02-10344 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10060 | Emerson | KEYSTONE F89-014 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.01 | FCV28023 | VBF | Hypersaline Water | AS2129 Table E
0 | FCV | 28 | 221 | FCV 28221 | 80 | VBFE1S1 | 80VBFE1S1-Double Acting-Positioner | UFG Mill 3 Feed Hopper HP Process Water Flow Control Valve 2 | 28-1504-PW-SS2-80 | 2000-F28-PID-PR-10003 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | PW | SS2 | 80 | 16 | 50 | 600 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 3 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F28-CP-403 | 2000-PP007-B02-10343 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10112 | Emerson | KEYSTONE F89-004 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.11 | FCV28221 | VBF | Hypersaline Water | AS2129 Table E
0 | FCV | 28 | 223 | FCV 28223 | 150 | VBFE1S1 | 150VBFE1S1-Double Acting-Positioner | UFG Mill 3 Feed Hopper HP Process Water Flow Control Valve 1 | 28-0100-PW-SS2-200 | 2000-F28-PID-PR-10003 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | PW | SS2 | 200 | 256 | 384 | 600 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 6 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F28-CP-403 | 2000-PP007-B02-10343 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10060 | Emerson | KEYSTONE F89-014 | SMC IP8100 031 J (4-20mA) | F24.20 | F24.20.11 | FCV28223 | VBF | Hypersaline Water | AS2129 Table E
0 | LCV | 28 | 73 | LCV 28073 | 200 | VDTD1L1 | 200VDTD1L1-Double Acting-Positioner | Ultra Fine Grinding Mill 2 Discharge Recycle Valve | 28-0723-CON-RL1-200 | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 200 | 50 | 200 | 90 | 80 | VTA | - | 220 | ~40% | 1.61 | 700 | 8 | Detail 2 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | Transmitter | - | F28-CP-406 | 2000-PP007-B02-10345 | PP007 | PP007 |  | Dual Valves | eDart YDP200B Poly yDart Valve | 2000-PP007-B02-10069 | Dual Valves | Pneumatic cylinder | SMCIP8101 electropneumatic positioner and air filter regulator to 700 kPag included | F28.20 | F28.20.02 | LCV28073 | VDT | Concentrate Slurry | AS2129 Table D
0 | LCV | 28 | 74 | LCV 28074 | 200 | VDTD1L1 | 200VDTD1L1-Double Acting-Positioner | UFG Mill 2 Discharge Hopper Feed Valve | 28-0739-CON-RL1-200 | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 200 | 50 | 200 | 90 | 80 | VTA | - | 220 | ~40% | 1.61 | 700 | 8 | Detail 2 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | Transmitter | - | F28-CP-406 | 2000-PP007-B02-10345 | PP007 | PP007 |  | Dual Valves | eDart YDP200B Poly yDart Valve | 2000-PP007-B02-10069 | Dual Valves | Pneumatic cylinder | SMCIP8101 electropneumatic positioner and air filter regulator to 700 kPag included | F28.20 | F28.20.02 | LCV28074 | VDT | Concentrate Slurry | AS2129 Table D
0 | LCV | 28 | 261 | LCV 28261 | 200 | VDTD1L1 | 200VDTD1L1-Double Acting-Positioner | UFG Mill 3 Discharge Recycle Level Control Valve | 20-0753-CON-RL1-200 | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 200 | 135 | 200 | 90 | 80 | VTA | - | 220 | ~40% | 1.61 | 700 | 8 | Detail 2 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | Transmitter | - | F28-CP-401 | 2000-PP007-B02-10341 | PP007 | PP007 |  | Dual Valves | eDart YDP200B Poly yDart Valve | 2000-PP007-B02-10069 | Dual Valves | Pneumatic cylinder | SMCIP8101 electropneumatic positioner and air filter regulator to 700 kPag included | F28.20 | F28.20.20 | LCV28261 | VDT | Concentrate Slurry | AS2129 Table D
0 | LCV | 28 | 273 | LCV 28273 | 200 | VDTD1L1 | 200VDTD1L1-Double Acting-Positioner | UFG Mill 3 Discharge Hopper Level Control Valve | 20-0757-CON-RL1-200 | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 200 | 135 | 200 | 90 | 80 | VTA | - | 220 | ~40% | 1.61 | 700 | 8 | Detail 2 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | Transmitter | - | F28-CP-401 | 2000-PP007-B02-10341 | PP007 | PP007 |  | Dual Valves | eDart YDP200B Poly yDart Valve | 2000-PP007-B02-10069 | Dual Valves | Pneumatic cylinder | SMCIP8101 electropneumatic positioner and air filter regulator to 700 kPag included | F28.20 | F28.20.20 | LCV28273 | VDT | Concentrate Slurry | AS2129 Table D
0 | LCV | 28 | 328 | LCV 28328 | 50 | VB03S1 | 50VB03S1-Double Acting-Positioner | UFG Product Hopper Process Water Level Control Valve | 28-0763-PW-SS3-50 | 2000-F28-PID-PR-10005 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | PW | SS3 | 50 | 40 | 60 | 600 | VTA | VTA | N/A | N/A | N/A | 1.07 | 1400 | 2 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F28-CP-407 | 2000-PP007-B02-10346 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10106 | Emerson | KEYSTONE F89-009 | BIPO NON PST SMC IP8100 031 J X318 | F24.20 | F24.20.01 | LCV28328 | VB0 | Hypersaline Water | AS2129 Table E
0 | PCV | 28 | 43 | PCV 28043 | 25 | PCV | 25PCV-N/A-Water | UFG GSW Tank Back Pressure Regulating Valve | 28-0999-PSW-MSG3-25 | 2000-F28-PID-PR-10001 | N/A | Stage 1 | Greenfield | PSW | MSG3 | 25 | 0 | 14 | 950 | 950 | 450 | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Water | N/A | N/A | PP007 | N/A | Set Pressure @ 500kPag | Calorex Pty Ltd | Roma Fig. A72 | 2000-PP007-B02-10404 | N/A | N/A | N/A | F28.10 | F28.10.01 | PCV28043 | PCV | Process Scheme Water | AS2129 Table E
0 | PCV | 28 | 53 | PCV 28053 | 50 | PCV | 50PCV-N/A-Water | Ultra Fine Grinding Mill 2 Gland Seal Water Pressure Regulating Valve | 28-0733-PSW-MSG3-50 | 2000-F28-PID-PR-10002 | N/A | Stage 1 | Greenfield | PSW | MSG3 | 50 | 0 | 14 | 500 | 500 | 50 | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Water | N/A | N/A | PP007 | N/A | Set Pressure @ 450kPa | Calorex Pty Ltd | Roma Fig. 514 | 2000-PP007-B02-10403 | N/A | N/A | N/A | F28.10 | F28.10.01 | PCV28053 | PCV | Process Scheme Water | AS2129 Table E
0 | PCV | 28 | 57 | PCV 28057 | 80 | PCV | 80PCV-N/A-Water | Ultra Fine Grinding Mill 2 HP Water Pressure Regulating Valve | 28-0738-PW-SS2-80 | 2000-F28-PID-PR-10002 | N/A | Stage 1 | Greenfield | PW | SS2 | 80 | 0 | 14 | 650 | 650 | 200 | N/A | N/A | N/A | 1.07 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Water | N/A | N/A | PP007 | N/A | Set Pressure @ 450kPa | Calorex Pty Ltd | Roma Fig-213 | 2000-PP007-B02-10410 | N/A | N/A | N/A | F24.20 | F24.20.01 | PCV28057 | PCV | Hypersaline Water | AS2129 Table E
1 | PCV | 28 | 366 | PCV 28366 | 50 | PCV | 50PCV-N/A-Water | Ultra Fine Grinding Mill 3 Gland Seal Water Pressure Regulating Valve | 28-0734-PSW-MSG3-50 | 2000-F28-PID-PR-10004 | N/A | Stage 2 | Greenfield | PSW | MSG3 | 50 | 0 | 14 | 500 | 500 | 50 | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Water | N/A | N/A | PP007 | N/A | Set Pressure @ 450kPa | Calorex Pty Ltd | Roma Fig. 514 | 2000-PP007-B02-10416 | N/A | N/A | N/A | F28.10 | F28.10.35 | PCV28366 | PCV | Process Scheme Water | AS2129 Table E
1 | PCV | 28 | 460 | PCV 28460 | 80 | PCV | 80PCV-N/A-Water | Ultra Fine Grinding Mill 3 HP Water Pressure Regulating Valve | 28-0767-PW-SS2-80 | 2000-F28-PID-PR-10004 | N/A | Stage 2 | Greenfield | PW | SS2 | 80 | 0 | 14 | 650 | 650 | 200 | N/A | N/A | N/A | 1.07 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Water | N/A | N/A | PP007 | N/A | Set Pressure @ 450kPa | Calorex Pty Ltd | Roma Fig-213 | 2000-PP007-B02-10410 | N/A | N/A | N/A | F24.20 | F24.20.11 | PCV28460 | PCV | Hypersaline Water | AS2129 Table E
0 | PRV | 28 | 60 | PRV 28060 | 50 | PRV | 50PRV-N/A-Water | Ultra Fine Grinding Mill 2 HP Water Pressure Release Valve | 28-0859-PW-SS2-50 | 2000-F28-PID-PR-10002 | N/A | Stage 1 | Greenfield | PW | SS2 | 50 | 0 | 100 | 650 | 650 | 150 | N/A | N/A | N/A | 1.07 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Water | N/A | N/A | PP007 | N/A | Set Pressure @ 500kPa | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10409 | N/A | N/A | N/A | F24.20 | F24.20.01 | PRV28060 | PRV | Hypersaline Water | AS2129 Table E
0 | PRV | 28 | 450 | PRV 28450 | 32 | N/A |  | UFG 2/3 Air Receiver Pressure Release Valve |  | 2000-F24-PID-PR-10027 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME024 | N/A | Vendor Supply Set Pressure @ 1000 kPag | NUOVA General Industrial | F32 OT |  |  |  |  | F28.10 | F28.10.02 | PRV28450 | N/A | #N/A | #N/A
1 | PRV | 28 | 461 | PRV 28461 | 50 | PRV | 50PRV-N/A-Water | Ultra Fine Grinding Mill 3 HP Water Pressure Release Valve | 28-1503-PSW-SS2-50 | 2000-F28-PID-PR-10004 | N/A | Stage 2 | Greenfield | PSW | SS2 | 50 | 0 | 100 | 650 | 650 | 150 | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Water | N/A | N/A | PP007 | N/A | Set Pressure @ 500kPa | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10409 | N/A | N/A | N/A | F24.20 | F24.20.11 | PRV28461 | PRV | Process Scheme Water | AS2129 Table E
0 | SV | 28 | 400 | SV 28400 | 25 | SV | 25SV-Solenoid-FO | UFG PRODUCT PUMP 1 GLAND WATER | 28-0828-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F28.20 | F28.20.03 | SV28400 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 28 | 404 | SV 28404 | 25 | SV | 25SV-Solenoid-FO | UFG PRODUCT PUMP 2 GLAND WATER | 28-0829-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F28.20 | F28.20.03 | SV28404 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 28 | 408 | SV 28408 | 25 | SV | 25SV-Solenoid-FO | UFG MILL 2 FEED PUMP GLAND WATER | 28-0827-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F28.20 | F28.20.04 | SV28408 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 28 | 412 | SV 28412 | 25 | SV | 25SV-Solenoid-FO | UFG MILL 2 DISCHARGE PUMP GLAND WATER | 28-0852-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F28.20 | F28.20.07 | SV28412 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 28 | 416 | SV 28416 | 25 | SV | 25SV-Solenoid-FO | UFG MILL 2 ISACHARGER PUMP GLAND WATER | 28-0826-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F28.20 | F28.20.05 | SV28416 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 28 | 430 | SV 28430 | 25 | SV | 25SV-Solenoid-FO | UFG MILL 3 ISACHARGER PUMP GLAND WATER | 28-0807-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F28.20 | F28.20.15 | SV28430 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 28 | 433 | SV 28433 | 25 | SV | 25SV-Solenoid-FO | UFG MILL 3 FEED PUMP GLAND WATER | 28-0806-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F28.20 | F28.20.19 | SV28433 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 28 | 436 | SV 28436 | 25 | SV | 25SV-Solenoid-FO | UFG MILL 3 DISCHARGE PUMP GLAND WATER | 28-0853-GW-SS3-25 | 2000-F24-PID-PR-10004 | N/A | Stage 1 | Greenfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F28.20 | F28.20.13 | SV28436 | SV | Hypersaline Water | AS2129 Table E
0 | XCV | 28 | 12 | XCV 28012 | 300 | VKGD1L1 | 300VKGD1L1-Double Acting-Positioner-Table E drilling | UFG Mill 2 Media Hopper Discharge Valve |  | 2000-F28-PID-PR-10001 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | - | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 700 | 12 | Detail 2 | FC | Double Acting | Manual Isolation | No Solenoid | Yes | Transmitter | Table E drilling | F28-CP-402 | 2000-PP007-B02-10342 | PP007 | PP007 | Actuator to come with transducer for position feedback Valve to be AS 2129 Table E | Emerson | Clarkson KGD | 2000-PP007-B02-10117 | Emerson | Pneumatic cylinder | Air Cylinder WITH POSITIONER/FEEDBACK Included | F28.20 | F28.20.02 | XCV28012 | VKG | Concentrate Slurry | #N/A
0 | XCV | 28 | 212 | XCV 28212 | 300 | VKGD1L1 | 300VKGD1L1-Double Acting-Positioner-Table E drilling | UFG Mill 3 Media Hopper Discharge Valve |  | 2000-F28-PID-PR-10003 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | - | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 700 | 12 | Detail 2 | FC | Double Acting | Manual Isolation | No Solenoid | Yes | Transmitter | Table E drilling | F28-CP-402 | 2000-PP007-B02-10342 | PP007 | PP007 | Actuator to come with transducer for position feedback Valve to be AS 2129 Table E | Emerson | Clarkson KGD | 2000-PP007-B02-10117 | Emerson | Pneumatic cylinder | Air Cylinder WITH POSITIONER/FEEDBACK Included | F28.20 | F28.20.20 | XCV28212 | VKG | Concentrate Slurry | #N/A
0 | XV | 28 | 2 | XV 28002 | 50 | VB03S1 | 50VB03S1-Double Acting | UFG Mill 2 Water Collection Tank HP Precess Water Inpiut | 28-0735-PW-SS3-50 | 2000-F28-PID-PR-10001 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | PW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV28002 | No | Position Switches | - | F28-CP-406 | 2000-PP007-B02-10345 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10008 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F24.20 | F24.20.01 | XV28002 | VB0 | Hypersaline Water | AS2129 Table E
0 | XV | 28 | 31 | XV 28031 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | UFG Mill 2 Feed Pump Suction Valve | 200-MECH-RL1 | 2000-F28-PID-PR-10001 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 56 | 144 | 0.473 | 1.64 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28031 | No | Position Switches | - | F28-CP-404 | 2000-PP007-B02-10344 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.04 | XV28031 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 32 | XV 28032 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Mill 2 Feed Pump Discharge Drain Valve | 28-0728-CON-RL1-150 | 2000-F28-PID-PR-10001 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 56 | 144 | 0.473 | 1.64 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV28032 | No | Position Switches | - | F28-CP-404 | 2000-PP007-B02-10344 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.04 | XV28032 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 36 | XV 28036 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Mill 2 Feed Pump Suction Drain Valve | 200-MECH-RL1 | 2000-F28-PID-PR-10001 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 56 | 144 | 0.473 | 1.64 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV28036 | No | Position Switches | - | F28-CP-404 | 2000-PP007-B02-10344 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.04 | XV28036 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 42 | XV 28042 | 50 | VBE1S1 | 50VBE1S1-Double Acting | UFG GSW Tank Raw Water | 75-0730-PSW-PE16-63 | 2000-F28-PID-PR-10001 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | PSW | PE16 | 63 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV28042 | No | Position Switches | - | F28-CP-404 | 2000-PP007-B02-10344 | PP007 | PP007 |  | Emerson | K-BALL F194 | 2000-PP007-B02-10015 | Emerson | KEYSTONE F89-004 | SWIT TOP TVF-M2WGNMM | F24.70 | F24.70.01 | XV28042 | VBE | Process Scheme Water | AS2129 Table E PN16
0 | XV | 28 | 59 | XV 28059 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Ultra Fine Grinding Mill 2 Feed Valve | 28-0728-CON-RL1-150 | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 56 | 144 | 0.473 | 1.64 | 700 | 6 | Detail 4 | FC | Double Acting | Single Acting | SV28059 | No | Position Switches | - | F28MUF402-JB04 | 2000-ME039-D02-10018 | PP007 | ME039 | Glencore supplied solenoid and cabinet | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.04 | XV28059 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 64 | XV 28064 | 50 | VBD1S1 | 50VBD1S1-Double Acting | Ultra Fine Grinding Mill 2 Gland Water Valve | 28-0733-PSW-MSG3-50 | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | PSW | MSG3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 2 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC28064 | No | Position Switches | - | F28-CP-406 | 2000-PP007-B02-10345 | PP007 | PP007 |  | Unimech | ARITA ARTTBV-TE | 2000-PP007-B02-10012 | Unimech | Pneumatic cylinder | Arita Limit Switch | F28.10 | F28.10.01 | XV28064 | VBD | Process Scheme Water | AS2129 Table E
0 | XV | 28 | 66 | XV 28066 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting-DUPLEX | Ultra Fine Grinding Mill 2 Process Water Addition Valve | 28-0728-CON-RL1-150 | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 4 | FC | Double Acting | Single Acting | SV28066 | No | Position Switches | DUPLEX | F28MUF402-JB04 | 2000-ME039-D02-10018 | PP007 | ME039 | Glencore supplied solenoid and cabinet. Duplex SS gate required. | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F24.20 | F24.20.01 | XV28066 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 69 | XV 28069 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Mill 2 Concentrate Trash Screen Flotation Concentrate Bypass Valve | 28-1753-CON-RL1-80 | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | 56 | 144 | 0.596 | 1.07 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28069 | No | Position Switches | - | F28-CP-406 | 2000-PP007-B02-10345 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.01 | XV28069 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 70 | XV 28070 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Mill 2 Concentrate Trash Screen Flotation Concentrate Inlet Valve | 28-1754-CON-RL1-80 | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | 56 | 144 | 0.596 | 1.07 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28070 | No | Position Switches | - | F28-CP-406 | 2000-PP007-B02-10345 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.01 | XV28070 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 92 | XV 28092 | 300 | VKGD1L1 | 300VKGD1L1-Double Acting | UFG Mill 2 Discharge Pump 1 Suction Valve | 300-MECH-RL1 | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 10 | 25 | 0.327 | 1.41 | 700 | 12 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28092 | No | Position Switches | - | F28-CP-406 | 2000-PP007-B02-10345 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10080 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.07 | XV28092 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 93 | XV 28093 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Mill 2 Discharge Pump 1 Drain Valve | 300-MECH-RL1 | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 10 | 25 | 0.327 | 1.41 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV28093 | No | Position Switches | - | F28-CP-406 | 2000-PP007-B02-10345 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.07 | XV28093 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 101 | XV 28101 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28101 | No | Position Switches | - | F28CY421-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28101 | N/A | #N/A | #N/A
0 | XV | 28 | 102 | XV 28102 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28102 | No | Position Switches | - | F28CY421-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28102 | N/A | #N/A | #N/A
0 | XV | 28 | 103 | XV 28103 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28103 | No | Position Switches | - | F28CY421-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28103 | N/A | #N/A | #N/A
0 | XV | 28 | 104 | XV 28104 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28104 | No | Position Switches | - | F28CY421-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28104 | N/A | #N/A | #N/A
0 | XV | 28 | 105 | XV 28105 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28105 | No | Position Switches | - | F28CY421-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28105 | N/A | #N/A | #N/A
0 | XV | 28 | 106 | XV 28106 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28106 | No | Position Switches | - | F28CY421-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28106 | N/A | #N/A | #N/A
0 | XV | 28 | 107 | XV 28107 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28107 | No | Position Switches | - | F28CY421-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28107 | N/A | #N/A | #N/A
0 | XV | 28 | 108 | XV 28108 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28108 | No | Position Switches | - | F28CY421-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28108 | N/A | #N/A | #N/A
0 | XV | 28 | 109 | XV 28109 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28109 | No | Position Switches | - | F28CY421-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28109 | N/A | #N/A | #N/A
0 | XV | 28 | 110 | XV 28110 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28110 | No | Position Switches | - | F28CY421-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28110 | N/A | #N/A | #N/A
0 | XV | 28 | 111 | XV 28111 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28111 | No | Position Switches | - | F28CY421-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28111 | N/A | #N/A | #N/A
0 | XV | 28 | 112 | XV 28112 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28112 | No | Position Switches | - | F28CY421-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28112 | N/A | #N/A | #N/A
0 | XV | 28 | 113 | XV 28113 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28113 | No | Position Switches | - | F28CY421-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28113 | N/A | #N/A | #N/A
0 | XV | 28 | 114 | XV 28114 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28114 | No | Position Switches | - | F28CY421-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28114 | N/A | #N/A | #N/A
0 | XV | 28 | 115 | XV 28115 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28115 | No | Position Switches | - | F28CY421-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28115 | N/A | #N/A | #N/A
0 | XV | 28 | 116 | XV 28116 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28116 | No | Position Switches | - | F28CY421-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28116 | N/A | #N/A | #N/A
0 | XV | 28 | 117 | XV 28117 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28117 | No | Position Switches | - | F28CY421-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28117 | N/A | #N/A | #N/A
0 | XV | 28 | 118 | XV 28118 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28118 | No | Position Switches | - | F28CY421-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28118 | N/A | #N/A | #N/A
0 | XV | 28 | 119 | XV 28119 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28119 | No | Position Switches | - | F28CY421-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28119 | N/A | #N/A | #N/A
0 | XV | 28 | 120 | XV 28120 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28120 | No | Position Switches | - | F28CY421-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28120 | N/A | #N/A | #N/A
0 | XV | 28 | 121 | XV 28121 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28121 | No | Position Switches | - | F28CY421-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28121 | N/A | #N/A | #N/A
0 | XV | 28 | 122 | XV 28122 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28122 | No | Position Switches | - | F28CY421-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28122 | N/A | #N/A | #N/A
0 | XV | 28 | 123 | XV 28123 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28123 | No | Position Switches | - | F28CY421-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28123 | N/A | #N/A | #N/A
0 | XV | 28 | 124 | XV 28124 |  | N/A |  | UFG Mill 2 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28124 | No | Position Switches | - | F28CY421-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.08 | XV28124 | N/A | #N/A | #N/A
0 | XV | 28 | 134 | XV 28134 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Sump Pump 1 to UFG Mill 2 Trash Screen Valve | 28-0745-FD-RL1-80 | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | FD | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28134 | No | Position Switches | - | F28-CP-407 | 2000-PP007-B02-10346 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.01 | XV28134 | VKG | Floor Drainage | AS2129 Table D
0 | XV | 28 | 135 | XV 28135 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Sump Pump 1 to UFG Mill 3 Trash Screen Valve | 28-2040-FD-RL1-80 | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | FD | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28135 | No | Position Switches | - | F28-CP-407 | 2000-PP007-B02-10346 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.01 | XV28135 | VKG | Floor Drainage | AS2129 Table D
0 | XV | 28 | 146 | XV 28146 |  | N/A |  | UFG Mill 2 Scuttle Valve |  | 2000-F28-PID-PR-10002 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | F28MUF402-JB04 | N/A | ME039 | ME039 | Vendor Supply | [6 empty] | F28.20 | F28.20.02 | XV28146 | N/A | #N/A | #N/A
0 | XV | 28 | 202 | XV 28202 | 50 | VB03S1 | 50VB03S1-Double Acting | UFG Mill 3 Water Collection Tank Process Water Inlet Valve | 28-0101-PW-SS3-50 | 2000-F28-PID-PR-10003 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | PW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV28202 | No | Position Switches | - | F28-CP-401 | 2000-PP007-B02-10341 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10008 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F24.20 | F24.20.11 | XV28202 | VB0 | Hypersaline Water | AS2129 Table E
0 | XV | 28 | 204 | XV 28204 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Sump Pump 2 to UFG Mill 3 Trash Screen Valve | 28-0749-FD-RL1-80 | 2000-F28-PID-PR-10003 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | FD | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28204 | No | Position Switches | - | F28-CP-402 | 2000-PP007-B02-10342 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.01 | XV28204 | VKG | Floor Drainage | AS2129 Table D
0 | XV | 28 | 205 | XV 28205 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Sump Pump 2 to UFG Mill 2 Trash Screen Valve | 28-1066-FD-RL1-80 | 2000-F28-PID-PR-10003 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | FD | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28205 | No | Position Switches | - | F28-CP-402 | 2000-PP007-B02-10342 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.01 | XV28205 | VKG | Floor Drainage | AS2129 Table D
0 | XV | 28 | 231 | XV 28231 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | UFG Mill 3 Feed Pump Suction Valve | 200-MECH-RL1 | 2000-F28-PID-PR-10003 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 56 | 144 | 0.473 | 1.64 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28231 | No | Position Switches | - | F28-CP-403 | 2000-PP007-B02-10343 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.19 | XV28231 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 232 | XV 28232 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Mill 3 Feed Pump Discharge Drain Valve | 28-0747-CON-RL1-150 | 2000-F28-PID-PR-10003 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 56 | 144 | 0.473 | 1.64 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28232 | No | Position Switches | - | F28-CP-403 | 2000-PP007-B02-10343 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.19 | XV28232 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 236 | XV 28236 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Mill 3 Feed Pump Suction Drain Valve | 200-MECH-RL1 | 2000-F28-PID-PR-10003 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 56 | 144 | 0.473 | 1.64 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28236 | No | Position Switches | - | F28-CP-403 | 2000-PP007-B02-10343 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.19 | XV28236 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 282 | XV 28282 | 300 | VKGD1L1 | 300VKGD1L1-Double Acting | UFG Mill 3 Discharge Pump Suction Valve | 300-MECH-RL1 | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 10 | 25 | 0.327 | 1.41 | 700 | 12 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28282 | No | Position Switches | - | F28-CP-401 | 2000-PP007-B02-10341 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10080 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.13 | XV28282 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 283 | XV 28283 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Mill 3 Discharge Pump Drain Valve | 300-MECH-RL1 | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 10 | 25 | 0.327 | 1.41 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV28283 | No | Position Switches | - | F28-CP-401 | 2000-PP007-B02-10341 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.13 | XV28283 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 320 | XV 28320 | 150 | VBFD1S2 | 150VBFD1S2-Double Acting | UFG Product Hopper Process Water Valve |  | 2000-F28-PID-PR-10005 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 6 | Detail 7 | FC | Double Acting | Single Acting | SV28320 | No | Position Switches | - | F28-CP-407 | 2000-PP007-B02-10346 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10058 | Emerson | KEYSTONE F89-014 | 2000043108 TVF-M2WGNMM | F24.20 | F24.20.01 | XV28320 | VBF | #N/A | #N/A
0 | XV | 28 | 322 | XV 28322 | 300 | VKGD1L1 | 300VKGD1L1-Double Acting | UFG Product Pump 1 Suction Valve | 300-MECH-RL1 | 2000-F28-PID-PR-10005 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.171 | 1.22 | 700 | 12 | Detail 4 | FC | Double Acting | Single Acting | SV28322 | No | Position Switches | - | F28-CP-407 | 2000-PP007-B02-10346 | PP007 | PP007 |  | Emerson | Clarkson KGD | '2000-PP007-B02-10080 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.03 | XV28322 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 323 | XV 28323 | 100 | VKGD1L1 | 100VKGD1L1-Double Acting | UFG Product Pump 1 Drain Valve | 300-MECH-RL1 | 2000-F28-PID-PR-10005 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.171 | 1.22 | 700 | 4 | Detail 4 | FO | Double Acting | Single Acting | SV28323 | No | Position Switches | - | F28-CP-407 | 2000-PP007-B02-10346 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10046 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.03 | XV28323 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 324 | XV 28324 | 250 | VKGD1L1 | 250VKGD1L1-Double Acting | UFG Product Pump 1 Discharge Valve | 250-MECH-RL1 | 2000-F28-PID-PR-10005 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 250 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.171 | 1.22 | 700 | 10 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28324 | No | Position Switches | - | F28-CP-407 | 2000-PP007-B02-10346 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10075 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.03 | XV28324 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 325 | XV 28325 | 300 | VKGD1L1 | 300VKGD1L1-Double Acting | UFG Product Pump 2 Suction Valve | 300-MECH-RL1 | 2000-F28-PID-PR-10005 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.171 | 1.22 | 700 | 12 | Detail 4 | FC | Double Acting | Single Acting | SV28325 | No | Position Switches | - | F28-CP-407 | 2000-PP007-B02-10346 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10080 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.03 | XV28325 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 326 | XV 28326 | 100 | VKGD1L1 | 100VKGD1L1-Double Acting | UFG Product Pump 2 Drain Valve | 300-MECH-RL1 | 2000-F28-PID-PR-10005 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.171 | 1.22 | 700 | 4 | Detail 4 | FO | Double Acting | Single Acting | SV28326 | No | Position Switches | - | F28-CP-407 | 2000-PP007-B02-10346 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10046 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.03 | XV28326 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 327 | XV 28327 | 250 | VKGD1L1 | 250VKGD1L1-Double Acting | UFG Product Pump 2 Discharge Valve | 250-MECH-RL1 | 2000-F28-PID-PR-10005 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 250 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.171 | 1.22 | 700 | 10 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28327 | No | Position Switches | - | F28-CP-407 | 2000-PP007-B02-10346 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10075 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.03 | XV28327 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 331 | XV 28331 | 25 | VB03S1 | 25VB03S1-Double Acting-Solenoid on Valve | UFG Mill 1 Product Sample Flushing Valve | 28-0884-PW-SS3-50 | 2000-F28-PID-PR-10005 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | PW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 1 | Detail 7 | FC | Double Acting | Single Acting | SV28331 | No | Position Switches | Solenoid on Valve | Solenoid on Valve | N/A | PP007 | N/A | Solenoids to be installed on Valve |  |  | 2000-PP007-B02-10132 |  |  |  | F24.20 | F24.20.01 | XV28331 | VB0 | Hypersaline Water | AS2129 Table E
0 | XV | 28 | 332 | XV 28332 | 50 | VDD1L1 | 50VDD1L1-Double Acting-Solenoid on Valve | UFG Mill 1 Product Sample Valve | 28-1705-CON-PE10-63 | 2000-F28-PID-PR-10005 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | PE10 | 63 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV28332 | No | Position Switches | Solenoid on Valve | Solenoid on Valve | N/A | PP007 | N/A | Solenoids to be installed on Valve |  |  | 2000-PP007-B02-10141 |  |  |  | F34.20 | F34.20.01 | XV28332 | VDD | Concentrate Slurry | AS2129 Table D PN10
0 | XV | 28 | 338 | XV 28338 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Ultra Fine Grinding Mill 3 Feed Valve | 28-0747-CON-RL1-150 | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 56 | 144 | 0.473 | 1.64 | 700 | 6 | Detail 4 | FC | Double Acting | Single Acting | SV28338 | No | Position Switches | - | F28MUF403-JB04 | 2000-ME039-D02-10018 | PP007 | ME039 | Glencore supplied solenoid and cabinet | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F28.20 | F28.20.19 | XV28338 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 341 | XV 28341 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting-DUPLEX | UFG Mill 3 HP Process Water Valve | 28-0747-CON-RL1-150 | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 4 | FC | Double Acting | Single Acting | SV28341 | No | Position Switches | DUPLEX | F28MUF403-JB04 | 2000-ME039-D02-10018 | PP007 | ME039 | Glencore supplied solenoid and cabinet. Duplex SS gate required. | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F24.20 | F24.20.11 | XV28341 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 342 | XV 28342 | 50 | VB03S1 | 50VB03S1-Double Acting | UFG Mill 3 Gland Water Valve | 28-0734-PSW-MSG3-50 | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | PSW | MSG3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 2 | Detail 9 | FC | Double Acting | Double Acting | SVO/SVC28342 | No | Position Switches | - | F28-CP-401 | 2000-PP007-B02-10341 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10008 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F28.10 | F28.10.35 | XV28342 | VB0 | Process Scheme Water | AS2129 Table E
0 | XV | 28 | 395 | XV 28395 |  | N/A |  | UFG Mill 3 Scuttle Valve |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | F28MUF403-JB04 | N/A | ME039 | ME039 | Vendor Supply | [6 empty] | F28.20 | F28.20.20 | XV28395 | N/A | #N/A | #N/A
0 | XV | 28 | 463 | XV 28463 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Mill 3 Concentrate Trash Screen Flotation Concentrate Inlet Valve | 28-1755-CON-RL1-80 | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.171 | 1.22 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28463 | No | Position Switches | - | F28-CP-401 | 2000-PP007-B02-10341 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.08 | XV28463 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 464 | XV 28464 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | UFG Mill 3 Concentrate Trash Screen Flotation Concentrate Bypass Valve | 28-1756-CON-RL1-80 | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield | CON | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.171 | 1.22 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28464 | No | Position Switches | - | F28-CP-401 | 2000-PP007-B02-10341 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.08 | XV28464 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 28 | 500 | XV 28500 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28500 | No | Position Switches | - | F28CY431-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28500 | N/A | #N/A | #N/A
0 | XV | 28 | 501 | XV 28501 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28501 | No | Position Switches | - | F28CY431-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28501 | N/A | #N/A | #N/A
0 | XV | 28 | 502 | XV 28502 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28502 | No | Position Switches | - | F28CY431-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28502 | N/A | #N/A | #N/A
0 | XV | 28 | 503 | XV 28503 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28503 | No | Position Switches | - | F28CY431-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28503 | N/A | #N/A | #N/A
0 | XV | 28 | 504 | XV 28504 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28504 | No | Position Switches | - | F28CY431-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28504 | N/A | #N/A | #N/A
0 | XV | 28 | 505 | XV 28505 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28505 | No | Position Switches | - | F28CY431-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28505 | N/A | #N/A | #N/A
0 | XV | 28 | 506 | XV 28506 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28506 | No | Position Switches | - | F28CY431-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28506 | N/A | #N/A | #N/A
0 | XV | 28 | 507 | XV 28507 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28507 | No | Position Switches | - | F28CY431-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28507 | N/A | #N/A | #N/A
0 | XV | 28 | 508 | XV 28508 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28508 | No | Position Switches | - | F28CY431-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28508 | N/A | #N/A | #N/A
0 | XV | 28 | 509 | XV 28509 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28509 | No | Position Switches | - | F28CY431-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28509 | N/A | #N/A | #N/A
0 | XV | 28 | 510 | XV 28510 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28510 | No | Position Switches | - | F28CY431-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28510 | N/A | #N/A | #N/A
0 | XV | 28 | 511 | XV 28511 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28511 | No | Position Switches | - | F28CY431-CP01 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28511 | N/A | #N/A | #N/A
0 | XV | 28 | 512 | XV 28512 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28512 | No | Position Switches | - | F28CY431-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28512 | N/A | #N/A | #N/A
0 | XV | 28 | 513 | XV 28513 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28513 | No | Position Switches | - | F28CY431-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28513 | N/A | #N/A | #N/A
0 | XV | 28 | 514 | XV 28514 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28514 | No | Position Switches | - | F28CY431-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28514 | N/A | #N/A | #N/A
0 | XV | 28 | 515 | XV 28515 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28515 | No | Position Switches | - | F28CY431-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28515 | N/A | #N/A | #N/A
0 | XV | 28 | 516 | XV 28516 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28516 | No | Position Switches | - | F28CY431-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28516 | N/A | #N/A | #N/A
0 | XV | 28 | 517 | XV 28517 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28517 | No | Position Switches | - | F28CY431-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28517 | N/A | #N/A | #N/A
0 | XV | 28 | 518 | XV 28518 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28518 | No | Position Switches | - | F28CY431-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28518 | N/A | #N/A | #N/A
0 | XV | 28 | 519 | XV 28519 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28519 | No | Position Switches | - | F28CY431-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28519 | N/A | #N/A | #N/A
0 | XV | 28 | 520 | XV 28520 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28520 | No | Position Switches | - | F28CY431-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28520 | N/A | #N/A | #N/A
0 | XV | 28 | 521 | XV 28521 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28521 | No | Position Switches | - | F28CY431-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28521 | N/A | #N/A | #N/A
0 | XV | 28 | 522 | XV 28522 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28522 | No | Position Switches | - | F28CY431-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28522 | N/A | #N/A | #N/A
0 | XV | 28 | 523 | XV 28523 |  | N/A |  | UFG Mill 3 Cyclone Cluster Actuated Feed Valves |  | 2000-F28-PID-PR-10004 | 2000-F24-PID-PR-10027 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC28523 | No | Position Switches | - | F28CY431-CP02 | N/A | ME005B | ME005B | Vendor Supply | [6 empty] | F28.20 | F28.20.12 | XV28523 | N/A | #N/A | #N/A
0 | FCV | 30 | 338 | FCV 30338 | 50 | VDE1S2 | 50VDE1S2-Double Acting-Positioner | CIL 2 Barren Eluate Feed Flow Control Valve | 65-4205-BE-PE8-90 | 2000-F65-PID-PR-10005 | 2000-F30-PID-PR-10007 | Stage 2 | Brownfield | BE | PE8 | 90 | 0 | 30 | 280 | 0 | 125 | N/A | N/A | N/A | 1.1 | 1000 | 2 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F30-CP-405 | 2000-PP007-B02-10368 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10142 |  |  |  | F66.10 | F66.10.10 | FCV30338 | VDE | Barren Eluate | AS2129 Table D PN10
1 | FCV | 30 | 421 | FCV 30421 | 25 | VDE1S2 | 25VDE1S2-Double Acting-Positioner | Leach Feed Distribution Cyanide Flow Control Valve | 30-4028-CN-SS2-25 | 2000-F30-PID-PR-10016 | 2000-F30-PID-PR-10016 | Stage 2 | Brownfield | CN | SS2 | 25 | 0 | 5 | 200 | 200 | 50 | N/A | N/A | N/A | 1.1 | 1000 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F30-CP-403 | 2000-PP007-B02-10366 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10135 |  |  |  | F72.80 | F72.80.05 | FCV30421 | VDE | Cyanide Solution | AS2129 Table E
1 | FCV | 30 | 422 | FCV 30422 | 25 | VDE1S2 | 25VDE1S2-Double Acting-Positioner | CIL 2 Leach Tank 2 Cyanide Flow Control Valve | 30-4104-CN-SS2-25 | 2000-F30-PID-PR-10016 | 2000-F30-PID-PR-10016 | Stage 2 | Brownfield | CN | SS2 | 25 | 0 | 5 | 200 | 200 | 50 | N/A | N/A | N/A | 1.1 | 1000 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F30-CP-404 | 2000-PP007-B02-10367 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10135 |  |  |  | F72.80 | F72.80.05 | FCV30422 | VDE | Cyanide Solution | AS2129 Table E
1 | FCV | 30 | 423 | FCV 30423 | 25 | VDE1S2 | 25VDE1S2-Double Acting-Positioner | CIL 2 Leach Tank 3 Cyanide Flow Control Valve | 30-4105-CN-SS2-25 | 2000-F30-PID-PR-10016 | 2000-F30-PID-PR-10016 | Stage 2 | Brownfield | CN | SS2 | 25 | 0 | 5 | 200 | 200 | 50 | N/A | N/A | N/A | 1.1 | 1000 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F30-CP-404 | 2000-PP007-B02-10367 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10135 |  |  |  | F72.80 | F72.80.05 | FCV30423 | VDE | Cyanide Solution | AS2129 Table E
1 | FCV | 30 | 424 | FCV 30424 | 25 | VDE1S2 | 25VDE1S2-Double Acting-Positioner | CIL 2 Leach Tank 4 Cyanide Flow Control Valve | 30-4106-CN-SS2-25 | 2000-F30-PID-PR-10016 | 2000-F30-PID-PR-10016 | Stage 2 | Brownfield | CN | SS2 | 25 | 0 | 5 | 200 | 200 | 50 | N/A | N/A | N/A | 1.1 | 1000 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F30-CP-404 | 2000-PP007-B02-10367 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10135 |  |  |  | F72.80 | F72.80.05 | FCV30424 | VDE | Cyanide Solution | AS2129 Table E
1 | FCV | 30 | 425 | FCV 30425 | 25 | VDE1S2 | 25VDE1S2-Double Acting-Positioner | CIL 2 Leach Tank 5 Cyanide Flow Control Valve | 30-4107-CN-SS2-25 | 2000-F30-PID-PR-10016 | 2000-F30-PID-PR-10016 | Stage 2 | Brownfield | CN | SS2 | 25 | 0 | 5 | 200 | 200 | 50 | N/A | N/A | N/A | 1.1 | 1000 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F30-CP-404 | 2000-PP007-B02-10367 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10135 |  |  |  | F72.80 | F72.80.05 | FCV30425 | VDE | Cyanide Solution | AS2129 Table E
1 | FCV | 30 | 426 | FCV 30426 | 25 | VDE1S2 | 25VDE1S2-Double Acting-Positioner | CIL 2 Leach Tank 6 Cyanide Flow Control Valve | 30-4115-CN-SS2-25 | 2000-F30-PID-PR-10016 | 2000-F30-PID-PR-10016 | Stage 2 | Brownfield | CN | SS2 | 25 | 0 | 5 | 200 | 200 | 50 | N/A | N/A | N/A | 1.1 | 1000 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F30-CP-404 | 2000-PP007-B02-10367 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10135 |  |  |  | F72.80 | F72.80.05 | FCV30426 | VDE | Cyanide Solution | AS2129 Table E
0 | FCV | 30 | 557 | FCV 30557 | 25 | VGLE1S1 | 25VGLE1S1-Double Acting-Positioner | CIL 2 Oxygen Injection Pump 1 Injector 1 Flow Control Valve | 30-4204-OXY-SS6-25 | 2000-F30-PID-PR-10007 | 2000-F30-PID-PR-10007 | Stage 2 | Brownfield | OXY | SS6 | 25 | 0 | 75 | 700 | 700 | 150 | N/A | N/A | N/A | OXYGEN | 1400 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F30-CP-405 | 2000-PP007-B02-10368 | PP007 | PP007 |  | Emerson | FISHER 025 24000SVF | 2000-PP007-B02-10005 | Emerson | Pneumatic actuator | DVC2000,HART Communicating-HC 4-20mA | F30.30 | F30.30.06 | FCV30557 | VGL | Oxygen | AS2129 Table E
0 | FCV | 30 | 559 | FCV 30559 | 25 | VGLE1S1 | 25VGLE1S1-Double Acting-Positioner | CIL 2 Oxygen Injection Pump 1 Injector 2 Flow Control Valve | 30-4205-OXY-SS6-25 | 2000-F30-PID-PR-10007 | 2000-F30-PID-PR-10007 | Stage 2 | Brownfield | OXY | SS6 | 25 | 0 | 75 | 700 | 700 | 150 | N/A | N/A | N/A | OXYGEN | 1400 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F30-CP-405 | 2000-PP007-B02-10368 | PP007 | PP007 |  | Emerson | FISHER 025 24000SVF | 2000-PP007-B02-10005 | Emerson | Pneumatic actuator | DVC2000,HART Communicating-HC 4-20mA | F30.30 | F30.30.06 | FCV30559 | VGL | Oxygen | AS2129 Table E
0 | FCV | 30 | 572 | FCV 30572 | 25 | VGLE1S1 | 25VGLE1S1-Double Acting-Positioner | CIL 2 Oxygen Injection Pump 2 Injector 1 Flow Control Valve | 30-4206-OXY-SS6-25 | 2000-F30-PID-PR-10007 | 2000-F30-PID-PR-10007 | Stage 2 | Brownfield | OXY | SS6 | 25 | 0 | 75 | 700 | 700 | 150 | N/A | N/A | N/A | OXYGEN | 1400 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F30-CP-406 | 2000-PP007-B02-10369 | PP007 | PP007 |  | Emerson | FISHER 025 24000SVF | 2000-PP007-B02-10005 | Emerson | Pneumatic actuator | DVC2000,HART Communicating-HC 4-20mA | F30.30 | F30.30.06 | FCV30572 | VGL | Oxygen | AS2129 Table E
0 | FCV | 30 | 574 | FCV 30574 | 25 | VGLE1S1 | 25VGLE1S1-Double Acting-Positioner | CIL 2 Oxygen Injection Pump 2 Injector 2 Flow Control Valve | 30-4207-OXY-SS6-25 | 2000-F30-PID-PR-10007 | 2000-F30-PID-PR-10007 | Stage 2 | Brownfield | OXY | SS6 | 25 | 0 | 75 | 700 | 700 | 150 | N/A | N/A | N/A | OXYGEN | 1400 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F30-CP-406 | 2000-PP007-B02-10369 | PP007 | PP007 |  | Emerson | FISHER 025 24000SVF | 2000-PP007-B02-10005 | Emerson | Pneumatic actuator | DVC2000,HART Communicating-HC 4-20mA | F30.30 | F30.30.06 | FCV30574 | VGL | Oxygen | AS2129 Table E
0 | HV | 30 | 443 | HV 30443 | 250 | VKGD1L1 | 250VKGD1L1-Manual | Final Concentrate Pumps to Concentrate Thickener Feed Box Manual Valve | 30-3101-FS-RL1-250 | 2000-F30-PID-PR-10001 | N/A | Stage 1 | Brownfield | FS | RL1 | 250 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 0.221 | 1.28 | 700 | 10 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | Clarkson KGD | 2000-PP007-B02-10076 | Emerson | Manual handwheel | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.01 | HV30443 | VKG | Flotation Slurry | AS2129 Table D
0 | HV | 30 | 444 | HV 30444 | 250 | VKGD1L1 | 250VKGD1L1-Manual | Final Concentrate Pumps to Filter Feed Tanks Feed Box Bypass Manual Valve | 30-3009-FS-RL1-250 | 2000-F30-PID-PR-10001 | N/A | Stage 1 | Brownfield | FS | RL1 | 250 | N/A | N/A | N/A | N/A | N/A | 82 | 210 | 0.221 | 1.28 | 700 | 10 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | Clarkson KGD | 2000-PP007-B02-10076 | Emerson | Manual handwheel | P+F PXM NCB5-18GM40-Z0 24VDC | F18.20 | F18.20.01 | HV30444 | VKG | Flotation Slurry | AS2129 Table D
0 | PCV | 30 | 586 | PCV 30586 | 50 | PCV | 50PCV-N/A-Oxygen | CIL 2 Adsorption Tanks Oxygen Injection Pressure Control Valve | 30-4223-OXY-SS6-50 | 2000-F30-PID-PR-10013 | N/A | Stage 2 | Brownfield | OXY | SS6 | 50 | 680 | 1060 | 800 | 150 | 150 | N/A | N/A | N/A | OXYGEN | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Oxygen | N/A | N/A | PP007 | N/A | Set at 650kPag | Fisher | 1098-EGR | 2000-PP007-B02-10420 | Fisher | Size 40 | N/A | F30.30 | F30.30.06 | PCV30586 | PCV | Oxygen | AS2129 Table E
0 | PCV | 30 | 587 | PCV 30587 | 25 | PCV | 25PCV-N/A-Oxygen | CIL 2 Leach Tank 1 Oxygen Injection Pressure Control Valve | 30-4204-OXY-SS6-25 | 2000-F30-PID-PR-10007 | N/A | Stage 2 | Brownfield | OXY | SS6 | 25 | 150 | 180 | 800 | 100 | 100 | N/A | N/A | N/A | OXYGEN | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Oxygen | N/A | N/A | PP007 | N/A | Set at 700kPag | Fisher | MR95H-3063-2995955 | 2000-PP007-B02-10418 | N/A | N/A | N/A | F30.30 | F30.30.06 | PCV30587 | PCV | Oxygen | AS2129 Table E
0 | PCV | 30 | 589 | PCV 30589 | 25 | PCV | 25PCV-N/A-Oxygen | CIL 2 Leach Tank 2 Oxygen Injection Pressure Control Valve | 30-4206-OXY-SS6-25 | 2000-F30-PID-PR-10007 | N/A | Stage 2 | Brownfield | OXY | SS6 | 25 | 150 | 180 | 800 | 100 | 100 | N/A | N/A | N/A | OXYGEN | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Oxygen | N/A | N/A | PP007 | N/A | Set at 700kPag | Fisher | MR95H-3063-2995955 | 2000-PP007-B02-10418 | N/A | N/A | N/A | F30.30 | F30.30.06 | PCV30589 | PCV | Oxygen | AS2129 Table E
0 | SV | 30 | 403 | SV 30403 | 25 | SV | 25SV-Solenoid-FO | Concentrate Pre-Leach Thickener Underflow Pump 1 Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F30.20 | F30.20.05 | SV30403 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 30 | 408 | SV 30408 | 25 | SV | 25SV-Solenoid-FO | Concentrate Pre-Leach Thickener Underflow Pump 2 Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F30.20 | F30.20.05 | SV30408 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 30 | 434 | SV 30434 | 25 | SV | 25SV-Solenoid-FO | Concentrate Leach Transfer Pump 1 Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F30.30 | F30.30.13 | SV30434 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 30 | 440 | SV 30440 | 25 | SV | 25SV-Solenoid-FO | Concentrate Leach Transfer Pump 2 Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F30.30 | F30.30.13 | SV30440 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 30 | 447 | SV 30447 | 25 | SV | 25SV-Solenoid-FO | CONCENTRATE THICKENER U/F PUMP 1 GLAND WATER | 30-3051-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Brownfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F30.40 | F30.40.02 | SV30447 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 30 | 452 | SV 30452 | 25 | SV | 25SV-Solenoid-FO | CONCENTRATE THICKENER U/F PUMP 2 GLAND WATER | 30-3052-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Brownfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F30.40 | F30.40.02 | SV30452 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 30 | 466 | SV 30466 | 25 | SV | 25SV-Solenoid-FO | CIL 3 Tails Pump 1 Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F30.30 | F30.30.05 | SV30466 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 30 | 472 | SV 30472 | 25 | SV | 25SV-Solenoid-FO | CIL 3 Tails Pump 2 Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F30.30 | F30.30.05 | SV30472 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 30 | 552 | SV 30552 | 25 | SV | 25SV-Solenoid-FO | CIL 2 Oxygen Injection Pump 1 Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F30.30 | F30.30.06 | SV30552 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 30 | 567 | SV 30567 | 25 | SV | 25SV-Solenoid-FO | CIL 2 Oxygen Injection Pump 2 Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F30.30 | F30.30.06 | SV30567 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 30 | 590 | SV 30590 | 25 | SV | 25SV-Solenoid-FC | CIL 3 Barren Carbon Screen Underflow Hopper Area Sump Pump Compressed Air Valve | 30-4251-IA-MSG3-25 | 2000-F30-PID-PR-10020 | N/A | Stage 2 | Brownfield | IA | MSG3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AIR | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F30.10 | F30.10.17 | SV30590 | SV | Instrument Air | AS2129 Table E
0 | XV | 30 | 401 | XV 30401 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Concentrate Pre-Leach Thickener Underflow Pump 1 Suction Drain Valve | 30-4021-CON-RL1-200 | 2000-F30-PID-PR-10004 | 2000-F30-PID-PR-10004 | Stage 2 | Brownfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV30401 | No | Position Switches | - | F30-CP-407 | 2000-PP007-B02-10370 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.20 | F30.20.05 | XV30401 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 402 | XV 30402 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Concentrate Pre-Leach Thickener Underflow Pump 1 Discharge Valve | 30-4067-CON-RL1-150 | 2000-F30-PID-PR-10004 | 2000-F30-PID-PR-10004 | Stage 2 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30402 | No | Position Switches | - | F30-CP-407 | 2000-PP007-B02-10370 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.20 | F30.20.05 | XV30402 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 406 | XV 30406 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Concentrate Pre-Leach Thickener Underflow Pump 2 Suction Drain Valve | 30-4022-CON-RL1-200 | 2000-F30-PID-PR-10004 | 2000-F30-PID-PR-10004 | Stage 2 | Brownfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV30406 | No | Position Switches | - | F30-CP-407 | 2000-PP007-B02-10370 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.20 | F30.20.05 | XV30406 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 407 | XV 30407 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Concentrate Pre-Leach Thickener Underflow Pump 2 Discharge Valve | 30-4023-CON-RL1-150 | 2000-F30-PID-PR-10004 | 2000-F30-PID-PR-10004 | Stage 2 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30407 | No | Position Switches | - | F30-CP-407 | 2000-PP007-B02-10370 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.20 | F30.20.05 | XV30407 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 413 | XV 30413 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Concentrate Pre-Leach Thickener Underflow Pumps to CIL 2 Feed Distribution Box Valve | 30-4000-CON-RL1-150 | 2000-F30-PID-PR-10004 | 2000-F30-PID-PR-10004 | Stage 2 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30413 | No | Position Switches | - | F30-CP-408 | 2000-PP007-B02-10371 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.20 | F30.20.05 | XV30413 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 414 | XV 30414 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Concentrate Pre-Leach Thickener Underflow Pumps to CIL 2 Feed Distribution Box Valve | 30-4067-CON-RL1-150 | 2000-F30-PID-PR-10004 | 2000-F30-PID-PR-10004 | Stage 2 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30414 | No | Position Switches | - | F30-CP-408 | 2000-PP007-B02-10371 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.20 | F30.20.05 | XV30414 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 415 | XV 30415 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | Concentrate Pre-Leach Thickener Underflow Pumps to CIL 2 Feed Distribution Box Drain Valve | 30-4000-CON-RL1-150 | 2000-F30-PID-PR-10004 | 2000-F30-PID-PR-10004 | Stage 2 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 2 | Detail 4 | FO | Double Acting | Single Acting | SV30415 | No | Position Switches | - | F30-CP-408 | 2000-PP007-B02-10371 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.20 | F30.20.05 | XV30415 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 416 | XV 30416 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | Concentrate Pre-Leach Thickener Underflow Pumps to CIL 2 Feed Distribution Box Drain Valve | 30-4067-CON-RL1-150 | 2000-F30-PID-PR-10004 | 2000-F30-PID-PR-10004 | Stage 2 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 2 | Detail 4 | FO | Double Acting | Single Acting | SV30416 | No | Position Switches | - | F30-CP-408 | 2000-PP007-B02-10371 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.20 | F30.20.05 | XV30416 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 419 | XV 30419 | 25 | VB03S1 | 25VB03S1-Double Acting | CIL 2 Feed Primary Sampler Sample Flushing Water Valve | 30-4233-CW-SS3-25 | 2000-F30-PID-PR-10004 | 2000-F30-PID-PR-10004 | Stage 2 | Brownfield | CW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 1 | Detail 7 | FC | Double Acting | Single Acting | SV30419 | No | Position Switches | - | F30-CP-408 | 2000-PP007-B02-10371 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10001 | Emerson | KEYSTONE F89-003 | SWIT TOP TVF-M2WGNMM | F30.20 | F30.20.07 | XV30419 | VB0 | Cyanide Water | AS2129 Table E
0 | XV | 30 | 420 | XV 30420 | 50 | VDD1L1 | 50VDD1L1-Double Acting | CIL 2 Feed Primary Sampler Sample Isolation Valve | 30-4216-CON-PE10-63 | 2000-F30-PID-PR-10004 | 2000-F30-PID-PR-10004 | Stage 2 | Brownfield | CON | PE10 | 63 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV30420 | No | Position Switches | - | F30-CP-408 | 2000-PP007-B02-10371 | PP007 | PP007 |  | KDV | Series 37 Straight Through (ST) | 2000-PP007-B02-10017 | KDV | Pneumatic cylinder | IMTEX Std Box Mech on/off Sw KDV/Linear Drive +2 Terminal | F30.20 | F30.20.05 | XV30420 | VDD | Concentrate Slurry | AS2129 Table D PN10
0 | XV | 30 | 428 | XV 30428 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Concentrate Pre-Leach Thickener Underflow Pump 1 Suction Flushing Valve | 30-4188-CW-RL1-80 | 2000-F30-PID-PR-10004 | 2000-F30-PID-PR-10004 | Stage 2 | Brownfield | CW | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30428 | No | Position Switches | - | F30-CP-407 | 2000-PP007-B02-10370 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.20 | F30.20.07 | XV30428 | VKG | Cyanide Water | AS2129 Table D
0 | XV | 30 | 429 | XV 30429 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Concentrate Pre-Leach Thickener Underflow Pump 2 Suction Flushing Valve | 30-4189-CW-RL1-80 | 2000-F30-PID-PR-10004 | 2000-F30-PID-PR-10004 | Stage 2 | Brownfield | CW | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30429 | No | Position Switches | - | F30-CP-407 | 2000-PP007-B02-10370 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.20 | F30.20.07 | XV30429 | VKG | Cyanide Water | AS2129 Table D
0 | XV | 30 | 431 | XV 30431 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | Concentrate Leach Transfer Pump 1 Suction Valve | 30-4230-CON-RL1-200 | 2000-F30-PID-PR-10006 | 2000-F30-PID-PR-10006 | Stage 2 | Brownfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30431 | No | Position Switches | - | F30-CP-409 | 2000-PP007-B02-10372 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.13 | XV30431 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 432 | XV 30432 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Concentrate Leach Transfer Pump 1 Suction Drain Valve | 30-4230-CON-RL1-200 | 2000-F30-PID-PR-10006 | 2000-F30-PID-PR-10006 | Stage 2 | Brownfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV30432 | No | Position Switches | - | F30-CP-409 | 2000-PP007-B02-10372 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.13 | XV30432 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 433 | XV 30433 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Concentrate Leach Transfer Pump 1 Discharge Valve | 30-4068-CON-RL3-150 | 2000-F30-PID-PR-10006 | 2000-F30-PID-PR-10006 | Stage 2 | Brownfield | CON | RL3 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30433 | No | Position Switches | - | F30-CP-409 | 2000-PP007-B02-10372 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.13 | XV30433 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 437 | XV 30437 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | Concentrate Leach Transfer Pump 2 Suction Valve | 30-4231-CON-RL1-200 | 2000-F30-PID-PR-10006 | 2000-F30-PID-PR-10006 | Stage 2 | Brownfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30437 | No | Position Switches | - | F30-CP-409 | 2000-PP007-B02-10372 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.13 | XV30437 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 438 | XV 30438 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Concentrate Leach Transfer Pump 2 Suction Drain Valve | 30-4231-CON-RL1-200 | 2000-F30-PID-PR-10006 | 2000-F30-PID-PR-10006 | Stage 2 | Brownfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV30438 | No | Position Switches | - | F30-CP-409 | 2000-PP007-B02-10372 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.13 | XV30438 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 439 | XV 30439 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | Concentrate Leach Transfer Pump 2 Discharge Valve | 30-4070-CON-RL3-150 | 2000-F30-PID-PR-10006 | 2000-F30-PID-PR-10006 | Stage 2 | Brownfield | CON | RL3 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30439 | No | Position Switches | - | F30-CP-409 | 2000-PP007-B02-10372 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.13 | XV30439 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 445 | XV 30445 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Concentrate Thickener Underflow Pump 1 Suction Drain Valve | F30-3022-CON-RL1-200 | 2000-F30-PID-PR-10002 | 2000-F30-PID-PR-10001 | Stage 1 | Brownfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV30445 | No | Position Switches | - | F30-CP-401 | 2000-PP007-B02-10347 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.40 | F30.40.02 | XV30445 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 446 | XV 30446 | 150 | VKGD1L2 | 150VKGD1L2-Double Acting | Concentrate Thickener Underflow Pump 1 Discharge Valve | F30-3017-CON-RL1-150 | 2000-F30-PID-PR-10002 | 2000-F30-PID-PR-10001 | Stage 1 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30446 | No | Position Switches | - | F30-CP-401 | 2000-PP007-B02-10347 | PP007 | PP007 |  | Emerson | Clarkson KGA+ | 2000-PP007-B02-10063 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.40 | F30.40.02 | XV30446 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 450 | XV 30450 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Concentrate Thickener Underflow Pump 2 Suction Drain Valve | F30-3023-CON-RL1-200 | 2000-F30-PID-PR-10002 | 2000-F30-PID-PR-10001 | Stage 1 | Brownfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV30450 | No | Position Switches | - | F30-CP-401 | 2000-PP007-B02-10347 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.40 | F30.40.02 | XV30450 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 451 | XV 30451 | 150 | VKGD1L2 | 150VKGD1L2-Double Acting | Concentrate Thickener Underflow Pump 2 Discharge Valve | F30-3018-CON-RL1-150 | 2000-F30-PID-PR-10002 | 2000-F30-PID-PR-10001 | Stage 1 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30451 | No | Position Switches | - | F30-CP-401 | 2000-PP007-B02-10347 | PP007 | PP007 |  | Emerson | Clarkson KGA+ | 2000-PP007-B02-10063 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.40 | F30.40.02 | XV30451 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 457 | XV 30457 | 150 | VKGD1L2 | 150VKGD1L2-Double Acting | Concentrate Thickener Underflow Pumps Recirculation Valve | F30-3024-CON-RL1-150 | 2000-F30-PID-PR-10002 | 2000-F30-PID-PR-10002 | Stage 1 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30457 | No | Position Switches | - | F30-CP-402 | 2000-PP007-B02-10348 | PP007 | PP007 |  | Emerson | Clarkson KGA+ | 2000-PP007-B02-10063 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.40 | F30.40.02 | XV30457 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 458 | XV 30458 | 150 | VKGD1L2 | 150VKGD1L2-Double Acting | Concentrate Thickener Underflow Pumps to Filter Feed Tanks Valve | F30-3017-CON-RL1-150 | 2000-F30-PID-PR-10002 | 2000-F30-PID-PR-10002 | Stage 1 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30458 | No | Position Switches | - | F30-CP-402 | 2000-PP007-B02-10348 | PP007 | PP007 |  | Emerson | Clarkson KGA+ | 2000-PP007-B02-10063 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.40 | F30.40.02 | XV30458 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 463 | XV 30463 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | CIL 3 Tails Pump 1 Suction Valve | 30-4108-CON-RL1-200 | 2000-F30-PID-PR-10011 | 2000-F30-PID-PR-10011 | Stage 2 | Brownfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30463 | No | Position Switches | - | F30-CP-410 | 2000-PP007-B02-10373 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.05 | XV30463 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 464 | XV 30464 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | CIL 3 Tails Pump 1 Suction Drain Valve | 30-4108-CON-RL1-200 | 2000-F30-PID-PR-10011 | 2000-F30-PID-PR-10011 | Stage 2 | Brownfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV30464 | No | Position Switches | - | F30-CP-410 | 2000-PP007-B02-10373 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.05 | XV30464 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 465 | XV 30465 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | CIL 3 Tails Pump 1 Discharge Valve | 30-4110-CON-RL1-150 | 2000-F30-PID-PR-10011 | 2000-F30-PID-PR-10011 | Stage 2 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30465 | No | Position Switches | - | F30-CP-410 | 2000-PP007-B02-10373 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.05 | XV30465 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 469 | XV 30469 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | CIL 3 Tails Pump 2 Suction Valve | 30-4109-CON-RL1-200 | 2000-F30-PID-PR-10011 | 2000-F30-PID-PR-10011 | Stage 2 | Brownfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30469 | No | Position Switches | - | F30-CP-410 | 2000-PP007-B02-10373 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.05 | XV30469 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 470 | XV 30470 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | CIL 3 Tails Pump 2 Suction Drain Valve | 30-4109-CON-RL1-200 | 2000-F30-PID-PR-10011 | 2000-F30-PID-PR-10011 | Stage 2 | Brownfield | CON | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV30470 | No | Position Switches | - | F30-CP-410 | 2000-PP007-B02-10373 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.05 | XV30470 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 471 | XV 30471 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | CIL 3 Tails Pump 2 Discharge Valve | 30-4111-CON-RL1-150 | 2000-F30-PID-PR-10011 | 2000-F30-PID-PR-10011 | Stage 2 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30471 | No | Position Switches | - | F30-CP-410 | 2000-PP007-B02-10373 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.05 | XV30471 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 475 | XV 30475 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | Concentrate Thickener Underflow Pumps to Filter Feed Tanks Drain Valve | F30-3017-CON-RL1-150 | 2000-F30-PID-PR-10002 | 2000-F30-PID-PR-10002 | Stage 1 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 2 | Detail 4 | FO | Double Acting | Single Acting | SV30475 | No | Position Switches | - | F30-CP-402 | 2000-PP007-B02-10348 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.40 | F30.40.02 | XV30475 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 476 | XV 30476 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | Concentrate Thickener Underflow Pumps Recirculation Drain Valve | F30-3024-CON-RL1-150 | 2000-F30-PID-PR-10002 | 2000-F30-PID-PR-10002 | Stage 1 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 2 | Detail 4 | FO | Double Acting | Single Acting | SV30476 | No | Position Switches | - | F30-CP-402 | 2000-PP007-B02-10348 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.40 | F30.40.02 | XV30476 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 477 | XV 30477 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Concentrate Thickener Underflow Pump 1 Suction Flushing Valve | 30-3083-PW-RL1-80 | 2000-F30-PID-PR-10002 | 2000-F30-PID-PR-10001 | Stage 1 | Brownfield | PW | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30477 | No | Position Switches | - | F30-CP-401 | 2000-PP007-B02-10347 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.40 | F30.40.05 | XV30477 | VKG | Hypersaline Water | AS2129 Table D
0 | XV | 30 | 478 | XV 30478 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Concentrate Thickener Underflow Pump 2 Suction Flushing Valve | 30-3084-PW-RL1-80 | 2000-F30-PID-PR-10002 | 2000-F30-PID-PR-10001 | Stage 1 | Brownfield | PW | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30478 | No | Position Switches | - | F30-CP-401 | 2000-PP007-B02-10347 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.40 | F30.40.05 | XV30478 | VKG | Hypersaline Water | AS2129 Table D
0 | XV | 30 | 481 | XV 30481 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | CIL 2 Leach Feed Box Lime Addition Valve | 30-4059-LS-RL1-80 | 2000-F30-PID-PR-10016 | 2000-F30-PID-PR-10016 | Stage 2 | Brownfield | LS | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30481 | No | Position Switches | - | F30-CP-403 | 2000-PP007-B02-10366 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F72.110 | F72.110.03 | XV30481 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 30 | 483 | XV 30483 | 80 | VBFD1L1 | 80VBFD1L1-Double Acting | CIL 3 Tails Hopper Water Valve | 30-2356-CW-PE8-90 | 2000-F30-PID-PR-10011 | 2000-F30-PID-PR-10011 | Stage 2 | Brownfield | CW | PE8 | 90 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 7 | FC | Double Acting | Single Acting | SV30483 | No | Position Switches | - | F30-CP-410 | 2000-PP007-B02-10373 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10025 |  |  |  | F30.30 | F30.30.16 | XV30483 | VBF | Cyanide Water | AS2129 Table D PN10
0 | XV | 30 | 484 | XV 30484 | 200 | VKGD1L3 | 200VKGD1L3-Double Acting | Acid Effluent & Fine Carbon Pump 2 Suction Valve | 200-MECH-RL5 | 2000-F30-PID-PR-10020 | 2000-F30-PID-PR-10020 | Stage 2 | Brownfield | AE | RL5 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30484 | No | Position Switches | - | F30-CP-411 | 2000-PP007-B02-10374 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10150 |  |  |  | F30.30 | F30.30.02 | XV30484 | VKG | Acid Effluent | #N/A
0 | XV | 30 | 486 | XV 30486 | 80 | VKGD1L3 | 80VKGD1L3-Double Acting | Acid Effluent & Fine Carbon Pump 2 Suction Drain Valve | 200-MECH-RL5 | 2000-F30-PID-PR-10020 | 2000-F30-PID-PR-10020 | Stage 2 | Brownfield | AE | RL5 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV30486 | No | Position Switches | - | F30-CP-411 | 2000-PP007-B02-10374 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10146 |  |  |  | F30.30 | F30.30.02 | XV30486 | VKG | Acid Effluent | #N/A
0 | XV | 30 | 487 | XV 30487 | 150 | VKGD1L3 | 150VKGD1L3-Double Acting | Acid Effluent & Fine Carbon Pump 2 Discharge Valve | 30-4221-AE-RL5-150 | 2000-F30-PID-PR-10020 | 2000-F30-PID-PR-10020 | Stage 2 | Brownfield | AE | RL5 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30487 | No | Position Switches | - | F30-CP-411 | 2000-PP007-B02-10374 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10149 |  |  |  | F30.30 | F30.30.02 | XV30487 | VKG | Acid Effluent | #N/A
0 | XV | 30 | 489 | XV 30489 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Concentrate Leach Transfer Orifice Station Drain | 30-4039-CON-RL3-150 | 2000-F30-PID-PR-10006 | 2000-F30-PID-PR-10006 | Stage 2 | Brownfield | CON | RL3 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV30489 | No | Position Switches | - | F30-CP-409 | 2000-PP007-B02-10372 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.13 | XV30489 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 491 | XV 30491 | 50 | VB03S1 | 50VB03S1-Double Acting-Solenoid on Valve | CIL 3 Barren Carbon Sizing Screen Spray Water Valve | 30-4044-CW-SS3-50 | 2000-F30-PID-PR-10020 | 2000-F30-PID-PR-10020 | Stage 2 | Brownfield | CW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV30491 | No | Position Switches | Solenoid on Valve | Solenoid on Valve | N/A | PP007 | N/A | Solenoids to be installed on Valve | Emerson | K-BALL F182 | 2000-PP007-B02-10107 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F30.30 | F30.30.16 | XV30491 | VB0 | Cyanide Water | AS2129 Table E
0 | XV | 30 | 494 | XV 30494 | 200 | VKGD1L3 | 200VKGD1L3-Double Acting | Acid Effluent & Fine Carbon Pump 1 Suction Valve | 200-MECH-RL5 | 2000-F30-PID-PR-10020 | 2000-F30-PID-PR-10020 | Stage 2 | Brownfield | AE | RL5 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30494 | No | Position Switches | - | F30-CP-411 | 2000-PP007-B02-10374 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10150 |  |  |  | F30.30 | F30.30.02 | XV30494 | VKG | Acid Effluent | #N/A
0 | XV | 30 | 495 | XV 30495 | 80 | VKGD1L3 | 80VKGD1L3-Double Acting | Acid Effluent & Fine Carbon Pump 1 Suction Drain Valve | 200-MECH-RL5 | 2000-F30-PID-PR-10020 | 2000-F30-PID-PR-10020 | Stage 2 | Brownfield | AE | RL5 | 200 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 3 | Detail 4 | FO | Double Acting | Single Acting | SV30495 | No | Position Switches | - | F30-CP-411 | 2000-PP007-B02-10374 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10146 |  |  |  | F30.30 | F30.30.02 | XV30495 | VKG | Acid Effluent | #N/A
0 | XV | 30 | 496 | XV 30496 | 150 | VKGD1L3 | 150VKGD1L3-Double Acting | Acid Effluent & Fine Carbon Pump 1 Discharge Valve | 30-4117-AE-RL5-150 | 2000-F30-PID-PR-10020 | 2000-F30-PID-PR-10020 | Stage 2 | Brownfield | AE | RL5 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC30496 | No | Position Switches | - | F30-CP-411 | 2000-PP007-B02-10374 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10149 |  |  |  | F30.30 | F30.30.02 | XV30496 | VKG | Acid Effluent | #N/A
0 | XV | 30 | 550 | XV 30550 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting | CIL 2 Oxygen Injection Pump 1 Suction Valve | 30-4031-CON-RL1-400 | 2000-F30-PID-PR-10007 | 2000-F30-PID-PR-10007 | Stage 2 | Brownfield | CON | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 16 | Detail 4 | FC | Double Acting | Single Acting | SV30550 | No | Position Switches | - | F30-CP-405 | 2000-PP007-B02-10368 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10089 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.06 | XV30550 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 555 | XV 30555 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | CIL 2 Oxygen Injection Pump 1 Discharge Drain Valve | 30-4032-CON-RL1-300 | 2000-F30-PID-PR-10007 | 2000-F30-PID-PR-10007 | Stage 2 | Brownfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV30555 | No | Position Switches | - | F30-CP-405 | 2000-PP007-B02-10368 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.06 | XV30555 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 562 | XV 30562 | 350 | VKGD1L1 | 350VKGD1L1-Double Acting | CIL 2 Oxygen Injection Pump 1 Discharge Valve | 30-4032-CON-RL1-300 | 2000-F30-PID-PR-10007 | 2000-F30-PID-PR-10007 | Stage 2 | Brownfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 14 | Detail 4 | FC | Double Acting | Single Acting | SV30562 | No | Position Switches | - | F30-CP-405 | 2000-PP007-B02-10368 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10084 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.06 | XV30562 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 565 | XV 30565 | 400 | VKGD1L1 | 400VKGD1L1-Double Acting | CIL 2 Oxygen Injection Pump 2 Suction Valve | 30-4202-CON-RL1-400 | 2000-F30-PID-PR-10007 | 2000-F30-PID-PR-10007 | Stage 2 | Brownfield | CON | RL1 | 400 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 16 | Detail 4 | FC | Double Acting | Single Acting | SV30565 | No | Position Switches | - | F30-CP-406 | 2000-PP007-B02-10369 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10089 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.06 | XV30565 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 570 | XV 30570 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | CIL 2 Oxygen Injection Pump 2 Discharge Drain Valve | 30-4203-CON-RL1-300 | 2000-F30-PID-PR-10007 | 2000-F30-PID-PR-10007 | Stage 2 | Brownfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 6 | Detail 4 | FO | Double Acting | Single Acting | SV30570 | No | Position Switches | - | F30-CP-406 | 2000-PP007-B02-10369 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.06 | XV30570 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 577 | XV 30577 | 350 | VKGD1L1 | 350VKGD1L1-Double Acting | CIL 2 Oxygen Injection Pump 2 Discharge Valve | 30-4203-CON-RL1-300 | 2000-F30-PID-PR-10007 | 2000-F30-PID-PR-10007 | Stage 2 | Brownfield | CON | RL1 | 300 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.515 | 1.7 | 700 | 14 | Detail 4 | FC | Double Acting | Single Acting | SV30577 | No | Position Switches | - | F30-CP-406 | 2000-PP007-B02-10369 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10084 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.06 | XV30577 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 30 | 597 | XV 30597 | 100 | VKGD1L1 | 100VKGD1L1-Double Acting | Milk Of Lime Ringmain Drain Valve 2 | 30-4265-LS-PE10-110 | 2000-F30-PID-PR-10016 | 2000-F30-PID-PR-10016 | Stage 2 | Brownfield | LS | PE10 | 110 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 4 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV30597 | No | Position Switches | - | F30-CP-412 | 2000-PP007-B02-10351 | PP007 | PP007 | Actuated via Manual 4-Way Valve located in control panel | Emerson | Clarkson KGD | 2000-PP007-B02-10046 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F72.110 | F72.110.03 | XV30597 | VKG | Lime Slurry | AS2129 Table D PN10
0 | XV | 30 | 598 | XV 30598 | 100 | VKGD1L1 | 100VKGD1L1-Double Acting | Milk Of Lime Ringmain Drain Valve 3 | 30-4266-LS-PE10-110 | 2000-F30-PID-PR-10016 | 2000-F30-PID-PR-10016 | Stage 2 | Brownfield | LS | PE10 | 110 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 4 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV30598 | No | Position Switches | - | F30-CP-412 | 2000-PP007-B02-10351 | PP007 | PP007 | Actuated via Manual 4-Way Valve located in control panel | Emerson | Clarkson KGD | 2000-PP007-B02-10046 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F72.110 | F72.110.03 | XV30598 | VKG | Lime Slurry | AS2129 Table D PN10
0 | SV | 34 | 406 | SV 34406 | 25 | SV | 25SV-Solenoid-FO | UFG Mill 1 Product Pump Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 1 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F34.20 | F34.20.01 | SV34406 | SV | Hypersaline Water | AS2129 Table E
0 | XV | 34 | 402 | XV 34402 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | UFG Mill 1 Product Pump Suction Valve | 150-MECH-RL1 | 2000-F34-PID-PR-10002 | 2000-F34-PID-PR-10001 | Stage 1 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.171 | 1.22 | 700 | 6 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC34402 | No | Position Switches | - | F34-CP-401 | 2000-PP007-B02-10349 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F34.20 | F34.20.01 | XV34402 | VKG | Concentrate Slurry | AS2129 Table D
1 | XV | 34 | 403 | XV 34403 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | UFG Mill 1 Product Pump Suction Drain Valve | 150-MECH-RL1 | 2000-F34-PID-PR-10002 | 2000-F34-PID-PR-10001 | Stage 1 | Brownfield | CON | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 4 | 9 | 0.171 | 1.22 | 700 | 2 | Detail 4 | FO | Double Acting | Single Acting | SV34403 | No | Position Switches | - | F34-CP-401 | 2000-PP007-B02-10349 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F34.20 | F34.20.01 | XV34403 | VKG | Concentrate Slurry | AS2129 Table D
0 | SV | 35 | 437 | SV 35437 | 25 | SV | 25SV-Solenoid-FO | UFG Circuit 2 Feed Pump Gland Water Solenoid Valve | 35-3050-GW-SS3-25 | 2000-F24-PID-PR-10003 | N/A | Stage 1 | Brownfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F35.20 | F35.20.01 | SV35437 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 35 | 445 | SV 35445 | 25 | SV | 25SV-Solenoid-FO | UFG Circuit 3 Feed Pump Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F35.20 | F35.20.01 | SV35445 | SV | Hypersaline Water | AS2129 Table E
1 | XV | 35 | 422 | XV 35422 | 100 | VKGD1L2 | 100VKGD1L2-Double Acting | UFG Circuit 2 Feed Pump Suction Isolation Valve | 35-4238-CON-RL1-100 | 2000-F35-PID-PR-10006 | 2000-F35-PID-PR-10001 | Stage 2 | Brownfield | CON | RL1 | 100 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 4 | Detail 4 | FC | Double Acting | Single Acting | SV35422 | No | Position Switches | - | F35-CP-402 | 2000-PP007-B02-10375 | PP007 | PP007 |  | Emerson | Clarkson KGA+ | 2000-PP007-B02-10047 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.08 | XV35422 | VKG | Concentrate Slurry | AS2129 Table D
1 | XV | 35 | 423 | XV 35423 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | UFG Circuit 2 Feed Pump Drain Valve | 35-2275-CON-RL1-100 | 2000-F35-PID-PR-10006 | 2000-F35-PID-PR-10001 | Stage 2 | Brownfield | CON | RL1 | 100 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 2 | Detail 4 | FO | Double Acting | Single Acting | SV35423 | No | Position Switches | - | F35-CP-402 | 2000-PP007-B02-10375 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.08 | XV35423 | VKG | Concentrate Slurry | AS2129 Table D
1 | XV | 35 | 424 | XV 35424 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | UFG Circuit 2 Feed Pump Flushing Water Valve | 35-4016-PW-SS3-50 | 2000-F35-PID-PR-10006 | 2000-F35-PID-PR-10001 | Stage 2 | Brownfield | PW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 2 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC35424 | No | Position Switches | - | F35-CP-402 | 2000-PP007-B02-10375 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.10 | XV35424 | VKG | Hypersaline Water | AS2129 Table E
0 | XV | 35 | 427 | XV 35427 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | UFG Circuit 1 Feed Pump Discharge Drain Valve | 35-4004-CON-RL1-80 | 2000-F35-PID-PR-10006 | 2000-F35-PID-PR-10001 | Stage 2 | Brownfield | CON | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 2 | Detail 4 | FO | Double Acting | Single Acting | SV35427 | No | Position Switches | - | F35-CP-401 | 2000-PP007-B02-10350 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.11
0 | XV | 35 | 429 | XV 35429 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | UFG Circuit 1 Feed Pump Discharge Flushing Water Valve | 35-4147-PW-SS3-50 | 2000-F35-PID-PR-10006 | 2000-F35-PID-PR-10001 | Stage 2 | Brownfield | PW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 2 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC35429 | No | Position Switches | - | F35-CP-401 | 2000-PP007-B02-10350 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.10
0 | XV | 35 | 431 | XV 35431 | 100 | VKGD1L2 | 100VKGD1L2-Double Acting | Filter Feed Tank A Isolation Valve | 100-MECH-RL1 | 2000-F35-PID-PR-10002 | 2000-F35-PID-PR-10001 | Stage 1 | Brownfield | CON | RL1 | 100 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 4 | Detail 4 | FC | Double Acting | Single Acting | SV35431 | No | Position Switches | - | F35-CP-401 | 2000-PP007-B02-10350 | PP007 | PP007 |  | Emerson | Clarkson KGA+ | 2000-PP007-B02-10047 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.01 | XV35431 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 35 | 432 | XV 35432 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | Filter Feed Tank A Discharge Drain Valve | 100-MECH-RL1 | 2000-F35-PID-PR-10002 | 2000-F35-PID-PR-10001 | Stage 1 | Brownfield | CON | RL1 | 100 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 2 | Detail 4 | FO | Double Acting | Single Acting | SV35432 | No | Position Switches | - | F35-CP-401 | 2000-PP007-B02-10350 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.01 | XV35432 | VKG | Concentrate Slurry | AS2129 Table D
0 | XV | 35 | 433 | XV 35433 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | Filter Feed Tank A Discharge Flushing Water Valve | 35-3013-PW-SS1-50 | 2000-F35-PID-PR-10002 | 2000-F35-PID-PR-10001 | Stage 1 | Brownfield | PW | SS1 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 2 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC35433 | No | Position Switches | - | F35-CP-401 | 2000-PP007-B02-10350 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.04 | XV35433 | VKG | Hypersaline Water | AS2129 Table D
1 | XV | 35 | 440 | XV 35440 | 100 | VKGD1L2 | 100VKGD1L2-Double Acting | UFG Circuit 3 Feed Pump Suction Isolation Valve | 35-4239-CON-RL1-100 | 2000-F35-PID-PR-10006 | 2000-F35-PID-PR-10001 | Stage 2 | Brownfield | CON | RL1 | 100 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 4 | Detail 4 | FC | Double Acting | Single Acting | SV35440 | No | Position Switches | - | F35-CP-402 | 2000-PP007-B02-10375 | PP007 | PP007 |  | Emerson | Clarkson KGA+ | 2000-PP007-B02-10047 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.08 | XV35440 | VKG | Concentrate Slurry | AS2129 Table D
1 | XV | 35 | 441 | XV 35441 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | UFG Circuit 3 Feed Pump Drain Valve | 35-2275-CON-RL1-100 | 2000-F35-PID-PR-10006 | 2000-F35-PID-PR-10001 | Stage 2 | Brownfield | CON | RL1 | 100 | N/A | N/A | N/A | N/A | N/A | 70 | 180 | 0.595 | 1.9 | 700 | 2 | Detail 4 | FO | Double Acting | Single Acting | SV35441 | No | Position Switches | - | F35-CP-402 | 2000-PP007-B02-10375 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.08 | XV35441 | VKG | Concentrate Slurry | AS2129 Table D
1 | XV | 35 | 442 | XV 35442 | 50 | VKGD1L1 | 50VKGD1L1-Double Acting | UFG Circuit 3 Feed Pump Flushing Water Valve | 35-4048-PW-SS3-50 | 2000-F35-PID-PR-10006 | 2000-F35-PID-PR-10001 | Stage 2 | Brownfield | PW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 2 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC35442 | No | Position Switches | - | F35-CP-402 | 2000-PP007-B02-10375 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10018 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F35.20 | F35.20.10 | XV35442 | VKG | Hypersaline Water | AS2129 Table E
1 | FCV | 65 | 413 | FCV 65413 | 80 | VDD1S1 | 80VDD1S1-Double Acting-Positioner | CIL3 Loaded Carbon Pump Transfer Water Addition Valve | 65-4011-CW-SS1-100 | 2000-F30-PID-PR-10017 | 2000-F30-PID-PR-10017 | Stage 2 | Brownfield | CW | SS1 | 100 | 0 | 30 | 200 | 200 | 50 | 120 | 180 | 0.55 | 1.65 | 700 | 3 | Detail 1 | FL | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F65-CP-401 | 2000-PP007-B02-10377 | PP007 | PP007 |  | Emerson | KDV | 2000-PP007-B02-10145 | Century |  | SMC IP8100 032 J (4-20mA) | F30.30 | F30.30.14 | FCV65413 | VDD | Cyanide Water | AS2129 Table D
0 | SV | 65 | 408 | SV 65408 | 25 | SV | 25SV-Solenoid-FO | CIL 3 Loaded Carbon Pump Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Brownfield | GW | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F30.30 | F30.30.14 | SV65408 | SV | Hypersaline Water | AS2129 Table E
0 | XV | 65 | 405 | XV 65405 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | CIL 3 Loaded Carbon Pump Suction Drain Valve | 65-4246-SC-RL1-150 | 2000-F30-PID-PR-10017 | 2000-F30-PID-PR-10017 | Stage 2 | Brownfield | SC | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC65405 | No | Position Switches | - | F65-CP-401 | 2000-PP007-B02-10377 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.14 | XV65405 | VKG | Carbon Slurry | AS2129 Table D
0 | XV | 65 | 406 | XV 65406 | 100 | VBFD1S2 | 100VBFD1S2-Double Acting | CIL 3 Loaded Carbon Pump Water Eduction Valve | 65-4011-CW-SS1-100 | 2000-F30-PID-PR-10017 | 2000-F30-PID-PR-10017 | Stage 2 | Brownfield | CW | SS1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 4 | Detail 7 | FO | Double Acting | Single Acting | SV65406 | No | Position Switches | - | F65-CP-401 | 2000-PP007-B02-10377 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10042 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F30.30 | F30.30.16 | XV65406 | VBF | Cyanide Water | AS2129 Table D
0 | XV | 65 | 407 | XV 65407 | 150 | VKGD1L1 | 150VKGD1L1-Double Acting | CIL 3 Loaded Carbon Transfer Hopper Valve | 65-4246-SC-RL1-150 | 2000-F30-PID-PR-10017 | 2000-F30-PID-PR-10017 | Stage 2 | Brownfield | SC | RL1 | 150 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 6 | Detail 4 | FC | Double Acting | Single Acting | SV65407 | No | Position Switches | - | F65-CP-401 | 2000-PP007-B02-10377 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10062 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F30.30 | F30.30.14 | XV65407 | VKG | Carbon Slurry | AS2129 Table D
0 | XV | 65 | 416 | XV 65416 | 80 | VBFD1S1 | 80VBFD1S1-Double Acting | CIL 3 Loaded Carbon Transfer Hopper Water Addition Valve | 65-4015-CW-SS3-50 | 2000-F30-PID-PR-10017 | 2000-F30-PID-PR-10017 | Stage 2 | Brownfield | CW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 3 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC65416 | No | Position Switches | - | F65-CP-401 | 2000-PP007-B02-10377 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10026 |  |  |  | F30.30 | F30.30.14 | XV65416 | VBF | Cyanide Water | AS2129 Table E
0 | XV | 65 | 445 | XV 65445 | 50 | VB03S1 | 50VB03S1-Double Acting-Solenoid on Valve | CIL3 Loaded Carbon Screen Spray Water Valve | 65-4240-CW-SS3-50 | 2000-F30-PID-PR-10017 | 2000-F30-PID-PR-10017 | Stage 2 | Brownfield | CW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | 120 | 180 | 0.55 | 1.65 | 700 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV65445 | No | Position Switches | Solenoid on Valve | Solenoid on Valve | N/A | PP007 | N/A | Solenoids to be installed on Valve | Emerson | K-BALL F182 | 2000-PP007-B02-10107 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F30.30 | F30.30.16 | XV65445 | VB0 | Cyanide Water | AS2129 Table E
0 | HV | 66 | 460 | HV 66460 | 80 | VBFD1S2 | 80VBFD1S2-Manual | Electrowinning Tank Area Sump Discharge to Gravity Tank Manual Valve | 66-3082-FD-SS1-80 | 2000-F66-PID-PR-10003 | N/A | Stage 1 | Greenfield | FD | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10029 | Emerson | Manual Lever | 2000043108 TVF-M2WGNMM | F66.30 | F66.30.02 | HV66460 | VBF | Floor Drainage | AS2129 Table D
0 | HV | 66 | 461 | HV 66461 | 80 | VBFD1S2 | 80VBFD1S2-Manual | Electrowinning Tank Area Sump Discharge to CIL 4 Eluate Tank 1 Manual Valve | 66-4165-FD-SS1-80 | 2000-F66-PID-PR-10003 | N/A | Stage 1 | Greenfield | FD | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10029 | Emerson | Manual Lever | 2000043108 TVF-M2WGNMM | F66.30 | F66.30.02 | HV66461 | VBF | Floor Drainage | AS2129 Table D
0 | HV | 66 | 462 | HV 66462 | 80 | VBFD1S2 | 80VBFD1S2-Manual | Electrowinning Tank Area Sump Discharge to CIL 4 Eluate Tank 2 Manual Valve | 66-4170-FD-SS1-80 | 2000-F66-PID-PR-10003 | N/A | Stage 1 | Greenfield | FD | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10029 | Emerson | Manual Lever | 2000043108 TVF-M2WGNMM | F66.30 | F66.30.02 | HV66462 | VBF | Floor Drainage | AS2129 Table D
0 | HV | 66 | 463 | HV 66463 | 80 | VBFD1S2 | 80VBFD1S2-Manual | Electrowinning Tank Area Sump Discharge to Barren Eluate Tank Manual Valve | 66-3086-FD-SS1-80 | 2000-F66-PID-PR-10003 | N/A | Stage 1 | Greenfield | FD | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10029 | Emerson | Manual Lever | 2000043108 TVF-M2WGNMM | F66.30 | F66.30.02 | HV66463 | VBF | Floor Drainage | AS2129 Table D
0 | PCV | 66 | 466 | PCV 66466 | 15 | PCV | 15PCV-N/A-Air | Electrowinning Cells Plant Air Pressure Regulating Valve | 72-1309-IA-MSG3-25 | 2000-F81-PID-PR-10002 | N/A | Stage 1 | Brownfield | IA | MSG3 | 25 | 0 | 15 | 1000 | 1000 | 300 | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 700kPag | Calorex | Roma Fig 514 | 2000-PP007-B02-10401 | N/A | N/A | N/A | F24.60 | F24.60.04 | PCV66466 | PCV | Instrument Air | AS2129 Table E
0 | SV | 66 | 451 | SV 66451 | 25 | SV | 25SV-Solenoid-FC | Electrowinning Solution to CIL 4 Electrowinning Cells Sample Solenoid Valve | 66-4153-PE-SS3-25 | 2000-F66-PID-PR-10001 | N/A | Stage 2 | Brownfield | PE | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F66.20 | F66.20.02 | SV66451 | SV | Pregnant Eluate | AS2129 Table E
0 | SV | 66 | 452 | SV 66452 | 25 | SV | 25SV-Solenoid-FC | Electrowinning Solution to Barren Eluate Tank Sample Solenoid Valve | 66-4154-BE-SS3-25 | 2000-F66-PID-PR-10001 | N/A | Stage 2 | Brownfield | BE | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F66.20 | F66.20.02 | SV66452 | SV | Barren Eluate | AS2129 Table E
0 | SV | 66 | 453 | SV 66453 | 25 | SV | 25SV-Solenoid-FC | Gravity Electrowinning Solution to Gravity Electrowinning Cells Sample Solenoid Valve | 66-3057-PE-SS3-25 | 2000-F66-PID-PR-10003 | N/A | Stage 1 | Brownfield | PE | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F66.30 | F66.30.01 | SV66453 | SV | Pregnant Eluate | AS2129 Table E
0 | SV | 66 | 454 | SV 66454 | 25 | SV | 25SV-Solenoid-FC | Gravity Electrowinning Solution to Barren Eluate Tank Sample Solenoid Valve | 66-3056-BE-SS3-25 | 2000-F66-PID-PR-10003 | N/A | Stage 1 | Brownfield | BE | SS3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F66.30 | F66.30.01 | SV66454 | SV | Barren Eluate | AS2129 Table E
0 | XV | 66 | 401 | XV 66401 | 25 | VBD1S1 | 25VBD1S1-Spring Return | CIL 4 Eluate Circulation Tank 1 Caustic Isolation Valve | 72-4087-NS-MS1-25-TI | 2000-F66-PID-PR-10001 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | NS | MS1 | 25-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 1 | Detail 8 | FC | Spring Return | Single Acting | SV66401 | No | Position Switches | - | F66-CP-403 | 2000-PP007-B02-10390 | PP007 | PP007 |  | Unimech | ARTTBV-TE | 2000-PP007-B02-10002 | Unimech | Pneumatic actuator | Limit switch Included | F66.20 | F66.20.01 | XV66401 | VBD | Caustic Soda | AS2129 Table D
0 | XV | 66 | 402 | XV 66402 | 100 | VBE1S1 | 100VBE1S1-Double Acting | CIL 4 Eluate Circulation Tank 1 Pregnant Eluate Isolation Valve | 66-4155-PE-SS2-100-TI | 2000-F66-PID-PR-10001 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | PE | SS2 | 100-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 4 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC66402 | No | Position Switches | - | F66-CP-403 | 2000-PP007-B02-10390 | PP007 | PP007 |  | Emerson | K-BALL F194 | 2000-PP007-B02-10038 | Emerson | KEYSTONE F89-020 | TOPWORX TVF-M2WGNMM | F66.20 | F66.20.01 | XV66402 | VBE | Pregnant Eluate | AS2129 Table E
0 | XV | 66 | 403 | XV 66403 | 100 | VBE1S1 | 100VBE1S1-Double Acting | CIL 4 Eluate Circulation Tank 2 Pregnant Eluate Isolation Valve | 66-4169-PE-SS2-100-TI | 2000-F66-PID-PR-10001 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | PE | SS2 | 100-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | 4 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC66403 | No | Position Switches | - | F66-CP-403 | 2000-PP007-B02-10390 | PP007 | PP007 |  | Emerson | K-BALL F194 | 2000-PP007-B02-10038 | Emerson | KEYSTONE F89-020 | TOPWORX TVF-M2WGNMM | F66.20 | F66.20.01 | XV66403 | VBE | Pregnant Eluate | AS2129 Table E
0 | XV | 66 | 408 | XV 66408 | 25 | VBD1S1 | 25VBD1S1-Spring Return | CIL 4 Eluate Circulation Tank 2 Caustic Isolation Valve | 66-4167-NS-MS1-25-TI | 2000-F66-PID-PR-10001 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | NS | MS1 | 25-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 1 | Detail 8 | FC | Spring Return | Single Acting | SV66408 | No | Position Switches | - | F66-CP-403 | 2000-PP007-B02-10390 | PP007 | PP007 |  | Unimech | ARTTBV-TE | 2000-PP007-B02-10002 | Unimech | Pneumatic actuator | Limit switch Included | F66.20 | F66.20.01 | XV66408 | VBD | Caustic Soda | AS2129 Table D
0 | XV | 66 | 409 | XV 66409 | 150 | VBD1S1 | 150VBD1S1-Double Acting | CIL 4 Eluate Circulation Tank 1 Pregnant Solution Isolation Valve | 66-4166-PE-SS1-150-TI | 2000-F66-PID-PR-10001 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | PE | SS1 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 6 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC66409 | No | Position Switches | - | F66-CP-403 | 2000-PP007-B02-10390 | PP007 | PP007 |  | Unimech | ARTTBV-TE | 2000-PP007-B02-10050 | Unimech | Pneumatic actuator | Limit switch Included | F66.20 | F66.20.01 | XV66409 | VBD | Pregnant Eluate | AS2129 Table D
0 | XV | 66 | 410 | XV 66410 | 150 | VBD1S1 | 150VBD1S1-Double Acting | CIL 4 Eluate Circulation Tank 2 Pregnant Solution Isolation Valve | 66-4168-PE-SS1-150-TI | 2000-F66-PID-PR-10001 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | PE | SS1 | 150-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 6 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC66410 | No | Position Switches | - | F66-CP-403 | 2000-PP007-B02-10390 | PP007 | PP007 |  | Unimech | ARTTBV-TE | 2000-PP007-B02-10050 | Unimech | Pneumatic actuator | Limit switch Included | F66.20 | F66.20.01 | XV66410 | VBD | Pregnant Eluate | AS2129 Table D
0 | XV | 66 | 411 | XV 66411 | 100 | VBFD1S2 | 100VBFD1S2-Double Acting | CIL 4 Electrowinning Cell 1 to Sludge Dewatering Cone Actuated Valve 1 | 66-4178-BE-SS1-100 | 2000-F66-PID-PR-10002 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | BE | SS1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV66411 | No | Position Switches | - | F66-CP-401 | 2000-PP007-B02-10389 | PP007 | PP007 | Actuated via Manual 4-Way Valve located in control panel | Emerson | GRL | 2000-PP007-B02-10042 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F66.20 | F66.20.03 | XV66411 | VBF | Barren Eluate | AS2129 Table D
0 | XV | 66 | 412 | XV 66412 | 100 | VBFD1S2 | 100VBFD1S2-Double Acting | CIL 4 Electrowinning Cell 1 to Sludge Dewatering Cone Actuated Valve 2 | 66-4178-BE-SS1-100 | 2000-F66-PID-PR-10002 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | BE | SS1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV66412 | No | Position Switches | - | F66-CP-401 | 2000-PP007-B02-10389 | PP007 | PP007 | Actuated via Manual 4-Way Valve located in control panel | Emerson | GRL | 2000-PP007-B02-10042 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F66.20 | F66.20.03 | XV66412 | VBF | Barren Eluate | AS2129 Table D
0 | XV | 66 | 413 | XV 66413 | 100 | VBFD1S2 | 100VBFD1S2-Double Acting | CIL 4 Electrowinning Cell 2 to Sludge Dewatering Cone Actuated Valve 1 | 66-4179-BE-SS1-100 | 2000-F66-PID-PR-10002 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | BE | SS1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV66413 | No | Position Switches | - | F66-CP-401 | 2000-PP007-B02-10389 | PP007 | PP007 | Actuated via Manual 4-Way Valve located in control panel | Emerson | GRL | 2000-PP007-B02-10042 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F66.20 | F66.20.04 | XV66413 | VBF | Barren Eluate | AS2129 Table D
0 | XV | 66 | 414 | XV 66414 | 100 | VBFD1S2 | 100VBFD1S2-Double Acting | CIL 4 Electrowinning Cell 2 to Sludge Dewatering Cone Actuated Valve 2 | 66-4179-BE-SS1-100 | 2000-F66-PID-PR-10002 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | BE | SS1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV66414 | No | Position Switches | - | F66-CP-401 | 2000-PP007-B02-10389 | PP007 | PP007 | Actuated via Manual 4-Way Valve located in control panel | Emerson | GRL | 2000-PP007-B02-10042 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F66.20 | F66.20.04 | XV66414 | VBF | Barren Eluate | AS2129 Table D
0 | XV | 66 | 415 | XV 66415 | 100 | VBD1S1 | 100VBD1S1-Double Acting | CIL 4 Electrowinning Pump 1 to CIL 4 Electrowinning Cells Isolation Valve | 66-4171-PE-SS1-100-TI | 2000-F66-PID-PR-10001 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | PE | SS1 | 100-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC66415 | No | Position Switches | - | F66-CP-404 | 2000-PP007-B02-10391 | PP007 | PP007 |  | Unimech | ARTTBV-TE | 2000-PP007-B02-10036 | Unimech | Pneumatic actuator | Limit switch Included | F66.20 | F66.20.01 | XV66415 | VBD | Pregnant Eluate | AS2129 Table D
0 | XV | 66 | 416 | XV 66416 | 100 | VBD1S1 | 100VBD1S1-Double Acting | CIL 4 Electrowinning Pump 1 to Barren Tank Isolation Valve | 66-4160-BE-SS1-100-TI | 2000-F66-PID-PR-10001 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | BE | SS1 | 100-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC66416 | No | Position Switches | - | F66-CP-404 | 2000-PP007-B02-10391 | PP007 | PP007 |  | Unimech | ARTTBV-TE | 2000-PP007-B02-10036 | Unimech | Pneumatic actuator | Limit switch Included | F66.20 | F66.20.01 | XV66416 | VBD | Barren Eluate | AS2129 Table D
0 | XV | 66 | 417 | XV 66417 | 100 | VBD1S1 | 100VBD1S1-Double Acting | CIL 4 Electrowinning Pump 2 to CIL 4 Electrowinning Cells Isolation Valve | 66-4161-PE-SS1-100-TI | 2000-F66-PID-PR-10001 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | PE | SS1 | 100-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC66417 | No | Position Switches | - | F66-CP-404 | 2000-PP007-B02-10391 | PP007 | PP007 |  | Unimech | ARTTBV-TE | 2000-PP007-B02-10036 | Unimech | Pneumatic actuator | Limit switch Included | F66.20 | F66.20.01 | XV66417 | VBD | Pregnant Eluate | AS2129 Table D
0 | XV | 66 | 418 | XV 66418 | 100 | VBD1S1 | 100VBD1S1-Double Acting | CIL 4 Electrowinning Pump 2 to Barren Tank Isolation Valve | 66-4162-BE-SS1-100-TI | 2000-F66-PID-PR-10001 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | BE | SS1 | 100-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC66418 | No | Position Switches | - | F66-CP-404 | 2000-PP007-B02-10391 | PP007 | PP007 |  | Unimech | ARTTBV-TE | 2000-PP007-B02-10036 | Unimech | Pneumatic actuator | Limit switch Included | F66.20 | F66.20.01 | XV66418 | VBD | Barren Eluate | AS2129 Table D
0 | XV | 66 | 421 | XV 66421 | 25 | VBD1S1 | 25VBD1S1-Spring Return | Gravity Electrowinning Tank Caustic Isolation Valve | 72-4088-NS-MS1-25-TI | 2000-F66-PID-PR-10003 | 2000-F81-PID-PR-10002 | Stage 2 | Brownfield | NS | MS1 | 25-TI | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 1 | Detail 8 | FC | Spring Return | Single Acting | SV66421 | No | Position Switches | - | F66-CP-403 | 2000-PP007-B02-10390 | PP007 | PP007 |  | Unimech | ARTTBV-TE | 2000-PP007-B02-10002 | Unimech | Pneumatic actuator | Limit switch Included | F72.60 | F72.60.02 | XV66421 | VBD | Caustic Soda | AS2129 Table D
0 | XV | 66 | 426 | XV 66426 | 100 | VBFD1S2 | 100VBFD1S2-Double Acting | Gravity Electrowinning Cell to Sludge Dewatering Cone Actuated Valve 1 | 66-3090-BE-SS1-100 | 2000-F66-PID-PR-10003 | 2000-F81-PID-PR-10002 | Stage 1 | Brownfield | BE | SS1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV66426 | No | Position Switches | - | F66-CP-401 | 2000-PP007-B02-10389 | PP007 | PP007 | Actuated via Manual 4-Way Valve located in control panel | Emerson | GRL | 2000-PP007-B02-10042 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F66.30 | F66.30.04 | XV66426 | VBF | Barren Eluate | AS2129 Table D
0 | XV | 66 | 428 | XV 66428 | 100 | VBFD1S2 | 100VBFD1S2-Double Acting | Gravity Electrowinning Cell to Sludge Dewatering Cone Actuated Valve 2 | 66-3090-BE-SS1-100 | 2000-F66-PID-PR-10003 | 2000-F81-PID-PR-10002 | Stage 1 | Brownfield | BE | SS1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV66428 | No | Position Switches | - | F66-CP-401 | 2000-PP007-B02-10389 | PP007 | PP007 | Actuated via Manual 4-Way Valve located in control panel | Emerson | GRL | 2000-PP007-B02-10042 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F66.30 | F66.30.04 | XV66428 | VBF | Barren Eluate | AS2129 Table D
0 | XV | 66 | 429 | XV 66429 | 100 | VBFD1S2 | 100VBFD1S2-Double Acting | Gravity Electrowinning Pump to Gravity Electrowinning Cell Valve | 66-3093-PE-SS1-100 | 2000-F66-PID-PR-10003 | 2000-F81-PID-PR-10002 | Stage 1 | Brownfield | PE | SS1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC66429 | No | Position Switches | - | F66-CP-402 | 2000-PP007-B02-10352 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10042 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F66.30 | F66.30.01 | XV66429 | VBF | Pregnant Eluate | AS2129 Table D
0 | XV | 66 | 430 | XV 66430 | 100 | VBFD1S2 | 100VBFD1S2-Double Acting | Gravity Electrowinning Pump to Barren Eluate Tank Valve | 66-3034-BE-SS1-100 | 2000-F66-PID-PR-10003 | 2000-F81-PID-PR-10002 | Stage 1 | Brownfield | BE | SS1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC66430 | No | Position Switches | - | F66-CP-402 | 2000-PP007-B02-10352 | PP007 | PP007 |  | Emerson | GRL | 2000-PP007-B02-10042 | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM | F66.30 | F66.30.01 | XV66430 | VBF | Barren Eluate | AS2129 Table D
0 | FCV | 72 | 7 | FCV 72007 |  | N/A |  | Flocculant Mixing Tank Scheme Water Flow Control Valve | 72-1060-PSW-MS2-100 | 2000-F72-PID-PR-10004 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PSW | MS2 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME029 | N/A | Solenoids to be installed on Valve | [6 empty] | F72.120 | F72.120.02 | FCV72007 | N/A | Process Scheme Water | AS2129 Table E
0 | FCV | 72 | 13 | FCV 72013 |  | N/A |  | Flocculant Mixing Tank Wetting Head Scheme Water Flow Control Valve | 72-1060-PSW-MS2-100 | 2000-F72-PID-PR-10004 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | PSW | MS2 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | Manual Isolation | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME029 | N/A | Solenoids to be installed on Valve | [6 empty] | F72.120 | F72.120.02 | FCV72013 | N/A | Process Scheme Water | AS2129 Table E
0 | FCV | 72 | 407 | FCV 72407 | 50 | N/A |  | Lime Slaking Vortex Prewetter 1 Raw Water Flow Control Valve | 72-1026-BW-SS3-50 | 2000-F72-PID-PR-10001 | N/A | Stage 2 | Greenfield | BW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | N/A | N/A | ME013 | N/A | Instrument Air direct to valve | [6 empty] | F24.40 | F24.40.10 | FCV72407 | N/A | Hypersaline Water | AS2129 Table E
0 | FCV | 72 | 408 | FCV 72408 | 50 | N/A |  | Slaked Lime Discharge Hopper 1 Raw Water Flow Control Valve | 72-1025-BW-SS3-50 | 2000-F72-PID-PR-10001 | N/A | Stage 2 | Greenfield | BW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F72-CP-403 | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F24.40 | F24.40.10 | FCV72408 | N/A | Hypersaline Water | AS2129 Table E
0 | FCV | 72 | 427 | FCV 72427 | 50 | N/A |  | Lime Slaking Vortex Prewetter 2 Raw Water Flow Control Valve | 72-1927-BW-SS1-100 | 2000-F72-PID-PR-10002 | N/A | Stage 2 | Greenfield | BW | SS1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2 | Detail 1 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | N/A | N/A | ME013 | N/A | Instrument Air direct to valve | [6 empty] | F24.40 | F24.40.10 | FCV72427 | N/A | Hypersaline Water | AS2129 Table D
0 | FCV | 72 | 428 | FCV 72428 | 50 | N/A |  | Slaked Lime Discharge Hopper 2 Raw Water Flow Control Valve | 72-1928-BW-SS1-80 | 2000-F72-PID-PR-10002 | N/A | Stage 2 | Greenfield | BW | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2 | Detail 1 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F72-CP-403 | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F24.40 | F24.40.10 | FCV72428 | N/A | Hypersaline Water | AS2129 Table D
0 | FCV | 72 | 616 | FCV 72616 | 25 | VBD1T1 | 25VBD1T1-Double Acting-Positioner | CIL 4 Acid Dilution Tank Acid Inlet Flow Control Valve | 72-1127-HCL-PE8-32 | 2000-F72-PID-PR-10007 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | HCL | PE8 | 32 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 1 | Detail 1 | FC | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | F72-CP-411 | 2000-PP007-B02-10384 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10133 |  |  |  | F72.70 | F72.70.02 | FCV72616 | VBD | Hydrochloric Acid | AS2129 Table D PN10
0 | FCV | 72 | 632 | FCV 72632 | 50 | VBD1C1 | 50VBD1C1-Double Acting-Positioner-Solenoid on Valve | Oxygen Plant Cooling System Cooling Water Flow Control Valve | 13-0204-COW-MSG1-80-TI | 2000-F72-PID-PR-10011 | 2000-F24-PID-PR-10007 | Stage 2 | Greenfield | COW | MSG1 | 80-TI | 40 | 60 | 250 | VTA | VTA | N/A | N/A | N/A | 1 | 700 | 2 | Detail 1 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | No | Solenoid on Valve | Solenoid on Valve | N/A | PP007 | N/A | Solenoids to be installed on Valve |  |  | 2000-PP007-B02-10137 |  |  |  | F13.10 | F13.10.55 | FCV72632 | VBD | Cooling Water | AS2129 Table D
0 | PCV | 72 | 82 | PCV 72082 | 15 | PCV | 15PCV-N/A-Air | Copper Sulphate Delivery Plant Air Pressure Regulating Valve 1 | 72-1309-IA-MSG3-25 | 2000-F72-PID-PR-10008 | N/A | Stage 1 | Greenfield | IA | MSG3 | 25 | 0 | 80 | 1000 | 1000 | 725 | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 275kPag | Calorex Pty Ltd | Roma Fig. 514 | 2000-PP007-B02-10401 | N/A | N/A | N/A | F24.60 | F24.60.03 | PCV72082 | PCV | Instrument Air | AS2129 Table E
0 | PCV | 72 | 88 | PCV 72088 | 15 | PCV | 15PCV-N/A-Air | Copper Sulphate Delivery Plant Air Pressure Regulating Valve 2 | 72-1314-IA-MSG3-25 | 2000-F72-PID-PR-10008 | N/A | Stage 1 | Greenfield | IA | MSG3 | 25 | 0 | 80 | 1000 | 1000 | 725 | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 275kPag | Calorex Pty Ltd | Roma Fig. 514 | 2000-PP007-B02-10401 | N/A | N/A | N/A | F24.60 | F24.60.03 | PCV72088 | PCV | Instrument Air | AS2129 Table E
0 | PCV | 72 | 128 | PCV 72128 | 15 | PCV | 15PCV-N/A-Air | PAX Delivery Plant Air Pressure Regulating Valve 2 | 72-2154-IA-MSG3-25 | 2000-F72-PID-PR-10010 | N/A | Stage 1 | Greenfield | IA | MSG3 | 25 | 0 | 80 | 1000 | 1000 | 725 | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 200kPag | Calorex Pty Ltd | Roma Fig. 514 | 2000-PP007-B02-10401 | N/A | N/A | N/A | F24.60 | F24.60.03 | PCV72128 | PCV | Instrument Air | AS2129 Table E
0 | PCV | 72 | 132 | PCV 72132 | 15 | PCV | 15PCV-N/A-Air | PAX Delivery Plant Air Pressure Regulating Valve 1 | 72-1308-IA-MSG3-25 | 2000-F72-PID-PR-10010 | N/A | Stage 1 | Greenfield | IA | MSG3 | 25 | 0 | 80 | 1000 | 1000 | 725 | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 275kPag | Calorex Pty Ltd | Roma Fig. 514 | 2000-PP007-B02-10401 | N/A | N/A | N/A | F24.60 | F24.60.03 | PCV72132 | PCV | Instrument Air | AS2129 Table E
0 | PCV | 72 | 211 | PCV 72211 | 15 | PCV | 15PCV-N/A-Air | Hydrogen Peroxide Delivery Plant Air Pressure Regulating Valve | 72-1260-IA-MSG3-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | IA | MSG3 | 25 | 0 | 80 | 1000 | 1000 | 780 | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 275kPag | Calorex Pty Ltd | Roma Fig. 514 | 2000-PP007-B02-10401 | N/A | N/A | N/A | F72.10 | F72.10.13 | PCV72211 | PCV | Instrument Air | AS2129 Table E
0 | PCV | 72 | 532 | PCV 72532 | 15 | PCV | 15PCV-N/A-Air | Cyanide Delivery Plant Air Distribution 1 Pressure Control Valve | 72-1161-IA-MSG3-25 | 2000-F72-PID-PR-10005 | N/A | Stage 2 | Greenfield | IA | MSG3 | 25 | 0 | 72 | 1000 | 1000 | 800 | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 200kPag | Calorex Pty Ltd | Roma Fig. 514 | 2000-PP007-B02-10401 | N/A | N/A | N/A | F72.10 | F72.10.37 | PCV72532 | PCV | Instrument Air | AS2129 Table E
0 | PCV | 72 | 543 | PCV 72543 | 15 | PCV | 15PCV-N/A-Air | Cyanide Delivery Plant Air Distribution 2 Pressure Control Valve | 72-2180-IA-MSG3-25 | 2000-F72-PID-PR-10005 | N/A | Stage 2 | Greenfield | IA | MSG3 | 25 | 0 | 72 | 1000 | 1000 | 800 | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 200kPag | Calorex Pty Ltd | Roma Fig. 514 | 2000-PP007-B02-10401 | N/A | N/A | N/A | F72.10 | F72.10.37 | PCV72543 | PCV | Instrument Air | AS2129 Table E
0 | PCV | 72 | 702 | PCV 72702 | 15 | PCV | 15PCV-N/A-Air | Lead Nitrate Delivery Plant Air Pressure Regulating Valve | 72-1307-IA-MSG3-25 | 2000-F72-PID-PR-10015 | N/A | Stage 2 | Greenfield | IA | MSG3 | 25 | 0 | 72 | 1000 | 1000 | 725 | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 275kPag | Calorex Pty Ltd | Roma Fig. 514 | 2000-PP007-B02-10401 | N/A | N/A | N/A | F72.10 | F72.10.37 | PCV72702 | PCV | Instrument Air | AS2129 Table E
0 | PRV | 72 | 2 | PRV 72002 |  | N/A |  | Flocculant Silo Pressure Release Valve |  | 2000-F72-PID-PR-10004 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME029 | N/A | [7 empty] | F72.120 | F72.120.02 | PRV72002 | N/A | #N/A | #N/A
0 | PRV | 72 | 20 | PRV 72020 |  | N/A |  | Flocculant Transfer Pump Pressure Release Valve |  | 2000-F72-PID-PR-10004 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME029 | N/A | [7 empty] | F72.120 | F72.120.03 | PRV72020 | N/A | #N/A | #N/A
0 | PRV | 72 | 51 | PRV 72051 | 80 | PRV | 80PRV-N/A-Reagent | Flotation Tailings Thickener Flocculant Dosing Pump 1 Pressure Release Valve | 72-1230-FL-MS1-80 | 2000-F72-PID-PR-10004 | N/A | Stage 1 | Greenfield | FL | MS1 | 80 | N/A | 25 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-161 | 2000-PP007-B02-10414 | N/A | N/A | N/A | F72.120 | F72.120.05 | PRV72051 | PRV | Flocculant | AS2129 Table D
0 | PRV | 72 | 52 | PRV 72052 | 80 | PRV | 80PRV-N/A-Reagent | Flotation Tailings Thickener Flocculant Dosing Pump 2 Pressure Release Valve | 72-1231-FL-MS1-80 | 2000-F72-PID-PR-10004 | N/A | Stage 1 | Greenfield | FL | MS1 | 80 | N/A | 25 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-161 | 2000-PP007-B02-10414 | N/A | N/A | N/A | F72.120 | F72.120.05 | PRV72052 | PRV | Flocculant | AS2129 Table D
0 | PRV | 72 | 83 | PRV 72083 | 25 | PRV | 25PRV-N/A-Air | Copper Sulphate Delivery Plant Air Pressure Release Valve 1 | 72-1309-IA-MSG3-25 | 2000-F72-PID-PR-10008 | N/A | Stage 1 | Greenfield | IA | MSG3 | 25 | N/A | 160 | 275 | N/A | N/A | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 275kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10408 | N/A | N/A | N/A | F24.60 | F24.60.03 | PRV72083 | PRV | Instrument Air | AS2129 Table E
0 | PRV | 72 | 89 | PRV 72089 | 25 | PRV | 25PRV-N/A-Air | Copper Sulphate Delivery Plant Air Pressure Release Valve 2 | 72-1314-IA-MSG3-25 | 2000-F72-PID-PR-10008 | N/A | Stage 1 | Greenfield | IA | MSG3 | 25 | N/A | 160 | 275 | N/A | N/A | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 275kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10408 | N/A | N/A | N/A | F24.60 | F24.60.03 | PRV72089 | PRV | Instrument Air | AS2129 Table E
0 | PRV | 72 | 91 | PRV 72091 | 15 | PRV | 15PRV-N/A-Reagent | Copper Sulphate Dosing Pump 1 Pressure Release Valve | 72-1148-CO-SS1-15 | 2000-F72-PID-PR-10008 | N/A | Stage 1 | Greenfield | CO | SS1 | 15 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.15 | 700 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.40 | F72.40.02 | PRV72091 | PRV | Copper Sulphate | AS2129 Table D
0 | PRV | 72 | 92 | PRV 72092 | 15 | PRV | 15PRV-N/A-Reagent | Copper Sulphate Dosing Pump 2 Pressure Release Valve | 72-1150-CO-SS1-15 | 2000-F72-PID-PR-10008 | N/A | Stage 1 | Greenfield | CO | SS1 | 15 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.15 | 700 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.40 | F72.40.02 | PRV72092 | PRV | Copper Sulphate | AS2129 Table D
0 | PRV | 72 | 101 | PRV 72101 | 15 | PRV | 15PRV-N/A-Reagent | Copper Sulphate Dosing Pump 3 Pressure Release Valve | 72-1156-CO-SS1-15 | 2000-F72-PID-PR-10008 | N/A | Stage 1 | Greenfield | CO | SS1 | 15 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.15 | 700 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.40 | F72.40.02 | PRV72101 | PRV | Copper Sulphate | AS2129 Table D
0 | PRV | 72 | 115 | PRV 72115 | 15 | PRV | 15PRV-N/A-Reagent | Frother Dosing Pump 1 Pressure Release Valve | 72-1450-FR-SS1-15 | 2000-F72-PID-PR-10009 | N/A | Stage 1 | Greenfield | FR | SS1 | 15 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.30 | F72.30.02 | PRV72115 | PRV | Frother | AS2129 Table D
0 | PRV | 72 | 116 | PRV 72116 | 15 | PRV | 15PRV-N/A-Reagent | Frother Dosing Pump 2 Pressure Release Valve | 72-1452-FR-SS1-15 | 2000-F72-PID-PR-10009 | N/A | Stage 1 | Greenfield | FR | SS1 | 15 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.30 | F72.30.02 | PRV72116 | PRV | Frother | AS2129 Table D
0 | PRV | 72 | 117 | PRV 72117 | 15 | PRV | 15PRV-N/A-Reagent | Frother Dosing Pump 3 Pressure Release Valve | 72-1459-FR-SS1-15 | 2000-F72-PID-PR-10009 | N/A | Stage 1 | Greenfield | FR | SS1 | 15 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.30 | F72.30.02 | PRV72117 | PRV | Frother | AS2129 Table D
0 | PRV | 72 | 118 | PRV 72118 | 15 | PRV | 15PRV-N/A-Reagent | Frother Dosing Pump 4 Pressure Release Valve | 72-1456-FR-SS1-15 | 2000-F72-PID-PR-10009 | N/A | Stage 1 | Greenfield | FR | SS1 | 15 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.30 | F72.30.03 | PRV72118 | PRV | Frother | AS2129 Table D
0 | PRV | 72 | 119 | PRV 72119 | 15 | PRV | 15PRV-N/A-Reagent | Frother Dosing Pump 5 Pressure Release Valve | 72-1458-FR-SS1-15 | 2000-F72-PID-PR-10009 | N/A | Stage 1 | Greenfield | FR | SS1 | 15 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.30 | F72.30.03 | PRV72119 | PRV | Frother | AS2129 Table D
0 | PRV | 72 | 129 | PRV 72129 | 25 | PRV | 25PRV-N/A-Air | PAX Delivery Plant Air Pressure Release Valve 2 | 72-2154-IA-MSG3-25 | 2000-F72-PID-PR-10010 | N/A | Stage 1 | Greenfield | IA | MSG3 | 25 | N/A | 160 | 275 | N/A | N/A | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 275kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10408 | N/A | N/A | N/A | F24.60 | F24.60.03 | PRV72129 | PRV | Instrument Air | AS2129 Table E
0 | PRV | 72 | 133 | PRV 72133 | 25 | PRV | 25PRV-N/A-Air | PAX Delivery Plant Air Pressure Release Valve 1 | 72-1308-IA-MSG3-25 | 2000-F72-PID-PR-10010 | N/A | Stage 1 | Greenfield | IA | MSG3 | 25 | N/A | 160 | 275 | N/A | N/A | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 275kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10408 | N/A | N/A | N/A | F24.60 | F24.60.03 | PRV72133 | PRV | Instrument Air | AS2129 Table E
0 | PRV | 72 | 141 | PRV 72141 | 20 | PRV | 20PRV-N/A-Reagent | PAX Dosing Pump 1 Pressure Release Valve | 72-1108-XA-SS1-50 | 2000-F72-PID-PR-10010 | N/A | Stage 1 | Greenfield | XA | SS1 | 50 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10407 | N/A | N/A | N/A | F72.20 | F72.20.02 | PRV72141 | PRV | Xanthate | AS2129 Table D
0 | PRV | 72 | 142 | PRV 72142 | 20 | PRV | 20PRV-N/A-Reagent | PAX Dosing Pump 2 Pressure Release Valve | 72-1544-XA-SS1-50 | 2000-F72-PID-PR-10010 | N/A | Stage 1 | Greenfield | XA | SS1 | 50 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10407 | N/A | N/A | N/A | F72.20 | F72.20.02 | PRV72142 | PRV | Xanthate | AS2129 Table D
0 | PRV | 72 | 143 | PRV 72143 | 20 | PRV | 20PRV-N/A-Reagent | PAX Dosing Pump 3 Pressure Release Valve | 72-1539-XA-SS1-50 | 2000-F72-PID-PR-10010 | N/A | Stage 1 | Greenfield | XA | SS1 | 50 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10407 | N/A | N/A | N/A | F72.20 | F72.20.02 | PRV72143 | PRV | Xanthate | AS2129 Table D
0 | PRV | 72 | 151 | PRV 72151 | 15 | PRV | 15PRV-N/A-Reagent | PAX Dosing Pump 4 Pressure Release Valve | 72-1466-XA-SS1-50 | 2000-F72-PID-PR-10010 | N/A | Stage 1 | Greenfield | XA | SS1 | 50 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.20 | F72.20.03 | PRV72151 | PRV | Xanthate | AS2129 Table D
0 | PRV | 72 | 153 | PRV 72153 | 15 | PRV | 15PRV-N/A-Reagent | PAX Dosing Pump 5 Pressure Release Valve | 72-1465-XA-SS1-50 | 2000-F72-PID-PR-10010 | N/A | Stage 1 | Greenfield | XA | SS1 | 50 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.20 | F72.20.03 | PRV72153 | PRV | Xanthate | AS2129 Table D
0 | PRV | 72 | 165 | PRV 72165 | 25 | PRV | 25PRV-N/A-Reagent | Antiscalant Dosing Pump 1 Pressure Release Valve | 72-2509-AS-SS1-25 | 2000-F72-PID-PR-10013 | N/A | Stage 1 | Greenfield | AS | SS1 | 25 | 0 | 0.005 | N/A | N/A | 800 | N/A | N/A | N/A | 1.1 | 700 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 800 kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.130 | F72.130.01 | PRV72165 | PRV | Antiscalant | AS2129 Table D
0 | PRV | 72 | 205 | PRV 72205 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Delivery Pressure Release Valve | 72-0673-HP-SS5-50 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 50 | N/A | 160 | 220 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 275kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.01 | PRV72205 | PRV | Hydrogen Peroxide | AS2129 Table E
0 | PRV | 72 | 208 | PRV 72208 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Storage Tank Outlet Pressure Release Valve | 72-0674-HP-SS5-50 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 50 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.01 | PRV72208 | PRV | Hydrogen Peroxide | AS2129 Table E
0 | PRV | 72 | 212 | PRV 72212 | 25 | PRV | 25PRV-N/A-Air | Hydrogen Peroxide Delivery Plant Air Pressure Release Valve | 72-1260-IA-MSG3-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | IA | MSG3 | 25 | N/A | 160 | 220 | N/A | N/A | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 275kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10408 | N/A | N/A | N/A | F72.10 | F72.10.13 | PRV72212 | PRV | Instrument Air | AS2129 Table E
1 | PRV | 72 | 223 | PRV 72223 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Dosing Pump 1 Pressure Release Valve 1 | 72-0786-HP-SS5-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 25 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.04 | PRV72223 | PRV | Hydrogen Peroxide | AS2129 Table E
1 | PRV | 72 | 224 | PRV 72224 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Dosing Pump 2 Pressure Release Valve 1 | 72-0787-HP-SS5-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 25 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.04 | PRV72224 | PRV | Hydrogen Peroxide | AS2129 Table E
1 | PRV | 72 | 225 | PRV 72225 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Dosing Pump 3 Pressure Release Valve 1 | 72-0788-HP-SS5-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 25 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.04 | PRV72225 | PRV | Hydrogen Peroxide | AS2129 Table E
1 | PRV | 72 | 226 | PRV 72226 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Inline Mixer 1 Pressure Release Valve | 72-0786-HP-SS5-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 25 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.04 | PRV72226 | PRV | Hydrogen Peroxide | AS2129 Table E
1 | PRV | 72 | 229 | PRV 72229 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Inline Mixer 2 Pressure Release Valve | 72-0787-HP-SS5-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 25 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.04 | PRV72229 | PRV | Hydrogen Peroxide | AS2129 Table E
1 | PRV | 72 | 230 | PRV 72230 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Dosing Pump 1 Pressure Release Valve 2 | 72-0786-HP-SS5-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 25 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.04 | PRV72230 | PRV | Hydrogen Peroxide | AS2129 Table E
1 | PRV | 72 | 231 | PRV 72231 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Dosing Pump 2 Pressure Release Valve 2 | 72-0787-HP-SS5-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 25 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.04 | PRV72231 | PRV | Hydrogen Peroxide | AS2129 Table E
1 | PRV | 72 | 232 | PRV 72232 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Dosing Pump 3 Pressure Release Valve 2 | 72-0788-HP-SS5-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 25 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.04 | PRV72232 | PRV | Hydrogen Peroxide | AS2129 Table E
1 | PRV | 72 | 233 | PRV 72233 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Dosing Pump 3 Pressure Release Valve 3 | 72-0913-HP-SS5-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 25 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.04 | PRV72233 | PRV | Hydrogen Peroxide | AS2129 Table E
1 | PRV | 72 | 234 | PRV 72234 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Dosing Pump 4 Pressure Release Valve 1 | 72-2273-HP-SS5-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 25 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.04 | PRV72234 | PRV | Hydrogen Peroxide | AS2129 Table E
1 | PRV | 72 | 235 | PRV 72235 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Dosing Pump 4 Pressure Release Valve 2 | 72-2273-HP-SS5-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 25 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.04 | PRV72235 | PRV | Hydrogen Peroxide | AS2129 Table E
1 | PRV | 72 | 236 | PRV 72236 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Inline Mixer 3 Pressure Release Valve | 72-2273-HP-SS5-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 25 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.04 | PRV72236 | PRV | Hydrogen Peroxide | AS2129 Table E
1 | PRV | 72 | 239 | PRV 72239 | 15 | PRV | 15PRV-N/A-Reagent | Hydrogen Peroxide Dosing Pump 3 Pressure Release Valve 4 | 72-0798-HP-SS5-25 | 2000-F72-PID-PR-10014 | N/A | Stage 1 | Greenfield | HP | SS5 | 25 | N/A | 1.5 | 600 | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10406 | N/A | N/A | N/A | F72.140 | F72.140.04 | PRV72239 | PRV | Hydrogen Peroxide | AS2129 Table E
0 | PRV | 72 | 402 | PRV 72402 | 350 | N/A |  | Lime Silo 1 Pressure Release Valve 1 |  | 2000-F72-PID-PR-10001 | N/A | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME013 | ME013 | [7 empty] | F72.110 | F72.110.01 | PRV72402 | N/A | #N/A | #N/A
0 | PRV | 72 | 417 | PRV 72417 | 350 | N/A |  | Lime Silo 1 Pressure Release Valve 2 |  | 2000-F72-PID-PR-10001 | N/A | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.01 | PRV72417 | N/A | #N/A | #N/A
0 | PRV | 72 | 418 | PRV 72418 | 350 | N/A |  | Lime Silo 1 Pressure Release Valve 3 |  | 2000-F72-PID-PR-10001 | N/A | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.01 | PRV72418 | N/A | #N/A | #N/A
0 | PRV | 72 | 422 | PRV 72422 | 350 | N/A |  | Lime Silo 2 Pressure Release Valve 1 |  | 2000-F72-PID-PR-10002 | N/A | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.16 | PRV72422 | N/A | #N/A | #N/A
0 | PRV | 72 | 429 | PRV 72429 | 350 | N/A |  | Lime Silo 2 Pressure Release Valve 2 |  | 2000-F72-PID-PR-10002 | N/A | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.16 | PRV72429 | N/A | #N/A | #N/A
0 | PRV | 72 | 430 | PRV 72430 | 350 | N/A |  | Lime Silo 2 Pressure Release Valve 3 |  | 2000-F72-PID-PR-10002 | N/A | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.16 | PRV72430 | N/A | #N/A | #N/A
0 | PRV | 72 | 481 | PRV 72481 | 32 | PRV | 32PRV-N/A-Reagent | Concentrae Pre-Leach Thickener Flocculant Dosing Pump Pressure Release Valve | 72-4060-FL-MS1-50 | 2000-F72-PID-PR-10016 | N/A | Stage 2 | Greenfield | FL | MS1 | 50 | N/A | 5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600 kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10412 | N/A | N/A | N/A | F72.120 | F72.120.06 | PRV72481 | PRV | Flocculant | AS2129 Table D
0 | PRV | 72 | 482 | PRV 72482 | 32 | PRV | 32PRV-N/A-Reagent | Thickeners Standby Flocculant Dosing Pump Pressure Release Valve | 72-4064-FL-MS1-50 | 2000-F72-PID-PR-10016 | N/A | Stage 2 | Greenfield | FL | MS1 | 50 | N/A | 5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600 kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10412 | N/A | N/A | N/A | F72.120 | F72.120.06 | PRV72482 | PRV | Flocculant | AS2129 Table D
0 | PRV | 72 | 483 | PRV 72483 | 32 | PRV | 32PRV-N/A-Reagent | Concentrate Thickener Flocculant Dosing Pump Pressure Release Valve | 72-4065-FL-MS1-50 | 2000-F72-PID-PR-10016 | N/A | Stage 2 | Greenfield | FL | MS1 | 50 | N/A | 5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600 kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10412 | N/A | N/A | N/A | F72.120 | F72.120.06 | PRV72483 | PRV | Flocculant | AS2129 Table D
0 | PRV | 72 | 487 | PRV 72487 | 32 | N/A |  | CIL 4 Reagents Air Receiver |  | 2000-F24-PID-PR-10016 | N/A | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | - | N/A | N/A | ME024 | N/A | Vendor Supply Set Pressure @ 1000 kPag | NUOVA General Industrial | F32 OT |  |  |  |  | F72.10 | F72.10.13 | PRV72487 | N/A | #N/A | #N/A
0 | PRV | 72 | 533 | PRV 72533 | 25 | PRV | 25PRV-N/A-Air | Cyanide Delivery Plant Air Distribution 1 Pressure Relief Valve | 72-1161-IA-MSG3-25 | 2000-F72-PID-PR-10005 | N/A | Stage 2 | Greenfield | IA | MSG3 | 25 | N/A | 72 | 200 | N/A | N/A | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 200kPa | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10408 | N/A | N/A | N/A | F72.10 | F72.10.37 | PRV72533 | PRV | Instrument Air | AS2129 Table E
0 | PRV | 72 | 544 | PRV 72544 | 25 | PRV | 25PRV-N/A-Air | Cyanide Delivery Plant Air Distribution 2 Pressure Relief Valve | 72-2081-IA-MSG3-25 | 2000-F72-PID-PR-10005 | N/A | Stage 2 | Greenfield | IA | MSG3 | 25 | N/A | 72 | 200 | N/A | N/A | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 200kPa | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10408 | N/A | N/A | N/A | F72.10 | F72.10.37 | PRV72544 | PRV | Instrument Air | AS2129 Table E
0 | PRV | 72 | 703 | PRV 72703 | 25 | PRV | 25PRV-N/A-Air | Lead Nitrate Delivery Plant Air Pressure Release Valve | 72-1307-IA-MSG3-25 | 2000-F72-PID-PR-10015 | N/A | Stage 2 | Greenfield | IA | MSG3 | 25 | N/A | 72 | 275 | N/A | N/A | N/A | N/A | N/A | AIR | 1400 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Air | N/A | N/A | PP007 | N/A | Set Pressure @ 275kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10408 | N/A | N/A | N/A | F72.10 | F72.10.37 | PRV72703 | PRV | Instrument Air | AS2129 Table E
0 | PRV | 72 | 710 | PRV 72710 | 32 | PRV | 32PRV-N/A-Reagent | Lead Nitrate Dosing Pump 2 Pressure Release Valve | 72-1144-LN-SS1-50 | 2000-F72-PID-PR-10015 | N/A | Stage 2 | Greenfield | LN | SS1 | 50 | N/A | 5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600 kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10412 | N/A | N/A | N/A | F72.90 | F72.90.02 | PRV72710 | PRV | Lead Nitrate | AS2129 Table D
0 | PRV | 72 | 711 | PRV 72711 | 32 | PRV | 32PRV-N/A-Reagent | Lead Nitrate Dosing Pump 1 Pressure Release Valve | 72-1139-LN-SS1-50 | 2000-F72-PID-PR-10015 | N/A | Stage 2 | Greenfield | LN | SS1 | 50 | N/A | 5 | 600 | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | N/A | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Reagent | N/A | N/A | PP007 | N/A | Set Pressure @ 600 kPag | Calorex Pty Ltd | Roma Fig-160-2N | 2000-PP007-B02-10412 | N/A | N/A | N/A | F72.90 | F72.90.02 | PRV72711 | PRV | Lead Nitrate | AS2129 Table D
0 | SV | 72 | 160 | SV 72160 | 25 | SV | 25SV-Solenoid-FC | Pax Area Sump Pump Air Feed Solenoid Valve | 72-1310-IA-MSG3-25 | 2000-F72-PID-PR-10010 | N/A | Stage 1 | Greenfield | IA | MSG3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F72.20 | F72.20.05 | SV72160 | SV | Instrument Air | AS2129 Table E
1 | SV | 72 | 214 | SV 72214 | 25 | SV | 25SV-Solenoid-FC | Hydrogen Peroxide Area Sump Pump Air Feed Solenoid Valve | 72-2075-IA-MSG3-25 | 2000-F72-PID-PR-10014 | N/A | Stage 2 | Greenfield | IA | MSG3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F72.140 | F72.140.03 | SV72214 | SV | Instrument Air | AS2129 Table E
0 | SV | 72 | 452 | SV 72452 | 25 | SV | 25SV-Solenoid-FO | Slaked Lime Transfer Pump 1 Gland Water Solenoid Valve |  | 2000-F72-PID-PR-10001 | N/A | Stage 2 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F24.30 | F24.30.07 | SV72452 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 72 | 470 | SV 72470 | 25 | SV | 25SV-Solenoid-FO | Lime Ringmain Pump 1 Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F72.110 | F72.110.02 | SV72470 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 72 | 474 | SV 72474 | 25 | SV | 25SV-Solenoid-FO | Lime Ringmain Pump 2 Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F72.110 | F72.110.02 | SV72474 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 72 | 495 | SV 72495 | 25 | SV | 25SV-Solenoid-FO | Slaked Lime Transfer Pump 2 Gland Water Solenoid Valve |  | 2000-F24-PID-PR-10014 | N/A | Stage 2 | Brownfield | GW | SS3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FO | Solenoid | Single Acting | N/A | No | No | FO | N/A | N/A | PP007 | N/A |  | SMC | VXZ2D2LZ2A 24VDC | 2000-PP007-B02-10504 | N/A | N/A | N/A | F72.110 | F72.110.10 | SV72495 | SV | Hypersaline Water | AS2129 Table E
0 | SV | 72 | 617 | SV 72617 | 25 | SV | 25SV-Solenoid-FC | Hydrochloric Acid Area Sump Pump Air Feed Solenoid Valve | 72-2497-IA-MSG3-25 | 2000-F72-PID-PR-10007 | N/A | Stage 2 | Greenfield | IA | MSG3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F72.70 | F72.70.04 | SV72617 | SV | Instrument Air | AS2129 Table E
0 | SV | 72 | 712 | SV 72712 | 25 | SV | 25SV-Solenoid-FC | Lead Nitrate Area Sump Pump Air Feed Solenoid Valve | 72-2064-IA-MSG3-25 | 2000-F72-PID-PR-10015 | N/A | Stage 2 | Greenfield | IA | MSG3 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 1 | Detail 11 | FC | Solenoid | Single Acting | N/A | No | No | FC | N/A | N/A | PP007 | N/A |  | SMC | VXZ262LZ2A 24VDC | 2000-PP007-B02-10503 | N/A | N/A | N/A | F72.90 | F72.90.03 | SV72712 | SV | Instrument Air | AS2129 Table E
0 | XV | 72 | 3 | XV 72003 |  | N/A |  | Flocculant Silo Dehumidifier Delivery Flow Control Valve |  | 2000-F72-PID-PR-10004 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME029 | N/A | Solenoids to be installed on Valve | [6 empty] | F72.120 | F72.120.02 | XV72003 | N/A | #N/A | #N/A
0 | XV | 72 | 8 | XV 72008 |  | N/A |  | Flocculant Silo Flow Control Valve |  | 2000-F72-PID-PR-10004 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | No Solenoid | No | Check Detail | Solenoid on Valve | Solenoid on Valve | N/A | ME029 | N/A | Solenoids to be installed on Valve | [6 empty] | F72.120 | F72.120.02 | XV72008 | N/A | #N/A | #N/A
0 | XV | 72 | 85 | XV 72085 | 80 | VBD1S1 | 80VBD1S1-Spring Return | Copper Sulphate Storage Tank Delivery Control Valve 1 | 72-1145-CO-SS1-80 | 2000-F72-PID-PR-10008 | 2000-F72-PID-PR-10008 | Stage 1 | Greenfield | CO | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.15 | 700 | 3 | Detail 8 | FC | Spring Return | Single Acting | SV72085 | No | Position Switches | - | F72-CP-401 | 2000-PP007-B02-10353 | PP007 | PP007 |  | Unimech | ARITA ARTTBV-TE | 2000-PP007-B02-10022 | Unimech | Pneumatic cylinder | Arita Limit Switch | F72.40 | F72.40.01 | XV72085 | VBD | Copper Sulphate | AS2129 Table D
0 | XV | 72 | 87 | XV 72087 | 80 | VBD1S1 | 80VBD1S1-Spring Return | Copper Sulphate Storage Tank Delivery Control Valve 2 | 72-1551-CO-SS1-80 | 2000-F72-PID-PR-10008 | 2000-F72-PID-PR-10008 | Stage 1 | Greenfield | CO | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.15 | 700 | 3 | Detail 8 | FC | Spring Return | Single Acting | SV72087 | No | Position Switches | - | F72-CP-401 | 2000-PP007-B02-10353 | PP007 | PP007 |  | Unimech | ARITA ARTTBV-TE | 2000-PP007-B02-10022 | Unimech | Pneumatic cylinder | Arita Limit Switch | F72.40 | F72.40.01 | XV72087 | VBD | Copper Sulphate | AS2129 Table D
0 | XV | 72 | 110 | XV 72110 | 80 | VBD1S1 | 80VBD1S1-Spring Return | Frother Storage Tank Feed Valve | 72-1160-FR-SS1-80 | 2000-F72-PID-PR-10009 | 2000-F72-PID-PR-10008 | Stage 1 | Greenfield | FR | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Detail 8 | FC | Spring Return | Single Acting | SV72110 | No | Position Switches | - | F72-CP-401 | 2000-PP007-B02-10353 | PP007 | PP007 |  | Unimech | ARITA ARTTBV-TE | 2000-PP007-B02-10022 | Unimech | Pneumatic cylinder | Arita Limit Switch | F72.30 | F72.30.01 | XV72110 | VBD | Frother | AS2129 Table D
0 | XV | 72 | 135 | XV 72135 | 80 | VBD1S1 | 80VBD1S1-Double Acting-IECEX RATED | Pax Storage Tank Feed Valve 1 | 72-1181-XA-SS1-80 | 2000-F72-PID-PR-10010 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | XA | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Detail 7 | FC | Double Acting | Single Acting | SV72135 | No | Position Switches | IECEX RATED | F72-CP-402 | 2000-PP007-B02-10354 | PP007 | PP007 | IECEx certified Ex ia IIC T6 Gb (at ambient temp >50 deg C) |  |  | 2000-PP007-B02-10143 |  |  |  | F72.20 | F72.20.01 | XV72135 | VBD | Xanthate | AS2129 Table D
0 | XV | 72 | 137 | XV 72137 | 80 | VBD1S1 | 80VBD1S1-Double Acting-IECEX RATED | Pax Storage Tank Feed Valve 2 | 72-1555-XA-SS1-80 | 2000-F72-PID-PR-10010 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | XA | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Detail 7 | FC | Double Acting | Single Acting | SV72137 | No | Position Switches | IECEX RATED | F72-CP-402 | 2000-PP007-B02-10354 | PP007 | PP007 | IECEx certified Ex ia IIC T6 Gb (at ambient temp >50 deg C) |  |  | 2000-PP007-B02-10143 |  |  |  | F72.20 | F72.20.01 | XV72137 | VBD | Xanthate | AS2129 Table D
0 | XV | 72 | 139 | XV 72139 | 50 | VBD1S1 | 50VBD1S1-Double Acting-IECEX RATED | Pax Storage Tank Discharge Valve | 72-1186-XA-SS1-50 | 2000-F72-PID-PR-10010 | 2000-F24-PID-PR-10013 | Stage 1 | Greenfield | XA | SS1 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV72139 | No | Position Switches | IECEX RATED | F72-CP-402 | 2000-PP007-B02-10354 | PP007 | PP007 | IECEx certified Ex ia IIC T6 Gb (at ambient temp >50 deg C) |  |  | 2000-PP007-B02-10138 |  |  |  | F72.20 | F72.20.01 | XV72139 | VBD | Xanthate | AS2129 Table D
0 | XV | 72 | 203 | XV 72203 | 50 | VBE1S4 | 50VBE1S4-Double Acting | Hydrogen Peroxide Storage Tank Feed Valve | 72-0673-HP-SS5-50 | 2000-F72-PID-PR-10014 | 2000-F24-PID-PR-10016 | Stage 1 | Greenfield | HP | SS5 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV72203 | No | Position Switches | - | F72-CP-407 | 2000-PP007-B02-10355 | PP007 | PP007 |  | Emerson | K-BALL F194 - Hydrogen Peroxide | 2000-PP007-B02-10016 | Emerson | KEYSTONE F89-004 | SWIT TOP TVF-M2WGNMM | F72.140 | F72.140.01 | XV72203 | VBE | Hydrogen Peroxide | AS2129 Table E
0 | XV | 72 | 240 | XV 72240 | 25 | VBE1S4 | 25VBE1S4-Double Acting | Hydrogen Peroxide Dosing Pump Discharge Valve 1 | 72-0913-HP-SS5-25 | 2000-F72-PID-PR-10014 | 2000-F24-PID-PR-10016 | Stage 2 | Greenfield | HP | SS5 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 1 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC72240 | No | Position Switches | - | F72-CP-407 | 2000-PP007-B02-10355 | PP007 | PP007 |  | Emerson | K-BALL F194 - Hydrogen Peroxide | 2000-PP007-B02-10134 | Emerson | KEYSTONE F89-004 | SWIT TOP TVF-M2WGNMM | F72.140 | F72.140.04 | XV72240 | VBE | Hydrogen Peroxide | AS2129 Table E
0 | XV | 72 | 241 | XV 72241 | 25 | VBE1S4 | 25VBE1S4-Double Acting | Hydrogen Peroxide Dosing Pump Discharge Valve 2 | 72-0913-HP-SS5-25 | 2000-F72-PID-PR-10014 | 2000-F24-PID-PR-10016 | Stage 2 | Greenfield | HP | SS5 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 1 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC72241 | No | Position Switches | - | F72-CP-407 | 2000-PP007-B02-10355 | PP007 | PP007 |  | Emerson | K-BALL F194 - Hydrogen Peroxide | 2000-PP007-B02-10134 | Emerson | KEYSTONE F89-004 | SWIT TOP TVF-M2WGNMM | F72.140 | F72.140.04 | XV72241 | VBE | Hydrogen Peroxide | AS2129 Table E
0 | XV | 72 | 242 | XV 72242 | 25 | VBE1S4 | 25VBE1S4-Double Acting | Hydrogen Peroxide Dosing Pump Discharge Valve 3 | 72-0798-HP-SS5-25 | 2000-F72-PID-PR-10014 | 2000-F24-PID-PR-10016 | Stage 2 | Greenfield | HP | SS5 | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 1400 | 1 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC72242 | No | Position Switches | - | F72-CP-407 | 2000-PP007-B02-10355 | PP007 | PP007 |  | Emerson | K-BALL F194 - Hydrogen Peroxide | 2000-PP007-B02-10134 | Emerson | KEYSTONE F89-004 | SWIT TOP TVF-M2WGNMM | F72.140 | F72.140.04 | XV72242 | VBE | Hydrogen Peroxide | AS2129 Table E
0 | XV | 72 | 409 | XV 72409 |  | N/A |  | Lime Slaking Mill Ball Kibble Loading Hopper Gate 1 | MECH | 2000-F72-PID-PR-10001 | 2000-F72-PID-PR-10003 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV72409 | No | Position Switches | - | F72HP658-CP | N/A | ME090 | ME090 | Actuated Gate | [6 empty] | F72.110 | F72.110.11 | XV72409 | N/A | #N/A | #N/A
0 | XV | 72 | 410 | XV 72410 |  | N/A |  | Lime Slaking Mill Ball Kibble Loading Hopper Gate 1 | MECH | 2000-F72-PID-PR-10001 | 2000-F72-PID-PR-10003 | Stage 2 | Greenfield |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Detail 12 | FL | Double Acting | Manual 4-Way Isolation | HV72410 | No | Position Switches | - | F72HP658-CP | N/A | ME090 | ME090 | Actuated Gate | [6 empty] | F72.110 | F72.110.11 | XV72410 | N/A | #N/A | #N/A
0 | XV | 72 | 413 | XV 72413 | 100 | N/A |  | Slaked Lime Discharge Hopper 1 Drain Valve |  | 2000-F72-PID-PR-10001 | N/A | Stage 2 | Greenfield | LS | MS1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 4 | FC | Double Acting | Single Acting | SV72413 | No | Position Switches | - | F72-CP-403 | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.05 | XV72413 | N/A | Lime Slurry | AS2129 Table D
0 | XV | 72 | 415 | XV 72415 | 100 | N/A |  | Slaked Lime Discharge Hopper 2 Drain Valve |  | 2000-F72-PID-PR-10002 | N/A | Stage 2 | Greenfield | LS | MS1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 4 | FC | Double Acting | Single Acting | SV72415 | No | Position Switches | - | F72-CP-403 | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.10 | XV72415 | N/A | Lime Slurry | AS2129 Table D
0 | XV | 72 | 419 | XV 72419 | 100 | N/A |  | Lime Silo 1 Filling Line Isolation Valve 1 |  | 2000-F72-PID-PR-10001 | N/A | Stage 2 | Greenfield | BA | MSG1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 4 | FC | Double Acting | Single Acting | SV72419 | No | Position Switches | - | F72SI411-CP | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.01 | XV72419 | N/A | Blower Air | AS2129 Table D
0 | XV | 72 | 420 | XV 72420 | 100 | N/A |  | Lime Silo 1 Filling Line Isolation Valve 2 |  | 2000-F72-PID-PR-10001 | N/A | Stage 2 | Greenfield | BA | MSG1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 4 | FC | Double Acting | Single Acting | SV72420 | No | Position Switches | - | F72SI411-CP | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.01 | XV72420 | N/A | Blower Air | AS2129 Table D
0 | XV | 72 | 433 | XV 72433 | 100 | N/A |  | Lime Silo 2 Filling Line Isolation Valve 1 |  | 2000-F72-PID-PR-10002 | N/A | Stage 2 | Greenfield | BA | MSG1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 4 | FC | Double Acting | Single Acting | SV72433 | No | Position Switches | - | F72SI412-CP | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.16 | XV72433 | N/A | Blower Air | AS2129 Table D
0 | XV | 72 | 434 | XV 72434 | 100 | N/A |  | Lime Silo 2 Filling Line Isolation Valve 2 |  | 2000-F72-PID-PR-10002 | N/A | Stage 2 | Greenfield | BA | MSG1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 4 | FC | Double Acting | Single Acting | SV72434 | No | Position Switches | - | F72SI412-CP | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.16 | XV72434 | N/A | Blower Air | AS2129 Table D
0 | XV | 72 | 441 | XV 72441 | 250 | VKGD1L1 | 250VKGD1L1-Double Acting | Lime Ringmain Pump 1 Suction Valve | 250-MECH-RL1 | 2000-F72-PID-PR-10003 | 2000-F24-PID-PR-10016 | Stage 2 | Greenfield | LS | RL1 | 250 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 10 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72441 | No | Position Switches | - | F72-CP-408 | 2000-PP007-B02-10381 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10075 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F72.110 | F72.110.02 | XV72441 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 442 | XV 72442 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Lime Ringmain Pump 1 Suction Flushing Valve | 250-MECH-RL1 | 2000-F72-PID-PR-10003 | 2000-F24-PID-PR-10016 | Stage 2 | Greenfield | LS | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72442 | No | Position Switches | - | F72-CP-408 | 2000-PP007-B02-10381 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F24.40 | F24.40.10 | XV72442 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 443 | XV 72443 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Lime Ringmain Pump 1 Suction Drain Valve | 250-MECH-RL1 | 2000-F72-PID-PR-10003 | 2000-F24-PID-PR-10016 | Stage 2 | Greenfield | LS | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72443 | No | Position Switches | - | F72-CP-408 | 2000-PP007-B02-10381 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F72.110 | F72.110.02 | XV72443 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 444 | XV 72444 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | Lime Ringmain Pump 1 Discharge Valve | 72-1058-LS-RL1-200 | 2000-F72-PID-PR-10003 | 2000-F24-PID-PR-10016 | Stage 2 | Greenfield | LS | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72444 | No | Position Switches | - | F72-CP-408 | 2000-PP007-B02-10381 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F72.110 | F72.110.02 | XV72444 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 445 | XV 72445 | 250 | VKGD1L1 | 250VKGD1L1-Double Acting | Lime Ringmain Pump 2 Suction Valve | 250-MECH-RL1 | 2000-F72-PID-PR-10003 | 2000-F24-PID-PR-10016 | Stage 2 | Greenfield | LS | RL1 | 250 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 10 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72445 | No | Position Switches | - | F72-CP-413 | 2000-PP007-B02-10386 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10075 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F72.110 | F72.110.02 | XV72445 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 446 | XV 72446 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Lime Ringmain Pump 2 Suction Flushing Valve | 250-MECH-RL1 | 2000-F72-PID-PR-10003 | 2000-F24-PID-PR-10016 | Stage 2 | Greenfield | LS | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72446 | No | Position Switches | - | F72-CP-413 | 2000-PP007-B02-10386 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F24.40 | F24.40.10 | XV72446 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 447 | XV 72447 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Lime Ringmain Pump 2 Suction Drain Valve | 250-MECH-RL1 | 2000-F72-PID-PR-10003 | 2000-F24-PID-PR-10016 | Stage 2 | Greenfield | LS | RL1 | 80 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72447 | No | Position Switches | - | F72-CP-413 | 2000-PP007-B02-10386 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F72.110 | F72.110.02 | XV72447 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 448 | XV 72448 | 200 | VKGD1L1 | 200VKGD1L1-Double Acting | Lime Ringmain Pump 2 Discharge Valve | 72-1051-LS-RL1-200 | 2000-F72-PID-PR-10003 | 2000-F24-PID-PR-10016 | Stage 2 | Greenfield | LS | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 8 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72448 | No | Position Switches | - | F72-CP-413 | 2000-PP007-B02-10386 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10070 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F72.110 | F72.110.02 | XV72448 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 452 | XV 72452 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Lime Ringmain Pump 1 Discharge Drain Valve | 72-1058-LS-RL1-200 | 2000-F72-PID-PR-10003 | 2000-F24-PID-PR-10016 | Stage 2 | Greenfield | LS | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72452 | No | Position Switches | - | F72-CP-408 | 2000-PP007-B02-10381 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F72.110 | F72.110.02 | XV72452 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 453 | XV 72453 | 80 | VKGD1L1 | 80VKGD1L1-Double Acting | Lime Ringmain Pump 2 Discharge Drain Valve | 72-1051-LS-RL1-200 | 2000-F72-PID-PR-10003 | 2000-F24-PID-PR-10016 | Stage 2 | Greenfield | LS | RL1 | 200 | N/A | N/A | N/A | N/A | N/A | 75 | 150 | 0.2 | 1.24 | 700 | 3 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72453 | No | Position Switches | - | F72-CP-413 | 2000-PP007-B02-10386 | PP007 | PP007 |  | Emerson | Clarkson KGD | 2000-PP007-B02-10033 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC | F72.110 | F72.110.02 | XV72453 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 457 | XV 72457 | 50 | VBFD1S2 | 50VBFD1S2-Double Acting | Slaked Lime Wet Scrubber 1 Actuated Feed Valve |  | 2000-F72-PID-PR-10001 | N/A | Stage 2 | Greenfield | BW | SS1 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2 | Detail 7 | FO | Double Acting | Single Acting | SV72457 | No | Position Switches | - | F72-CP-403 | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F24.40 | F24.40.10 | XV72457 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 72 | 458 | XV 72458 | 100 | VKGD1L2 | 100VKGD1L2-Double Acting | Slaked Lime Hydro-Cyclone 1 Actuated Feed Valve |  | 2000-F72-PID-PR-10001 | N/A | Stage 2 | Greenfield | LS | RL1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72458 | No | Position Switches | - | F72-CP-404 | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.05 | XV72458 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 459 | XV 72459 | 100 | VKGD1L2 | 100VKGD1L2-Double Acting | Slaked Lime Hydro-Cyclone 1 Actuated Feed Valve |  | 2000-F72-PID-PR-10001 | N/A | Stage 2 | Greenfield | LS | RL1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72459 | No | Position Switches | - | F72-CP-404 | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.05 | XV72459 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 460 | XV 72460 | 100 | VKGD1L2 | 100VKGD1L2-Double Acting | Slaked Lime Hydro-Cyclone 1 Actuated Feed Valve |  | 2000-F72-PID-PR-10001 | N/A | Stage 2 | Greenfield | LS | RL1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72460 | No | Position Switches | - | F72-CP-404 | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.05 | XV72460 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 464 | XV 72464 | 50 | VB03S1 | 50VB03S1-Double Acting | Milk of Lime Area Sump Pump 1 Flushing Valve | 72-xxx-BW-SS3-50 | 2000-F72-PID-PR-10003 | 2000-F72-PID-PR-10003 | Stage 2 | Greenfield | BW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV72464 | No | Position Switches | - | F72-CP-413 | 2000-PP007-B02-10386 | PP007 | PP007 |  | Emerson | K-BALL F182 | 2000-PP007-B02-10008 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F24.40 | F24.40.10 | XV72464 | VB0 | Hypersaline Water | AS2129 Table E
0 | XV | 72 | 465 | XV 72465 | 50 | VB03S1 | 50VB03S1-Double Acting | Milk of Lime Area Sump Pump 2 Flushing Valve | 72-2485-BW-SS3-50 | 2000-F72-PID-PR-10003 | 2000-F72-PID-PR-10003 | Stage 2 | Greenfield | BW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV72465 | No | Position Switches | - | N/A | N/A | PP007 | N/A | Instrument Air direct to valve | Emerson | K-BALL F182 | 2000-PP007-B02-10008 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F24.40 | F24.40.10 | XV72465 | VB0 | Hypersaline Water | AS2129 Table E
0 | XV | 72 | 466 | XV 72466 | 50 | VB03S1 | 50VB03S1-Double Acting | Milk of Lime Area Sump Pump 3 Flushing Valve | 72-2486-BW-SS3-50 | 2000-F72-PID-PR-10003 | 2000-F72-PID-PR-10003 | Stage 2 | Greenfield | BW | SS3 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 1400 | 2 | Detail 7 | FC | Double Acting | Single Acting | SV72466 | No | Position Switches | - | N/A | N/A | PP007 | N/A | Instrument Air direct to valve | Emerson | K-BALL F182 | 2000-PP007-B02-10008 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM | F24.40 | F24.40.10 | XV72466 | VB0 | Hypersaline Water | AS2129 Table E
0 | XV | 72 | 467 | XV 72467 | 100 | VKGD1L2 | 100VKGD1L2-Double Acting | Slaked Lime Hydro-Cyclone 2 Actuated Feed Valve |  | 2000-F72-PID-PR-10002 | N/A | Stage 2 | Greenfield | LS | RL1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72467 | No | Position Switches | - | F72-CP-404 | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.10 | XV72467 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 468 | XV 72468 | 100 | VKGD1L2 | 100VKGD1L2-Double Acting | Slaked Lime Hydro-Cyclone 2 Actuated Feed Valve |  | 2000-F72-PID-PR-10002 | N/A | Stage 2 | Greenfield | LS | RL1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72468 | No | Position Switches | - | F72-CP-404 | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.10 | XV72468 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 469 | XV 72469 | 100 | VKGD1L2 | 100VKGD1L2-Double Acting | Slaked Lime Hydro-Cyclone 2 Actuated Feed Valve |  | 2000-F72-PID-PR-10002 | N/A | Stage 2 | Greenfield | LS | RL1 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC72469 | No | Position Switches | - | F72-CP-404 | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F72.110 | F72.110.10 | XV72469 | VKG | Lime Slurry | AS2129 Table D
0 | XV | 72 | 473 | XV 72473 | 50 | VBFD1S2 | 50VBFD1S2-Double Acting | Slaked Lime Wet Scrubber 2 Actuated Feed Valve |  | 2000-F72-PID-PR-10002 | N/A | Stage 2 | Greenfield | BW | SS1 | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2 | Detail 7 | FO | Double Acting | Single Acting | SV72473 | No | Position Switches | - | F72-CP-403 | N/A | ME013 | ME013 | Vendor Supply | [6 empty] | F24.40 | F24.40.10 | XV72473 | VBF | Hypersaline Water | AS2129 Table D
0 | XV | 72 | 536 | XV 72536 | 150 | VBD1C1 | 150VBD1C1-Double Acting | Cyanide Storage Tank 1 Discharge Valve | 72-1085-CN-MS1-150 | 2000-F72-PID-PR-10005 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CN | MS1 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 6 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC72536 | No | Position Switches | - | F72-CP-409 | 2000-PP007-B02-10382 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10049 | Emerson | KEYSTONE F89-085 | TOPWORX TVF-M2WGNMM | F72.80 | F72.80.02 | XV72536 | VBD | Cyanide Solution | AS2129 Table D
0 | XV | 72 | 537 | XV 72537 | 150 | VBD1C1 | 150VBD1C1-Double Acting | Cyanide Storage Tank 2 Discharge Valve | 72-1086-CN-MS1-150 | 2000-F72-PID-PR-10005 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CN | MS1 | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 6 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC72537 | No | Position Switches | - | F72-CP-409 | 2000-PP007-B02-10382 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10049 | Emerson | KEYSTONE F89-085 | TOPWORX TVF-M2WGNMM | F72.80 | F72.80.02 | XV72537 | VBD | Cyanide Solution | AS2129 Table D
0 | XV | 72 | 538 | XV 72538 | 80 | VBE1C1 | 80VBE1C1-Double Acting | Cyanide Storage Tank 1 Inlet Valve | 72-1092-CN-PE16-90 | 2000-F72-PID-PR-10005 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CN | PE16 | 90 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC72538 | No | Position Switches | - | F72-CP-409 | 2000-PP007-B02-10382 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10024 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM | F72.80 | F72.80.02 | XV72538 | VBE | Cyanide Solution | AS2129 Table E PN16
0 | XV | 72 | 539 | XV 72539 | 80 | VBE1C1 | 80VBE1C1-Double Acting | Cyanide Storage Tank 2 Inlet Valve | 72-0316-CN-PE16-90 | 2000-F72-PID-PR-10005 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CN | PE16 | 90 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC72539 | No | Position Switches | - | F72-CP-409 | 2000-PP007-B02-10382 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10024 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM | F72.80 | F72.80.02 | XV72539 | VBE | Cyanide Solution | AS2129 Table E PN16
0 | XV | 72 | 541 | XV 72541 | 80 | VBD1C1 | 80VBD1C1-Spring Return | Cyanide Delivery to Cyanide Storage Tank 1 Inlet Valve | 72-1080-CN-MS1-80 | 2000-F72-PID-PR-10005 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CN | MS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Detail 8 | FC | Spring Return | Single Acting | SV72541 | No | Position Switches | - | F72-CP-414 | 2000-PP007-B02-10387 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10020 | Emerson | KEYSTONE F89-032 | TOPWORX TVF-M2WGNMM | F72.80 | F72.80.01 | XV72541 | VBD | Cyanide Solution | AS2129 Table D
0 | XV | 72 | 542 | XV 72542 | 80 | VBD1C1 | 80VBD1C1-Spring Return | Cyanide Delivery to Cyanide Storage Tank 2 Inlet Valve | 72-0315-CN-MS1-80 | 2000-F72-PID-PR-10005 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | CN | MS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Detail 8 | FC | Spring Return | Single Acting | SV72542 | No | Position Switches | - | F72-CP-414 | 2000-PP007-B02-10387 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10020 | Emerson | KEYSTONE F89-032 | TOPWORX TVF-M2WGNMM | F72.80 | F72.80.01 | XV72542 | VBD | Cyanide Solution | AS2129 Table D
0 | XV | 72 | 594 | XV 72594 | 80 | VBD1C1 | 80VBD1C1-Spring Return | Caustic Delivery to Caustic Storage Tank Inlet Valve | 72-1100-NS-MS1-80 | 2000-F72-PID-PR-10006 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | NS | MS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Detail 8 | FC | Spring Return | Single Acting | SV72594 | No | Position Switches | - | F72-CP-410 | 2000-PP007-B02-10383 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10020 | Emerson | KEYSTONE F89-032 | TOPWORX TVF-M2WGNMM | F72.60 | F72.60.01 | XV72594 | VBD | Caustic Soda | AS2129 Table D
0 | XV | 72 | 596 | XV 72596 | 80 | VBD1C1 | 80VBD1C1-Double Acting | Caustic Storage Tank Discharge Valve | 72-1101-NS-MS1-80 | 2000-F72-PID-PR-10006 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | NS | MS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Detail 7 | FC | Double Acting | Single Acting | SV72596 | No | Position Switches | - | F72-CP-410 | 2000-PP007-B02-10383 | PP007 | PP007 |  | Emerson | KTM EB11 | 2000-PP007-B02-10019 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM | F72.60 | F72.60.01 | XV72596 | VBD | Caustic Soda | AS2129 Table D
0 | XV | 72 | 601 | XV 72601 | 80 | VBD1T1 | 80VBD1T1-Spring Return | Hydrochloric Acid Delivery to Acid Storage Tank Inlet Valve | 72-1120-HCL-PE8-90 | 2000-F72-PID-PR-10007 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | HCL | PE8 | 90 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Detail 8 | FC | Spring Return | Single Acting | SV72601 | No | Position Switches | - | F72-CP-411 | 2000-PP007-B02-10384 | PP007 | PP007 |  | George Fischer | GF 546 Pro | 2000-PP007-B02-10023 | George Fischer | Pneumatic actuator PPA80 PPGF FC | Limit Switch Included | F72.70 | F72.70.01 | XV72601 | VBD | Hydrochloric Acid | AS2129 Table D PN10
0 | XV | 72 | 603 | XV 72603 | 100 | VBD1T1 | 100VBD1T1-Double Acting | Hydrochloric Acid Storage Tank Outlet Valve | 72-1122-HCL-PE8-110 | 2000-F72-PID-PR-10007 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | HCL | PE8 | 110 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 7 | FC | Double Acting | Single Acting | SV72603 | No | Position Switches | - | F72-CP-411 | 2000-PP007-B02-10384 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10147 |  |  |  | F72.70 | F72.70.01 | XV72603 | VBD | Hydrochloric Acid | AS2129 Table D PN10
0 | XV | 72 | 614 | XV 72614 | 80 | VBFE1L1 | 80VBFE1L1-Spring Return | CIL 4 Acid Dilution Tank Scheme Water Inlet Valve | 72-3073-PSW-PE16-90 | 2000-F72-PID-PR-10007 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | PSW | PE16 | 90 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1 | 700 | 3 | Detail 8 | FC | Spring Return | Single Acting | SV72614 | No | Position Switches | - | F72-CP-411 | 2000-PP007-B02-10384 | PP007 | PP007 |  | Emerson | GRW | 2000-PP007-B02-10031 | Emerson | KEYSTONE F89-009 | TOPWORX TVF-M2WGNMM | F24.70 | F24.70.02 | XV72614 | VBF | Process Scheme Water | AS2129 Table E PN16
0 | XV | 72 | 637 | XV 72637 | 50 | VBD1T1 | 50VBD1T1-Double Acting | CIL 4 Acid Dilution Tank Acid Recirculation Valve | 72-1115-HCL-PE8-63 | 2000-F72-PID-PR-10007 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | HCL | PE8 | 63 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 2 | Detail 7 | FO | Double Acting | Single Acting | SV72637 | No | Position Switches | - | F72-CP-411 | 2000-PP007-B02-10384 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10139 |  |  |  | F72.70 | F72.70.03 | XV72637 | VBD | Hydrochloric Acid | AS2129 Table D PN10
0 | XV | 72 | 639 | XV 72639 | 100 | VBD1T1 | 100VBD1T1-Double Acting | CIL 4 Acid Dilution Tank Acid Discharge Valve | 72-2543-HCL-PE8-110 | 2000-F72-PID-PR-10007 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | HCL | PE8 | 110 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 4 | Detail 9 | FL | Double Acting | Double Acting | SVO/SVC72639 | No | Position Switches | - | F72-CP-411 | 2000-PP007-B02-10384 | PP007 | PP007 |  |  |  | 2000-PP007-B02-10147 |  |  |  | F72.70 | F72.70.03 | XV72639 | VBD | Hydrochloric Acid | AS2129 Table D PN10
0 | XV | 72 | 705 | XV 72705 | 80 | VBD1S1 | 80VBD1S1-Spring Return | Lead Nitrate Delivery to Lead Nitrate Storage Tank Valve | 72-1140-LN-SS1-80 | 2000-F72-PID-PR-10015 | 2000-F24-PID-PR-10029 | Stage 2 | Greenfield | LN | SS1 | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | 700 | 3 | Detail 8 | FC | Spring Return | Single Acting | SV72705 | No | Position Switches | - | F72-CP-411 | 2000-PP007-B02-10384 | PP007 | PP007 |  | Unimech | ARITA ARTTBV-TE | 2000-PP007-B02-10022 | Unimech | Pneumatic cylinder | Arita Limit Switch | F72.90 | F72.90.01 | XV72705 | VBD | Lead Nitrate | AS2129 Table D
0 | HV | 75 | 401 | HV 75401 | 450 | VBFD1S2 | 450VBFD1S2-Manual | Suction Turret to Saline Water Pump 1 Suction Manual Valve | 75-3044-BW-SS1-450 | 2000-F75-PID-PR-10002 | N/A | Stage 1 | Brownfield | BW | SS1 | 450 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 18 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10093 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F24.50 | F24.50.04 | HV75401 | VBF | Hypersaline Water | AS2129 Table D
0 | HV | 75 | 403 | HV 75403 | 400 | VBFD1S2 | 400VBFD1S2-Manual | Saline Water Pump 1 Discharge Manual Valve | 75-3042-BW-SS1-400 | 2000-F75-PID-PR-10002 | N/A | Stage 1 | Brownfield | BW | SS1 | 400 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 16 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10087 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F24.50 | F24.50.04 | HV75403 | VBF | Hypersaline Water | AS2129 Table D
0 | HV | 75 | 411 | HV 75411 | 450 | VBFD1S2 | 450VBFD1S2-Manual | Suction Turret to Saline Water Pump 2 Suction Manual Valve | 75-3045-BW-SS1-450 | 2000-F75-PID-PR-10002 | N/A | Stage 1 | Brownfield | BW | SS1 | 450 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 18 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10093 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F24.50 | F24.50.04 | HV75411 | VBF | Hypersaline Water | AS2129 Table D
0 | HV | 75 | 413 | HV 75413 | 400 | VBFD1S2 | 400VBFD1S2-Manual | Saline Water Pump 2 Discharge Manual Valve | 75-3041-BW-SS1-400 | 2000-F75-PID-PR-10002 | N/A | Stage 1 | Brownfield | BW | SS1 | 400 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 16 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10087 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F24.50 | F24.50.04 | HV75413 | VBF | Hypersaline Water | AS2129 Table D
0 | HV | 75 | 421 | HV 75421 | 450 | VBFD1S2 | 450VBFD1S2-Manual | Suction Turret to Saline Water Pump 3 Suction Manual Valve | 75-3046-BW-SS1-450 | 2000-F75-PID-PR-10002 | N/A | Stage 1 | Brownfield | BW | SS1 | 450 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 18 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10093 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F24.50 | F24.50.04 | HV75421 | VBF | Hypersaline Water | AS2129 Table D
0 | HV | 75 | 423 | HV 75423 | 400 | VBFD1S2 | 400VBFD1S2-Manual | Saline Water Pump 3 Discharge Manual Valve | 75-3040-BW-SS1-400 | 2000-F75-PID-PR-10002 | N/A | Stage 1 | Brownfield | BW | SS1 | 400 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.07 | 700 | 16 | Manual | N/A | Manual | Manual Isolation | No Solenoid | No | Position Switches | - | N/A | N/A | PP007 | N/A | Manual Valves with positioner feedback | Emerson | GRL | 2000-PP007-B02-10087 | Emerson | Gearbox | 2000043108 TVF-M2WGNMM | F24.50 | F24.50.04 | HV75423 | VBF | Hypersaline Water | AS2129 Table D
1 | LCV | 75 | 690 | LCV 75690 | 80 | VBFD1S1 | 80VBFD1S1-Double Acting-Positioner | Gland Water Tank Level Control Valve | 75-3007-BW-SS1-80 | 2000-F75-PID-PR-10007 | 2000-F75-PID-PR-10007 | Stage 1 | Brownfield | BW | SS1 | 80 | 0 | 35 | 600 | 600 | 10 | N/A | N/A | N/A | 1.07 | 700 | 3 | Detail 1 | FO | Double Acting | Manual Isolation | Manual Isolation | Yes | No | - | N/A | N/A | PP007 | N/A |  | Emerson | GRW | 2000-PP007-B02-10144 | Emerson | KEYSTONE F89-085 | SMC IP8100 031 J (4-20mA) | F24.40 | F24.40.12
0 | XV | 75 | 608 | XV 75608 | 400 | VKGE1L1 | 400VKGE1L1-Double Acting-ANSI flanges | Tails Flushing HP Process Water | 75-8062-TL-RL2-400 | 2000-F75-PID-PR-25008 | 2000-F24-PID-PR-10007 | Stage 2 | Brownfield | TL | RL2 | 400 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 1400 | 16 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC75608 | No | Position Switches | ANSI flanges | F23-CP-405 | 2000-PP007-B02-10388 | PP007 | PP007 | ANSI 150 LB flat faced flanges |  |  | 2000-PP007-B02-10131 |  |  |  | TBA | TBA
0 | XV | 75 | 609 | XV 75609 | 400 | VKGE1L1 | 400VKGE1L1-Double Acting-ANSI flanges | Tails Flushing HP Process Water | 75-8062-TL-RL2-400 | 2000-F75-PID-PR-25008 | 2000-F24-PID-PR-10007 | Stage 2 | Brownfield | TL | RL2 | 400 | N/A | N/A | N/A | N/A | N/A | 70 | 220 | 0.547 | 1.63 | 1400 | 16 | Detail 3 | FL | Double Acting | Double Acting | SVO/SVC75609 | No | Position Switches | ANSI flanges | F23-CP-405 | 2000-PP007-B02-10388 | PP007 | PP007 | ANSI 150 LB flat faced flanges |  |  | 2000-PP007-B02-10131 |  |  |  | TBA | TBA | XV75609 | VKG | #N/A | AS2129 Table E

## Valve Detail
CONTROL VALVE DETAILS
Detail | Position Controller | Actuator | Solenoid | Position Feedback | Features
Detail 1 | Yes | Double Acting | Manual Isolation
Detail 2 | Yes | Double Acting | Manual Isolation | Transmitter
Detail 3 |  | Double Acting | Double Acting | Position Switches
Detail 4 |  | Double Acting | Single Acting | Position Switches
Detail 5 |  | Double Acting | Double Acting | Position Switches | Hydraulic
Detail 6 |  | Double Acting | Single Acting | Position Switches | Hydraulic
Detail 7 |  | Double Acting | Single Acting | Position Switches
Detail 8 |  | Spring Return | Single Acting | Position Switches
Detail 9 |  | Double Acting | Double Acting | Position Switches
Detail 10 |  | Double Acting | Double Acting | Position Switches | Hydraulic
Detail 11 |  | Solenoid | Single Acting
Detail 12 |  | Double Acting | Manual 4-Way Isolation | Position Switches
Detail 13 | Yes | Electric 240VAC | Manual Isolation | Transmitter | Electric driven
Detail 14 | Yes | Electric 240VAC | Manual Isolation | Position Switches | Electric driven
Detail 15 |  | Electric 24VDC | Manual Isolation | Position Switches | Electric driven
Manual |  | Manual | Manual Isolation | Position Switches
N/A |  | N/A | N/A | N/A
Valve Type | Definition |  | Fluid Code | Description
RV | Relief Valve |  | AA | Aeration Air
TV | Tech Taylor Valve |  | AE | Acid Effluent
VA | Air Release / Vacuum Breaker Valve |  | AS | Antiscalant
VB | Ball Valve |  | BA | Blower Air
VBF | Butterfly Valve |  | BE | Barren Eluate
VC | Check Valve |  | BW | Hypersaline Water
VD | Diaphragm Valve |  | BW-H | Bore Water (Hypersaline) High Pressure
VDT | Dart Valve |  | BW-L | Bore Water (Hypersaline) Low Pressure
VG | Gate Valve |  | CA | Compressed Air
VGL | Globe Valve |  | CN | Cyanide Solution
VF | Float Valve |  | CO | Copper Sulphate
VKG | Knife Gate Valve |  | CON | Concentrate Slurry
VN | Needle Valve |  | COW | Cooling Water
VP | Valve Pressure / Sustaining |  | CR | Crusher Oil
VPI | Pinch Valve |  | CS | Cyanide Slurry
VPL | Plug Valve |  | CT | Calcine Tailings
VR | Rotary Valve |  | CW | Cyanide Water
VTW | 3 Way Valve |  | DCW | Decant Cyanide Water
FLV | Flushing Water Valve |  | DL | Diesel Fuel
GLV | Gland Water Valve |  | FA | Flotation Air
SCV | Scour/Drain Valve |  | FD | Floor Drainage
|  |  | FL | Flocculant
Pressure Code | Valve Class |  | FR | Frother
01/02 | Socket or Threaded |  | FS | Flotation Slurry
D1 | AS2129 Table D / AS4087 PN14 |  | FT | Final Tailings
E1 | AS2129 Table E / AS4087 PN18 |  | FW | Fire Water
F1 | AS2129 Table F / AS4087 PN21 |  | GW | Hypersaline Water
H1 | AS2129 Table H / AS4087 PN35 |  | GW-H | Gland Water (Hypersaline) High Pressure
|  |  | GW-L | Gland Water (Hypersaline) Low Pressure
Piping Code | Flanges |  | HCL | Hydrochloric Acid
CERAMIC | AS2129 Table D |  | HO | Hydraulic Oil
MECH |  |  | HO-H | Hydraulic Oil
MS1 | AS2129 Table D |  | HO-R | Hydraulic Oil Return
MS2 | AS2129 Table E |  | HP | Hydrogen Peroxide
MSG1 | AS2129 Table D |  | HPE | Hydrochloric Acid / Pregnant Eluate
MSG3 | AS2129 Table E |  | IA | Instrument Air
PE10 | AS2129 Table D PN10 |  | LN | Lead Nitrate
PE16 | AS2129 Table E PN16 |  | LO | Lubricating Oil
PE20 | AS2129 Table E PN20 |  | LO-H | Lubricating Oil – High Pressure
PE8 | AS2129 Table D PN10 |  | LO-L | Lubricating Oil – Low Pressure
RL1 | AS2129 Table D |  | LO-M | Lubricating Oil – Medium Pressure
RL2 | AS2129 Table E |  | LPG | Fuel Gas
RL3 | AS2129 Table D |  | LS | Lime Slurry
SS1 | AS2129 Table D |  | MS | Mill Slurry
SS2 | AS2129 Table E |  | NS | Caustic Soda
SS3 | AS2129 Table E |  | OG | Off Gas
SS5 | AS2129 Table E |  | OXY | Oxygen
SS6 | AS2129 Table E |  | PE | Pregnant Eluate
SS7 | AS2129 Table E |  | POT | Potable Water
XS | AS2129 Table D |  | PSW | Process Scheme Water
|  |  | PW | Hypersaline Water
|  |  | PW-H | Process Water High (Hypersaline)
|  |  | PW-H | Process Water High (Hypersaline)
|  |  | PW-L | Process Water Low (Hypersaline)
|  |  | SC | Carbon Slurry
|  |  | SW | Shower Water
|  |  | TE | Teric
|  |  | TH | Thermal Oil
|  |  | TW | Transfer Water
|  |  | V-H | Vent
|  |  | V-L | Vent
|  |  | WM | UFG Media and Process Water
|  |  | WW | Washdown Water
|  |  | XA | Xanthate

## Control Panel List
CONTROL PANEL LIST
Package | Tag Number | Air P&ID | Stage | Valve TAG | Solenoid Tag | Location Description | Detail | Failure State | Sum of Area Number
ME001.4 | Solenoid on Valve | 2000-F24-PID-PR-10024 | Stage 1 | FCV 16011 | Manual Isolation | Rougher Flotation Cell 1 Low Pressure Air Flow Control Valve | N/A | N/A | 16
|  |  |  | FCV 16051 | Manual Isolation | Rougher Flotation Cell 2 Low Pressure Air Flow Control Valve | N/A | N/A | 16
|  |  |  | FCV 16061 | Manual Isolation | Rougher Flotation Cell 3 Low Pressure Air Flow Control Valve | N/A | N/A | 16
|  |  |  | FCV 16081 | Manual Isolation | Scavenger Flotation Cell 1 Low Pressure Air Flow Control Valve | N/A | N/A | 16
|  |  |  | FCV 16091 | Manual Isolation | Scavenger Flotation Cell 2 Low Pressure Air Flow Control Valve | N/A | N/A | 16
|  |  |  | FCV 16101 | Manual Isolation | Scavenger Flotation Cell 3 Low Pressure Air Flow Control Valve | N/A | N/A | 16
|  |  |  | FCV 16111 | Manual Isolation | Scavenger Flotation Cell 4 Low Pressure Air Flow Control Valve | N/A | N/A | 16
|  |  |  | LCV 16013A | Manual Isolation | Rougher Flotation Cell 2 Level Control Valve A | N/A | N/A | 16
|  |  |  | LCV 16013B | Manual Isolation | Rougher Flotation Cell 2 Level Control Valve B | N/A | N/A | 16
|  |  |  | LCV 16053A | Manual Isolation | Rougher Flotation Cell 3 Level Control Valve A | N/A | N/A | 16
|  |  |  | LCV 16053B | Manual Isolation | Rougher Flotation Cell 3 Level Control Valve B | N/A | N/A | 16
|  |  |  | LCV 16063A | Manual Isolation | Scavenger Flotation Cell 1 Level Control Valve A | N/A | N/A | 16
|  |  |  | LCV 16063B | Manual Isolation | Scavenger Flotation Cell 1 Level Control Valve B | N/A | N/A | 16
|  |  |  | LCV 16083A | Manual Isolation | Scavenger Flotation Cell 2 Level Control Valve A | N/A | N/A | 16
|  |  |  | LCV 16083B | Manual Isolation | Scavenger Flotation Cell 2 Level Control Valve B | N/A | N/A | 16
|  |  |  | LCV 16093A | Manual Isolation | Scavenger Flotation Cell 3 Level Control Valve A | N/A | N/A | 16
|  |  |  | LCV 16093B | Manual Isolation | Scavenger Flotation Cell 3 Level Control Valve B | N/A | N/A | 16
|  |  |  | LCV 16103A | Manual Isolation | Scavenger Flotation Cell 4 Level Control Valve A | N/A | N/A | 16
|  |  |  | LCV 16103B | Manual Isolation | Scavenger Flotation Cell 4 Level Control Valve B | N/A | N/A | 16
|  |  |  | LCV 16113A | Manual Isolation | Flotation Discharge Box Level Control Valve A | N/A | N/A | 16
|  |  |  | LCV 16113B | Manual Isolation | Flotation Discharge Box Level Control Valve B | N/A | N/A | 16
ME005A | F13-CP-412 | 2000-F24-PID-PR-10025 | Stage 1 | XV 13110 | SVO/SVC13110 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13111 | SVO/SVC13111 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
| F13CY401-CP02 | 2000-F24-PID-PR-10025 | Stage 1 | XV 13094 | SVO/SVC13094 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13095 | SVO/SVC13095 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13096 | SVO/SVC13096 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13097 | SVO/SVC13097 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13098 | SVO/SVC13098 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13099 | SVO/SVC13099 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13100 | SVO/SVC13100 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13101 | SVO/SVC13101 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13102 | SVO/SVC13102 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
| F13CY401-CP03 | 2000-F24-PID-PR-10025 | Stage 1 | XV 13103 | SVO/SVC13103 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13104 | SVO/SVC13104 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13105 | SVO/SVC13105 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13106 | SVO/SVC13106 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13107 | SVO/SVC13107 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
|  |  |  | XV 13108 | SVO/SVC13108 | Vendor Package Actuated Cyclone Feed Valves | Detail 3 | FL | 13
ME005B | F28CY421-CP01 | 2000-F24-PID-PR-10027 | Stage 1 | XV 28101 | SVO/SVC28101 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28102 | SVO/SVC28102 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28103 | SVO/SVC28103 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28104 | SVO/SVC28104 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28105 | SVO/SVC28105 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28106 | SVO/SVC28106 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28107 | SVO/SVC28107 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28108 | SVO/SVC28108 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28109 | SVO/SVC28109 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28110 | SVO/SVC28110 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28111 | SVO/SVC28111 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28112 | SVO/SVC28112 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
| F28CY421-CP02 | 2000-F24-PID-PR-10027 | Stage 1 | XV 28113 | SVO/SVC28113 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28114 | SVO/SVC28114 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28115 | SVO/SVC28115 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28116 | SVO/SVC28116 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28117 | SVO/SVC28117 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28118 | SVO/SVC28118 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28119 | SVO/SVC28119 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28120 | SVO/SVC28120 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28121 | SVO/SVC28121 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28122 | SVO/SVC28122 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28123 | SVO/SVC28123 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28124 | SVO/SVC28124 | UFG Mill 2 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
| F28CY431-CP01 | 2000-F24-PID-PR-10027 | Stage 1 | XV 28500 | SVO/SVC28500 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28501 | SVO/SVC28501 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28502 | SVO/SVC28502 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28503 | SVO/SVC28503 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28504 | SVO/SVC28504 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28505 | SVO/SVC28505 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28506 | SVO/SVC28506 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28507 | SVO/SVC28507 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28508 | SVO/SVC28508 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28509 | SVO/SVC28509 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28510 | SVO/SVC28510 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28511 | SVO/SVC28511 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
| F28CY431-CP02 | 2000-F24-PID-PR-10027 | Stage 1 | XV 28512 | SVO/SVC28512 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28513 | SVO/SVC28513 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28514 | SVO/SVC28514 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28515 | SVO/SVC28515 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28516 | SVO/SVC28516 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28517 | SVO/SVC28517 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28518 | SVO/SVC28518 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28519 | SVO/SVC28519 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28520 | SVO/SVC28520 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28521 | SVO/SVC28521 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28522 | SVO/SVC28522 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
|  |  |  | XV 28523 | SVO/SVC28523 | UFG Mill 3 Cyclone Cluster Actuated Feed Valves | Detail 3 | FL | 28
ME007 | F21-CP-001 | 2000-F24-PID-PR-10024 | Stage 2 | XV 21013A | HV21013A | CIL 4 Feed Distribution Box Isolation Gate 1 | Detail 12 | FL | 21
|  |  |  | XV 21013B | HV21013B | CIL 4 Feed Distribution Box Isolation Gate 2 | Detail 12 | FL | 21
|  |  |  | XV 21014A | HV21014A | CIL 4 Feed Distribution Box Isolation Gate 3 | Detail 12 | FL | 21
|  |  |  | XV 21014B | HV21014B | CIL 4 Feed Distribution Box Isolation Gate 4 | Detail 12 | FL | 21
|  |  |  | XV 21081A | HV21081A | CIL 4 Tank 1 Discharge Launder Isolation Gate 1 | Detail 12 | FL | 21
|  |  |  | XV 21081B | HV21081B | CIL 4 Tank 1 Discharge Launder Isolation Gate 2 | Detail 12 | FL | 21
|  |  |  | XV 21082A | HV21082A | CIL 4 Tank 1 Discharge Launder Isolation Gate 3 | Detail 12 | FL | 21
|  |  |  | XV 21082B | HV21082B | CIL 4 Tank 1 Discharge Launder Isolation Gate 4 | Detail 12 | FL | 21
| F21-CP-002 | 2000-F24-PID-PR-10024 | Stage 2 | XV 21121A | HV21121A | CIL 4 Tank 2 Discharge Launder Isolation Gate 1 | Detail 12 | FL | 21
|  |  |  | XV 21121B | HV21121B | CIL 4 Tank 2 Discharge Launder Isolation Gate 2 | Detail 12 | FL | 21
|  |  |  | XV 21122A | HV21122A | CIL 4 Tank 2 Discharge Launder Isolation Gate 3 | Detail 12 | FL | 21
|  |  |  | XV 21122B | HV21122B | CIL 4 Tank 2 Discharge Launder Isolation Gate 4 | Detail 12 | FL | 21
|  |  |  | XV 21161A | HV21161A | CIL 4 Tank 3 Discharge Launder Isolation Gate 1 | Detail 12 | FL | 21
|  |  |  | XV 21161B | HV21161B | CIL 4 Tank 3 Discharge Launder Isolation Gate 2 | Detail 12 | FL | 21
|  |  |  | XV 21162A | HV21162A | CIL 4 Tank 3 Discharge Launder Isolation Gate 3 | Detail 12 | FL | 21
|  |  |  | XV 21162B | HV21162B | CIL 4 Tank 3 Discharge Launder Isolation Gate 4 | Detail 12 | FL | 21
| F21-CP-003 | 2000-F24-PID-PR-10024 | Stage 2 | XV 21181A | HV21181A | CIL 4 Tank 4 Discharge Launder Isolation Gate 1 | Detail 12 | FL | 21
|  |  |  | XV 21181B | HV21181B | CIL 4 Tank 4 Discharge Launder Isolation Gate 2 | Detail 12 | FL | 21
|  |  |  | XV 21182A | HV21182A | CIL 4 Tank 4 Discharge Launder Isolation Gate 3 | Detail 12 | FL | 21
|  |  |  | XV 21182B | HV21182B | CIL 4 Tank 4 Discharge Launder Isolation Gate 4 | Detail 12 | FL | 21
|  |  |  | XV 21201A | HV21201A | CIL 4 Tank 5 Discharge Launder Isolation Gate 1 | Detail 12 | FL | 21
|  |  |  | XV 21201B | HV21201B | CIL 4 Tank 5 Discharge Launder Isolation Gate 2 | Detail 12 | FL | 21
|  |  |  | XV 21202A | HV21202A | CIL 4 Tank 5 Discharge Launder Isolation Gate 3 | Detail 12 | FL | 21
|  |  |  | XV 21202B | HV21202B | CIL 4 Tank 5 Discharge Launder Isolation Gate 4 | Detail 12 | FL | 21
| F21-CP-004 | 2000-F24-PID-PR-10024 | Stage 2 | XV 21241A | HV21241A | CIL 4 Tank 6 Discharge Launder Isolation Gate 1 | Detail 12 | FL | 21
|  |  |  | XV 21241B | HV21241B | CIL 4 Tank 6 Discharge Launder Isolation Gate 2 | Detail 12 | FL | 21
|  |  |  | XV 21242A | HV21242A | CIL 4 Tank 6 Discharge Launder Isolation Gate 3 | Detail 12 | FL | 21
|  |  |  | XV 21242B | HV21242B | CIL 4 Tank 6 Discharge Launder Isolation Gate 4 | Detail 12 | FL | 21
|  |  |  | XV 21261A | HV21261A | CIL 4 Tank 7 Discharge Launder Isolation Gate 1 | Detail 12 | FL | 21
|  |  |  | XV 21261B | HV21261B | CIL 4 Tank 7 Discharge Launder Isolation Gate 2 | Detail 12 | FL | 21
|  |  |  | XV 21262A | HV21262A | CIL 4 Tank 7 Discharge Launder Isolation Gate 3 | Detail 12 | FL | 21
|  |  |  | XV 21262B | HV21262B | CIL 4 Tank 7 Discharge Launder Isolation Gate 4 | Detail 12 | FL | 21
| F21-CP-005 | 2000-F24-PID-PR-10024 | Stage 2 | XV 21271A | HV21271A | CIL 4 Tank 8 Discharge Launder Isolation Gate 1 | Detail 12 | FL | 21
|  |  |  | XV 21271B | HV21271B | CIL 4 Tank 8 Discharge Launder Isolation Gate 2 | Detail 12 | FL | 21
|  | 2000-F24-PID-PR-10029 | Stage 2 | XV 21280 | SV21280 | CIL 4 Carbon Sizing Screen Spray Water Valve | Detail 7 | FC | 21
ME013 | F72-CP-403 | N/A | Stage 2 | FCV 72408 | Manual Isolation | Slaked Lime Discharge Hopper 1 Raw Water Flow Control Valve | Detail 1 | FC | 72
|  |  |  | FCV 72428 | Manual Isolation | Slaked Lime Discharge Hopper 2 Raw Water Flow Control Valve | Detail 1 | FO | 72
|  |  |  | XV 72413 | SV72413 | Slaked Lime Discharge Hopper 1 Drain Valve | Detail 4 | FC | 72
|  |  |  | XV 72415 | SV72415 | Slaked Lime Discharge Hopper 2 Drain Valve | Detail 4 | FC | 72
|  |  |  | XV 72457 | SV72457 | Slaked Lime Wet Scrubber 1 Actuated Feed Valve | Detail 7 | FO | 72
|  |  |  | XV 72473 | SV72473 | Slaked Lime Wet Scrubber 2 Actuated Feed Valve | Detail 7 | FO | 72
| F72-CP-404 | N/A | Stage 2 | XV 72458 | SVO/SVC72458 | Slaked Lime Hydro-Cyclone 1 Actuated Feed Valve | Detail 3 | FL | 72
|  |  |  | XV 72459 | SVO/SVC72459 | Slaked Lime Hydro-Cyclone 1 Actuated Feed Valve | Detail 3 | FL | 72
|  |  |  | XV 72460 | SVO/SVC72460 | Slaked Lime Hydro-Cyclone 1 Actuated Feed Valve | Detail 3 | FL | 72
|  |  |  | XV 72467 | SVO/SVC72467 | Slaked Lime Hydro-Cyclone 2 Actuated Feed Valve | Detail 3 | FL | 72
|  |  |  | XV 72468 | SVO/SVC72468 | Slaked Lime Hydro-Cyclone 2 Actuated Feed Valve | Detail 3 | FL | 72
|  |  |  | XV 72469 | SVO/SVC72469 | Slaked Lime Hydro-Cyclone 2 Actuated Feed Valve | Detail 3 | FL | 72
| F72SI411-CP | N/A | Stage 2 | XV 72419 | SV72419 | Lime Silo 1 Filling Line Isolation Valve 1 | Detail 4 | FC | 72
|  |  |  | XV 72420 | SV72420 | Lime Silo 1 Filling Line Isolation Valve 2 | Detail 4 | FC | 72
| F72SI412-CP | N/A | Stage 2 | XV 72433 | SV72433 | Lime Silo 2 Filling Line Isolation Valve 1 | Detail 4 | FC | 72
|  |  |  | XV 72434 | SV72434 | Lime Silo 2 Filling Line Isolation Valve 2 | Detail 4 | FC | 72
| N/A | N/A | Stage 2 | PRV 72402 | No Solenoid | Lime Silo 1 Pressure Release Valve 1 | N/A | N/A | 72
|  |  |  | PRV 72422 | No Solenoid | Lime Silo 2 Pressure Release Valve 1 | N/A | N/A | 72
|  |  |  | PRV 72417 | No Solenoid | Lime Silo 1 Pressure Release Valve 2 | N/A | N/A | 72
|  |  |  | PRV 72418 | No Solenoid | Lime Silo 1 Pressure Release Valve 3 | N/A | N/A | 72
|  |  |  | PRV 72429 | No Solenoid | Lime Silo 2 Pressure Release Valve 2 | N/A | N/A | 72
|  |  |  | PRV 72430 | No Solenoid | Lime Silo 2 Pressure Release Valve 3 | N/A | N/A | 72
ME015 | Solenoid on Valve | 2000-F24-PID-PR-10025 | Stage 1 | FCV 14033 | Manual Isolation | Gravity Concentrator 1 Fluidising Water Flow Control Valve | Detail 1 | FC | 14
|  |  |  | FCV 14043 | Manual Isolation | Gravity Concentrator 2 Fluidising Water Flow Control Valve | Detail 1 | FC | 14
ME027B | N/A | N/A | Stage 2 | SV 21305 | N/A | CIL 4 Secondary Tails Sampler Spray Water Solenoid | N/A | N/A | 21
|  |  |  | SV 21308 | N/A | CIL 4 Tails Tertiary Sampler Spray Water Solenoid | N/A | N/A | 21
|  |  |  | SV 21311 | N/A | CIL 4 Primary Tails Sampler Spray Water Solenoid | N/A | N/A | 21
|  |  |  | SV 21317 | N/A | CIL 4 Tails Final Sample Dewatering Module Instrument Air Solenoid | N/A | N/A | 21
ME039 | F28MUF402-JB04 | 2000-F24-PID-PR-10027 | Stage 1 | XV 28059 | SV28059 | Ultra Fine Grinding Mill 2 Feed Valve | Detail 4 | FC | 28
|  |  |  | XV 28066 | SV28066 | Ultra Fine Grinding Mill 2 Process Water Addition Valve | Detail 4 | FC | 28
|  |  |  | XV 28146 | No Solenoid | UFG Mill 2 Scuttle Valve | N/A | N/A | 28
| F28MUF403-JB04 | 2000-F24-PID-PR-10027 | Stage 1 | XV 28338 | SV28338 | Ultra Fine Grinding Mill 3 Feed Valve | Detail 4 | FC | 28
|  |  |  | XV 28341 | SV28341 | UFG Mill 3 HP Process Water Valve | Detail 4 | FC | 28
|  |  |  | XV 28395 | No Solenoid | UFG Mill 3 Scuttle Valve | N/A | N/A | 28
ME074 | F16SA401-CP | 2000-F24-PID-PR-10013 | Stage 1 | XV 13173 | SVO/SVC13173 | Flotation Feed Sampler Upstream Flush Valve | Detail 3 | FC | 13
|  |  |  | XV 13174 | SVO/SVC13174 | Flotation Feed Sampler Downstream Flush Valve | Detail 3 | FC | 13
|  |  |  | XV 13175 | SVO/SVC13175 | Flotation Feed Sampler Cutter | Detail 3 | FL | 13
| F17SA416-CP | 2000-F24-PID-PR-10008 | Stage 1 | XV 17085 | SVO/SVC17085 | Flotation Tailings Feed Sampler Upstream Flush Valve | Detail 3 | FC | 17
|  |  |  | XV 17086 | SVO/SVC17086 | Flotation Tailings Feed Sampler Down Steam Flush Valve | Detail 3 | FC | 17
|  |  |  | XV 17087 | SVO/SVC17087 | Flotation Tailings Feed Sampler Sample Valve | Detail 3 | FL | 17
ME090 | F72HP658-CP | 2000-F72-PID-PR-10003 | Stage 2 | XV 72409 | HV72409 | Lime Slaking Mill Ball Kibble Loading Hopper Gate 1 | Detail 12 | FL | 72
|  |  |  | XV 72410 | HV72410 | Lime Slaking Mill Ball Kibble Loading Hopper Gate 1 | Detail 12 | FL | 72
| XV13220_CP | 2000-F24-PID-PR-10012 | Stage 1 | XV 13220 | SVO/SVC13220 | Recycle Crusher Bypass Gate | Detail 3 | FL | 13
ME093 | F13GA421-CP01 | 2000-F24-PID-PR-10013 | Stage 1 | XV 13386 | SVO/SVC13386 | Trash Screen 1 Feed Gate | Detail 3 | FL | 13
|  |  |  | XV 13387 | SVO/SVC13387 | Trash Screen 2 Feed Gate | Detail 3 | FL | 13
|  |  |  | XV 13388 | SVO/SVC13388 | Trash Screen 3 Feed Gate | Detail 3 | FL | 13
|  |  |  | XV 13389 | SVO/SVC13389 | Trash Screen 4 Feed Gate | Detail 3 | FL | 13
| F16GA425-CP01 | 2000-F24-PID-PR-10024 | Stage 1 | XV 16025 | SVO/SVC16025 | Rougher 1 Concentrate Cleaner Launder Gate | Detail 3 | FL | 16
|  |  |  | XV 16026 | SVO/SVC16026 | Rougher 1 Final Concentrate Launder Gate | Detail 3 | FL | 16
N/A | N/A | 2000-F24-PID-PR-10012 | Stage 1 | TCV 12127 | Manual Isolation | Primary Crusher 2 Oil Chiller Temperature Control Valve | Detail 1 | FO | 12
|  |  |  | LCV 24456 | Manual Isolation | Raw Water Booster Tank Level Control Valve | Detail 1 | FC | 24
|  | 2000-F24-PID-PR-10007 | Stage 1 | LCV 24431 | Manual Isolation | Raw Water Tank Level Control Valve | Detail 1 | FC | 24
|  | N/A | Stage 1 | PCV 28366 | No Solenoid | Ultra Fine Grinding Mill 3 Gland Seal Water Pressure Regulating Valve | N/A | N/A | 28
|  |  |  | PCV 72082 | No Solenoid | Copper Sulphate Delivery Plant Air Pressure Regulating Valve 1 | N/A | N/A | 72
|  |  |  | PCV 72132 | No Solenoid | PAX Delivery Plant Air Pressure Regulating Valve 1 | N/A | N/A | 72
|  |  |  | PCV 72211 | No Solenoid | Hydrogen Peroxide Delivery Plant Air Pressure Regulating Valve | N/A | N/A | 72
|  |  |  | PRV 12390 | No Solenoid | Primary Crushing 2 Air Receiver Pressure Release Valve | N/A | N/A | 12
|  |  |  | PRV 13235 | No Solenoid | Vendor Package Lube Oil Pressure Relief Valves | N/A | N/A | 13
|  |  |  | PRV 13285 | No Solenoid | Vendor Package Lube Oil Pressure Relief Valves | N/A | N/A | 13
|  |  |  | PRV 13450 | No Solenoid | Mill Air Receiver Pressure Release Valve | N/A | N/A | 13
|  |  |  | PRV 13452 | No Solenoid | Classificatoin Air Receiver Pressure Release Valve | N/A | N/A | 13
|  |  |  | PRV 13454 | No Solenoid | Recycle Crushing/COS Vault Air Receiver Pressure Release Valve | N/A | N/A | 13
|  |  |  | PRV 16180 | No Solenoid | Flotation/Thickener Air Receiver Pressure Release Valve | N/A | N/A | 16
|  |  |  | PRV 21330 | No Solenoid | CIL 4 / Elution Air Receiver | N/A | N/A | 21
|  |  |  | PRV 24481 | No Solenoid | Plant Air Receiver Pressure Release Valve 1 | N/A | N/A | 24
|  |  |  | PRV 24635 | No Solenoid | Process Water/Reagents/Trash Screens Air Receiver Pressure Release Valve | N/A | N/A | 24
|  |  |  | PRV 28450 | No Solenoid | UFG 2/3 Air Receiver Pressure Release Valve | N/A | N/A | 28
|  |  |  | PRV 72002 | No Solenoid | Flocculant Silo Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72020 | No Solenoid | Flocculant Transfer Pump Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72051 | No Solenoid | Flotation Tailings Thickener Flocculant Dosing Pump 1 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72052 | No Solenoid | Flotation Tailings Thickener Flocculant Dosing Pump 2 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72083 | No Solenoid | Copper Sulphate Delivery Plant Air Pressure Release Valve 1 | N/A | N/A | 72
|  |  |  | PRV 72091 | No Solenoid | Copper Sulphate Dosing Pump 1 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72092 | No Solenoid | Copper Sulphate Dosing Pump 2 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72101 | No Solenoid | Copper Sulphate Dosing Pump 3 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72115 | No Solenoid | Frother Dosing Pump 1 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72116 | No Solenoid | Frother Dosing Pump 2 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72117 | No Solenoid | Frother Dosing Pump 3 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72118 | No Solenoid | Frother Dosing Pump 4 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72119 | No Solenoid | Frother Dosing Pump 5 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72133 | No Solenoid | PAX Delivery Plant Air Pressure Release Valve 1 | N/A | N/A | 72
|  |  |  | PRV 72141 | No Solenoid | PAX Dosing Pump 1 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72142 | No Solenoid | PAX Dosing Pump 2 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72143 | No Solenoid | PAX Dosing Pump 3 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72151 | No Solenoid | PAX Dosing Pump 4 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72153 | No Solenoid | PAX Dosing Pump 5 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72205 | No Solenoid | Hydrogen Peroxide Delivery Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72208 | No Solenoid | Hydrogen Peroxide Storage Tank Outlet Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72212 | No Solenoid | Hydrogen Peroxide Delivery Plant Air Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72223 | No Solenoid | Hydrogen Peroxide Dosing Pump 1 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72224 | No Solenoid | Hydrogen Peroxide Dosing Pump 2 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72225 | No Solenoid | Hydrogen Peroxide Dosing Pump 3 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72226 | No Solenoid | Hydrogen Peroxide Inline Mixer 1 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72230 | No Solenoid | Hydrogen Peroxide Inline Mixer 2 Pressure Release Valve | N/A | N/A | 72
|  |  |  | SV 13061 | N/A | SAG Mill Feed Conveyor Spray Water 1 | Detail 11 | FC | 13
|  |  |  | SV 13062 | N/A | SAG Mill Feed Conveyor Spray Water 2 | Detail 11 | FC | 13
|  |  |  | SV 13063 | N/A | SAG Mill Feed Conveyor Spray Water 3 | Detail 11 | FC | 13
|  |  |  | SV 13464 | N/A | TRASH DEWATERING SCREEN UNDERFLOW PUMP GLAND WATER | Detail 11 | FO | 13
|  |  |  | SV 16155 | N/A | SAMPLE RETURN PUMP 1 GLAND WATER | Detail 11 | FO | 16
|  |  |  | SV 16165 | N/A | SAMPLE RETURN PUMP 2 GLAND WATER | Detail 11 | FO | 16
|  |  |  | SV 18500 | N/A | Final Concentrate Pump 1 Gland Water | Detail 11 | FO | 18
|  |  |  | SV 18504 | N/A | Final Concentrate Pump 2 Gland Water | Detail 11 | FO | 18
|  |  |  | SV 18508 | N/A | Cleaner Flotation Cell Recirculation Pump 1 Gland Water | Detail 11 | FO | 18
|  |  |  | SV 18512 | N/A | Cleaner Flotation Cell Recirculation Pump 2 Gland Water | Detail 11 | FO | 18
|  |  |  | SV 18524 | N/A | Cleaner-Scavenger Flotation Cell Recirculation Pump 1 Gland Water | Detail 11 | FO | 18
|  |  |  | SV 18528 | N/A | Cleaner-Scavenger Flotation Cell Recirculation Pump 2 Gland Water | Detail 11 | FO | 18
|  |  |  | SV 18532 | N/A | Cleaner-Scavenger Flotation Cell Tails Pump 1 Gland Water | Detail 11 | FO | 18
|  |  |  | SV 18536 | N/A | Cleaner-Scavenger Flotation Cell Tails Pump 2 Gland Water | Detail 11 | FO | 18
|  |  |  | SV 23480 | N/A | FINAL TAILS PUMP 1 GLAND WATER | Detail 11 | FO | 23
|  |  |  | SV 23484 | N/A | FINAL TAILS PUMP 2 GLAND WATER | Detail 11 | FO | 23
|  |  |  | SV 23488 | N/A | FINAL TAILS PUMP 3 GLAND WATER | Detail 11 | FO | 23
|  |  |  | SV 23492 | N/A | FINAL TAILS PUMP 4 GLAND WATER | Detail 11 | FO | 23
|  |  |  | SV 24512 | N/A | MILL WATER PUMP 1 GLAND WATER | Detail 11 | FO | 24
|  |  |  | SV 28400 | N/A | UFG PRODUCT PUMP 1 GLAND WATER | Detail 11 | FO | 28
|  |  |  | SV 28404 | N/A | UFG PRODUCT PUMP 2 GLAND WATER | Detail 11 | FO | 28
|  |  |  | SV 28408 | N/A | UFG MILL 2 FEED PUMP GLAND WATER | Detail 11 | FO | 28
|  |  |  | SV 28412 | N/A | UFG MILL 2 DISCHARGE PUMP GLAND WATER | Detail 11 | FO | 28
|  |  |  | SV 28416 | N/A | UFG MILL 2 ISACHARGER PUMP GLAND WATER | Detail 11 | FO | 28
|  |  |  | HV 12262 | No Solenoid | Primary Crusher 2 Cooling Water Pump 1 Suction Manual Valve | Manual | N/A | 12
|  |  |  | HV 12263 | No Solenoid | Primary Crusher 2 Cooling Water Pump 1 Discharge Manual Valve | Manual | N/A | 12
|  |  |  | HV 12264 | No Solenoid | Primary Crusher 2 Cooling Water Pump 2 Suction Manual Valve | Manual | N/A | 12
|  |  |  | HV 12265 | No Solenoid | Primary Crusher 2 Cooling Water Pump 2 Discharge Manual Valve | Manual | N/A | 12
|  |  |  | HV 13422 | No Solenoid | Cooling Water Mill Pump 1 Suction Manual Valve | Manual | N/A | 13
|  |  |  | HV 13423 | No Solenoid | Cooling Water Mill Pump 1 Discharge Manual Valve | Manual | N/A | 13
|  |  |  | HV 13424 | No Solenoid | Cooling Water Mill Pump 2 Suction Manual Valve | Manual | N/A | 13
|  |  |  | HV 13425 | No Solenoid | Cooling Water Mill Pump 2 Discharge Manual Valve | Manual | N/A | 13
|  |  |  | HV 13431 | No Solenoid | Chiller Recirculating Water Pump 1 Suction Manual Valve | Manual | N/A | 13
|  |  |  | HV 13432 | No Solenoid | Chiller Recirculating Water Pump 1 Discharge Manual Valve | Manual | N/A | 13
|  |  |  | HV 13433 | No Solenoid | Chiller Recirculating Water Pump 2 Suction Manual Valve | Manual | N/A | 13
|  |  |  | HV 13434 | No Solenoid | Chiller Recirculating Water Pump 2 Discharge Manual Valve | Manual | N/A | 13
|  |  |  | HV 13442 | No Solenoid | Chiller 1 Discharge Manual Valve | Manual | N/A | 13
|  |  |  | HV 13444 | No Solenoid | Chiller 2 Discharge Manual Valve | Manual | N/A | 13
|  |  |  | HV 13446 | No Solenoid | Chiller 3 Discharge Manual Valve | Manual | N/A | 13
|  |  |  | HV 13448 | No Solenoid | Chiller 4 Discharge Manual Valve | Manual | N/A | 13
|  |  |  | SV 16357 | N/A | FLOATATION CELLS DRAIN PUMP GLAND WATER | Detail 11 | FO | 16
|  |  |  | HV 24507 | No Solenoid | Raw Water Feed Booster Pumps to Raw Water Tank Manual Valve | Manual | N/A | 24
|  |  |  | HV 24508 | No Solenoid | Saline Water Pumps to Raw Water Tank Manual Valve | Manual | N/A | 24
|  |  |  | PCV 24452 | No Solenoid | LP Gland Water Back Pressure Regulating Valve 2 | N/A | N/A | 24
|  |  |  | PCV 24462 | No Solenoid | HP Gland Water Back Pressure Regulating Valve 1 | N/A | N/A | 24
|  |  |  | PCV 24463 | No Solenoid | HP Gland Water Back Pressure Regulating Valve 2 | N/A | N/A | 24
|  |  |  | PCV 28053 | No Solenoid | Ultra Fine Grinding Mill 2 Gland Seal Water Pressure Regulating Valve | N/A | N/A | 28
|  |  |  | PCV 28057 | No Solenoid | Ultra Fine Grinding Mill 2 HP Water Pressure Regulating Valve | N/A | N/A | 28
|  |  |  | PCV 28460 | No Solenoid | Ultra Fine Grinding Mill 3 HP Water Pressure Regulating Valve | N/A | N/A | 28
|  |  |  | SV 28436 | N/A | UFG MILL 3 DISCHARGE PUMP GLAND WATER | Detail 11 | FO | 28
|  |  |  | HV 30443 | No Solenoid | Final Concentrate Pumps to Concentrate Thickener Feed Box Manual Valve | Manual | N/A | 30
|  |  |  | HV 30444 | No Solenoid | Final Concentrate Pumps to Filter Feed Tanks Feed Box Bypass Manual Valve | Manual | N/A | 30
|  |  |  | SV 30447 | N/A | CONCENTRATE THICKENER U/F PUMP 1 GLAND WATER | Detail 11 | FO | 30
|  |  |  | SV 30452 | N/A | CONCENTRATE THICKENER U/F PUMP 2 GLAND WATER | Detail 11 | FO | 30
|  |  |  | SV 35437 | N/A | UFG Circuit 2 Feed Pump Gland Water Solenoid Valve | Detail 11 | FO | 35
|  |  |  | SV 66453 | N/A | Gravity Electrowinning Solution to Gravity Electrowinning Cells Sample Solenoid Valve | Detail 11 | FC | 66
|  |  |  | SV 66454 | N/A | Gravity Electrowinning Solution to Barren Eluate Tank Sample Solenoid Valve | Detail 11 | FC | 66
|  |  |  | HV 75401 | No Solenoid | Suction Turret to Saline Water Pump 1 Suction Manual Valve | Manual | N/A | 75
|  |  |  | HV 75403 | No Solenoid | Saline Water Pump 1 Discharge Manual Valve | Manual | N/A | 75
|  |  |  | HV 75411 | No Solenoid | Suction Turret to Saline Water Pump 2 Suction Manual Valve | Manual | N/A | 75
|  |  |  | HV 75413 | No Solenoid | Saline Water Pump 2 Discharge Manual Valve | Manual | N/A | 75
|  |  |  | HV 75421 | No Solenoid | Suction Turret to Saline Water Pump 3 Suction Manual Valve | Manual | N/A | 75
|  |  |  | HV 75423 | No Solenoid | Saline Water Pump 3 Discharge Manual Valve | Manual | N/A | 75
|  |  |  | SV 12220 | N/A | Primary Crusher 2 Discharge Chamber Spray Water | Detail 11 | FC | 12
|  |  |  | SV 12550 | N/A | Stockpile Feed Conveyor Tail End Spray Water | Detail 11 | FC | 12
|  |  |  | SV 14118 | N/A | INTENSIVE CYANIDE LEACH REACTOR TRANSFER PUMP GLAND WATER | Detail 11 | FO | 14
|  |  |  | SV 17104 | N/A | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 1 GLAND WATER | Detail 11 | FO | 17
|  |  |  | SV 17114 | N/A | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 2 GLAND WATER | Detail 11 | FO | 17
|  |  |  | PCV 24453 | No Solenoid | LP Gland Water Back Pressure Regulating Valve 1 | N/A | N/A | 24
|  |  |  | SV 24515 | N/A | MILL WATER PUMP 2 GLAND WATER | Detail 11 | FO | 24
|  |  |  | SV 24518 | N/A | HIGH PRESSURE PROCESS WATER PUMP 1 GLAND WATER | Detail 11 | FO | 24
|  |  |  | SV 24521 | N/A | HIGH PRESSURE PROCESS WATER PUMP 2 GLAND WATER | Detail 11 | FO | 24
|  |  |  | PCV 28043 | No Solenoid | UFG GSW Tank Back Pressure Regulating Valve | N/A | N/A | 28
|  |  |  | SV 13185 | N/A | Recycle Crusher C Scheme Water Solenoid Valve | Detail 11 | FO | 13
|  |  |  | PCV 13186 | No Solenoid | Recycle Crusher C Scheme Water Pressure Control Valve | N/A | N/A | 13
|  |  |  | SV 13292 | N/A | Recycle Crusher C Scheme Water Solenoid Valve | Detail 11 | FO | 13
|  |  |  | PCV 13293 | No Solenoid | Recycle Crusher D Scheme Water Pressure Control Valve | N/A | N/A | 13
|  |  |  | SV 13344 | N/A | Recycle Crusher Discharge Conveyor Raw Water Solenoid Valve 1 | Detail 11 | FC | 13
|  |  |  | SV 13345 | N/A | Recycle Crusher Discharge Conveyor Raw Water Solenoid Valve 2 | Detail 11 | FC | 13
|  |  |  | PCV 72128 | No Solenoid | PAX Delivery Plant Air Pressure Regulating Valve 2 | N/A | N/A | 72
|  |  |  | PRV 72129 | No Solenoid | PAX Delivery Plant Air Pressure Release Valve 2 | N/A | N/A | 72
|  |  |  | PCV 72088 | No Solenoid | Copper Sulphate Delivery Plant Air Pressure Regulating Valve 2 | N/A | N/A | 72
|  |  |  | PRV 72089 | No Solenoid | Copper Sulphate Delivery Plant Air Pressure Release Valve 2 | N/A | N/A | 72
|  |  |  | PRV 28060 | No Solenoid | Ultra Fine Grinding Mill 2 HP Water Pressure Release Valve | N/A | N/A | 28
|  |  |  | PRV 28461 | No Solenoid | Ultra Fine Grinding Mill 3 HP Water Pressure Release Valve | N/A | N/A | 28
|  |  |  | HV 66460 | No Solenoid | Electrowinning Tank Area Sump Discharge to Gravity Tank Manual Valve | Manual | N/A | 66
|  |  |  | HV 66461 | No Solenoid | Electrowinning Tank Area Sump Discharge to CIL 4 Eluate Tank 1 Manual Valve | Manual | N/A | 66
|  |  |  | HV 66462 | No Solenoid | Electrowinning Tank Area Sump Discharge to CIL 4 Eluate Tank 2 Manual Valve | Manual | N/A | 66
|  |  |  | HV 66463 | No Solenoid | Electrowinning Tank Area Sump Discharge to Barren Eluate Tank Manual Valve | Manual | N/A | 66
|  |  |  | HV 23420 | No Solenoid | Final Tails Slurry Line D Isolation Manual Valve | Manual | N/A | 23
|  |  |  | HV 23433 | No Solenoid | Final Tails Slurry Line B Isolation Manual Valve | Manual | N/A | 23
|  |  |  | HV 23444 | No Solenoid | Final Tails Slurry Line A Isolation Manual Valve | Manual | N/A | 23
|  |  |  | HV 23455 | No Solenoid | Final Tails Slurry Line C Isolation Manual Valve | Manual | N/A | 23
|  |  |  | XV 13069 | No Solenoid | Emergency Feed Bin Stockpile Spray Water Valve | Detail 15 | FC | 13
|  |  |  | SV 34406 | N/A | UFG Mill 1 Product Pump Gland Water Solenoid Valve | Detail 11 | FO | 34
|  |  |  | PCV 24721 | No Solenoid | Fire Water Pressure Regulating Valve - Brownfields Tie In Point | N/A | N/A | 24
|  |  |  | PRV 72487 | No Solenoid | CIL 4 Reagents Air Receiver | N/A | N/A | 72
|  |  |  | SV 14125 | N/A | Leach Aid Screw Feeder Air Line Valve | Detail 11 | FO | 14
|  |  |  | PCV 66466 | No Solenoid | Electrowinning Cells Plant Air Pressure Regulating Valve | N/A | N/A | 66
|  |  |  | PRV 24722 | No Solenoid | Fire Water Pressure Relief Valve - Brownfields Tie In Point | N/A | N/A | 24
|  |  |  | SV 72160 | N/A | Pax Area Sump Pump Air Feed Solenoid Valve | Detail 11 | FC | 72
|  |  |  | PRV 72165 | No Solenoid | Antiscalant Dosing Pump 1 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 24483 | No Solenoid | Plant Air Receiver Pressure Release Valve 2 | N/A | N/A | 24
|  |  |  | SV 28433 | N/A | UFG MILL 3 FEED PUMP GLAND WATER | Detail 11 | FO | 28
|  |  |  | SV 28430 | N/A | UFG MILL 3 ISACHARGER PUMP GLAND WATER | Detail 11 | FO | 28
|  |  |  | SV 12584 | N/A | Stockpile Feed Conveyor Spillage Tray Spray Bar 1 | Detail 11 | FC | 12
|  |  |  | SV 12585 | N/A | Stockpile Feed Conveyor Spillage Tray Spray Bar 2 | Detail 11 | FC | 12
|  |  |  | SV 12586 | N/A | Stockpile Feed Conveyor Spillage Tray Spray Bar 3 | Detail 11 | FC | 12
|  |  |  | SV 12587 | N/A | Stockpile Feed Conveyor Spillage Tray Spray Bar 4 | Detail 11 | FC | 12
|  |  |  | SV 12588 | N/A | Stockpile Feed Conveyor Spillage Tray Spray Bar 5 | Detail 11 | FC | 12
|  |  |  | SV 12589 | N/A | Stockpile Feed Conveyor Spillage Tray Spray Bar 6 | Detail 11 | FC | 12
|  |  |  | SV 12590 | N/A | Stockpile Feed Conveyor Spillage Tray Spray Bar 7 | Detail 11 | FC | 12
|  |  |  | SV 12591 | N/A | Stockpile Feed Conveyor Spillage Tray Spray Bar 8 | Detail 11 | FC | 12
|  |  | Stage 2 | SV 66451 | N/A | Electrowinning Solution to CIL 4 Electrowinning Cells Sample Solenoid Valve | Detail 11 | FC | 66
|  |  |  | SV 66452 | N/A | Electrowinning Solution to Barren Eluate Tank Sample Solenoid Valve | Detail 11 | FC | 66
|  |  |  | PRV 22041 | No Solenoid | CIL 4 Elution & Acid Wash Column Pressure Relief Valve | N/A | N/A | 22
|  |  |  | PRV 22148 | No Solenoid | CIL 4 Elution Pumps Pressure Relief Valve | N/A | N/A | 22
|  |  |  | HV 22244 | No Solenoid | Kiln Abatement System Cooling Water Pump 1 Suction Manual Valve | Manual | N/A | 22
|  |  |  | HV 22245 | No Solenoid | Kiln Abatement System Cooling Water Pump 1 Discharge Manual Valve | Manual | N/A | 22
|  |  |  | HV 22246 | No Solenoid | Kiln Abatement System Cooling Water Pump 2 Suction Manual Valve | Manual | N/A | 22
|  |  |  | FCV 72407 | Manual Isolation | Lime Slaking Vortex Prewetter 1 Raw Water Flow Control Valve | Detail 1 | FC | 72
|  |  |  | FCV 72427 | Manual Isolation | Lime Slaking Vortex Prewetter 2 Raw Water Flow Control Valve | Detail 1 | FO | 72
|  |  |  | PCV 72532 | No Solenoid | Cyanide Delivery Plant Air Distribution 1 Pressure Control Valve | N/A | N/A | 72
|  |  |  | PRV 72533 | No Solenoid | Cyanide Delivery Plant Air Distribution 1 Pressure Relief Valve | N/A | N/A | 72
|  |  |  | PCV 72543 | No Solenoid | Cyanide Delivery Plant Air Distribution 2 Pressure Control Valve | N/A | N/A | 72
|  |  |  | PRV 72544 | No Solenoid | Cyanide Delivery Plant Air Distribution 2 Pressure Relief Valve | N/A | N/A | 72
|  |  |  | PCV 72702 | No Solenoid | Lead Nitrate Delivery Plant Air Pressure Regulating Valve | N/A | N/A | 72
|  |  |  | PRV 72703 | No Solenoid | Lead Nitrate Delivery Plant Air Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72710 | No Solenoid | Lead Nitrate Dosing Pump 2 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72711 | No Solenoid | Lead Nitrate Dosing Pump 1 Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72481 | No Solenoid | Concentrae Pre-Leach Thickener Flocculant Dosing Pump Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72482 | No Solenoid | Thickeners Standby Flocculant Dosing Pump Pressure Release Valve | N/A | N/A | 72
|  |  |  | PRV 72483 | No Solenoid | Concentrate Thickener Flocculant Dosing Pump Pressure Release Valve | N/A | N/A | 72
|  |  |  | PCV 21346 | No Solenoid | CIL 4 Tank 1 Oxygen Injection Header Pressure Regulating Valve | N/A | N/A | 21
|  |  |  | PCV 21355 | No Solenoid | CIL 4 Tank 2 Oxygen Injection Header Pressure Regulating Valve | N/A | N/A | 21
|  |  |  | SV 30403 | N/A | Concentrate Pre-Leach Thickener Underflow Pump 1 Gland Water Solenoid Valve | Detail 11 | FO | 30
|  |  |  | SV 30408 | N/A | Concentrate Pre-Leach Thickener Underflow Pump 2 Gland Water Solenoid Valve | Detail 11 | FO | 30
|  |  |  | SV 30434 | N/A | Concentrate Leach Transfer Pump 1 Gland Water Solenoid Valve | Detail 11 | FO | 30
|  |  |  | SV 30440 | N/A | Concentrate Leach Transfer Pump 2 Gland Water Solenoid Valve | Detail 11 | FO | 30
|  |  |  | SV 30466 | N/A | CIL 3 Tails Pump 1 Gland Water Solenoid Valve | Detail 11 | FO | 30
|  |  |  | SV 30472 | N/A | CIL 3 Tails Pump 2 Gland Water Solenoid Valve | Detail 11 | FO | 30
|  |  |  | SV 30552 | N/A | CIL 2 Oxygen Injection Pump 1 Gland Water Solenoid Valve | Detail 11 | FO | 30
|  |  |  | SV 30567 | N/A | CIL 2 Oxygen Injection Pump 2 Gland Water Solenoid Valve | Detail 11 | FO | 30
|  |  |  | SV 35445 | N/A | UFG Circuit 3 Feed Pump Gland Water Solenoid Valve | Detail 11 | FO | 35
|  |  |  | SV 65408 | N/A | CIL 3 Loaded Carbon Pump Gland Water Solenoid Valve | Detail 11 | FO | 65
|  |  |  | SV 22260 | N/A | CIL 4 Barren Carbon Pump Gland Water Solenoid Valve | Detail 11 | FO | 22
|  |  |  | SV 21320 | N/A | CIL 4 Tank 1 Oxygen Injection Pump Gland Water Solenoid Valve | Detail 11 | FO | 21
|  |  |  | SV 21324 | N/A | CIL 4 Tank 2 Oxygen Injection Pump Gland Water Solenoid Valve | Detail 11 | FO | 21
|  |  |  | SV 72470 | N/A | Lime Ringmain Pump 1 Gland Water Solenoid Valve | Detail 11 | FO | 72
|  |  |  | SV 72474 | N/A | Lime Ringmain Pump 2 Gland Water Solenoid Valve | Detail 11 | FO | 72
|  |  |  | HV 22247 | No Solenoid | Kiln Abatement System Cooling Water Pump 2 Discharge Manual Valve | Manual | N/A | 22
|  |  |  | SV 30590 | N/A | CIL 3 Barren Carbon Screen Underflow Hopper Area Sump Pump Compressed Air Valve | Detail 11 | FC | 30
|  |  |  | SV 72495 | N/A | Slaked Lime Transfer Pump 2 Gland Water Solenoid Valve | Detail 11 | FO | 72
|  |  |  | PRV 22035 | No Solenoid | Elution Air Receiver | N/A | N/A | 22
|  |  |  | PCV 30586 | No Solenoid | CIL 2 Adsorption Tanks Oxygen Injection Pressure Control Valve | N/A | N/A | 30
|  |  |  | PCV 30587 | No Solenoid | CIL 2 Leach Tank 1 Oxygen Injection Pressure Control Valve | N/A | N/A | 30
|  |  |  | PCV 30589 | No Solenoid | CIL 2 Leach Tank 2 Oxygen Injection Pressure Control Valve | N/A | N/A | 30
|  |  |  | SV 72617 | N/A | Hydrochloric Acid Area Sump Pump Air Feed Solenoid Valve | Detail 11 | FC | 72
|  |  |  | SV 72712 | N/A | Lead Nitrate Area Sump Pump Air Feed Solenoid Valve | Detail 11 | FC | 72
|  |  |  | PCV 21339 | No Solenoid | Oxygen Plant Discharge Pressure Regulating Valve | N/A | N/A | 21
|  |  |  | PCV 24672 | No Solenoid | Fire Water Pressure Regulating Valve - Elution Heater Oil System | N/A | N/A | 24
|  |  |  | PRV 24652 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | PRV 24654 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | PRV 24657 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | PRV 24663 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | PRV 24675 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | PRV 24687 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | PRV 24694 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | PRV 24682 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | PRV 24684 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | PRV 24689 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | PRV 24702 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | PRV 24707 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | PRV 24716 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | PRV 24712 | No Solenoid | Firewater Thermal Expansion Valve | N/A | N/A | 24
|  |  |  | SV 72452 | N/A | Slaked Lime Transfer Pump 1 Gland Water Solenoid Valve | Detail 11 | FO | 72
|  |  |  | SV 72214 | N/A | Hydrogen Peroxide Area Sump Pump Air Feed Solenoid Valve | Detail 11 | FC | 72
|  | 2000-F72-PID-PR-10003 | Stage 2 | XV 72465 | SV72465 | Milk of Lime Area Sump Pump 2 Flushing Valve | Detail 7 | FC | 72
|  |  |  | XV 72466 | SV72466 | Milk of Lime Area Sump Pump 3 Flushing Valve | Detail 7 | FC | 72
|  | 2000-F75-PID-PR-10007 | Stage 1 | LCV 75690 | Manual Isolation | Gland Water Tank Level Control Valve | Detail 1 | FO | 75
| Solenoid on Valve | 2000-F24-PID-PR-10012 | Stage 1 | XV 12005 | SV12005 | ROM Bin Spray Water | Detail 7 | FC | 12
|  |  |  | XV 12006 | (blank) | ROM Apron Feeder Spray Water | Detail 7 | FC | 12
|  |  |  | XV 12551 | SV12551 | Stockpile Feed Conveyor Head End Spray Water | Detail 7 | FC | 12
|  |  |  | XV 12259 | SV12259 | Primary Crusher 2 Cooling Water Tank Scheme Water Inlet Valve | Detail 7 | FC | 12
|  | 2000-F24-PID-PR-10007 | Stage 2 | FCV 72632 | Manual Isolation | Oxygen Plant Cooling System Cooling Water Flow Control Valve | Detail 1 | FO | 72
|  | 2000-F24-PID-PR-10027 | Stage 1 | XV 28331 | SV28331 | UFG Mill 1 Product Sample Flushing Valve | Detail 7 | FC | 28
|  |  |  | XV 28332 | SV28332 | UFG Mill 1 Product Sample Valve | Detail 7 | FC | 28
|  | 2000-F24-PID-PR-10013 | Stage 1 | FCV 72007 | Manual Isolation | Flocculant Mixing Tank Scheme Water Flow Control Valve | N/A | N/A | 72
|  |  |  | FCV 72013 | Manual Isolation | Flocculant Mixing Tank Wetting Head Scheme Water Flow Control Valve | N/A | N/A | 72
|  |  |  | XV 72003 | No Solenoid | Flocculant Silo Dehumidifier Delivery Flow Control Valve | N/A | N/A | 72
|  |  |  | XV 72008 | No Solenoid | Flocculant Silo Flow Control Valve | N/A | N/A | 72
|  | 2000-F30-PID-PR-10017 | Stage 2 | XV 65445 | SV65445 | CIL3 Loaded Carbon Screen Spray Water Valve | Detail 7 | FC | 65
|  | 2000-F30-PID-PR-10020 | Stage 2 | XV 30491 | SV30491 | CIL 3 Barren Carbon Sizing Screen Spray Water Valve | Detail 7 | FC | 30
PP007 | F13-CP-402 | 2000-F24-PID-PR-10013 | Stage 1 | XV 13361 | SV13361 | Trash Screen 1 Spray Water | Detail 7 | FC | 13
|  |  |  | XV 13371 | SV13371 | Trash Screen 2 Spray Water | Detail 7 | FC | 13
|  |  |  | XV 13391 | SV13391 | Trash Screen 4 Spray Water | Detail 7 | FC | 13
|  |  |  | XV 13401 | SV13401 | Trash Screen 3 Spray Water | Detail 7 | FC | 13
| F13-CP-403 | 2000-F24-PID-PR-10011 | Stage 1 | FCV 13075A | Manual Isolation | Primary Cyclone Feed Hopper Process Water 1 | Detail 1 | FC | 13
|  |  |  | FCV 13075B | Manual Isolation | Primary Cyclone Feed Hopper Process Water 2 | Detail 1 | FC | 13
| F13-CP-404 | 2000-F24-PID-PR-10011 | Stage 1 | XV 13077 | SV13077 | Primary Cyclone Feed Hopper Drain | Detail 4 | FO | 13
|  |  |  | XV 13081 | SV13081 | Cyclone Feed Pump Suction Drain | Detail 4 | FO | 13
|  |  |  | XV 13083 | SV13083 | Cyclone Feed Pump Suction Process Water | Detail 4 | FC | 13
|  |  |  | XV 13084 | SV13084 | Cyclone Feed Pump Discharge Drain | Detail 4 | FO | 13
|  |  |  | XV 13460 | SV13460 | CYCLONE FEED PUMP GLAND WATER | Detail 8 | FO | 13
|  |  |  | XV 13074 | SV13074 | Cyclone Feed Pump Suction Flushing Water | Detail 4 | FC | 13
|  |  |  | TCV 13129 | Manual Isolation | Cyclone Feed Pump Motor Cooling Water Temperature Control Valve | Detail 1 | FL | 13
| F13-CP-405 | 2000-F24-PID-PR-10011 | Stage 1 | FCV 13125 | Manual Isolation | SAG Mill VSD Cooling System Cooling Water Flow Control Valve | Detail 1 | FO | 13
|  |  |  | FCV 13126 | Manual Isolation | Ball Mill VSD Cooling System Cooling Water Flow Control Valve | Detail 1 | FO | 13
|  |  |  | FCV 13127 | Manual Isolation | Cyclone Feed Pump VSD Cooling System Cooling Water Flow Control Valve | Detail 1 | FO | 13
| F13-CP-406 | 2000-F24-PID-PR-10013 | Stage 1 | XV 13374 | SV13374 | Trash Dewatering Screen Spray Water | Detail 7 | FC | 13
|  |  |  | XV 13384 | SV13384 | Trash Dewatering Screen Bypass | Detail 4 | FO | 13
| F13-CP-407 | 2000-F24-PID-PR-10025 | Stage 1 | FCV 13121 | Manual Isolation | SAG Mill Feed Box Process Water | Detail 1 | FC | 13
|  |  |  | FCV 13141 | Manual Isolation | Ball Mill Feed Chute Process Water | Detail 1 | FC | 13
|  |  |  | XV 13114 | SVO/SVC13114 | Cyclone Underflow Boil Box to Ball Mill Feed Box 1 Line 1 | Detail 3 | FL | 13
|  |  |  | XV 13115 | SVO/SVC13115 | Cyclone Underflow Boil Box to Ball Mill Feed Box 1 Line 2 | Detail 3 | FL | 13
|  |  |  | XV 13116 | SVO/SVC13116 | Cyclone Underflow Boil Box to Sag Mill Feed Box | Detail 3 | FL | 13
| F13-CP-408 | 2000-F24-PID-PR-10013 | Stage 1 | XV 13360 | SV13360 | Trash Screen Final Collection Box Process Water | Detail 7 | FC | 13
| F13-CP-409 | 2000-F24-PID-PR-10011 | Stage 1 | FCV 13071 | Manual Isolation | SAG Mill Discharge Screen Process Water Flow Control Valve | Detail 1 | FC | 13
|  |  |  | FCV 13123 | Manual Isolation | SAG Mill Trommel Spray Water Flow Control Valve | Detail 1 | FC | 13
|  |  |  | FCV 13143 | Manual Isolation | Ball Mill Trommel Spray Water Valve | Detail 1 | FC | 13
|  |  |  | TCV 13410 | Manual Isolation | SAG Mill Motor 1 Cooling Water Temperature Control Valve | Detail 1 | FL | 13
|  |  |  | TCV 13412 | Manual Isolation | SAG Mill Motor 2 Cooling Water Temperature Control Valve | Detail 1 | FL | 13
|  |  |  | TCV 13414 | Manual Isolation | Ball Mill Motor 1 Cooling Water Temperature Control Valve | Detail 1 | FL | 13
|  |  |  | TCV 13416 | Manual Isolation | Ball Mill Motor 2 Cooling Water Temperature Control Valve | Detail 1 | FL | 13
| F13-CP-410 | 2000-F24-PID-PR-10013 | Stage 1 | XV 13441 | SVO/SVC13441 | Chiller 1 Feed Valve | Detail 9 | FL | 13
|  |  |  | XV 13443 | SVO/SVC13443 | Chiller 2 Feed Valve | Detail 9 | FL | 13
|  |  |  | XV 13445 | SVO/SVC13445 | Chiller 3 Feed Valve | Detail 9 | FL | 13
|  |  |  | XV 13447 | SVO/SVC13447 | Chiller 4 Feed Valve | Detail 9 | FL | 13
|  |  |  | XV 13419 | SVO/SVC13419 | Chiller Tank Valve | Detail 9 | FL | 13
| F13-CP-411 | 2000-F24-PID-PR-10013 | Stage 1 | XV 13418 | SVO/SVC13418 | Cooling Water Tank 2 Valve | Detail 9 | FL | 13
| F13-CP-412 | 2000-F24-PID-PR-10025 | Stage 1 | XV 13088 | SV13088 | Gravity Cyclone 1 HP Process Water | Detail 4 | FC | 13
|  |  |  | XV 13089 | SV13089 | Gravity Cyclone 2 HP Process Water | Detail 4 | FC | 13
| F13-HU-407 | N/A | Stage 1 | XV 13082 | SVO/SVC13082 | Cyclone Feed Pump Suction Valve | Detail 5 | FL | 13
| F14-CP-401 | 2000-F24-PID-PR-10025 | Stage 1 | XV 14031 | SVO/SVC14031 | Gravity Concentrator 1 Feed Valve | Detail 3 | FL | 14
|  |  |  | XV 14041 | SVO/SVC14041 | Gravity Concentrator 2 Feed Valve | Detail 3 | FL | 14
|  |  |  | XV 14051 | SV14051 | Gravity Concentrator 1 Feed Bypass to Tails Launder Valve | Detail 4 | FO | 14
|  |  |  | XV 14052 | SV14052 | Gravity Concentrator 2 Feed Bypass to Tails Launder Valve | Detail 4 | FO | 14
| F14-CP-402 | 2000-F24-PID-PR-10025 | Stage 1 | FCV 14001 | Manual Isolation | Gravity Screen 1 Feed Box Process Water | Detail 1 | FC | 14
|  |  |  | FCV 14002 | Manual Isolation | Gravity Screen 2 Feed Box Process Water | Detail 1 | FC | 14
|  |  |  | XV 14061 | SV14061 | Gravity Screen Oversize Chutes Process Water | Detail 7 | FC | 14
|  |  |  | XV 14012 | SV14012 | Gravity Screen 1 Spray Water Flow Control Valve | Detail 7 | FC | 14
|  |  |  | XV 14014 | SV14014 | Gravity Screen 2 Spray Water Flow Control Valve | Detail 7 | FC | 14
| F16-CP-401 | 2000-F24-PID-PR-10013 | Stage 1 | XV 13382 | SVO/SVC13382 | Trash Dewatering Screen Underflow Pump Suction Valve | Detail 3 | FL | 13
|  |  |  | XV 13383 | SVO/SVC13383 | Trash Dewatering Screen Underflow Pump Suction Drain Valve | Detail 3 | FL | 13
|  |  |  | XV 16152 | SVO/SVC16152 | Sample Return Pump 1 Sunction Valve | Detail 3 | FL | 16
|  |  |  | XV 16153 | SV16153 | Sample Return Pump 1 Drain Valve | Detail 4 | FO | 16
|  |  |  | XV 16162 | SVO/SVC16162 | Sample Return Pump 2 Sunction Valve | Detail 3 | FL | 16
|  |  |  | XV 16163 | SV16163 | Sample Return Pump 2 Drain Valve | Detail 4 | FO | 16
| F16-CP-403 | 2000-F24-PID-PR-10008 | Stage 1 | FCV 16001 | Manual Isolation | Rougher Flotation Cell 1 Procees Water Flow Control Valve | Detail 1 | FC | 16
| F17-CP-401 | 2000-F24-PID-PR-10024 | Stage 1 | XV 17091 | SV17091 | Flotation Tailings Thickener Underflow Cone Discharge Valve 1 | Detail 4 | FC | 17
|  |  |  | XV 17092 | SV17092 | Flotation Tailings Thickener Underflow Cone Discharge Valve 2 | Detail 4 | FC | 17
|  |  |  | XV 17093 | SV17093 | Flotation Tailings Thickener Underflow Cone Discharge Valve 3 | Detail 4 | FC | 17
|  |  |  | XV 17094 | SV17094 | Flotation Tailings Thickener Underflow Cone Discharge Valve 4 | Detail 4 | FC | 17
|  |  |  | XV 17095 | SVO/SVC17095 | Flotation Tailings Thickener Underflow Pump 1 Suction Flushing Valve | Detail 3 | FL | 17
|  |  |  | XV 17096 | SVO/SVC17096 | Flotation Tailings Thickener Underflow Pump 2 Suction Flushing Valve | Detail 3 | FL | 17
| F17-CP-402 | 2000-F24-PID-PR-10024 | Stage 1 | XV 17101 | SVO/SVC17101 | Flotation Tailings Thickener Underflow Pump 1 Discharge Flushing Valve | Detail 3 | FL | 17
|  |  |  | XV 17102 | SV17102 | Flotation Tailings Thickener Underflow Pump 1 Discharge Drain Valve | Detail 4 | FO | 17
|  |  |  | XV 17103 | SVO/SVC17103 | Flotation Tailings Thickener Underflow Pump 1 Discharge Valve | Detail 3 | FL | 17
|  |  |  | XV 17111 | SVO/SVC17111 | Flotation Tailings Thickener Underflow Pump 2 Discharge Flushing Valve | Detail 3 | FL | 17
|  |  |  | XV 17112 | SV17112 | Flotation Thickener Underflow Pump 2 Discharge Drain Valve | Detail 4 | FO | 17
|  |  |  | XV 17113 | SVO/SVC17113 | Flotation Thickener Underflow Pump 2 Discharge Valve | Detail 3 | FL | 17
| F17-CP-403 | 2000-F24-PID-PR-10024 | Stage 1 | XV 17123 | SVO/SVC17123 | Flotation Tailings Thickener Underflow Discharge Header Valve | Detail 3 | FL | 17
|  |  |  | XV 17124 | SV17124 | Flotation Tailings Thickener Underflow Pumps Discharge Header Drain Valve | Detail 4 | FO | 17
|  |  |  | XV 17125 | SVO/SVC17125 | Flotation Tailings Thickener Underflow Pumps Flotation Tailings Thickener Recirculation Bypass Valve | Detail 3 | FL | 17
|  |  |  | XV 17126 | SVO/SVC17126 | Flotation Tailings Thickener Underflow Pumps Flotation Tailings Thickener Recirculation Bypass Drain Valve | Detail 3 | FL | 17
|  |  |  | XV 17131 | SVO/SVC17131 | Flotation Tailings Thickener Underflow Pumps Discharge Header Flushing Valve | Detail 3 | FL | 17
| F17-CP-404 | 2000-F24-PID-PR-10024 | Stage 1 | XV 17005 | SVO/SVC17005 | Final Tails Sample Pump Suction Valve | Detail 3 | FL | 17
|  |  |  | XV 17006 | SV17006 | Final Tails Sample Pump Suction Drain | Detail 4 | FO | 17
|  |  |  | XV 17007 | SV17007 | Final Tails Sample Pump Discharge Drain | Detail 4 | FO | 17
|  |  |  | XV 16122 | SVO/SVC16122 | Flotation Cells Drain Pump Isolation Valve | Detail 3 | FL | 16
|  |  |  | XV 16123 | SVO/SVC16123 | Flotation Cells Drain Pump Drain Valve | Detail 3 | FL | 16
|  |  |  | XV 16080 | SVO/SVC16080 | Flotation Discharge Box Drain Valve | Detail 3 | FL | 16
| F17-CP-405 | 2000-F24-PID-PR-10007 | Stage 1 | FCV 17127 | Manual Isolation | Flotation Tailings Thickener Underflow Pumps CIL 2 Feed Box Valve | Detail 2 | FO | 17
|  |  |  | FCV 17128 | Manual Isolation | Flotation Tailings Thickener Underflow Pumps CIL 3 Feed Box Valve | Detail 2 | FO | 17
|  |  | Stage 2 | XV 21011 | HV21011 | Milk Of Lime Ringmain Drain Valve 1 | Detail 12 | FL | 21
| F17-CP-406 | 2000-F24-PID-PR-10007 | Stage 1 | FCV 17130 | Manual Isolation | Flotation Tailings Thickener Underflow Pumps to Final Tails Tank Pinch Valve | Detail 2 | FO | 17
|  |  |  | XV 17132 | SVO/SVC17132 | Flotation Tailings Thickener Underflow Pumps to Final Tails Tank Isolation Valve | Detail 3 | FL | 17
| F17-CP-407 | 2000-F24-PID-PR-10008 | Stage 1 | FCV 17001 | Manual Isolation | Flotation Tailings Thickener Flocculant In-Line Mixer Process Water Flow Control Valve | Detail 1 | FC | 17
|  |  |  | SVO 17019 | SV17019 | Flotation Tailings Thickener Turbidity Element Air Flushing Solenoid Valve | Detail 11 | FC | 17
| F17-HU-422 | N/A | Stage 1 | XV 17009 | SVO/SVC17009 | Flotation Tailings Thickener Recirculation Feed Box Isolation Valve | Detail 5 | FL | 17
| F18-CP-401 | 2000-F24-PID-PR-10024 | Stage 1 | FCV 18056 | Manual Isolation | Cleaner Flotation Cell Air Flow Control Valve | N/A | N/A | 18
|  |  |  | FCV 18057 | Manual Isolation | Cleaner Flotation Cell Wash Water Flow Flow Control Valve | N/A | N/A | 18
|  |  |  | LCV 18011B | Manual Isolation | Cleaner Flotation Cell Feed Hopper Recycle Level Control Valve | Detail 2 | FO | 18
|  |  |  | LCV 18051 | Manual Isolation | Cleaner Flotation Cell Tank Slurry Level Control Valve | N/A | N/A | 18
| F18-CP-402 | 2000-F24-PID-PR-10024 | Stage 1 | FCV 18256 | Manual Isolation | Cleaner-Scavenger Flotation Cell Air Flow Control Valve | N/A | N/A | 18
|  |  |  | FCV 18257 | Manual Isolation | Cleaner-Scavenger Flotation Cell High Pressure Water Flow Control Valve | N/A | N/A | 18
|  |  |  | LCV 18201B | Manual Isolation | Cleaner Scavenger Recycle Level Control Valve | Detail 2 | FO | 18
|  |  |  | LCV 18251 | Manual Isolation | Cleaner-Scavenger Flotation Cell Tank Slurry Level Control Valve | N/A | N/A | 18
| F18-CP-403 | 2000-F24-PID-PR-10024 | Stage 1 | XV 18221 | SVO/SVC18221 | Cleaner Scavenger Flotation Cell Recirculation Pump 1 Suction Valve | Detail 3 | FL | 18
|  |  |  | XV 18222 | SV18222 | Cleaner Scavenger Flotation Cell Recirculation Pump 1 Drain Valve | Detail 4 | FO | 18
|  |  |  | XV 18223 | SVO/SVC18223 | Cleaner Scavenger Flotation Cell Recirculation Pump 1 Discharge Valve | Detail 3 | FL | 18
|  |  |  | XV 18224 | SVO/SVC18224 | Cleaner Scavenger Flotation Cell Recirculation Pump 2 Suction Valve | Detail 3 | FL | 18
|  |  |  | XV 18225 | SV18225 | Cleaner Scavenger Flotation Cell Recirculation Pump 2 Drain Valve | Detail 4 | FO | 18
|  |  |  | XV 18226 | SVO/SVC18226 | Cleaner Scavenger Flotation Cell Recirculation Pump 2 Discharge Valve | Detail 3 | FL | 18
| F18-CP-404 | 2000-F24-PID-PR-10024 | Stage 1 | LCV 18211 | Manual Isolation | Cleaner Scavenger Flotation Cell Tails Hopper Process Water Level Control Valve | Detail 1 | FC | 18
|  |  |  | XV 18015 | SV18015 | Cleaner Scavenger Flotation Cell Tails Hopper Process Water Isolation Valve | Detail 7 | FC | 18
| F18-CP-405 | 2000-F24-PID-PR-10024 | Stage 1 | XV 18231 | SVO/SVC18231 | Cleaner Scavenger Flotation Cell Tails Pump 1 Suction Valve | Detail 3 | FL | 18
|  |  |  | XV 18232 | SV18232 | Cleaner Scavenger Flotation Cell Tails Pump 1 Drain Valve | Detail 4 | FO | 18
|  |  |  | XV 18233 | SVO/SVC18233 | Cleaner Scavenger Flotation Cell Tails Pump 1 Discharge Valve | Detail 3 | FL | 18
|  |  |  | XV 18234 | SVO/SVC18234 | Cleaner Scavenger Flotation Cell Tails Pump 2 Suction Valve | Detail 3 | FL | 18
|  |  |  | XV 18235 | SV18235 | Cleaner Scavenger Flotation Cell Tails Pump 2 Drain Valve | Detail 4 | FO | 18
|  |  |  | XV 18236 | SVO/SVC18236 | Cleaner Scavenger Flotation Cell Tails Pump 2 Discharge Valve | Detail 3 | FL | 18
| F18-CP-406 | 2000-F24-PID-PR-10024 | Stage 1 | XV 18021 | SVO/SVC18021 | Final Concentrate Pump 1 Suction Valve | Detail 3 | FL | 18
|  |  |  | XV 18022 | SV18022 | Final Concentrate Pump 1 Drain Valve | Detail 4 | FO | 18
|  |  |  | XV 18023 | SVO/SVC18023 | Final Concentrate Pump 1 Discharge Valve | Detail 3 | FL | 18
|  |  |  | XV 18024 | SVO/SVC18024 | Final Concentrate Pump 2 Suction Valve | Detail 3 | FL | 18
|  |  |  | XV 18025 | SV18025 | Final Concentrate Pump 2 Drain Valve | Detail 4 | FO | 18
|  |  |  | XV 18026 | SVO/SVC18026 | Final Concentrate Pump 2 Discharge Valve | Detail 3 | FL | 18
|  |  |  | XV 18028 | SV18028 | Final Concentrate Sampler Discharge Valve | Detail 7 | FC | 18
|  |  |  | XV 18029 | SV18029 | Final Concentrate Sampler Discharge Process Water Valve | Detail 7 | FC | 18
| F18-CP-407 | 2000-F24-PID-PR-10024 | Stage 1 | XV 18031 | SVO/SVC18031 | Cleaner Flotation Cell Recirculation Pump 1 Suction Valve | Detail 3 | FL | 18
|  |  |  | XV 18032 | SV18032 | Cleaner Flotation Cell Recirculation Pump 1 Drain Valve | Detail 4 | FO | 18
|  |  |  | XV 18033 | SVO/SVC18033 | Cleaner Flotation Cell Recirculation Pump 1 Discharge Valve | Detail 3 | FL | 18
|  |  |  | XV 18034 | SVO/SVC18034 | Cleaner Flotation Cell Recirculation Pump 2 Suction Valve | Detail 3 | FL | 18
|  |  |  | XV 18035 | SV18035 | Cleaner Flotation Cell Recirculation Pump 2 Drain Valve | Detail 4 | FO | 18
|  |  |  | XV 18036 | SVO/SVC18036 | Cleaner Flotation Cell Recirculation Pump 2 Discharge Valve | Detail 3 | FL | 18
| F18-CP-408 | 2000-F24-PID-PR-10024 | Stage 1 | LCV 18201A | Manual Isolation | Cleaner Scavenger Flotation Cell Feed Hopper Process Water Level Control Valve | Detail 1 | FC | 18
|  |  |  | XV 18014 | SV18014 | Cleaner Scavenger Flotation Cell Feed Hopper Process Water Isolation Valve | Detail 7 | FC | 18
| F18-CP-409 | 2000-F24-PID-PR-10024 | Stage 1 | XV 18229 | SV18229 | Cleaner Scavenger Tails Sample Discharge Flushing Valve | Detail 7 | FC | 18
|  |  |  | XV 18239 | SV18239 | Cleaner Scavenger Tails Sample Discharge Valve | Detail 7 | FC | 18
|  |  |  | XV 18241 | SVO/SVC18241 | Cleaner Scavenger Tails Discharge to Flotation Discharge Box Valve | Detail 3 | FL | 18
|  |  |  | XV 18242 | SVO/SVC18242 | Cleaner Scavenger Tails Discharge to Scavenger Flotation Cell 1 Valve | Detail 3 | FL | 18
|  |  |  | XV 18243 | SV18243 | Cleaner Scavenger Tails Discharge to Flotation Discharge Box Drain Valve | Detail 4 | FO | 18
|  |  |  | XV 18244 | SV18244 | Cleaner Scavenger Tails Discharge to Scavenger Flotation Cell 1 Drain Valve | Detail 4 | FO | 18
| F18-CP-410 | 2000-F24-PID-PR-10024 | Stage 1 | LCV 18001 | Manual Isolation | Final Concentrate Hopper Process Water Level Control Valve | Detail 1 | FC | 18
|  |  |  | LCV 18011A | Manual Isolation | Cleaner Flotation Cell Feed Hopper Process Water Level Control Valve | Detail 1 | FC | 18
|  |  |  | XV 18038 | SV18038 | Cleaner Feed Sampler Discharge Valve | Detail 7 | FC | 18
|  |  |  | XV 18039 | SV18039 | Cleaner Feed Discharge Process Water Valve | Detail 7 | FC | 18
|  |  |  | XV 18012 | SV18012 | Final Concentrate Hopper Process Water Isolation Valve | Detail 7 | FC | 18
|  |  |  | XV 18013 | SV18013 | Cleaner Flotation Cell Feed Hopper Process Water Isolation Valve | Detail 7 | FC | 18
| F21-CP-401 | 2000-F24-PID-PR-10029 | Stage 2 | XV 21001 | SVO/SVC21001 | CIL 4 Tanks Cyanide Distribution Valve | Detail 9 | FL | 21
|  |  |  | FCV 21002 | Manual Isolation | CIL 4 Feed Distribution Box Cyanide Inlet Flow Control Valve | Detail 1 | FC | 21
|  |  |  | FCV 21003 | Manual Isolation | CIL 4 Tank 1 Cyanide Inlet Flow Control Valve | Detail 1 | FC | 21
|  |  |  | FCV 21004 | Manual Isolation | CIL 4 Tank 2 Cyanide Inlet Flow Control Valve | Detail 1 | FC | 21
|  |  |  | XV 21012 | SVO/SVC21012 | Milk Of Lime to CIL 4 Feed Distribution Box Supply Valve | Detail 3 | FL | 21
|  |  |  | FCV 21005 | Manual Isolation | CIL 4 Tank 3 Cyanide Inlet Flow Control Valve | Detail 1 | FC | 21
| F21-CP-402 | 2000-F24-PID-PR-10029 | Stage 2 | XV 21051 | SV21051 | CIL 4 Tank 1 Oxygen Injection Pump Suction Valve | Detail 4 | FC | 21
|  |  |  | XV 21052 | SV21052 | CIL 4 Tank 1 Oxygen Injection Pump Suction Drain Valve | Detail 4 | FO | 21
|  |  |  | XV 21053 | SV21053 | CIL 4 Tank 1 Oxygen Injection Pump Discharge Valve | Detail 4 | FC | 21
|  |  |  | XV 21056 | SV21056 | CIL 4 Tank 1 Oxygen Injection Pump Discharge Drain Valve | Detail 4 | FO | 21
|  |  |  | FCV 21347 | Manual Isolation | CIL 4 Tank 1 Oxygen Injection 1 Flow Control Valve | Detail 1 | FC | 21
|  |  |  | FCV 21349 | Manual Isolation | CIL 4 Tank 1 Oxygen Injection 2 Flow Control Valve | Detail 1 | FC | 21
| F21-CP-403 | 2000-F24-PID-PR-10007 | Stage 2 | XV 21091 | SV21091 | CIL 4 Tank 2 Oxygen Injection Pump Suction Valve | Detail 4 | FC | 21
|  |  |  | XV 21092 | SV21092 | CIL 4 Tank 2 Oxygen Injection Pump Suction Drain Valve | Detail 4 | FO | 21
|  |  |  | XV 21093 | SV21093 | CIL 4 Tank 2 Oxygen Injection Pump Discharge Valve | Detail 4 | FC | 21
|  |  |  | XV 21096 | SV21096 |  |  |  | 21
|  |  |  | FCV 21356 | Manual Isolation | CIL 4 Tank 2 Oxygen Injection 1 Flow Control Valve | Detail 1 | FC | 21
|  |  |  | FCV 21358 | Manual Isolation | CIL 4 Tank 2 Oxygen Injection 2 Flow Control Valve | Detail 1 | FC | 21
| F22-CP-401 | 2000-F24-PID-PR-10031 | Stage 2 | XV 21136 | SV21136 | CIL 4 Loaded Carbon Screen Spray Water Valve | Detail 7 | FC | 21
|  |  |  | XV 22011 | SV22011 | Loaded Carbon to CIL 4 Elution & Acid Wash Column Valve | Detail 8 | FC | 22
|  |  |  | XV 22016 | SV22016 | CIL 4 Elution & Acid Wash Column to CIL 4 Elution Filter Valve | Detail 8 | FC | 22
|  |  |  | XV 22051 | SV22051 | CIL 4 Elution Filters Acid Rinse Water to Final Collection Box Valve | Detail 8 | FC | 22
|  |  |  | XV 22054 | SV22054 | CIL 4 Elution Filters Pregnant Eluate to CIL 4 Elution Recovery Heat Exchanger Valve | Detail 8 | FC | 22
|  |  |  | XV 22138 | SV22138 | CIL 4 Loaded Carbon Transfer Vessel Scheme Water Inlet Valve | Detail 8 | FC | 22
|  |  |  | XV 22139 | SV22139 | CIL 4 Loaded Carbon Transfer Vessel Drain Valve | Detail 4 | FC | 22
| F22-CP-402 | 2000-F24-PID-PR-10031 | Stage 2 | XV 22022 | SV22022 | CIL 4 Carbon Eductor Pump to CIL 4 Elution & Acid Wash Column Valve | Detail 8 | FC | 22
|  |  |  | XV 22024 | SV22024 | CIL 4 Elution & Acid Wash Column Dilute Hydrochloric Acid Inlet Valve | Detail 8 | FC | 22
|  |  |  | XV 22026 | SV22026 | CIL 4 Carbon Eductor Pump Outlets To Screens Valve | Detail 8 | FC | 22
|  |  |  | XV 22030 | SV22030 | CIL 4 Elution & Acid Wash Column Pregnant Eluate Inlet Valve | Detail 8 | FO | 22
|  |  |  | XV 22034 | SV22034 | CIL 4 Elution & Acid Wash Column Inlet Drain Valve | Detail 8 | FC | 22
|  |  |  | XV 22057 | SV22057 | CIL 4 Elution & Acid Wash Column Drain to Screens Valve | Detail 8 | FC | 22
|  |  |  | PCV 22121 | No Solenoid | CIL 4 Elution Recovery Heat Exchanger To Eluate Tanks Pressure Control Valve | Detail 1 | FO | 22
|  |  |  | XV 22124 | SV22124 | CIL 4 Elution Recovery Heat Exchanger To CIL 4 Eluate Circulation Tank Valve | Detail 8 | FC | 22
|  |  |  | XV 22141 | SV22141 | CIL 4 Lean Eluate Tank Pregnant Eluate Inlet Valve | Detail 8 | FC | 22
|  |  |  | XV 22145 | SV22145 | CIL 4 Eluate Expansion Tank Pregnant Eluate Inlet Valve | Detail 8 | FC | 22
| F22-CP-403 | 2000-F24-PID-PR-10031 | Stage 2 | XV 22061 | SVO/SVC22061 | CIL 4 Elution & Acid Wash Column Drain to CIL 4 Regen Kiln Dewatering Screen Feed Box Valve | Detail 3 | FL | 22
|  |  |  | XV 22062 | SVO/SVC22062 | CIL 4 Elution & Acid Wash Column Drain to CIL 4 Carbon Sizing Screen Feed Box Valve | Detail 3 | FL | 22
|  |  |  | XV 22072 | SV22072 | CIL 4 Elution Area Sump Pump To CIL 4 Feed Distribution Box Valve | Detail 8 | FC | 22
|  |  |  | XV 22073 | SV22073 | CIL 4 Elution Area Sump Pump To Final Tails Collection Box Valve | Detail 7 | FO | 22
| F22-CP-404 | 2000-F24-PID-PR-10031 | Stage 2 | XV 22144 | SV22144 | CIL 4 Lean Eluate Tank Discharge Valve | Detail 8 | FC | 22
|  |  |  | XV 22147 | SV22147 | CIL 4 Eluate Expansion Tank Discharge Valve | Detail 8 | FC | 22
|  |  |  | XV 22153 | SV22153 | CIL 4 Elution Water Tank Discharge Valve | Detail 8 | FC | 22
|  |  |  | XV 22161 | SVO/SVC22161 | CIL 4 Elution Pump 1 Suction Valve | Detail 9 | FL | 22
|  |  |  | XV 22162 | SVO/SVC22162 | CIL 4 Elution Pump 1 Discharge Valve | Detail 9 | FL | 22
|  |  |  | XV 22163 | SVO/SVC22163 | CIL 4 Elution Pump 2 Suction Valve | Detail 9 | FL | 22
|  |  |  | XV 22164 | SVO/SVC22164 | CIL 4 Elution Pump 2 Discharge Valve | Detail 9 | FL | 22
| F22-CP-405 | 2000-F24-PID-PR-10031 | Stage 2 | XV 22194 | SV22194 | CIL 4 Barren Carbon Pump Suction Valve | Detail 7 | FO | 22
|  |  |  | XV 22201 | SV22201 | CIL 4 Carbon Quench Hopper to CIL 4 Barren Carbon Pump Valve | Detail 4 | FC | 22
|  |  |  | XV 22202 | SVO/SVC22202 | CIL 4 Barren Carbon Pump Suction Drain Valve | Detail 3 | FL | 22
|  |  |  | TCV 22228 | Manual Isolation | Kiln Mercury Abatement Cooling Water Temperature Control Valve | Detail 1 | FO | 22
|  |  |  | XV 22207 | SVO/SVC22207 | CIL 4 Carbon Quench Hopper Water Inlet Valve | Detail 9 | FL | 22
|  |  |  | XV 22251 | SV22251 | CIL 4 Carbon Regeneration Kiln Feed Hopper Discharge Valve | Detail 4 | FC | 22
|  |  |  | XV 22231 | SV22231 | Kiln Mercury Abatement Off-Gas Cooler Cooling Water Inlet TCV Bypass Valve | Detail 7 | FO | 22
| F22-CP-406 | 2000-F24-PID-PR-10031 | Stage 2 | XV 22241 | SV22241 | Kiln Abatement System Cooling Water Tank Scheme Water Valve | Detail 7 | FC | 22
| F22-CP-407 | 2000-F24-PID-PR-10031 | Stage 2 | XV 22021 | SVO/SVC22021 | CIL 4 Carbon Eductor Pump Scheme Water Valve | Detail 9 | FL | 22
|  |  |  | XV 22142 | SV22142 | CIL 4 Lean Eluate Tank Scheme Water Inlet Valve | Detail 8 | FC | 22
|  |  |  | XV 22151 | SV22151 | CIL 4 Elution Water Tank Scheme Water Inlet Valve | Detail 8 | FC | 22
|  |  |  | XV 22181 | SV22181 | Cyanide to CIL Elution Pumps Valve | Detail 8 | FC | 22
|  |  |  | XV 22191 | SV22191 | Caustic to CIL Elution Pumps Valve | Detail 8 | FC | 22
| F23-CP-401 | 2000-F24-PID-PR-10007 | Stage 1 | XV 23411 | SV23411 | Final Tails Pump 1 Suction Valve | Detail 4 | FC | 23
|  |  |  | XV 23412 | SV23412 | Final Tails Pump 1 Suction Flushing Water Valve | Detail 4 | FC | 23
|  |  |  | XV 23413 | SV23413 | Final Tails Pump 1 Suction Drain Valve | Detail 4 | FO | 23
|  |  |  | XV 23424 | SV23424 | Final Tails Pump 2 Suction Valve | Detail 4 | FC | 23
|  |  |  | XV 23425 | SV23425 | Final Tails Pump 2 Suction Flushing Water Valve | Detail 4 | FC | 23
|  |  |  | XV 23426 | SV23426 | Final Tails Pump 2 Suction Drain Valve | Detail 4 | FO | 23
| F23-CP-402 | 2000-F24-PID-PR-10007 | Stage 1 | XV 23414 | SVO/SVC23414 | Final Tails Pump 1 Discharge Valve | Detail 3 | FL | 23
|  |  |  | XV 23415 | SV23415 | Final Tails Pump 1 Discharge Flushing Water Valve | Detail 4 | FC | 23
|  |  |  | XV 23427 | SVO/SVC23427 | Final Tails Pump 2 Discharge Valve | Detail 3 | FL | 23
|  |  |  | XV 23428 | SV23428 | Final Tails Pump 2 Discharge Flushing Water Valve | Detail 4 | FC | 23
|  |  |  | FCV 23405 | Manual Isolation | Final Tails Tank Saline Water Feed Flow Control Valve | Detail 1 | FC | 23
|  |  |  | PCV 23410 | No Solenoid | Final Tails Pump 1 Upstream Flushing Valve | Detail 1 | FC | 23
|  |  |  | PCV 23423 | No Solenoid | Final Tails Pump 2 Upstream Flushing Valve | Detail 1 | FC | 23
| F23-CP-403 | 2000-F24-PID-PR-10007 | Stage 1 | XV 23402 | SVO/SVC23402 | Final Tails Tank Drain Valve | Detail 3 | FL | 23
|  |  |  | XV 23435 | SV23435 | Final Tails Pump 3 Suction Valve | Detail 4 | FC | 23
|  |  |  | XV 23436 | SV23436 | Final Tails Pump 3 Suction Flushing Water Valve | Detail 4 | FC | 23
|  |  |  | XV 23437 | SV23437 | Final Tails Pump 3 Suction Drain Valve | Detail 4 | FO | 23
|  |  |  | XV 23446 | SV23446 | Final Tails Pump 4 Suction Valve | Detail 4 | FC | 23
|  |  |  | XV 23447 | SV23447 | Final Tails Pump 4 Suction Flushing Water Valve | Detail 4 | FC | 23
|  |  |  | XV 23448 | SV23448 | Final Tails Pump 4 Suction Drain Valve | Detail 4 | FO | 23
| F23-CP-404 | 2000-F24-PID-PR-10007 | Stage 1 | XV 23438 | SVO/SVC23438 | Final Tails Pump 3 Discharge Valve | Detail 3 | FL | 23
|  |  |  | XV 23439 | SV23439 | Final Tails Pump 3 Discharge Flushing Water Valve | Detail 4 | FC | 23
|  |  |  | XV 23449 | SVO/SVC23449 | Final Tails Pump 4 Discharge Valve | Detail 3 | FL | 23
|  |  |  | XV 23450 | SV23450 | Final Tails Pump 4 Discharge Flushing Water Valve | Detail 4 | FC | 23
|  |  |  | PCV 23434 | No Solenoid | Final Tails Pump 3 Upstream Flushing Valve | Detail 1 | FC | 23
|  |  |  | PCV 23445 | No Solenoid | Final Tails Pump 4 Upstream Flushing Valve | Detail 1 | FC | 23
| F23-CP-405 | 2000-F24-PID-PR-10007 | Stage 1 | FCV 23456 | Manual Isolation | FIM 1 Valve Station Feed Flow Control Valve | Detail 1 | FC | 23
|  |  |  | XV 23457 | SV23457 | FIM 1 Valve Station Feed Valve 1 | Detail 4 | FC | 23
|  |  |  | XV 23458 | SV23458 | FIM 1 Valve Station Feed Valve 2 | Detail 4 | FC | 23
|  |  | Stage 2 | XV 75608 | SVO/SVC75608 | Tails Flushing HP Process Water | Detail 3 | FL | 75
|  |  |  | XV 75609 | SVO/SVC75609 | Tails Flushing HP Process Water | Detail 3 | FL | 75
| F24-CP-401 | 2000-F24-PID-PR-10013 | Stage 1 | LCV 24401 | Manual Isolation | Process Water Tank Level Control Valve | Detail 1 | FC | 24
|  |  |  | XV 24402 | SV24402 | Process Water Tank Saline Water Feed Valve | Detail 7 | FC | 24
| F24-CP-402 | 2000-F24-PID-PR-10013 | Stage 1 | XV 24411 | SVO/SVC24411 | Mill Water Pump 1 Suction Valve | Detail 9 | FL | 24
|  |  |  | XV 24412 | SVO/SVC24412 | Mill Water Pump 1 Discharge Valve | Detail 9 | FL | 24
|  |  |  | XV 24413 | SVO/SVC24413 | Mill Water Pump 2 Suction Valve | Detail 9 | FL | 24
|  |  |  | XV 24414 | SVO/SVC24414 | Mill Water Pump 2 Discharge Valve | Detail 9 | FL | 24
| F24-CP-403 | 2000-F24-PID-PR-10013 | Stage 1 | XV 24421 | SVO/SVC24421 | High Pressure Process Water Pump 1 Suction Valve | Detail 9 | FL | 24
|  |  |  | XV 24422 | SVO/SVC24422 | High Pressure Process Water Pump 1 Discharge Valve | Detail 9 | FL | 24
|  |  |  | XV 24423 | SVO/SVC24423 | High Pressure Process Water Pump 2 Suction Valve | Detail 9 | FL | 24
|  |  |  | XV 24424 | SVO/SVC24424 | High Pressure Process Water Pump 2 Discharge Valve | Detail 9 | FL | 24
| F24-CP-404 | 2000-F24-PID-PR-10007 | Stage 1 | XV 24501 | SVO/SVC24501 | Raw Water Feed Booster Pump 1 Suction Valve | Detail 9 | FL | 24
|  |  |  | XV 24502 | SVO/SVC24502 | Raw Water Feed Booster Pump 1 Discharge Valve | Detail 9 | FL | 24
|  |  |  | XV 24503 | SVO/SVC24503 | Raw Water Feed Booster Pump 2 Suction Valve | Detail 9 | FL | 24
|  |  |  | XV 24504 | SVO/SVC24504 | Raw Water Feed Booster Pump 2 Discharge Valve | Detail 9 | FL | 24
| F28-CP-401 | 2000-F24-PID-PR-10027 | Stage 1 | DCV 28281 | Manual Isolation | UFG Mill 3 Discharge Hopper Process Water Density Control Valve | Detail 1 | FC | 28
|  |  |  | LCV 28261 | Manual Isolation | UFG Mill 3 Discharge Recycle Level Control Valve | Detail 2 | FO | 28
|  |  |  | LCV 28273 | Manual Isolation | UFG Mill 3 Discharge Hopper Level Control Valve | Detail 2 | FO | 28
|  |  |  | XV 28282 | SVO/SVC28282 | UFG Mill 3 Discharge Pump Suction Valve | Detail 3 | FL | 28
|  |  |  | XV 28283 | SV28283 | UFG Mill 3 Discharge Pump Drain Valve | Detail 4 | FO | 28
|  |  |  | XV 28342 | SVO/SVC28342 | UFG Mill 3 Gland Water Valve | Detail 9 | FC | 28
|  |  |  | XV 28202 | SV28202 | UFG Mill 3 Water Collection Tank Process Water Inlet Valve | Detail 7 | FC | 28
|  |  |  | XV 28463 | SVO/SVC28463 | UFG Mill 3 Concentrate Trash Screen Flotation Concentrate Inlet Valve | Detail 3 | FL | 28
|  |  |  | XV 28464 | SVO/SVC28464 | UFG Mill 3 Concentrate Trash Screen Flotation Concentrate Bypass Valve | Detail 3 | FL | 28
| F28-CP-402 | 2000-F24-PID-PR-10027 | Stage 1 | XCV 28012 | No Solenoid | UFG Mill 2 Media Hopper Discharge Valve | Detail 2 | FC | 28
|  |  |  | XCV 28212 | No Solenoid | UFG Mill 3 Media Hopper Discharge Valve | Detail 2 | FC | 28
|  |  |  | XV 28205 | SVO/SVC28205 | UFG Sump Pump 2 to UFG Mill 2 Trash Screen Valve | Detail 3 | FL | 28
|  |  |  | XV 28204 | SVO/SVC28204 | UFG Sump Pump 2 to UFG Mill 3 Trash Screen Valve | Detail 3 | FL | 28
| F28-CP-403 | 2000-F24-PID-PR-10027 | Stage 1 | FCV 28221 | Manual Isolation | UFG Mill 3 Feed Hopper HP Process Water Flow Control Valve 2 | Detail 1 | FC | 28
|  |  |  | FCV 28223 | Manual Isolation | UFG Mill 3 Feed Hopper HP Process Water Flow Control Valve 1 | Detail 1 | FC | 28
|  |  |  | XV 28231 | SVO/SVC28231 | UFG Mill 3 Feed Pump Suction Valve | Detail 3 | FL | 28
|  |  |  | XV 28232 | SVO/SVC28232 | UFG Mill 3 Feed Pump Discharge Drain Valve | Detail 3 | FL | 28
|  |  |  | XV 28236 | SVO/SVC28236 | UFG Mill 3 Feed Pump Suction Drain Valve | Detail 3 | FL | 28
| F28-CP-404 | 2000-F24-PID-PR-10027 | Stage 1 | FCV 28021 | Manual Isolation | UFG Mill 2 Feed Hopper HP Process Water Flow Control Valve 2 | Detail 1 | FC | 28
|  |  |  | FCV 28023 | Manual Isolation | UFG Mill 2 Feed Hopper HP Process Water Flow Control Valve 1 | Detail 1 | FC | 28
|  |  |  | XV 28031 |  |  |  |  | 28
|  |  |  | XV 28032 | SV28032 | UFG Mill 2 Feed Pump Discharge Drain Valve | Detail 4 | FO | 28
|  |  |  | XV 28036 | SV28036 | UFG Mill 2 Feed Pump Suction Drain Valve | Detail 4 | FO | 28
|  |  |  | XV 28042 | SV28042 | UFG GSW Tank Raw Water | Detail 7 | FC | 28
| F28-CP-406 | 2000-F24-PID-PR-10027 | Stage 1 | DCV 28091 | Manual Isolation | UFG Mill 2 Discharge Hopper Process Water Density Control Valve | Detail 1 | FC | 28
|  |  |  | LCV 28073 | Manual Isolation | Ultra Fine Grinding Mill 2 Discharge Recycle Valve | Detail 2 | FO | 28
|  |  |  | LCV 28074 | Manual Isolation | UFG Mill 2 Discharge Hopper Feed Valve | Detail 2 | FO | 28
|  |  |  | XV 28002 | SV28002 | UFG Mill 2 Water Collection Tank HP Precess Water Inpiut | Detail 7 | FC | 28
|  |  |  | XV 28064 | SVO/SVC28064 | Ultra Fine Grinding Mill 2 Gland Water Valve | Detail 9 | FL | 28
|  |  |  | XV 28092 | SVO/SVC28092 | UFG Mill 2 Discharge Pump 1 Suction Valve | Detail 3 | FL | 28
|  |  |  | XV 28093 | SV28093 | UFG Mill 2 Discharge Pump 1 Drain Valve | Detail 4 | FO | 28
|  |  |  | XV 28069 | SVO/SVC28069 | UFG Mill 2 Concentrate Trash Screen Flotation Concentrate Bypass Valve | Detail 3 | FL | 28
|  |  |  | XV 28070 | SVO/SVC28070 | UFG Mill 2 Concentrate Trash Screen Flotation Concentrate Inlet Valve | Detail 3 | FL | 28
| F28-CP-407 | 2000-F24-PID-PR-10027 | Stage 1 | LCV 28328 | Manual Isolation | UFG Product Hopper Process Water Level Control Valve | Detail 1 | FC | 28
|  |  |  | XV 28322 | SV28322 | UFG Product Pump 1 Suction Valve | Detail 4 | FC | 28
|  |  |  | XV 28323 | SV28323 | UFG Product Pump 1 Drain Valve | Detail 4 | FO | 28
|  |  |  | XV 28324 | SVO/SVC28324 | UFG Product Pump 1 Discharge Valve | Detail 3 | FL | 28
|  |  |  | XV 28325 | SV28325 | UFG Product Pump 2 Suction Valve | Detail 4 | FC | 28
|  |  |  | XV 28326 | SV28326 | UFG Product Pump 2 Drain Valve | Detail 4 | FO | 28
|  |  |  | XV 28327 | SVO/SVC28327 | UFG Product Pump 2 Discharge Valve | Detail 3 | FL | 28
|  |  |  | XV 28320 | SV28320 | UFG Product Hopper Process Water Valve | Detail 7 | FC | 28
|  |  |  | XV 28134 | SVO/SVC28134 | UFG Sump Pump 1 to UFG Mill 2 Trash Screen Valve | Detail 3 | FL | 28
|  |  |  | XV 28135 | SVO/SVC28135 | UFG Sump Pump 1 to UFG Mill 3 Trash Screen Valve | Detail 3 | FL | 28
| F30-CP-401 | 2000-F30-PID-PR-10001 | Stage 1 | XV 30445 | SV30445 | Concentrate Thickener Underflow Pump 1 Suction Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30446 | SVO/SVC30446 | Concentrate Thickener Underflow Pump 1 Discharge Valve | Detail 3 | FL | 30
|  |  |  | XV 30450 | SV30450 | Concentrate Thickener Underflow Pump 2 Suction Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30451 | SVO/SVC30451 | Concentrate Thickener Underflow Pump 2 Discharge Valve | Detail 3 | FL | 30
|  |  |  | XV 30477 | SVO/SVC30477 | Concentrate Thickener Underflow Pump 1 Suction Flushing Valve | Detail 3 | FL | 30
|  |  |  | XV 30478 | SVO/SVC30478 | Concentrate Thickener Underflow Pump 2 Suction Flushing Valve | Detail 3 | FL | 30
| F30-CP-402 | 2000-F30-PID-PR-10002 | Stage 1 | XV 30457 | SVO/SVC30457 | Concentrate Thickener Underflow Pumps Recirculation Valve | Detail 3 | FL | 30
|  |  |  | XV 30458 | SVO/SVC30458 | Concentrate Thickener Underflow Pumps to Filter Feed Tanks Valve | Detail 3 | FL | 30
|  |  |  | XV 30475 | SV30475 | Concentrate Thickener Underflow Pumps to Filter Feed Tanks Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30476 | SV30476 | Concentrate Thickener Underflow Pumps Recirculation Drain Valve | Detail 4 | FO | 30
| F30-CP-403 | 2000-F30-PID-PR-10016 | Stage 2 | FCV 30421 | Manual Isolation | Leach Feed Distribution Cyanide Flow Control Valve | Detail 1 | FC | 30
|  |  |  | XV 30481 | SVO/SVC30481 | CIL 2 Leach Feed Box Lime Addition Valve | Detail 3 | FL | 30
| F30-CP-404 | 2000-F30-PID-PR-10016 | Stage 2 | FCV 30422 | Manual Isolation | CIL 2 Leach Tank 2 Cyanide Flow Control Valve | Detail 1 | FC | 30
|  |  |  | FCV 30423 | Manual Isolation | CIL 2 Leach Tank 3 Cyanide Flow Control Valve | Detail 1 | FC | 30
|  |  |  | FCV 30424 | Manual Isolation | CIL 2 Leach Tank 4 Cyanide Flow Control Valve | Detail 1 | FC | 30
|  |  |  | FCV 30425 | Manual Isolation | CIL 2 Leach Tank 5 Cyanide Flow Control Valve | Detail 1 | FC | 30
|  |  |  | FCV 30426 | Manual Isolation | CIL 2 Leach Tank 6 Cyanide Flow Control Valve | Detail 1 | FC | 30
| F30-CP-405 | 2000-F30-PID-PR-10007 | Stage 2 | FCV 30557 | Manual Isolation | CIL 2 Oxygen Injection Pump 1 Injector 1 Flow Control Valve | Detail 1 | FC | 30
|  |  |  | FCV 30559 | Manual Isolation | CIL 2 Oxygen Injection Pump 1 Injector 2 Flow Control Valve | Detail 1 | FC | 30
|  |  |  | XV 30550 | SV30550 | CIL 2 Oxygen Injection Pump 1 Suction Valve | Detail 4 | FC | 30
|  |  |  | XV 30555 | SV30555 | CIL 2 Oxygen Injection Pump 1 Discharge Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30562 | SV30562 | CIL 2 Oxygen Injection Pump 1 Discharge Valve | Detail 4 | FC | 30
|  |  |  | FCV 30338 | Manual Isolation | CIL 2 Barren Eluate Feed Flow Control Valve | Detail 1 | FC | 30
| F30-CP-406 | 2000-F30-PID-PR-10007 | Stage 2 | FCV 30572 | Manual Isolation | CIL 2 Oxygen Injection Pump 2 Injector 1 Flow Control Valve | Detail 1 | FC | 30
|  |  |  | FCV 30574 | Manual Isolation | CIL 2 Oxygen Injection Pump 2 Injector 2 Flow Control Valve | Detail 1 | FC | 30
|  |  |  | XV 30565 | SV30565 | CIL 2 Oxygen Injection Pump 2 Suction Valve | Detail 4 | FC | 30
|  |  |  | XV 30570 | SV30570 | CIL 2 Oxygen Injection Pump 2 Discharge Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30577 | SV30577 | CIL 2 Oxygen Injection Pump 2 Discharge Valve | Detail 4 | FC | 30
| F30-CP-407 | 2000-F30-PID-PR-10004 | Stage 2 | XV 30401 | SV30401 | Concentrate Pre-Leach Thickener Underflow Pump 1 Suction Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30406 | SV30406 | Concentrate Pre-Leach Thickener Underflow Pump 2 Suction Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30428 | SVO/SVC30428 | Concentrate Pre-Leach Thickener Underflow Pump 1 Suction Flushing Valve | Detail 3 | FL | 30
|  |  |  | XV 30429 | SVO/SVC30429 | Concentrate Pre-Leach Thickener Underflow Pump 2 Suction Flushing Valve | Detail 3 | FL | 30
|  |  |  | XV 30402 | SVO/SVC30402 | Concentrate Pre-Leach Thickener Underflow Pump 1 Discharge Valve | Detail 3 | FL | 30
|  |  |  | XV 30407 | SVO/SVC30407 | Concentrate Pre-Leach Thickener Underflow Pump 2 Discharge Valve | Detail 3 | FL | 30
| F30-CP-408 | 2000-F30-PID-PR-10004 | Stage 2 | XV 30414 | SVO/SVC30414 | Concentrate Pre-Leach Thickener Underflow Pumps to CIL 2 Feed Distribution Box Valve | Detail 3 | FL | 30
|  |  |  | XV 30416 | SV30416 | Concentrate Pre-Leach Thickener Underflow Pumps to CIL 2 Feed Distribution Box Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30413 | SVO/SVC30413 | Concentrate Pre-Leach Thickener Underflow Pumps to CIL 2 Feed Distribution Box Valve | Detail 3 | FL | 30
|  |  |  | XV 30415 | SV30415 | Concentrate Pre-Leach Thickener Underflow Pumps to CIL 2 Feed Distribution Box Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30419 | SV30419 | CIL 2 Feed Primary Sampler Sample Flushing Water Valve | Detail 7 | FC | 30
|  |  |  | XV 30420 | SV30420 | CIL 2 Feed Primary Sampler Sample Isolation Valve | Detail 7 | FC | 30
| F30-CP-409 | 2000-F30-PID-PR-10006 | Stage 2 | XV 30431 | SVO/SVC30431 | Concentrate Leach Transfer Pump 1 Suction Valve | Detail 3 | FL | 30
|  |  |  | XV 30432 | SV30432 | Concentrate Leach Transfer Pump 1 Suction Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30433 | SVO/SVC30433 | Concentrate Leach Transfer Pump 1 Discharge Valve | Detail 3 | FL | 30
|  |  |  | XV 30437 | SVO/SVC30437 | Concentrate Leach Transfer Pump 2 Suction Valve | Detail 3 | FL | 30
|  |  |  | XV 30438 | SV30438 | Concentrate Leach Transfer Pump 2 Suction Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30439 | SVO/SVC30439 | Concentrate Leach Transfer Pump 2 Discharge Valve | Detail 3 | FL | 30
|  |  |  | XV 30489 | SV30489 | Concentrate Leach Transfer Orifice Station Drain | Detail 4 | FO | 30
| F30-CP-410 | 2000-F30-PID-PR-10011 | Stage 2 | XV 30463 | SVO/SVC30463 | CIL 3 Tails Pump 1 Suction Valve | Detail 3 | FL | 30
|  |  |  | XV 30464 | SV30464 | CIL 3 Tails Pump 1 Suction Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30465 | SVO/SVC30465 | CIL 3 Tails Pump 1 Discharge Valve | Detail 3 | FL | 30
|  |  |  | XV 30469 | SVO/SVC30469 | CIL 3 Tails Pump 2 Suction Valve | Detail 3 | FL | 30
|  |  |  | XV 30470 | SV30470 | CIL 3 Tails Pump 2 Suction Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30471 | SVO/SVC30471 | CIL 3 Tails Pump 2 Discharge Valve | Detail 3 | FL | 30
|  |  |  | XV 30483 | SV30483 | CIL 3 Tails Hopper Water Valve | Detail 7 | FC | 30
| F30-CP-411 | 2000-F30-PID-PR-10020 | Stage 2 | XV 30494 | SVO/SVC30494 | Acid Effluent & Fine Carbon Pump 1 Suction Valve | Detail 3 | FL | 30
|  |  |  | XV 30495 | SV30495 | Acid Effluent & Fine Carbon Pump 1 Suction Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30484 | SVO/SVC30484 | Acid Effluent & Fine Carbon Pump 2 Suction Valve | Detail 3 | FL | 30
|  |  |  | XV 30486 | SV30486 | Acid Effluent & Fine Carbon Pump 2 Suction Drain Valve | Detail 4 | FO | 30
|  |  |  | XV 30487 | SVO/SVC30487 | Acid Effluent & Fine Carbon Pump 2 Discharge Valve | Detail 3 | FL | 30
|  |  |  | XV 30496 | SVO/SVC30496 | Acid Effluent & Fine Carbon Pump 1 Discharge Valve | Detail 3 | FL | 30
| F30-CP-412 | 2000-F30-PID-PR-10016 | Stage 2 | XV 30597 | HV30597 | Milk Of Lime Ringmain Drain Valve 2 | Detail 12 | FL | 30
|  |  |  | XV 30598 | HV30598 | Milk Of Lime Ringmain Drain Valve 3 | Detail 12 | FL | 30
| F34-CP-401 | 2000-F34-PID-PR-10001 | Stage 1 | XV 34402 | SVO/SVC34402 | UFG Mill 1 Product Pump Suction Valve | Detail 3 | FL | 34
|  |  |  | XV 34403 | SV34403 | UFG Mill 1 Product Pump Suction Drain Valve | Detail 4 | FO | 34
| F35-CP-401 | 2000-F35-PID-PR-10001 | Stage 1 | XV 35431 | SV35431 | Filter Feed Tank A Isolation Valve | Detail 4 | FC | 35
|  |  |  | XV 35432 | SV35432 | Filter Feed Tank A Discharge Drain Valve | Detail 4 | FO | 35
|  |  |  | XV 35433 | SVO/SVC35433 | Filter Feed Tank A Discharge Flushing Water Valve | Detail 3 | FL | 35
|  |  | Stage 2 | XV 35427 | SV35427 | UFG Circuit 1 Feed Pump Discharge Drain Valve | Detail 4 | FO | 35
|  |  |  | XV 35429 | SVO/SVC35429 | UFG Circuit 1 Feed Pump Discharge Flushing Water Valve | Detail 3 | FL | 35
| F35-CP-402 | 2000-F35-PID-PR-10001 | Stage 2 | XV 35440 | SV35440 | UFG Circuit 3 Feed Pump Suction Isolation Valve | Detail 4 | FC | 35
|  |  |  | XV 35422 | SV35422 | UFG Circuit 2 Feed Pump Suction Isolation Valve | Detail 4 | FC | 35
|  |  |  | XV 35423 | SV35423 | UFG Circuit 2 Feed Pump Drain Valve | Detail 4 | FO | 35
|  |  |  | XV 35424 | SVO/SVC35424 | UFG Circuit 2 Feed Pump Flushing Water Valve | Detail 3 | FL | 35
|  |  |  | XV 35441 | SV35441 | UFG Circuit 3 Feed Pump Drain Valve | Detail 4 | FO | 35
|  |  |  | XV 35442 | SVO/SVC35442 | UFG Circuit 3 Feed Pump Flushing Water Valve | Detail 3 | FL | 35
| F65-CP-401 | 2000-F30-PID-PR-10017 | Stage 2 | XV 65405 | SVO/SVC65405 | CIL 3 Loaded Carbon Pump Suction Drain Valve | Detail 3 | FL | 65
|  |  |  | XV 65406 | SV65406 | CIL 3 Loaded Carbon Pump Water Eduction Valve | Detail 7 | FO | 65
|  |  |  | XV 65407 | SV65407 | CIL 3 Loaded Carbon Transfer Hopper Valve | Detail 4 | FC | 65
|  |  |  | XV 65416 | SVO/SVC65416 | CIL 3 Loaded Carbon Transfer Hopper Water Addition Valve | Detail 9 | FL | 65
|  |  |  | FCV 65413 | Manual Isolation | CIL3 Loaded Carbon Pump Transfer Water Addition Valve | Detail 1 | FL | 65
| F66-CP-401 | 2000-F81-PID-PR-10002 | Stage 1 | XV 66426 | HV66426 | Gravity Electrowinning Cell to Sludge Dewatering Cone Actuated Valve 1 | Detail 12 | FL | 66
|  |  |  | XV 66428 | HV66428 | Gravity Electrowinning Cell to Sludge Dewatering Cone Actuated Valve 2 | Detail 12 | FL | 66
|  |  | Stage 2 | XV 66412 | HV66412 | CIL 4 Electrowinning Cell 1 to Sludge Dewatering Cone Actuated Valve 2 | Detail 12 | FL | 66
|  |  |  | XV 66414 | HV66414 | CIL 4 Electrowinning Cell 2 to Sludge Dewatering Cone Actuated Valve 2 | Detail 12 | FL | 66
|  |  |  | XV 66411 | HV66411 | CIL 4 Electrowinning Cell 1 to Sludge Dewatering Cone Actuated Valve 1 | Detail 12 | FL | 66
|  |  |  | XV 66413 | HV66413 | CIL 4 Electrowinning Cell 2 to Sludge Dewatering Cone Actuated Valve 1 | Detail 12 | FL | 66
| F66-CP-402 | 2000-F81-PID-PR-10002 | Stage 1 | XV 66429 | SVO/SVC66429 | Gravity Electrowinning Pump to Gravity Electrowinning Cell Valve | Detail 9 | FL | 66
|  |  |  | XV 66430 | SVO/SVC66430 | Gravity Electrowinning Pump to Barren Eluate Tank Valve | Detail 9 | FL | 66
| F66-CP-403 | 2000-F81-PID-PR-10002 | Stage 2 | XV 66401 | SV66401 | CIL 4 Eluate Circulation Tank 1 Caustic Isolation Valve | Detail 8 | FC | 66
|  |  |  | XV 66402 | SVO/SVC66402 | CIL 4 Eluate Circulation Tank 1 Pregnant Eluate Isolation Valve | Detail 9 | FL | 66
|  |  |  | XV 66403 | SVO/SVC66403 | CIL 4 Eluate Circulation Tank 2 Pregnant Eluate Isolation Valve | Detail 9 | FL | 66
|  |  |  | XV 66408 | SV66408 | CIL 4 Eluate Circulation Tank 2 Caustic Isolation Valve | Detail 8 | FC | 66
|  |  |  | XV 66409 | SVO/SVC66409 | CIL 4 Eluate Circulation Tank 1 Pregnant Solution Isolation Valve | Detail 9 | FL | 66
|  |  |  | XV 66410 | SVO/SVC66410 | CIL 4 Eluate Circulation Tank 2 Pregnant Solution Isolation Valve | Detail 9 | FL | 66
|  |  |  | XV 66421 | SV66421 | Gravity Electrowinning Tank Caustic Isolation Valve | Detail 8 | FC | 66
| F66-CP-404 | 2000-F81-PID-PR-10002 | Stage 2 | XV 66415 | SVO/SVC66415 | CIL 4 Electrowinning Pump 1 to CIL 4 Electrowinning Cells Isolation Valve | Detail 9 | FL | 66
|  |  |  | XV 66416 | SVO/SVC66416 | CIL 4 Electrowinning Pump 1 to Barren Tank Isolation Valve | Detail 9 | FL | 66
|  |  |  | XV 66417 | SVO/SVC66417 | CIL 4 Electrowinning Pump 2 to CIL 4 Electrowinning Cells Isolation Valve | Detail 9 | FL | 66
|  |  |  | XV 66418 | SVO/SVC66418 | CIL 4 Electrowinning Pump 2 to Barren Tank Isolation Valve | Detail 9 | FL | 66
| F72-CP-401 | 2000-F72-PID-PR-10008 | Stage 1 | XV 72085 | SV72085 | Copper Sulphate Storage Tank Delivery Control Valve 1 | Detail 8 | FC | 72
|  |  |  | XV 72087 | SV72087 | Copper Sulphate Storage Tank Delivery Control Valve 2 | Detail 8 | FC | 72
|  |  |  | XV 72110 | SV72110 | Frother Storage Tank Feed Valve | Detail 8 | FC | 72
| F72-CP-402 | 2000-F24-PID-PR-10013 | Stage 1 | XV 72135 | SV72135 | Pax Storage Tank Feed Valve 1 | Detail 7 | FC | 72
|  |  |  | XV 72137 | SV72137 | Pax Storage Tank Feed Valve 2 | Detail 7 | FC | 72
|  |  |  | XV 72139 | SV72139 | Pax Storage Tank Discharge Valve | Detail 7 | FC | 72
| F72-CP-407 | 2000-F24-PID-PR-10016 | Stage 1 | XV 72203 | SV72203 | Hydrogen Peroxide Storage Tank Feed Valve | Detail 7 | FC | 72
|  |  | Stage 2 | XV 72240 | SVO/SVC72240 | Hydrogen Peroxide Dosing Pump Discharge Valve 1 | Detail 9 | FL | 72
|  |  |  | XV 72241 | SVO/SVC72241 | Hydrogen Peroxide Dosing Pump Discharge Valve 2 | Detail 9 | FL | 72
|  |  |  | XV 72242 | SVO/SVC72242 | Hydrogen Peroxide Dosing Pump Discharge Valve 3 | Detail 9 | FL | 72
| F72-CP-408 | 2000-F24-PID-PR-10016 | Stage 2 | XV 72441 | SVO/SVC72441 | Lime Ringmain Pump 1 Suction Valve | Detail 3 | FL | 72
|  |  |  | XV 72442 | SVO/SVC72442 | Lime Ringmain Pump 1 Suction Flushing Valve | Detail 3 | FL | 72
|  |  |  | XV 72443 | SVO/SVC72443 | Lime Ringmain Pump 1 Suction Drain Valve | Detail 3 | FL | 72
|  |  |  | XV 72444 | SVO/SVC72444 | Lime Ringmain Pump 1 Discharge Valve | Detail 3 | FL | 72
|  |  |  | XV 72452 | SVO/SVC72452 | Lime Ringmain Pump 1 Discharge Drain Valve | Detail 3 | FL | 72
| F72-CP-409 | 2000-F24-PID-PR-10029 | Stage 2 | XV 72536 | SVO/SVC72536 | Cyanide Storage Tank 1 Discharge Valve | Detail 9 | FL | 72
|  |  |  | XV 72537 | SVO/SVC72537 | Cyanide Storage Tank 2 Discharge Valve | Detail 9 | FL | 72
|  |  |  | XV 72538 | SVO/SVC72538 | Cyanide Storage Tank 1 Inlet Valve | Detail 9 | FL | 72
|  |  |  | XV 72539 | SVO/SVC72539 | Cyanide Storage Tank 2 Inlet Valve | Detail 9 | FL | 72
| F72-CP-410 | 2000-F24-PID-PR-10029 | Stage 2 | XV 72594 | SV72594 | Caustic Delivery to Caustic Storage Tank Inlet Valve | Detail 8 | FC | 72
|  |  |  | XV 72596 | SV72596 | Caustic Storage Tank Discharge Valve | Detail 7 | FC | 72
| F72-CP-411 | 2000-F24-PID-PR-10029 | Stage 2 | XV 72601 | SV72601 | Hydrochloric Acid Delivery to Acid Storage Tank Inlet Valve | Detail 8 | FC | 72
|  |  |  | XV 72614 | SV72614 | CIL 4 Acid Dilution Tank Scheme Water Inlet Valve | Detail 8 | FC | 72
|  |  |  | XV 72705 | SV72705 | Lead Nitrate Delivery to Lead Nitrate Storage Tank Valve | Detail 8 | FC | 72
|  |  |  | XV 72603 | SV72603 | Hydrochloric Acid Storage Tank Outlet Valve | Detail 7 | FC | 72
|  |  |  | FCV 72616 | Manual Isolation | CIL 4 Acid Dilution Tank Acid Inlet Flow Control Valve | Detail 1 | FC | 72
|  |  |  | XV 72637 | SV72637 | CIL 4 Acid Dilution Tank Acid Recirculation Valve | Detail 7 | FO | 72
|  |  |  | XV 72639 | SVO/SVC72639 | CIL 4 Acid Dilution Tank Acid Discharge Valve | Detail 9 | FL | 72
| F72-CP-413 | 2000-F24-PID-PR-10016 | Stage 2 | XV 72445 | SVO/SVC72445 | Lime Ringmain Pump 2 Suction Valve | Detail 3 | FL | 72
|  |  |  | XV 72446 | SVO/SVC72446 | Lime Ringmain Pump 2 Suction Flushing Valve | Detail 3 | FL | 72
|  |  |  | XV 72447 | SVO/SVC72447 | Lime Ringmain Pump 2 Suction Drain Valve | Detail 3 | FL | 72
|  |  |  | XV 72448 | SVO/SVC72448 | Lime Ringmain Pump 2 Discharge Valve | Detail 3 | FL | 72
|  |  |  | XV 72453 | SVO/SVC72453 | Lime Ringmain Pump 2 Discharge Drain Valve | Detail 3 | FL | 72
|  | 2000-F72-PID-PR-10003 | Stage 2 | XV 72464 | SV72464 | Milk of Lime Area Sump Pump 1 Flushing Valve | Detail 7 | FC | 72
| F72-CP-414 | 2000-F24-PID-PR-10029 | Stage 2 | XV 72541 | SV72541 | Cyanide Delivery to Cyanide Storage Tank 1 Inlet Valve | Detail 8 | FC | 72
|  |  |  | XV 72542 | SV72542 | Cyanide Delivery to Cyanide Storage Tank 2 Inlet Valve | Detail 8 | FC | 72

## Control Valve Type
Valve Package | (All)
Valve Class | Valve Size | Control Valve Code | Stage | Count of Valve TAG
VTWD1C1 | 50 | 50VTWD1C1-Double Acting-Positioner-KTM-MB11 | Stage 1 | 1
VTWD1C1 | 80 | 80VTWD1C1-Double Acting-Positioner | Stage 1 | 1
VTWD1C1 | 100 | 100VTWD1C1-Double Acting-Positioner | Stage 1 | 4
VTWD1C1 | 100 | 100VTWD1C1-Double Acting-Positioner | Stage 2 | 1

## Control Panel Count
Package | PP007
Tag Number | Stage | Count of Valve TAG
F13-CP-402 | Stage 1 | 4
F13-CP-403 | Stage 1 | 2
F13-CP-404 | Stage 1 | 7
F13-CP-405 | Stage 1 | 3
F13-CP-406 | Stage 1 | 2
F13-CP-407 | Stage 1 | 5
F13-CP-408 | Stage 1 | 1
F13-CP-409 | Stage 1 | 7
F13-CP-410 | Stage 1 | 5
F13-CP-411 | Stage 1 | 1
F13-CP-412 | Stage 1 | 2
F13-HU-407 | Stage 1 | 1
F14-CP-401 | Stage 1 | 4
F14-CP-402 | Stage 1 | 5
F16-CP-401 | Stage 1 | 6
F16-CP-403 | Stage 1 | 1
F17-CP-401 | Stage 1 | 6
F17-CP-402 | Stage 1 | 6
F17-CP-403 | Stage 1 | 5
F17-CP-404 | Stage 1 | 6
F17-CP-405 | Stage 1 | 2
| Stage 2 | 1
F17-CP-406 | Stage 1 | 2
F17-CP-407 | Stage 1 | 2
F17-HU-422 | Stage 1 | 1
F18-CP-401 | Stage 1 | 4
F18-CP-402 | Stage 1 | 4
F18-CP-403 | Stage 1 | 6
F18-CP-404 | Stage 1 | 2
F18-CP-405 | Stage 1 | 6
F18-CP-406 | Stage 1 | 8
F18-CP-407 | Stage 1 | 6
F18-CP-408 | Stage 1 | 2
F18-CP-409 | Stage 1 | 6
F18-CP-410 | Stage 1 | 6
F21-CP-401 | Stage 2 | 6
F21-CP-402 | Stage 2 | 6
F21-CP-403 | Stage 2 | 6
F22-CP-401 | Stage 2 | 7
F22-CP-402 | Stage 2 | 10
F22-CP-403 | Stage 2 | 4
F22-CP-404 | Stage 2 | 7
F22-CP-405 | Stage 2 | 7
F22-CP-406 | Stage 2 | 1
F22-CP-407 | Stage 2 | 5
F23-CP-401 | Stage 1 | 6
F23-CP-402 | Stage 1 | 7
F23-CP-403 | Stage 1 | 7
F23-CP-404 | Stage 1 | 6
F23-CP-405 | Stage 1 | 3
| Stage 2 | 2
F24-CP-401 | Stage 1 | 2
F24-CP-402 | Stage 1 | 4
F24-CP-403 | Stage 1 | 4
F24-CP-404 | Stage 1 | 4
F28-CP-401 | Stage 1 | 9
F28-CP-402 | Stage 1 | 4
F28-CP-403 | Stage 1 | 5
F28-CP-404 | Stage 1 | 6
F28-CP-406 | Stage 1 | 9
F28-CP-407 | Stage 1 | 10
F30-CP-401 | Stage 1 | 6
F30-CP-402 | Stage 1 | 4
F30-CP-403 | Stage 2 | 2
F30-CP-404 | Stage 2 | 5
F30-CP-405 | Stage 2 | 6
F30-CP-406 | Stage 2 | 5
F30-CP-407 | Stage 2 | 6
F30-CP-408 | Stage 2 | 6
F30-CP-409 | Stage 2 | 7
F30-CP-410 | Stage 2 | 7
F30-CP-411 | Stage 2 | 6
F30-CP-412 | Stage 2 | 2
F34-CP-401 | Stage 1 | 2
F35-CP-401 | Stage 1 | 3
| Stage 2 | 2
F35-CP-402 | Stage 2 | 6
F65-CP-401 | Stage 2 | 5
F66-CP-401 | Stage 1 | 2
| Stage 2 | 4
F66-CP-402 | Stage 1 | 2
F66-CP-403 | Stage 2 | 7
F66-CP-404 | Stage 2 | 4
F72-CP-401 | Stage 1 | 3
F72-CP-402 | Stage 1 | 3
F72-CP-407 | Stage 1 | 1
| Stage 2 | 3
F72-CP-408 | Stage 2 | 5
F72-CP-409 | Stage 2 | 4
F72-CP-410 | Stage 2 | 2
F72-CP-411 | Stage 2 | 7
F72-CP-413 | Stage 2 | 6
F72-CP-414 | Stage 2 | 2

## Materials of construction
Valve TAG | Location Description | Fluid | Model No. | General Arrangement Drawing
PRV 72091 | Copper Sulphate Dosing Pump 1 Pressure Release Valve | Copper Sulphate | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72092 | Copper Sulphate Dosing Pump 2 Pressure Release Valve | Copper Sulphate | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72101 | Copper Sulphate Dosing Pump 3 Pressure Release Valve | Copper Sulphate | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72115 | Frother Dosing Pump 1 Pressure Release Valve | Lupofroth 168 | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72116 | Frother Dosing Pump 2 Pressure Release Valve | Lupofroth 168 | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72117 | Frother Dosing Pump 3 Pressure Release Valve | Lupofroth 168 | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72118 | Frother Dosing Pump 4 Pressure Release Valve | Lupofroth 168 | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72119 | Frother Dosing Pump 5 Pressure Release Valve | Lupofroth 168 | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72151 | PAX Dosing Pump 4 Pressure Release Valve | Potassium Amyl Xanthate | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72153 | PAX Dosing Pump 5 Pressure Release Valve | Potassium Amyl Xanthate | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72165 | Antiscalant Dosing Pump 1 Pressure Release Valve | Antiscalant | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72205 | Hydrogen Peroxide Delivery Pressure Release Valve | Hydrogen Peroxide | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72208 | Hydrogen Peroxide Storage Tank Outlet Pressure Release Valve | Hydrogen Peroxide | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72223 | Hydrogen Peroxide Dosing Pump 1 Pressure Release Valve | Hydrogen Peroxide | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72224 | Hydrogen Peroxide Dosing Pump 2 Pressure Release Valve | Hydrogen Peroxide | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72225 | Hydrogen Peroxide Dosing Pump 3 Pressure Release Valve | Hydrogen Peroxide | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72226 | Hydrogen Peroxide Inline Mixer 1 Pressure Release Valve | Hydrogen Peroxide | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72230 | Hydrogen Peroxide Inline Mixer 2 Pressure Release Valve | Hydrogen Peroxide | Roma Fig-160-2N | 2000-PP007-B02-10406
PRV 72141 | PAX Dosing Pump 1 Pressure Release Valve | Potassium Amyl Xanthate | Roma Fig-160-2N | 2000-PP007-B02-10407
PRV 72142 | PAX Dosing Pump 2 Pressure Release Valve | Potassium Amyl Xanthate | Roma Fig-160-2N | 2000-PP007-B02-10407
PRV 72143 | PAX Dosing Pump 3 Pressure Release Valve | Potassium Amyl Xanthate | Roma Fig-160-2N | 2000-PP007-B02-10407
PRV 72481 | Concentrae Pre-Leach Thickener Flocculant Dosing Pump Pressure Release Valve | Lupofroth 168 | Roma Fig-160-2N | 2000-PP007-B02-10412
PRV 72482 | Thickeners Standby Flocculant Dosing Pump Pressure Release Valve | Lupofroth 168 | Roma Fig-160-2N | 2000-PP007-B02-10412
PRV 72483 | Concentrate Thickener Flocculant Dosing Pump Pressure Release Valve | Lupofroth 168 | Roma Fig-160-2N | 2000-PP007-B02-10412
PRV 72710 | Lead Nitrate Dosing Pump 2 Pressure Release Valve | Lead Nitrate | Roma Fig-160-2N | 2000-PP007-B02-10412
PRV 72711 | Lead Nitrate Dosing Pump 1 Pressure Release Valve | Lead Nitrate | Roma Fig-160-2N | 2000-PP007-B02-10412
PRV 22148 | CIL 4 Elution Pumps Pressure Relief Valve | Pregnant Eluate up to 150*C | Roma Fig-161 | 2000-PP007-B02-10413
PRV 22041 | CIL 4 Elution & Acid Wash Column Pressure Relief Valve | Hydrochloric Acid up to 150*C | Roma Fig-161 | 2000-PP007-B02-10414
PRV 72051 | Flotation Tailings Thickener Flocculant Dosing Pump 1 Pressure Release Valve | Lupofroth 168 | Roma Fig-161 | 2000-PP007-B02-10414
PRV 72052 | Flotation Tailings Thickener Flocculant Dosing Pump 2 Pressure Release Valve | Lupofroth 168 | Roma Fig-161 | 2000-PP007-B02-10414

## Tubing change to 12mm
Item | Valve TAG | Valve Size | Valve Class | Location Description | P&ID | Panel | Panel Drawing | Solenoid Tag
1 | FCV 13075A | 300 | VBD1S4 | Primary Cyclone Feed Hopper Process Water 1 | 2000-F13-PID-PR-10002 | F13-CP-403 | 2000-PP007-B02-10302 | Manual Isolation
2 | FCV 13075B | 300 | VBD1S4 | Primary Cyclone Feed Hopper Process Water 2 | 2000-F13-PID-PR-10002 | F13-CP-403 | 2000-PP007-B02-10302 | Manual Isolation
3 | FCV 13121 | 300 | VBFD1S1 | SAG Mill Feed Box Process Water | 2000-F13-PID-PR-10003 | F13-CP-407 | 2000-PP007-B02-10306 | Manual Isolation
4 | FCV 13141 | 250 | VBFD1S1 | Ball Mill Feed Chute Process Water | 2000-F13-PID-PR-10004 | F13-CP-407 | 2000-PP007-B02-10306 | Manual Isolation
5 | XV 13077 | 300 | VKGD1L1 | Primary Cyclone Feed Hopper Drain | 2000-F13-PID-PR-10002 | F13-CP-404 | 2000-PP007-B02-10303 | SV13077
6 | XV 13081 | 300 | VKGD1C1 | Cyclone Feed Pump Suction Drain | 2000-F13-PID-PR-10002 | F13-CP-404 | 2000-PP007-B02-10303 | SV13081
7 | XV 13083 | 400 | VKGE1C1 | Cyclone Feed Pump Suction Process Water | 2000-F13-PID-PR-10002 | F13-CP-404 | 2000-PP007-B02-10303 | SV13083
8 | XV 13084 | 500 | VKGE1C1 | Cyclone Feed Pump Discharge Drain | 2000-F13-PID-PR-10002 | F13-CP-404 | 2000-PP007-B02-10303 | SV13084
9 | XV 13114 | 750 | VKGD1C1 | Cyclone Underflow Boil Box to Ball Mill Feed Box 1 Line 1 | 2000-F13-PID-PR-10002 | F13-CP-407 | 2000-PP007-B02-10306 | SVO/SVC13114
10 | XV 13115 | 750 | VKGD1C1 | Cyclone Underflow Boil Box to Ball Mill Feed Box 1 Line 2 | 2000-F13-PID-PR-10002 | F13-CP-407 | 2000-PP007-B02-10306 | SVO/SVC13115
11 | XV 13116 | 750 | VKGD1C1 | Cyclone Underflow Boil Box to Sag Mill Feed Box | 2000-F13-PID-PR-10002 | F13-CP-407 | 2000-PP007-B02-10306 | SVO/SVC13116
12 | XV 13382 | 250 | VKGD1L1 | Trash Dewatering Screen Underflow Pump Suction Valve | 2000-F13-PID-PR-10007 | F16-CP-401 | 2000-PP007-B02-10314 | SVO/SVC13382
13 | XV 13384 | 500 | VKGD1L1 | Trash Dewatering Screen Bypass | 2000-F13-PID-PR-10007 | F13-CP-406 | 2000-PP007-B02-10305 | SV13384
14 | XV 14031 | 400 | VKGD1C1 | Gravity Concentrator 1 Feed Valve | 2000-F14-PID-PR-10001 | F14-CP-401 | 2000-PP007-B02-10312 | SVO/SVC14031
15 | XV 14041 | 400 | VKGD1C1 | Gravity Concentrator 2 Feed Valve | 2000-F14-PID-PR-10001 | F14-CP-401 | 2000-PP007-B02-10312 | SVO/SVC14041
16 | XV 14051 | 400 | VKGD1C1 | Gravity Concentrator 1 Feed Bypass to Tails Launder Valve | 2000-F14-PID-PR-10001 | F14-CP-401 | 2000-PP007-B02-10312 | SV14051
17 | XV 14052 | 400 | VKGD1C1 | Gravity Concentrator 2 Feed Bypass to Tails Launder Valve | 2000-F14-PID-PR-10001 | F14-CP-401 | 2000-PP007-B02-10312 | SV14052
18 | XV 16122 | 300 | VKGD1L1 | Flotation Cells Drain Pump Isolation Valve | 2000-F16-PID-PR-10003 | F17-CP-404 | 2000-PP007-B02-10319 | SVO/SVC16122
19 | FCV 17127 | 350 | VPID1L1 | Flotation Tailings Thickener Underflow Pumps CIL 2 Feed Box Valve | 2000-F17-PID-PR-10002 | F17-CP-405 | 2000-PP007-B02-10320 | Manual Isolation
20 | FCV 17128 | 350 | VPID1L1 | Flotation Tailings Thickener Underflow Pumps CIL 3 Feed Box Valve | 2000-F17-PID-PR-10002 | F17-CP-405 | 2000-PP007-B02-10320 | Manual Isolation
21 | FCV 17130 | 400 | VPID1L1 | Flotation Tailings Thickener Underflow Pumps to Final Tails Tank Pinch Valve | 2000-F17-PID-PR-10002 | F17-CP-406 | 2000-PP007-B02-10321 | Manual Isolation
22 | XV 17091 | 600 | VKGD1L1 | Flotation Tailings Thickener Underflow Cone Discharge Valve 1 | 2000-F17-PID-PR-10002 | F17-CP-401 | 2000-PP007-B02-10316 | SV17091
23 | XV 17092 | 600 | VKGD1L1 | Flotation Tailings Thickener Underflow Cone Discharge Valve 2 | 2000-F17-PID-PR-10002 | F17-CP-401 | 2000-PP007-B02-10316 | SV17092
24 | XV 17093 | 600 | VKGD1L1 | Flotation Tailings Thickener Underflow Cone Discharge Valve 3 | 2000-F17-PID-PR-10002 | F17-CP-401 | 2000-PP007-B02-10316 | SV17093
25 | XV 17094 | 600 | VKGD1L1 | Flotation Tailings Thickener Underflow Cone Discharge Valve 4 | 2000-F17-PID-PR-10002 | F17-CP-401 | 2000-PP007-B02-10316 | SV17094
26 | XV 17102 | 300 | VKGD1L1 | Flotation Tailings Thickener Underflow Pump 1 Discharge Drain Valve | 2000-F17-PID-PR-10002 | F17-CP-402 | 2000-PP007-B02-10317 | SV17102
27 | XV 17103 | 750 | VKGD1L2 | Flotation Tailings Thickener Underflow Pump 1 Discharge Valve | 2000-F17-PID-PR-10002 | F17-CP-402 | 2000-PP007-B02-10317 | SVO/SVC17103
28 | XV 17112 | 300 | VKGD1L1 | Flotation Thickener Underflow Pump 2 Discharge Drain Valve | 2000-F17-PID-PR-10002 | F17-CP-402 | 2000-PP007-B02-10317 | SV17112
29 | XV 17113 | 750 | VKGD1L2 | Flotation Thickener Underflow Pump 2 Discharge Valve | 2000-F17-PID-PR-10002 | F17-CP-402 | 2000-PP007-B02-10317 | SVO/SVC17113
30 | XV 17123 | 750 | VKGD1L2 | Flotation Tailings Thickener Underflow Discharge Header Valve | 2000-F17-PID-PR-10002 | F17-CP-403 | 2000-PP007-B02-10318 | SVO/SVC17123
31 | XV 17124 | 250 | VKGD1L1 | Flotation Tailings Thickener Underflow Pumps Discharge Header Drain Valve | 2000-F17-PID-PR-10002 | F17-CP-403 | 2000-PP007-B02-10318 | SV17124
32 | XV 17125 | 500 | VKGD1L1 | Flotation Tailings Thickener Underflow Pumps Flotation Tailings Thickener Recirculation Bypass Valve | 2000-F17-PID-PR-10002 | F17-CP-403 | 2000-PP007-B02-10318 | SVO/SVC17125
33 | XV 17131 | 400 | VKGD1L1 | Flotation Tailings Thickener Underflow Pumps Discharge Header Flushing Valve | 2000-F17-PID-PR-10002 | F17-CP-403 | 2000-PP007-B02-10318 | SVO/SVC17131
34 | XV 17132 | 400 | VKGD1L1 | Flotation Tailings Thickener Underflow Pumps to Final Tails Tank Isolation Valve | 2000-F17-PID-PR-10002 | F17-CP-406 | 2000-PP007-B02-10321 | SVO/SVC17132
35 | LCV 18011B | 500 | N/A | Cleaner Flotation Cell Feed Hopper Recycle Level Control Valve | 2000-F18-PID-PR-10002 | F18-CP-401 | 2000-PP007-B02-10323 | Manual Isolation
36 | LCV 18051 | 500 | N/A | Cleaner Flotation Cell Tank Slurry Level Control Valve | 2000-F18-PID-PR-10002 | F18-CP-401 | 2000-PP007-B02-10323 | Manual Isolation
37 | LCV 18201B | 500 | N/A | Cleaner Scavenger Recycle Level Control Valve | 2000-F18-PID-PR-10004 | F18-CP-402 | 2000-PP007-B02-10324 | Manual Isolation
38 | LCV 18251 | 500 | N/A | Cleaner-Scavenger Flotation Cell Tank Slurry Level Control Valve | 2000-F18-PID-PR-10004 | F18-CP-402 | 2000-PP007-B02-10324 | Manual Isolation
39 | XV 18021 | 400 | VKGD1L1 | Final Concentrate Pump 1 Suction Valve | 2000-F18-PID-PR-10001 | F18-CP-406 | 2000-PP007-B02-10328 | SVO/SVC18021
40 | XV 18023 | 250 | VKGD1L1 | Final Concentrate Pump 1 Discharge Valve | 2000-F18-PID-PR-10001 | F18-CP-406 | 2000-PP007-B02-10328 | SVO/SVC18023
41 | XV 18024 | 400 | VKGD1L1 | Final Concentrate Pump 2 Suction Valve | 2000-F18-PID-PR-10001 | F18-CP-406 | 2000-PP007-B02-10328 | SVO/SVC18024
42 | XV 18026 | 250 | VKGD1L1 | Final Concentrate Pump 2 Discharge Valve | 2000-F18-PID-PR-10001 | F18-CP-406 | 2000-PP007-B02-10328 | SVO/SVC18026
43 | XV 18031 | 600 | VKGD1L1 | Cleaner Flotation Cell Recirculation Pump 1 Suction Valve | 2000-F18-PID-PR-10001 | F18-CP-407 | 2000-PP007-B02-10329 | SVO/SVC18031
44 | XV 18033 | 500 | VKGD1C1 | Cleaner Flotation Cell Recirculation Pump 1 Discharge Valve | 2000-F18-PID-PR-10001 | F18-CP-407 | 2000-PP007-B02-10329 | SVO/SVC18033
45 | XV 18034 | 600 | VKGD1L1 | Cleaner Flotation Cell Recirculation Pump 2 Suction Valve | 2000-F18-PID-PR-10001 | F18-CP-407 | 2000-PP007-B02-10329 | SVO/SVC18034
46 | XV 18036 | 500 | VKGD1C1 | Cleaner Flotation Cell Recirculation Pump 2 Discharge Valve | 2000-F18-PID-PR-10001 | F18-CP-407 | 2000-PP007-B02-10329 | SVO/SVC18036
47 | XV 18221 | 600 | VKGD1L1 | Cleaner Scavenger Flotation Cell Recirculation Pump 1 Suction Valve | 2000-F18-PID-PR-10003 | F18-CP-403 | 2000-PP007-B02-10325 | SVO/SVC18221
48 | XV 18223 | 500 | VKGD1C1 | Cleaner Scavenger Flotation Cell Recirculation Pump 1 Discharge Valve | 2000-F18-PID-PR-10003 | F18-CP-403 | 2000-PP007-B02-10325 | SVO/SVC18223
49 | XV 18224 | 600 | VKGD1L1 | Cleaner Scavenger Flotation Cell Recirculation Pump 2 Suction Valve | 2000-F18-PID-PR-10003 | F18-CP-403 | 2000-PP007-B02-10325 | SVO/SVC18224
50 | XV 18226 | 500 | VKGD1C1 | Cleaner Scavenger Flotation Cell Recirculation Pump 2 Discharge Valve | 2000-F18-PID-PR-10003 | F18-CP-403 | 2000-PP007-B02-10325 | SVO/SVC18226
51 | XV 18231 | 450 | VKGD1L1 | Cleaner Scavenger Flotation Cell Tails Pump 1 Suction Valve | 2000-F18-PID-PR-10003 | F18-CP-405 | 2000-PP007-B02-10327 | SVO/SVC18231
52 | XV 18233 | 400 | VKGD1L1 | Cleaner Scavenger Flotation Cell Tails Pump 1 Discharge Valve | 2000-F18-PID-PR-10003 | F18-CP-405 | 2000-PP007-B02-10327 | SVO/SVC18233
53 | XV 18234 | 450 | VKGD1L1 | Cleaner Scavenger Flotation Cell Tails Pump 2 Suction Valve | 2000-F18-PID-PR-10003 | F18-CP-405 | 2000-PP007-B02-10327 | SVO/SVC18234
54 | XV 18236 | 400 | VKGD1L1 | Cleaner Scavenger Flotation Cell Tails Pump 2 Discharge Valve | 2000-F18-PID-PR-10003 | F18-CP-405 | 2000-PP007-B02-10327 | SVO/SVC18236
55 | XV 18241 | 400 | VKGD1C1 | Cleaner Scavenger Tails Discharge to Flotation Discharge Box Valve | 2000-F18-PID-PR-10003 | F18-CP-409 | 2000-PP007-B02-10331 | SVO/SVC18241
56 | XV 18242 | 400 | VKGD1C1 | Cleaner Scavenger Tails Discharge to Scavenger Flotation Cell 1 Valve | 2000-F18-PID-PR-10003 | F18-CP-409 | 2000-PP007-B02-10331 | SVO/SVC18242
57 | XV 21051 | 400 | VKGD1L1 | CIL 4 Tank 1 Oxygen Injection Pump Suction Valve | 2000-F21-PID-PR-10001 | F21-CP-402 | 2000-PP007-B02-10357 | SV21051
58 | XV 21053 | 350 | VKGD1L1 | CIL 4 Tank 1 Oxygen Injection Pump Discharge Valve | 2000-F21-PID-PR-10001 | F21-CP-402 | 2000-PP007-B02-10357 | SV21053
59 | XV 21091 | 400 | VKGD1L1 | CIL 4 Tank 2 Oxygen Injection Pump Suction Valve | 2000-F21-PID-PR-10001 | F21-CP-403 | 2000-PP007-B02-10358 | SV21091
60 | XV 21093 | 350 | VKGD1L1 | CIL 4 Tank 2 Oxygen Injection Pump Discharge Valve | 2000-F21-PID-PR-10001 | F21-CP-403 | 2000-PP007-B02-10358 | SV21093
61 | XV 22251 | 250 | VKGD1L1 | CIL 4 Carbon Regeneration Kiln Feed Hopper Discharge Valve | 2000-F22-PID-PR-10005 | F22-CP-405 | 2000-PP007-B02-10363 | SV22251
62 | FCV 23405 | 350 | VBFD1S1 | Final Tails Tank Saline Water Feed Flow Control Valve | 2000-F23-PID-PR-10001 | F23-CP-402 | 2000-PP007-B02-10334 | Manual Isolation
63 | FCV 23456 | 350 | VBFE1S1 | FIM 1 Valve Station Feed Flow Control Valve | 2000-F23-PID-PR-10002 | F23-CP-405 | 2000-PP007-B02-10388 | Manual Isolation
64 | PCV 23410 | 400 | VBFD1S1 | Final Tails Pump 1 Upstream Flushing Valve | 2000-F23-PID-PR-10002 | F23-CP-402 | 2000-PP007-B02-10334 | No Solenoid
65 | PCV 23423 | 400 | VBFD1S1 | Final Tails Pump 2 Upstream Flushing Valve | 2000-F23-PID-PR-10002 | F23-CP-402 | 2000-PP007-B02-10334 | No Solenoid
66 | PCV 23434 | 400 | VBFD1S1 | Final Tails Pump 3 Upstream Flushing Valve | 2000-F23-PID-PR-10002 | F23-CP-404 | 2000-PP007-B02-10336 | No Solenoid
67 | PCV 23445 | 400 | VBFD1S1 | Final Tails Pump 4 Upstream Flushing Valve | 2000-F23-PID-PR-10002 | F23-CP-404 | 2000-PP007-B02-10336 | No Solenoid
68 | XV 23402 | 250 | VKGD1L1 | Final Tails Tank Drain Valve | 2000-F23-PID-PR-10001 | F23-CP-403 | 2000-PP007-B02-10335 | SVO/SVC23402
69 | XV 23411 | 600 | VKGD1L1 | Final Tails Pump 1 Suction Valve | 2000-F23-PID-PR-10002 | F23-CP-401 | 2000-PP007-B02-10333 | SV23411
70 | XV 23412 | 400 | VKGD1L1 | Final Tails Pump 1 Suction Flushing Water Valve | 2000-F23-PID-PR-10002 | F23-CP-401 | 2000-PP007-B02-10333 | SV23412
71 | XV 23414 | 600 | VKGE1L1 | Final Tails Pump 1 Discharge Valve | 2000-F23-PID-PR-10002 | F23-CP-402 | 2000-PP007-B02-10334 | SVO/SVC23414
72 | XV 23415 | 300 | VKGE1L1 | Final Tails Pump 1 Discharge Flushing Water Valve | 2000-F23-PID-PR-10002 | F23-CP-402 | 2000-PP007-B02-10334 | SV23415
73 | XV 23424 | 600 | VKGD1L1 | Final Tails Pump 2 Suction Valve | 2000-F23-PID-PR-10002 | F23-CP-401 | 2000-PP007-B02-10333 | SV23424
74 | XV 23425 | 400 | VKGD1L1 | Final Tails Pump 2 Suction Flushing Water Valve | 2000-F23-PID-PR-10002 | F23-CP-401 | 2000-PP007-B02-10333 | SV23425
75 | XV 23427 | 600 | VKGE1L1 | Final Tails Pump 2 Discharge Valve | 2000-F23-PID-PR-10002 | F23-CP-402 | 2000-PP007-B02-10334 | SVO/SVC23427
76 | XV 23428 | 300 | VKGE1L1 | Final Tails Pump 2 Discharge Flushing Water Valve | 2000-F23-PID-PR-10002 | F23-CP-402 | 2000-PP007-B02-10334 | SV23428
77 | XV 23435 | 600 | VKGD1L1 | Final Tails Pump 3 Suction Valve | 2000-F23-PID-PR-10002 | F23-CP-403 | 2000-PP007-B02-10335 | SV23435
78 | XV 23436 | 400 | VKGD1L1 | Final Tails Pump 3 Suction Flushing Water Valve | 2000-F23-PID-PR-10002 | F23-CP-403 | 2000-PP007-B02-10335 | SV23436
79 | XV 23438 | 600 | VKGE1L1 | Final Tails Pump 3 Discharge Valve | 2000-F23-PID-PR-10002 | F23-CP-404 | 2000-PP007-B02-10336 | SVO/SVC23438
80 | XV 23439 | 300 | VKGE1L1 | Final Tails Pump 3 Discharge Flushing Water Valve | 2000-F23-PID-PR-10002 | F23-CP-404 | 2000-PP007-B02-10336 | SV23439
81 | XV 23446 | 600 | VKGD1L1 | Final Tails Pump 4 Suction Valve | 2000-F23-PID-PR-10002 | F23-CP-403 | 2000-PP007-B02-10335 | SV23446
82 | XV 23447 | 400 | VKGD1L1 | Final Tails Pump 4 Suction Flushing Water Valve | 2000-F23-PID-PR-10002 | F23-CP-403 | 2000-PP007-B02-10335 | SV23447
83 | XV 23449 | 600 | VKGE1L1 | Final Tails Pump 4 Discharge Valve | 2000-F23-PID-PR-10002 | F23-CP-404 | 2000-PP007-B02-10336 | SVO/SVC23449
84 | XV 23450 | 300 | VKGE1L1 | Final Tails Pump 4 Discharge Flushing Water Valve | 2000-F23-PID-PR-10002 | F23-CP-404 | 2000-PP007-B02-10336 | SV23450
85 | XV 23457 | 350 | VKGE1L1 | FIM 1 Valve Station Feed Valve 1 | 2000-F23-PID-PR-10002 | F23-CP-405 | 2000-PP007-B02-10388 | SV23457
86 | XV 23458 | 250 | VKGE1L1 | FIM 1 Valve Station Feed Valve 2 | 2000-F23-PID-PR-10002 | F23-CP-405 | 2000-PP007-B02-10388 | SV23458
87 | LCV 24401 | 450 | VBFD1S1 | Process Water Tank Level Control Valve | 2000-F24-PID-PR-10001 | F24-CP-401 | 2000-PP007-B02-10337 | Manual Isolation
88 | XV 24402 | 500 | VBFD1S1 | Process Water Tank Saline Water Feed Valve | 2000-F24-PID-PR-10001 | F24-CP-401 | 2000-PP007-B02-10337 | SV24402
89 | XV 24411 | 750 | VBFD1L6 | Mill Water Pump 1 Suction Valve | 2000-F24-PID-PR-10001 | F24-CP-402 | 2000-PP007-B02-10338 | SVO/SVC24411
90 | XV 24412 | 750 | VBFD1L6 | Mill Water Pump 1 Discharge Valve | 2000-F24-PID-PR-10001 | F24-CP-402 | 2000-PP007-B02-10338 | SVO/SVC24412
91 | XV 24413 | 750 | VBFD1L6 | Mill Water Pump 2 Suction Valve | 2000-F24-PID-PR-10001 | F24-CP-402 | 2000-PP007-B02-10338 | SVO/SVC24413
92 | XV 24414 | 750 | VBFD1L6 | Mill Water Pump 2 Discharge Valve | 2000-F24-PID-PR-10001 | F24-CP-402 | 2000-PP007-B02-10338 | SVO/SVC24414
93 | XV 24421 | 600 | VBFD1L2 | High Pressure Process Water Pump 1 Suction Valve | 2000-F24-PID-PR-10001 | F24-CP-403 | 2000-PP007-B02-10339 | SVO/SVC24421
94 | XV 24422 | 500 | VBFE1L2 | High Pressure Process Water Pump 1 Discharge Valve | 2000-F24-PID-PR-10001 | F24-CP-403 | 2000-PP007-B02-10339 | SVO/SVC24422
95 | XV 24423 | 600 | VBFD1L2 | High Pressure Process Water Pump 2 Suction Valve | 2000-F24-PID-PR-10001 | F24-CP-403 | 2000-PP007-B02-10339 | SVO/SVC24423
96 | XV 24424 | 500 | VBFE1L2 | High Pressure Process Water Pump 2 Discharge Valve | 2000-F24-PID-PR-10001 | F24-CP-403 | 2000-PP007-B02-10339 | SVO/SVC24424
97 | XV 24501 | 350 | VBFD1S2 | Raw Water Feed Booster Pump 1 Suction Valve | 2000-F24-PID-PR-10017 | F24-CP-404 | 2000-PP007-B02-10340 | SVO/SVC24501
98 | XV 24502 | 250 | VBFD1S2 | Raw Water Feed Booster Pump 1 Discharge Valve | 2000-F24-PID-PR-10017 | F24-CP-404 | 2000-PP007-B02-10340 | SVO/SVC24502
99 | XV 24503 | 350 | VBFD1S2 | Raw Water Feed Booster Pump 2 Suction Valve | 2000-F24-PID-PR-10017 | F24-CP-404 | 2000-PP007-B02-10340 | SVO/SVC24503
100 | XV 24504 | 250 | VBFD1S2 | Raw Water Feed Booster Pump 2 Discharge Valve | 2000-F24-PID-PR-10017 | F24-CP-404 | 2000-PP007-B02-10340 | SVO/SVC24504
101 | XCV 28012 | 300 | VKGD1L1 | UFG Mill 2 Media Hopper Discharge Valve | 2000-F28-PID-PR-10001 | F28-CP-402 | 2000-PP007-B02-10342 | No Solenoid
102 | XCV 28212 | 300 | VKGD1L1 | UFG Mill 3 Media Hopper Discharge Valve | 2000-F28-PID-PR-10003 | F28-CP-402 | 2000-PP007-B02-10342 | No Solenoid
103 | XV 28092 | 300 | VKGD1L1 | UFG Mill 2 Discharge Pump 1 Suction Valve | 2000-F28-PID-PR-10002 | F28-CP-406 | 2000-PP007-B02-10345 | SVO/SVC28092
104 | XV 28282 | 300 | VKGD1L1 | UFG Mill 3 Discharge Pump Suction Valve | 2000-F28-PID-PR-10004 | F28-CP-401 | 2000-PP007-B02-10341 | SVO/SVC28282
105 | XV 28322 | 300 | VKGD1L1 | UFG Product Pump 1 Suction Valve | 2000-F28-PID-PR-10005 | F28-CP-407 | 2000-PP007-B02-10346 | SV28322
106 | XV 28324 | 250 | VKGD1L1 | UFG Product Pump 1 Discharge Valve | 2000-F28-PID-PR-10005 | F28-CP-407 | 2000-PP007-B02-10346 | SVO/SVC28324
107 | XV 28325 | 300 | VKGD1L1 | UFG Product Pump 2 Suction Valve | 2000-F28-PID-PR-10005 | F28-CP-407 | 2000-PP007-B02-10346 | SV28325
108 | XV 28327 | 250 | VKGD1L1 | UFG Product Pump 2 Discharge Valve | 2000-F28-PID-PR-10005 | F28-CP-407 | 2000-PP007-B02-10346 | SVO/SVC28327
109 | FV 30608A | 400 | N/A | Concentrate Thickener Underflow Cone Discharge Valve 1 | 2000-F30-PID-PR-10001 | F30-CP-401 | 2000-PP007-B02-10347 | SV30608A
110 | FV 30608B | 400 | N/A | Concentrate Thickener Underflow Cone Discharge Valve 2 | 2000-F30-PID-PR-10001 | F30-CP-401 | 2000-PP007-B02-10347 | SV30608B
111 | XV 30550 | 400 | VKGD1L1 | CIL 2 Oxygen Injection Pump 1 Suction Valve | 2000-F30-PID-PR-10007 | F30-CP-405 | 2000-PP007-B02-10368 | SV30550
112 | XV 30562 | 350 | VKGD1L1 | CIL 2 Oxygen Injection Pump 1 Discharge Valve | 2000-F30-PID-PR-10007 | F30-CP-405 | 2000-PP007-B02-10368 | SV30562
113 | XV 30565 | 400 | VKGD1L1 | CIL 2 Oxygen Injection Pump 2 Suction Valve | 2000-F30-PID-PR-10007 | F30-CP-406 | 2000-PP007-B02-10369 | SV30565
114 | XV 30577 | 350 | VKGD1L1 | CIL 2 Oxygen Injection Pump 2 Discharge Valve | 2000-F30-PID-PR-10007 | F30-CP-406 | 2000-PP007-B02-10369 | SV30577
115 | XV 72441 | 250 | VKGD1L1 | Lime Ringmain Pump 1 Suction Valve | 2000-F72-PID-PR-10003 | F72-CP-408 | 2000-PP007-B02-10381 | SVO/SVC72441
116 | XV 72445 | 250 | VKGD1L1 | Lime Ringmain Pump 2 Suction Valve | 2000-F72-PID-PR-10003 | F72-CP-413 | 2000-PP007-B02-10386 | SVO/SVC72445
117 | XV 75608 | 400 | VKGE1L1 | Tails Flushing HP Process Water | 2000-F75-PID-PR-25008 | F23-CP-405 | 2000-PP007-B02-10388 | SV75608
118 | XV 75609 | 400 | VKGE1L1 | Tails Flushing HP Process Water | 2000-F75-PID-PR-25008 | F23-CP-405 | 2000-PP007-B02-10388 | SV75609

## Pressure ratings
Pipe spec | Rating (kPag)
MS1 | 700
MS2 | 1400
MSG1 | 700
MSG2 | 1400
MSG3 | 1400
PE8 | 700
PE10 | 700
PE12.5 | 970
PE16 | 1200
PE20 | 1400
RL1 | 700
RL2 | 1400
RL3 | 700
SS1 | 700
SS2 | 1400
SS3 | 1400
SS4 | 700
SS5 | 1400
SS6 | 1400
SS7 | 700

## Emerson data
Control Valve Code | Order | Manuf. | Model | Actuator Manufacturer | Actuator Model | Positioner / Limit Switch Box / Proximity Sensor
100VBFD1S1-Double Acting-Positioner | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-006 | SMC IP8100 031 J (4-20mA)
100VBFD1S2-Double Acting | SP1 | Emerson | GRL | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM
100VBFE1S1-Double Acting | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-006 | 2000043108 TVF-M2WGNMM
100VKGD1L1-Double Acting | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
100VKGD1L2-Double Acting | SP1 | Emerson | Clarkson KGA+ | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
100VTWD1C1-Double Acting-Positioner | SP1 | Emerson | KTM MB11 T Port | Emerson | KTM AWN13 | SMC IP8100-031-J Included
1200VKGD1L2-Double Acting | SP1 | Emerson | Clarkson KGA+ | Emerson | Hydraulic cylinder | SWI LMT PXM P+F NCB5-18GM40-N0 5-24VDC
150VBFD1L1-Double Acting | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-014 | 2000043108 TVF-M2WGNMM
150VBFD1L1-Manual | SP1 | Emerson | GRW | Emerson | Manual Lever | 2000043108 TVF-M2WGNMM
150VBFD1S1-Double Acting-Positioner | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-014 | SMC IP8100 031 J (4-20mA)
150VBFD1S2-Double Acting | SP1 | Emerson | GRL | Emerson | KEYSTONE F89-014 | 2000043108 TVF-M2WGNMM
150VBFE1S1-Double Acting-Positioner | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-014 | SMC IP8100 031 J (4-20mA)
150VKGD1L1-Double Acting | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
150VKGD1L2-Double Acting | SP1 | Emerson | Clarkson KGA+ | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
150VKGE1C1-Double Acting | SP1 | Emerson | Clarkson KS1 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
200VBFD1S2-Double Acting | SP1 | Emerson | GRL | Emerson | KEYSTONE F89-032 | 2000043108 TVF-M2WGNMM
200VBFE1S1-Double Acting | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-032 | 2000043108 TVF-M2WGNMM
200VBFE1S1-Double Acting-Positioner | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-032 | SMC IP8100 031 J (4-20mA)
200VDTD1L1-Double Acting-Positioner | SP1 | Dual Valves | eDart YDP200B Poly yDart Valve | Dual Valves | Pneumatic cylinder | SMCIP8101 electropneumatic positioner and air filter regulator to 700 kPag included
200VKGD1L1-Double Acting | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
250VBFD1L1-Manual | SP1 | Emerson | GRW | Emerson | Gearbox | 2000043108 TVF-M2WGNMM
250VBFD1S1-Double Acting-Positioner | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-051 | SMC IP8100 031 J (4-20mA)
250VBFD1S2-Double Acting | SP1 | Emerson | GRL | Emerson | KEYSTONE F89-051 | 2000043108 TVF-M2WGNMM
250VBFD1S2-Manual | SP1 | Emerson | GRL | Emerson | Gearbox | 2000043108 TVF-M2WGNMM
250VKGD1L1-Double Acting | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
250VKGD1L1-Double Acting-Drain Plate | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
250VKGD1L1-Manual | SP1 | Emerson | Clarkson KGD | Emerson | Manual handwheel | P+F PXM NCB5-18GM40-Z0 24VDC
25VB03S1-Double Acting | SP1 | Emerson | K-BALL F182 | Emerson | KEYSTONE F89-003 | SWIT TOP TVF-M2WGNMM
300VBFD1L1-Manual | SP1 | Emerson | GRW | Emerson | Gearbox | 2000043108 TVF-M2WGNMM
300VBFD1S1-Double Acting-Positioner | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-085 | SMC IP8100 031 J (4-20mA)
300VKGD1C1-Double Acting | SP1 | Emerson | Clarkson KS1 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
300VKGD1L1-Double Acting | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
300VKGD1L1-Double Acting-Positioner-Table E drilling | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | Air Cylinder WITH POSITIONER/FEEDBACK Included
300VKGE1L1-Double Acting-Drain Plate | SP1 | Emerson | Clarkson KGA+ | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
350VBFD1S1-Double Acting-Positioner | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-085 | SMC IP8100 031 J (4-20mA)
350VBFD1S2-Double Acting | SP1 | Emerson | GRL | Emerson | KEYSTONE F89-085 | 2000043108 TVF-M2WGNMM
350VPID1L1-Double Acting-Positioner | SP1 | Jindex | CMR06OT-MYY58-TD40XX | Jindex | Pneu DA Internal positioner mechanism | Positioner Siemens PS2 4-20mA with position feed back 4-20mA and fail last circuit
400VBFD1S1-Double Acting-Positioner | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-085 | SMC IP8100 031 J (4-20mA)
400VBFD1S2-Manual | SP1 | Emerson | GRL | Emerson | Gearbox | 2000043108 TVF-M2WGNMM
400VKGD1C1-Double Acting | SP1 | Emerson | Clarkson KS1 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
400VKGD1L1-Double Acting | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
400VKGD1L1-Double Acting-Drain Plate | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
400VKGE1C1-Double Acting | SP1 | Emerson | Clarkson KS1 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
400VPID1L1-Double Acting-Positioner | SP1 | Jindex | CMR06OT-MYY58-TD40XX | Jindex | Pneu DA Internal positioner mechanism | Positioner Siemens PS2 4-20mA with position feed back 4-20mA and fail last circuit
40VB03S1-Spring Return | SP1 | Emerson | K-BALL F182 | Emerson | KEYSTONE F89-014 | SWIT TOP TVF-M2WGNMM
450VBFD1S1-Double Acting-Positioner | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-140 | SMC IP8100 031 J (4-20mA)
450VBFD1S2-Manual | SP1 | Emerson | GRL | Emerson | Gearbox | 2000043108 TVF-M2WGNMM
450VKGD1L1-Double Acting | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
500VBFD1S1-Double Acting | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-140 | 2000043108 TVF-M2WGNMM
500VBFE1L2-Double Acting | SP1 | Emerson | GRL | Emerson | KEYSTONE F89-140 | 2000043108 TVF-M2WGNMM
500VKGD1C1-Double Acting | SP1 | Emerson | Clarkson KS1 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
500VKGD1L1-Double Acting | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
500VKGE1C1-Double Acting | SP1 | Emerson | Clarkson KS1 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
50VB03S1-Double Acting | SP1 | Emerson | K-BALL F182 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM
50VB03S1-Double Acting-Positioner | SP1 | Emerson | K-BALL F182 | Emerson | KEYSTONE F89-009 | BIPO NON PST SMC IP8100 031 J X318
50VB03S1-Double Acting-Solenoid on Valve | SP1 | Emerson | K-BALL F182 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM
50VB03S1-Electric 24VDC | SP1 | Emerson | K-BALL F182 | Emerson | Keystone EPI 2 Model 063 (8 step) 24VDC energise to open, de-energise to close, no position feedback | None
50VB03S1-Manual | SP1 | Emerson | K-BALL F182 | Emerson | Manual Lever | SWIT TOP TVF-M2WGNMM
50VB03S1-Single Acting | SP1 | Emerson | K-BALL F182 | Emerson | KEYSTONE F89-009 | SWIT TOP TVF-M2WGNMM
50VBD1C1-Double Acting-Positioner | SP1 | Emerson | KTM EB11 | Emerson | KEYSTONE F89-004 | Positioner SMC IP8100 031 J X318
50VBD1S1-Double Acting | SP1 | Unimech | ARITA ARTTBV-TE | Unimech | Pneumatic cylinder | Arita Limit Switch
50VBE1S1-Double Acting | SP1 | Emerson | K-BALL F194 | Emerson | KEYSTONE F89-004 | SWIT TOP TVF-M2WGNMM
50VBE1S4-Double Acting | SP1 | Emerson | K-BALL F194 - Hydrogen Peroxide | Emerson | KEYSTONE F89-004 | SWIT TOP TVF-M2WGNMM
50VDD1L1-Double Acting | SP1 | KDV | Series 37 Straight Through (ST) | KDV | Pneumatic cylinder | IMTEX Std Box Mech on/off Sw KDV/Linear Drive +2 Terminal
50VDD1L1-Single Acting | SP1 | KDV | Series 37 Straight Through (ST) | KDV | Pneumatic cylinder | IMTEX Std Box Mech on/off Sw KDV/Linear Drive +2 Terminal
50VKGD1L1-Double Acting | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
600VBFD1L2-Double Acting | SP1 | Emerson | GRL | Emerson | KEYSTONE F89-240 | 2000043108 TVF-M2WGNMM
600VKGD1L1-Double Acting | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
600VKGD1L1-Double Acting-Drain Plate | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
600VKGE1L1-Double Acting-Drain Plate | SP1 | Emerson | Clarkson KGA+ | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
600VKGE1L1-Manual-Chain Wheel | SP1 | Emerson | Clarkson KGA+ | Emerson | Bevel gear with chainwheel | P+F PXM NCB5-18GM40-Z0 24VDC
750VBFD1L6-Double Acting | SP1 | Emerson | GRF | Emerson | KTM AW20 CD | 2000043108 TVF-M2WGNMM
750VKGD1C1-Double Acting | SP1 | Emerson | Clarkson KS1 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
750VKGD1L2-Double Acting | SP1 | Emerson | Clarkson KGA+ | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
80VBD1S1-Double Acting | SP1 | Unimech | ARITA ARTTBV-TE | Unimech | Pneumatic cylinder | Arita Limit Switch
80VBD1S1-Spring Return | SP1 | Unimech | ARITA ARTTBV-TE | Unimech | Pneumatic cylinder | Arita Limit Switch
80VBFD1L1-Double Acting-Positioner | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-004 | SMC IP8100 031 J (4-20mA)
80VBFD1S1-Double Acting-Solenoid on Valve | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-004 | 2000043108 TVF-M2WGNMM
80VBFD1S1-Manual | SP1 | Emerson | GRW | Emerson | Manual Lever | 2000043108 TVF-M2WGNMM
80VBFD1S2-Manual | SP1 | Emerson | GRL | Emerson | Manual Lever | 2000043108 TVF-M2WGNMM
80VBFE1S1-Double Acting | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-004 | 2000043108 TVF-M2WGNMM
80VBFE1S1-Double Acting-Positioner | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-004 | SMC IP8100 031 J (4-20mA)
80VBFE1S1-Double Acting-Solenoid on Valve | SP1 | Emerson | GRW | Emerson | KEYSTONE F89-004 | 2000043108 TVF-M2WGNMM
80VKGD1L1-Double Acting | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
80VKGD1L1-Double Acting | SP1 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
80VKGE1C1-Double Acting | SP1 | Emerson | Clarkson KS1 | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
80VTWD1C1-Double Acting-Positioner | SP1 | Emerson | KTM MB11 T Port | Emerson | KTM AGN13 | SMC IP8100-031-J Included
100VBD1S1-Double Acting | SP2 | Unimech | ARTTBV-TE | Unimech | Pneumatic actuator | Limit switch Included
100VBE1N1-Spring Return | SP2 | Emerson | KTM EB11 | Emerson | KEYSTONE F89-052 | TOPWORX TVF-M2WGNMM
100VBE1S1-Double Acting | SP2 | Emerson | K-BALL F194 | Emerson | KEYSTONE F89-020 | TOPWORX TVF-M2WGNMM
100VBFD1L2-Manual | SP2 | Emerson | GRL | Emerson | Manual Lever | TOPWORX TVF-M2WGNMM
100VBFD1L5-Double Acting | SP2 | Emerson | F990 | Emerson | KEYSTONE F89-006 | TOPWORX TVF-M2WGNMM
100VBFD1S2-Double Acting | SP2 | Emerson | GRL | Emerson | KEYSTONE F89-006 | TOPWORX TVF-M2WGNMM
100VBFE1L2-Spring Return | SP2 | Emerson | GRL | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM
100VBFE1S4-Spring Return | SP2 | Emerson | GRL | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM
100VKGD1L1-Double Acting | SP2 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
100VKGD1L2-Double Acting | SP2 | Emerson | Clarkson KGA+ | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
150VBD1C1-Double Acting | SP2 | Emerson | KTM EB11 | Emerson | KEYSTONE F89-085 | TOPWORX TVF-M2WGNMM
150VBD1S1-Double Acting | SP2 | Unimech | ARTTBV-TE | Unimech | Pneumatic actuator | Limit switch Included
150VBE1N1-Spring Return | SP2 | Emerson | KTM EB11 | Emerson | KEYSTONE F89-140 | TOPWORX TVF-M2WGNMM
150VBE1N1-Spring Return | SP2 | Emerson | KTM EB11 | Emerson | KEYSTONE F89-140 | TOPWORX TVF-M2WGNMM
150VBE1S1-Double Acting | SP2 | Emerson | K-BALL F194 | Emerson | KEYSTONE F89-051 | TOPWORX TVF-M2WGNMM
150VBFD1L2-Manual | SP2 | Emerson | GRL | Emerson | Manual Lever | TOPWORX TVF-M2WGNMM
150VBFD1L5-Spring Return | SP2 | Emerson | F990 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM
150VBFE1L2-Double Acting | SP2 | Emerson | GRL | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM
150VBFE1S4-Spring Return | SP2 | Emerson | GRL | Emerson | KEYSTONE F89-032 | TOPWORX TVF-M2WGNMM
150VKGD1L1-Double Acting | SP2 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
150VKGE1L1-Double Acting | SP2 | Emerson | Clarkson KGA+ | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
200VBE1N1-Spring Return | SP2 | Emerson | KTM EB11 | Emerson | KEYSTONE F89-240 | TOPWORX TVF-M2WGNMM
200VKGD1L1-Double Acting | SP2 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
250VKGD1L1-Double Acting | SP2 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
25VB03S1-Double Acting | SP2 | Emerson | K-BALL F182 | Emerson | KEYSTONE F89-003 | TOPWORX TVF-M2WGNMM
25VBD1S1-Spring Return | SP2 | Unimech | ARTTBV-TE | Unimech | Pneumatic actuator | Limit switch Included
25VDD1L2-Double Acting-Positioner | SP2 | KDV | Weir Type series 35 | KDV | Pneumatic actuator | SMC Smart Linear Positioner IP8001-032 I-P 4-20mA IN/OUT + 2 Alarms
25VDE1L2-Double Acting-Positioner | SP2 | KDV | Weir Type series 35 | KDV | Pneumatic actuator | SMC Smart Linear Positioner IP8001-032 I-P 4-20mA IN/OUT + 2 Alarms
25VGLE1S1-Double Acting-Positioner | SP2 | Emerson | FISHER 025 24000SVF | Emerson | Pneumatic actuator | DVC2000,HART Communicating-HC 4-20mA
350VKGD1L1-Double Acting | SP2 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
400VKGD1L1-Double Acting | SP2 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
40VBD1C1-Spring Return | SP2 | Emerson | KTM EB11 | Emerson | KEYSTONE F89-009 | TOPWORX TVF-M2WGNMM
50VB03S1-Double Acting | SP2 | Emerson | K-BALL F182 | Emerson | KEYSTONE F89-009 | TOPWORX TVF-M2WGNMM
50VB03S1-Double Acting-Solenoid on Valve | SP2 | Emerson | K-BALL F182 | Emerson | KEYSTONE F89-009 | TOPWORX TVF-M2WGNMM
50VB03S1-Spring Return | SP2 | Emerson | K-BALL F182 | Emerson | KEYSTONE F89-009 | TOPWORX TVF-M2WGNMM
50VBD1C1-Double Acting | SP2 | Emerson | KTM EB11 | Emerson | KEYSTONE F89-006 | TOPWORX TVF-M2WGNMM
50VBD1T1-Spring Return | SP2 | George Fischer | GF 546 Pro | George Fischer | Pneumatic actuator PPA40 PPGF FC | Limit Switch Included
50VBE1C1-Spring Return | SP2 | Emerson | KTM EB11 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM
50VDD1L1-Double Acting | SP2 | KDV | Series 37 Straight Through (ST) | KDV | Pneumatic actuator | IMTEX Std Box Mech on/off Sw KDV/Linear Drive +2 Terminal
50VKGD1L1-Double Acting | SP2 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
80VBD1C1-Double Acting | SP2 | Emerson | KTM EB11 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM
80VBD1C1-Spring Return | SP2 | Emerson | KTM EB11 | Emerson | KEYSTONE F89-032 | TOPWORX TVF-M2WGNMM
80VBD1S1-Spring Return | SP2 | Unimech | ARTTBV-TE | Unimech | Pneumatic actuator | Limit Switch Included
80VBD1T1-Spring Return | SP2 | George Fischer | GF 546 Pro | George Fischer | Pneumatic actuator PPA80 PPGF FC | Limit Switch Included
80VBE1C1-Double Acting | SP2 | Emerson | KTM EB11 | Emerson | KEYSTONE F89-014 | TOPWORX TVF-M2WGNMM
80VBFD1L1-Double Acting-Positioner | SP2 | Emerson | GRW | Emerson | KEYSTONE F89-004 | SMC IP8100 031 J (4-20mA)
80VBFD1S2-Double Acting | SP2 | Emerson | GRL | Emerson | KEYSTONE F89-004 | TOPWORX TVF-M2WGNMM
80VBFE1L1-Double Acting | SP2 | Emerson | GRW | Emerson | KEYSTONE F89-004 | TOPWORX TVF-M2WGNMM
80VBFE1L1-Spring Return | SP2 | Emerson | GRW | Emerson | KEYSTONE F89-009 | TOPWORX TVF-M2WGNMM
80VKGD1L1-Double Acting | SP2 | Emerson | Clarkson KGD | Emerson | Pneumatic cylinder | P+F PXM NCB5-18GM40-Z0 24VDC
100VBD1T1-Double Acting | SP3 | TBC | TBC | TBC | TBC | TBC
100VBE1S1-Spring Return | SP3 | TBC | TBC | TBC | TBC | TBC
100VBFD1L1-Double Acting | SP3 | TBC | TBC | TBC | TBC | TBC
150VKGD1L3-Double Acting | SP3 | TBC | TBC | TBC | TBC | TBC
200VKGD1L3-Double Acting | SP3 | TBC | TBC | TBC | TBC | TBC
250VKGE1L1-Double Acting | SP3 | TBC | TBC | TBC | TBC | TBC
25VB03S1-Double Acting-Solenoid on Valve | SP3 | TBC | TBC | TBC | TBC | TBC
25VBD1T1-Double Acting-Positioner | SP3 | TBC | TBC | TBC | TBC | TBC
25VBE1S4-Double Acting | SP3 | TBC | TBC | TBC | TBC | TBC
25VDE1S2-Double Acting-Positioner | SP3 | TBC | TBC | TBC | TBC | TBC
350VBFE1S1-Double Acting-Positioner | SP3 | TBC | TBC | TBC | TBC | TBC
350VKGE1L1-Double Acting | SP3 | TBC | TBC | TBC | TBC | TBC
400VKGE1L1-Double Acting-ANSI flanges | SP3 | TBC | TBC | TBC | TBC | TBC
50VBD1C1-Double Acting-Positioner-Solenoid on Valve | SP3 | TBC | TBC | TBC | TBC | TBC
50VBD1S1-Double Acting-IECEX RATED | SP3 | TBC | TBC | TBC | TBC | TBC
50VBD1T1-Double Acting | SP3 | TBC | TBC | TBC | TBC | TBC
50VBE1C1-Double Acting | SP3 | TBC | TBC | TBC | TBC | TBC
50VDD1L1-Double Acting-Solenoid on Valve | SP3 | TBC | TBC | TBC | TBC | TBC
50VDE1S2-Double Acting-Positioner | SP3 | TBC | TBC | TBC | TBC | TBC
50VTWD1C1-Double Acting-Positioner | SP3 | TBC | TBC | TBC | TBC | TBC
80VBD1S1-Double Acting-IECEX RATED | SP3 | TBC | TBC | TBC | TBC | TBC
80VBFD1L1-Double Acting | SP3 | TBC | TBC | TBC | TBC | TBC
80VBFD1S1-Double Acting | SP3 | TBC | TBC | TBC | TBC | TBC
80VBFD1S1-Double Acting-Positioner | SP3 | TBC | TBC | TBC | TBC | TBC
80VDD1S1-Double Acting-Positioner | SP3 | TBC | TBC | TBC | TBC | TBC
100VDE1S2-Double Acting-Positioner | SP3 | TBC | TBC | TBC | TBC | TBC
80VKGD1L3-Double Acting | SP3 | TBC | TBC | TBC | TBC | TBC

## Valve GAs
Control Valve Code | Document Number | Description | Emerson Order
100VBD1S1-DOUBLE ACTING | 2000-PP007-B02-10036 | GENERAL ARRANGEMENT DRAWING FOR 100VBD1S1-DOUBLE ACTING | SP2
100VBD1T1-Double Acting | 2000-PP007-B02-10147 | GENERAL ARRANGEMENT DRAWING FOR 100VBD1T1-DOUBLE ACTING | SP3
100VBE1N1-SPRING RETURN | 2000-PP007-B02-10037 | GENERAL ARRANGEMENT DRAWING FOR 100VBE1N1-SPRING RETURN | SP2
100VBE1S1-DOUBLE ACTING | 2000-PP007-B02-10038 | GENERAL ARRANGEMENT DRAWING FOR 100VBE1S1-DOUBLE ACTING | SP2
100VBE1S1-Spring Return | 2000-PP007-B02-10151 | GENERAL ARRANGEMENT DRAWING FOR 100VBE1S1-SPRING RETURN | SP3
100VBFD1L1-Double Acting | 2000-PP007-B02-10148 | GENERAL ARRANGEMENT DRAWING FOR 100VBFD1L1-DOUBLE ACTING | SP3
100VBFD1L2-MANUAL | 2000-PP007-B02-10039 | GENERAL ARRANGEMENT DRAWING FOR 100VBFD1L2-MANUAL | SP2
100VBFD1L5-DOUBLE ACTING | 2000-PP007-B02-10040 | GENERAL ARRANGEMENT DRAWING FOR 100VBFD1L5-DOUBLE ACTING | SP2
100VBFD1S1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10041 | GENERAL ARRANGEMENT DRAWING FOR 0100VBFD1S1-DOUBLE ACTING-POSITIONER | SP1
100VBFD1S2-DOUBLE ACTING | 2000-PP007-B02-10042 | GENERAL ARRANGEMENT DRAWING FOR 100VBFD1S2-DOUBLE ACTING | SP1
100VBFE1L2-SPRING RETURN | 2000-PP007-B02-10043 | GENERAL ARRANGEMENT DRAWING FOR 100VBFE1L2-SPRING RETURN | SP2
100VBFE1S1-DOUBLE ACTING | 2000-PP007-B02-10044 | GENERAL ARRANGEMENT DRAWING FOR 100VBFE1S1-DOUBLE ACTING | SP1
100VBFE1S4-SPRING RETURN | 2000-PP007-B02-10045 | GENERAL ARRANGEMENT DRAWING FOR 100VBFE1S4-SPRING RETURN | SP2
100VDE1S2-Double Acting-Positioner | 2000-PP007-B02-10155 | GENERAL ARRANGEMENT DRAWING FOR 100VDE1S2-DOUBLE ACTING-POSITIONER | SP3
100VKGD1L1-DOUBLE ACTING | 2000-PP007-B02-10046 | GENERAL ARRANGEMENT DRAWING FOR 100VKGD1L1-DOUBLE ACTING | SP1
100VKGD1L2-DOUBLE ACTING | 2000-PP007-B02-10047 | GENERAL ARRANGEMENT DRAWING FOR 100VKGD1L2-DOUBLE ACTING | SP1
100VTWD1C1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10048 | GENERAL ARRANGEMENT DRAWING FOR 100VTWD1C1-DOUBLE ACTING-POSITIONER | SP1
1200VKGD1L2-DOUBLE ACTING | 2000-PP007-B02-10105 | GENERAL ARRANGEMENT DRAWING FOR 1200VKGD1L2-DOUBLE ACTING | SP1
150VBD1C1-DOUBLE ACTING | 2000-PP007-B02-10049 | GENERAL ARRANGEMENT DRAWING FOR 150VBD1C1-DOUBLE ACTING | SP2
150VBD1S1-DOUBLE ACTING | 2000-PP007-B02-10050 | GENERAL ARRANGEMENT DRAWING FOR 150VBD1S1-DOUBLE ACTING | SP2
150VBE1N1-SPRING RETURN | 2000-PP007-B02-10051 | GENERAL ARRANGEMENT DRAWING FOR 150VBE1N1-SPRING RETURN | SP2
150VBE1S1-DOUBLE ACTING | 2000-PP007-B02-10052 | GENERAL ARRANGEMENT DRAWING FOR 150VBE1S1-DOUBLE ACTING | SP2
150VBFD1L1-DOUBLE ACTING | 2000-PP007-B02-10053 | GENERAL ARRANGEMENT DRAWING FOR 150VBFD1L1-DOUBLE ACTING | SP1
150VBFD1L1-MANUAL | 2000-PP007-B02-10054 | GENERAL ARRANGEMENT DRAWING FOR 150VBFD1L1-MANUAL | SP1
150VBFD1L2-MANUAL | 2000-PP007-B02-10055 | GENERAL ARRANGEMENT DRAWING FOR 150VBFD1L2-MANUAL | SP2
150VBFD1L5-SPRING RETURN | 2000-PP007-B02-10056 | GENERAL ARRANGEMENT DRAWING FOR 150VBFD1L5-SPRING RETURN | SP2
150VBFD1S1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10057 | GENERAL ARRANGEMENT DRAWING FOR 0150VBFD1S1-DOUBLE ACTING-POSITIONER | SP1
150VBFD1S2-DOUBLE ACTING | 2000-PP007-B02-10058 | GENERAL ARRANGEMENT DRAWING FOR 150VBFD1S2-DOUBLE ACTING | SP1
150VBFE1L2-DOUBLE ACTING | 2000-PP007-B02-10059 | GENERAL ARRANGEMENT DRAWING FOR 150VBFE1L2-DOUBLE ACTING | SP2
150VBFE1S1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10060 | GENERAL ARRANGEMENT DRAWING FOR 150VBFE1S1-DOUBLE ACTING-POSITIONER | SP1
150VBFE1S4-SPRING RETURN | 2000-PP007-B02-10061 | GENERAL ARRANGEMENT DRAWING FOR 150VBFE1S4-SPRING RETURN | SP2
150VKGD1L1-DOUBLE ACTING | 2000-PP007-B02-10062 | GENERAL ARRANGEMENT DRAWING FOR 150VKGD1L1-DOUBLE ACTING | SP1
150VKGD1L2-DOUBLE ACTING | 2000-PP007-B02-10063 | GENERAL ARRANGEMENT DRAWING FOR 150VKGD1L2-DOUBLE ACTING | SP1
150VKGD1L3-Double Acting | 2000-PP007-B02-10149 | GENERAL ARRANGEMENT DRAWING FOR 150VKGD1L3-DOUBLE ACTING | SP3
150VKGE1C1-DOUBLE ACTING | 2000-PP007-B02-10064 | GENERAL ARRANGEMENT DRAWING FOR 150VKGE1C1-DOUBLE ACTING | SP1
150VKGE1L1-DOUBLE ACTING | 2000-PP007-B02-10065 | GENERAL ARRANGEMENT DRAWING FOR 150VKGE1L1-DOUBLE ACTING | SP2
200VBE1N1-SPRING RETURN | 2000-PP007-B02-10066 | GENERAL ARRANGEMENT DRAWING FOR 200VBE1N1-SPRING RETURN | SP2
200VBFD1S2-DOUBLE ACTING | 2000-PP007-B02-10067 | GENERAL ARRANGEMENT DRAWING FOR 200VBFD1S2-DOUBLE ACTING | SP1
200VBFE1S1-DOUBLE ACTING | 2000-PP007-B02-10068 | GENERAL ARRANGEMENT DRAWING FOR 200VBFE1S1-DOUBLE ACTING | SP1
200VBFE1S1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10114 | GENERAL ARRANGEMENT DRAWING FOR 200VBFE1S1-DOUBLE ACTING-POSITIONER | SP1
200VDTD1L1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10069 | GENERAL ARRANGEMENT DRAWING FOR 200VDTD1L1-DOUBLE ACTING-POSITIONER | SP1
200VKGD1L1-DOUBLE ACTING | 2000-PP007-B02-10070 | GENERAL ARRANGEMENT DRAWING FOR 200VKGD1L1-DOUBLE ACTING | SP1
200VKGD1L3-Double Acting | 2000-PP007-B02-10150 | GENERAL ARRANGEMENT DRAWING FOR 200VKGD1L3-DOUBLE ACTING | SP3
250VBFD1L1-MANUAL | 2000-PP007-B02-10071 | GENERAL ARRANGEMENT DRAWING FOR 250VBFD1L1-MANUAL | SP1
250VBFD1S1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10072 | GENERAL ARRANGEMENT DRAWING FOR 0250VBFD1S1-DOUBLE ACTING-POSITIONER | SP1
250VBFD1S2-DOUBLE ACTING | 2000-PP007-B02-10073 | GENERAL ARRANGEMENT DRAWING FOR 250VBFD1S2-DOUBLE ACTING | SP1
250VBFD1S2-MANUAL | 2000-PP007-B02-10074 | GENERAL ARRANGEMENT DRAWING FOR 250VBFD1S2-MANUAL | SP1
250VKGD1L1-DOUBLE ACTING | 2000-PP007-B02-10075 | GENERAL ARRANGEMENT DRAWING FOR 250VKGD1L1-DOUBLE ACTING | SP1
250VKGD1L1-DOUBLE ACTING-DRAIN PLATE | 2000-PP007-B02-10116 | GENERAL ARRANGEMENT DRAWING FOR 250VKGD1L1-DOUBLE ACTING-DRAIN PLATE | SP1
250VKGD1L1-MANUAL | 2000-PP007-B02-10076 | GENERAL ARRANGEMENT DRAWING FOR 250VKGD1L1-MANUAL | SP1
250VKGE1L1-Double Acting | 2000-PP007-B02-10130 | GENERAL ARRANGEMENT DRAWING FOR 250VKGE1L1-DOUBLE ACTING | SP3
25VB03S1-DOUBLE ACTING | 2000-PP007-B02-10001 | GENERAL ARRANGEMENT DRAWING FOR 025VB03S1-DOUBLE ACTING | SP1
25VB03S1-Double Acting-Solenoid on Valve | 2000-PP007-B02-10132 | GENERAL ARRANGEMENT DRAWING FOR 025VB03S1-DOUBLE ACTING-SOLENOID ON VALVE | SP3
25VBD1S1-SPRING RETURN | 2000-PP007-B02-10002 | GENERAL ARRANGEMENT DRAWING FOR 025VBD1S1-SPRING RETURN | SP2
25VBD1T1-Double Acting-Positioner | 2000-PP007-B02-10133 | GENERAL ARRANGEMENT DRAWING FOR 025VBD1T1-DOUBLE ACTING-POSITIONER | SP3
25VBE1S4-Double Acting | 2000-PP007-B02-10134 | GENERAL ARRANGEMENT DRAWING FOR 025VBE1S4-DOUBLE ACTING | SP3
25VDD1L2-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10003 | GENERAL ARRANGEMENT DRAWING FOR 025VDD1L2-DOUBLE ACTING-POSITIONER | SP2
25VDE1L2-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10004 | GENERAL ARRANGEMENT DRAWING FOR 025VDE1L2-DOUBLE ACTING-POSITIONER | SP2
25VDE1S2-Double Acting-Positioner | 2000-PP007-B02-10135 | GENERAL ARRANGEMENT DRAWING FOR 025VDE1S2-DOUBLE ACTING-POSITIONER | SP3
25VGLE1S1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10005 | GENERAL ARRANGEMENT DRAWING FOR 025VGLE1S1-DOUBLE ACTING-POSITIONER | SP2
300VBFD1L1-MANUAL | 2000-PP007-B02-10077 | GENERAL ARRANGEMENT DRAWING FOR 300VBFD1L1-MANUAL | SP1
300VBFD1S1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10078 | GENERAL ARRANGEMENT DRAWING FOR 0300VBFD1S1-DOUBLE ACTING-POSITIONER | SP1
300VKGD1C1-DOUBLE ACTING | 2000-PP007-B02-10079 | GENERAL ARRANGEMENT DRAWING FOR 300VKGD1C1-DOUBLE ACTING | SP1
300VKGD1L1-DOUBLE ACTING | 2000-PP007-B02-10080 | GENERAL ARRANGEMENT DRAWING FOR 300VKGD1L1-DOUBLE ACTING | SP1
300VKGD1L1-DOUBLE ACTING-POSITIONER-TABLE E DRILLING | 2000-PP007-B02-10117 | GENERAL ARRANGEMENT DRAWING FOR 300VKGD1L1-DOUBLE ACTING-POSITIONER-TABLE E DRILLING | SP1
300VKGE1L1-DOUBLE ACTING-DRAIN PLATE | 2000-PP007-B02-10081 | GENERAL ARRANGEMENT DRAWING FOR 300VKGE1L1-DOUBLE ACTING-DRAIN PLATE | SP1
350VBFD1S1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10082 | GENERAL ARRANGEMENT DRAWING FOR 0350VBFD1S1-DOUBLE ACTING-POSITIONER | SP1
350VBFD1S2-DOUBLE ACTING | 2000-PP007-B02-10083 | GENERAL ARRANGEMENT DRAWING FOR 350VBFD1S2-DOUBLE ACTING | SP1
350VBFE1S1-Double Acting-Positioner | 2000-PP007-B02-10128 | GENERAL ARRANGEMENT DRAWING FOR 350VBFE1S1-DOUBLE ACTING-POSITIONER | SP3
350VKGD1L1-DOUBLE ACTING | 2000-PP007-B02-10084 | GENERAL ARRANGEMENT DRAWING FOR 350VKGD1L1-DOUBLE ACTING | SP2
350VKGE1L1-Double Acting | 2000-PP007-B02-10129 | GENERAL ARRANGEMENT DRAWING FOR 350VKGE1L1-DOUBLE ACTING | SP3
350VPID1L1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10085 | GENERAL ARRANGEMENT DRAWING FOR 350VPID1L1-DOUBLE ACTING-POSITIONER | SP1
400VBFD1S1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10086 | GENERAL ARRANGEMENT DRAWING FOR 0400VBFD1S1-DOUBLE ACTING-POSITIONER | SP1
400VBFD1S2-MANUAL | 2000-PP007-B02-10087 | GENERAL ARRANGEMENT DRAWING FOR 400VBFD1S2-MANUAL | SP1
400VKGD1C1-DOUBLE ACTING | 2000-PP007-B02-10088 | GENERAL ARRANGEMENT DRAWING FOR 400VKGD1C1-DOUBLE ACTING | SP1
400VKGD1L1-DOUBLE ACTING | 2000-PP007-B02-10089 | GENERAL ARRANGEMENT DRAWING FOR 400VKGD1L1-DOUBLE ACTING | SP1
400VKGD1L1-DOUBLE ACTING-DRAIN PLATE | 2000-PP007-B02-10118 | GENERAL ARRANGEMENT DRAWING FOR 400VKGD1L1-DOUBLE ACTING-DRAIN PLATE | SP1
400VKGE1C1-DOUBLE ACTING | 2000-PP007-B02-10090 | GENERAL ARRANGEMENT DRAWING FOR 400VKGE1C1-DOUBLE ACTING | SP1
400VKGE1L1-Double Acting-ANSI flanges | 2000-PP007-B02-10131 | GENERAL ARRANGEMENT DRAWING FOR 400VKGE1L1-DOUBLE ACTING-ANSI FLANGES | SP3
400VPID1L1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10091 | GENERAL ARRANGEMENT DRAWING FOR 400VPID1L1-DOUBLE ACTING-POSITIONER | SP1
40VB03S1-SPRING RETURN | 2000-PP007-B02-10006 | GENERAL ARRANGEMENT DRAWING FOR 040VB03S1-SPRING RETURN | SP1
40VBD1C1-SPRING RETURN | 2000-PP007-B02-10007 | GENERAL ARRANGEMENT DRAWING FOR 040VBD1C1-SPRING RETURN | SP2
450VBFD1S1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10092 | GENERAL ARRANGEMENT DRAWING FOR 0450VBFD1S1-DOUBLE ACTING-POSITIONER | SP1
450VBFD1S2-MANUAL | 2000-PP007-B02-10093 | GENERAL ARRANGEMENT DRAWING FOR 450VBFD1S2-MANUAL | SP1
450VKGD1L1-DOUBLE ACTING | 2000-PP007-B02-10094 | GENERAL ARRANGEMENT DRAWING FOR 450VKGD1L1-DOUBLE ACTING | SP1
500VBFD1S1-DOUBLE ACTING | 2000-PP007-B02-10095 | GENERAL ARRANGEMENT DRAWING FOR 500VBFD1S1-DOUBLE ACTING | SP1
500VBFE1L2-DOUBLE ACTING | 2000-PP007-B02-10096 | GENERAL ARRANGEMENT DRAWING FOR 500VBFE1L2-DOUBLE ACTING | SP1
500VKGD1C1-DOUBLE ACTING | 2000-PP007-B02-10097 | GENERAL ARRANGEMENT DRAWING FOR 500VKGD1C1-DOUBLE ACTING | SP1
500VKGD1C1-DOUBLE ACTING | 2000-PP007-B02-10123 | GENERAL ARRANGEMENT DRAWING FOR 500VKGD1C1-DOUBLE ACTING | SP1
500VKGD1L1-DOUBLE ACTING | 2000-PP007-B02-10098 | GENERAL ARRANGEMENT DRAWING FOR 500VKGD1L1-DOUBLE ACTING | SP1
500VKGE1C1-DOUBLE ACTING | 2000-PP007-B02-10120 | GENERAL ARRANGEMENT DRAWING FOR 500VKGE1C1-DOUBLE ACTING | SP1
50VB03S1-DOUBLE ACTING | 2000-PP007-B02-10008 | GENERAL ARRANGEMENT DRAWING FOR 050VB03S1-DOUBLE ACTING | SP1
50VB03S1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10106 | GENERAL ARRANGEMENT DRAWING FOR 050VB03S1-DOUBLE ACTING-POSITIONER | SP1
50VB03S1-DOUBLE ACTING-SOLENOID ON VALVE | 2000-PP007-B02-10107 | GENERAL ARRANGEMENT DRAWING FOR 050VB03S1-DOUBLE ACTING-SOLENOID ON VALVE | SP1
50VB03S1-Electric 24VDC | 2000-PP007-B02-10136 | GENERAL ARRANGEMENT DRAWING FOR 050VB03S1-ELECTRIC 24VDC | SP1
50VB03S1-ELECTRIC 24VDC | 2000-PP007-B02-10109 | GENERAL ARRANGEMENT DRAWING FOR 050VB03S1-ELECTRIC | SP1
50VB03S1-MANUAL | 2000-PP007-B02-10009 | GENERAL ARRANGEMENT DRAWING FOR 050VB03S1-MANUAL | SP1
50VB03S1-SINGLE ACTING | 2000-PP007-B02-10110 | GENERAL ARRANGEMENT DRAWING FOR 050VB03S1-SINGLE ACTING | SP1
50VB03S1-SPRING RETURN | 2000-PP007-B02-10010 | GENERAL ARRANGEMENT DRAWING FOR 050VB03S1-SPRING RETURN | SP2
50VBD1C1-DOUBLE ACTING | 2000-PP007-B02-10011 | GENERAL ARRANGEMENT DRAWING FOR 050VBD1C1-DOUBLE ACTING | SP2
50VBD1C1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10111 | GENERAL ARRANGEMENT DRAWING FOR 050VBD1C1-DOUBLE ACTING-POSITIONER | SP1
50VBD1C1-Double Acting-Positioner-Solenoid on Valve | 2000-PP007-B02-10137 | GENERAL ARRANGEMENT DRAWING FOR 050VBD1C1-DOUBLE ACTING-POSITIONER-SOLENOID ON VALVE | SP3
50VBD1S1-DOUBLE ACTING | 2000-PP007-B02-10012 | GENERAL ARRANGEMENT DRAWING FOR 050VBD1S1-DOUBLE ACTING | SP1
50VBD1S1-Double Acting-IECEX RATED | 2000-PP007-B02-10138 | GENERAL ARRANGEMENT DRAWING FOR 050VBD1S1-DOUBLE ACTING-IECEX RATED | SP3
50VBD1T1-Double Acting | 2000-PP007-B02-10139 | GENERAL ARRANGEMENT DRAWING FOR 050VBD1T1-DOUBLE ACTING | SP3
50VBD1T1-SPRING RETURN | 2000-PP007-B02-10013 | GENERAL ARRANGEMENT DRAWING FOR 050VBD1T1-SPRING RETURN | SP2
50VBE1C1-Double Acting | 2000-PP007-B02-10140 | GENERAL ARRANGEMENT DRAWING FOR 050VBE1C1-DOUBLE ACTING | SP3
50VBE1C1-SPRING RETURN | 2000-PP007-B02-10014 | GENERAL ARRANGEMENT DRAWING FOR 050VBE1C1-SPRING RETURN | SP2
50VBE1S1-DOUBLE ACTING | 2000-PP007-B02-10015 | GENERAL ARRANGEMENT DRAWING FOR 050VBE1S1-DOUBLE ACTING | SP1
50VBE1S4-DOUBLE ACTING | 2000-PP007-B02-10016 | GENERAL ARRANGEMENT DRAWING FOR 050VBE1S4-DOUBLE ACTING | SP1
50VDD1L1-DOUBLE ACTING | 2000-PP007-B02-10017 | GENERAL ARRANGEMENT DRAWING FOR 050VDD1L1-DOUBLE ACTING | SP1
50VDD1L1-Double Acting-Solenoid on Valve | 2000-PP007-B02-10141 | GENERAL ARRANGEMENT DRAWING FOR 050VDD1L1-DOUBLE ACTING-SOLENOID ON VALVE | SP3
50VDD1L1-SINGLE ACTING | 2000-PP007-B02-10115 | GENERAL ARRANGEMENT DRAWING FOR 050VDD1L1-SINGLE ACTING | SP1
50VDE1S2-Double Acting-Positioner | 2000-PP007-B02-10142 | GENERAL ARRANGEMENT DRAWING FOR 050VDE1S2-DOUBLE ACTING-POSITIONER | SP3
50VKGD1L1-DOUBLE ACTING | 2000-PP007-B02-10018 | GENERAL ARRANGEMENT DRAWING FOR 050VKGD1L1-DOUBLE ACTING | SP1
50VTWD1C1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10127 | GENERAL ARRANGEMENT DRAWING FOR 050VTWD1C1-DOUBLE ACTING-POSITIONER | SP3
600VBFD1L2-DOUBLE ACTING | 2000-PP007-B02-10099 | GENERAL ARRANGEMENT DRAWING FOR 600VBFD1L2-DOUBLE ACTING | SP1
600VKGD1L1-DOUBLE ACTING | 2000-PP007-B02-10100 | GENERAL ARRANGEMENT DRAWING FOR 600VKGD1L1-DOUBLE ACTING | SP1
600VKGD1L1-DOUBLE ACTING-DRAIN PLATE | 2000-PP007-B02-10119 | GENERAL ARRANGEMENT DRAWING FOR 600VKGD1L1-DOUBLE ACTING-DRAIN PLATE | SP1
600VKGE1L1-DOUBLE ACTING-DRAIN PLATE | 2000-PP007-B02-10101 | GENERAL ARRANGEMENT DRAWING FOR 600VKGE1L1-DOUBLE ACTING-DRAIN PLATE | SP1
600VKGE1L1-MANUAL-CHAIN WHEEL | 2000-PP007-B02-10121 | GENERAL ARRANGEMENT DRAWING FOR 600VKGE1L1-MANUAL-CHAIN WHEEL | SP1
750VBFD1L6-DOUBLE ACTING | 2000-PP007-B02-10102 | GENERAL ARRANGEMENT DRAWING FOR 750VBFD1L6-DOUBLE ACTING | SP1
750VKGD1C1-DOUBLE ACTING | 2000-PP007-B02-10103 | GENERAL ARRANGEMENT DRAWING FOR 750VKGD1C1-DOUBLE ACTING | SP1
750VKGD1L2-DOUBLE ACTING | 2000-PP007-B02-10104 | GENERAL ARRANGEMENT DRAWING FOR 750VKGD1L2-DOUBLE ACTING | SP1
80VBD1C1-DOUBLE ACTING | 2000-PP007-B02-10019 | GENERAL ARRANGEMENT DRAWING FOR 080VBD1C1-DOUBLE ACTING | SP2
80VBD1C1-SPRING RETURN | 2000-PP007-B02-10020 | GENERAL ARRANGEMENT DRAWING FOR 080VBD1C1-SPRING RETURN | SP2
80VBD1S1-DOUBLE ACTING | 2000-PP007-B02-10021 | GENERAL ARRANGEMENT DRAWING FOR 080VBD1S1-DOUBLE ACTING | SP1
80VBD1S1-Double Acting-IECEX RATED | 2000-PP007-B02-10143 | GENERAL ARRANGEMENT DRAWING FOR 080VBD1S1-DOUBLE ACTING-IECEX RATED | SP3
80VBD1S1-SPRING RETURN | 2000-PP007-B02-10022 | GENERAL ARRANGEMENT DRAWING FOR 080VBD1S1-SPRING RETURN | SP1
80VBD1T1-SPRING RETURN | 2000-PP007-B02-10023 | GENERAL ARRANGEMENT DRAWING FOR 080VBD1T1-SPRING RETURN | SP2
80VBE1C1-DOUBLE ACTING | 2000-PP007-B02-10024 | GENERAL ARRANGEMENT DRAWING FOR 080VBE1C1-DOUBLE ACTING | SP2
80VBFD1L1-DOUBLE ACTING | 2000-PP007-B02-10025 | GENERAL ARRANGEMENT DRAWING FOR 080VBFD1L1-DOUBLE ACTING | SP3
80VBFD1L1-Double Acting-Positioner | 2000-PP007-B02-10152 | GENERAL ARRANGEMENT DRAWING FOR 80VBFD1L1-DOUBLE ACTING-POSITIONER | SP1
80VBFD1L1-Double Acting-Positioner | 2000-PP007-B02-10153 | GENERAL ARRANGEMENT DRAWING FOR 80VBFD1L1-DOUBLE ACTING-POSITIONER | SP1
80VBFD1S1-DOUBLE ACTING | 2000-PP007-B02-10026 | GENERAL ARRANGEMENT DRAWING FOR 080VBFD1S1-DOUBLE ACTING | SP3
80VBFD1S1-Double Acting-Positioner | 2000-PP007-B02-10144 | GENERAL ARRANGEMENT DRAWING FOR 080VBFD1S1-DOUBLE ACTING-POSITIONER | SP3
80VBFD1S1-Double Acting-Solenoid on Valve | 2000-PP007-B02-10154 | GENERAL ARRANGEMENT DRAWING FOR 80VBFD1S1-DOUBLE ACTING-SOLENOID ON VALVE | SP1
80VBFD1S1-MANUAL | 2000-PP007-B02-10027 | GENERAL ARRANGEMENT DRAWING FOR 080VBFD1S1-MANUAL | SP1
80VBFD1S2-DOUBLE ACTING | 2000-PP007-B02-10028 | GENERAL ARRANGEMENT DRAWING FOR 080VBFD1S2-DOUBLE ACTING | SP2
80VBFD1S2-MANUAL | 2000-PP007-B02-10029 | GENERAL ARRANGEMENT DRAWING FOR 080VBFD1S2-MANUAL | SP1
80VBFE1L1-DOUBLE ACTING | 2000-PP007-B02-10030 | GENERAL ARRANGEMENT DRAWING FOR 080VBFE1L1-DOUBLE ACTING | SP2
80VBFE1L1-SPRING RETURN | 2000-PP007-B02-10031 | GENERAL ARRANGEMENT DRAWING FOR 080VBFE1L1-SPRING RETURN | SP2
80VBFE1S1-DOUBLE ACTING | 2000-PP007-B02-10032 | GENERAL ARRANGEMENT DRAWING FOR 080VBFE1S1-DOUBLE ACTING | SP1
80VBFE1S1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10112 | GENERAL ARRANGEMENT DRAWING FOR 080VBFE1S1-DOUBLE ACTING-POSITIONER | SP1
80VBFE1S1-DOUBLE ACTING-SOLENOID ON VALVE | 2000-PP007-B02-10113 | GENERAL ARRANGEMENT DRAWING FOR 080VBFE1S1-DOUBLE ACTING-SOLENOID ON VALVE | SP1
80VDD1S1-Double Acting-Positioner | 2000-PP007-B02-10145 | GENERAL ARRANGEMENT DRAWING FOR 080VDD1S1-DOUBLE ACTING-POSITIONER | SP3
80VKGD1L1-DOUBLE ACTING | 2000-PP007-B02-10033 | GENERAL ARRANGEMENT DRAWING FOR 080VKGD1L1-DOUBLE ACTING | SP1
80VKGD1L3-Double Acting | 2000-PP007-B02-10146 | GENERAL ARRANGEMENT DRAWING FOR 080VKGD1L3-DOUBLE ACTING | SP3
80VKGE1C1-DOUBLE ACTING | 2000-PP007-B02-10034 | GENERAL ARRANGEMENT DRAWING FOR 080VKGE1C1-DOUBLE ACTING | SP1
80VTWD1C1-DOUBLE ACTING-POSITIONER | 2000-PP007-B02-10035 | GENERAL ARRANGEMENT DRAWING FOR 080VTWD1C1-DOUBLE ACTING-POSITIONER | SP1

## Control Panel DRGS
Panel | Drawing | Description
F13-CP-402 | 2000-PP007-B02-10301 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F13-CP-402
F13-CP-403 | 2000-PP007-B02-10302 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F13-CP-403
F13-CP-404 | 2000-PP007-B02-10303 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F13-CP-404
F13-CP-405 | 2000-PP007-B02-10304 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F13-CP-405
F13-CP-406 | 2000-PP007-B02-10305 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F13-CP-406
F13-CP-407 | 2000-PP007-B02-10306 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F13-CP-407
F13-CP-408 | 2000-PP007-B02-10307 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F13-CP-408
F13-CP-409 | 2000-PP007-B02-10308 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F13-CP-409
F13-CP-410 | 2000-PP007-B02-10309 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F13-CP-410
F13-CP-411 | 2000-PP007-B02-10310 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F13-CP-411
F13-CP-412 | 2000-PP007-B02-10311 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F13-CP-412
F14-CP-401 | 2000-PP007-B02-10312 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F14-CP-401
F14-CP-402 | 2000-PP007-B02-10313 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F14-CP-402
F16-CP-401 | 2000-PP007-B02-10314 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F16-CP-401
F16-CP-403 | 2000-PP007-B02-10315 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F16-CP-403
F17-CP-401 | 2000-PP007-B02-10316 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F17-CP-401
F17-CP-402 | 2000-PP007-B02-10317 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F17-CP-402
F17-CP-403 | 2000-PP007-B02-10318 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F17-CP-403
F17-CP-404 | 2000-PP007-B02-10319 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F17-CP-404
F17-CP-405 | 2000-PP007-B02-10320 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F17-CP-405
F17-CP-406 | 2000-PP007-B02-10321 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F17-CP-406
F17-CP-407 | 2000-PP007-B02-10322 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F17-CP-407
F18-CP-401 | 2000-PP007-B02-10323 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F18-CP-401
F18-CP-402 | 2000-PP007-B02-10324 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F18-CP-402
F18-CP-403 | 2000-PP007-B02-10325 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F18-CP-403
F18-CP-404 | 2000-PP007-B02-10326 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F18-CP-404
F18-CP-405 | 2000-PP007-B02-10327 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F18-CP-405
F18-CP-406 | 2000-PP007-B02-10328 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F18-CP-406
F18-CP-407 | 2000-PP007-B02-10329 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F18-CP-407
F18-CP-408 | 2000-PP007-B02-10330 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F18-CP-408
F18-CP-409 | 2000-PP007-B02-10331 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F18-CP-409
F18-CP-410 | 2000-PP007-B02-10332 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F18-CP-410
F23-CP-401 | 2000-PP007-B02-10333 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F23-CP-401
F23-CP-402 | 2000-PP007-B02-10334 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F23-CP-402
F23-CP-403 | 2000-PP007-B02-10335 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F23-CP-403
F23-CP-404 | 2000-PP007-B02-10336 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F23-CP-404
F24-CP-401 | 2000-PP007-B02-10337 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F24-CP-401
F24-CP-402 | 2000-PP007-B02-10338 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F24-CP-402
F24-CP-403 | 2000-PP007-B02-10339 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F24-CP-403
F24-CP-404 | 2000-PP007-B02-10340 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F24-CP-404
F28-CP-401 | 2000-PP007-B02-10341 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F28-CP-401
F28-CP-402 | 2000-PP007-B02-10342 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F28-CP-402
F28-CP-403 | 2000-PP007-B02-10343 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F28-CP-403
F28-CP-404 | 2000-PP007-B02-10344 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F28-CP-404
F28-CP-406 | 2000-PP007-B02-10345 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F28-CP-406
F28-CP-407 | 2000-PP007-B02-10346 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F28-CP-407
F30-CP-401 | 2000-PP007-B02-10347 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F30-CP-401
F30-CP-402 | 2000-PP007-B02-10348 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F30-CP-402
F34-CP-401 | 2000-PP007-B02-10349 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F34-CP-401
F35-CP-401 | 2000-PP007-B02-10350 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F35-CP-401
F30-CP-412 | 2000-PP007-B02-10351 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F30-CP-412 (WAS F66-CP-401 - STAGE 1)
F66-CP-402 | 2000-PP007-B02-10352 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F66-CP-402
F72-CP-401 | 2000-PP007-B02-10353 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F72-CP-401
F72-CP-402 | 2000-PP007-B02-10354 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F72-CP-402
F72-CP-407 | 2000-PP007-B02-10355 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F72-CP-407
F21-CP-401 | 2000-PP007-B02-10356 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F21-CP-401
F21-CP-402 | 2000-PP007-B02-10357 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F21-CP-402
F21-CP-403 | 2000-PP007-B02-10358 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F21-CP-403
F22-CP-401 | 2000-PP007-B02-10359 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F22-CP-401
F22-CP-402 | 2000-PP007-B02-10360 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F22-CP-402
F22-CP-403 | 2000-PP007-B02-10361 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F22-CP-403
F22-CP-404 | 2000-PP007-B02-10362 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F22-CP-404
F22-CP-405 | 2000-PP007-B02-10363 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F22-CP-405
F22-CP-406 | 2000-PP007-B02-10364 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F22-CP-406
F22-CP-407 | 2000-PP007-B02-10365 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F22-CP-407
F30-CP-403 | 2000-PP007-B02-10366 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F30-CP-403
F30-CP-404 | 2000-PP007-B02-10367 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F30-CP-404
F30-CP-405 | 2000-PP007-B02-10368 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F30-CP-405
F30-CP-406 | 2000-PP007-B02-10369 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F30-CP-406
F30-CP-407 | 2000-PP007-B02-10370 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F30-CP-407
F30-CP-408 | 2000-PP007-B02-10371 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F30-CP-408
F30-CP-409 | 2000-PP007-B02-10372 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F30-CP-409
F30-CP-410 | 2000-PP007-B02-10373 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F30-CP-410
F30-CP-411 | 2000-PP007-B02-10374 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F30-CP-411
F35-CP-402 | 2000-PP007-B02-10375 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F35-CP-402 (WAS F30-CP-4BB - STAGE 2)
F65-CP-401 | 2000-PP007-B02-10377 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F65-CP-401
F72-CP-408 | 2000-PP007-B02-10381 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F72-CP-408
F72-CP-409 | 2000-PP007-B02-10382 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F72-CP-409
F72-CP-410 | 2000-PP007-B02-10383 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F72-CP-410
F72-CP-411 | 2000-PP007-B02-10384 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F72-CP-411
F72-CP-413 | 2000-PP007-B02-10386 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F72-CP-413
F72-CP-414 | 2000-PP007-B02-10387 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F72-CP-414
F23-CP-405 | 2000-PP007-B02-10388 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F23-CP-405 (WAS F35-CP-401 - STAGE 2)
F66-CP-401 | 2000-PP007-B02-10389 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F66-CP-401
F66-CP-403 | 2000-PP007-B02-10390 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F66-CP-403
F66-CP-404 | 2000-PP007-B02-10391 | GENERAL ARRANGEMENT DRAWING FOR CONTROL PANEL F66-CP-404

## Area Codes - Do Not Print (hidden)
0 | Construction Indirects
10 | Construction Indirects - Contractors
20 | Site Construction - General
30 | Site Construction Facilities
40 | Site Construction Facilities Other
50 | Construction Operations
60 | Construction Accomodation
100 | Treatment Plant - General
101 | Piperack
103 | Buried Services
104 | Overland Piping
111 | Bulk Site Earthworks
116 | Site Improvements
117 | Site Security Fencing
110
120 | Feed Preperation
121 | Primary Crushing
122 | Secondary Crushing
123 | Tertiary Crushing
124 | Dry Screening
125 | Stockpiling
130 | Milling
131 | Reclaim
132 | Grinding
133 | Classification
134 | Gravity Concentration
136 | Recycle Crushing
140 | Trash Removal & Thickening
141 | Trash Screening
142 | Feed Thickening
143 | Water Recycling
150
160 | Leaching
161 | Pre-Leach
162 | CIL
170 | Elution & Gold Room
171 | Carbon Recovery
173 | Elution
177 | Gold Room & Smelting
180 | Tails Handling
181 | Carbon Safety Screening
182 | Tails Thickening/CCDs
183 | Cyanide Destruct
184 | Tails Pumping
200 | Reagents & Plant Services
210 | Reagents
211 | Cyanide
212 | Lime
213 | Acids
214 | Caustic
215 | Flocculent
216 | Other Reagents
217 | Reagents General
218 | Reagents Storage
220 | Water Services
221 | Water Services - General
222 | Raw Water
223 | Process Water
224 | Potable Water
225 | Gland Seal Water
226 | Cooling Water
227 | Treated Water for Elution
228 | Fire Water
230 | Plant Services
232 | Water Treatment Plants
233 | Sewage Collection & Treatment
234 | Event Pond
240 | Air Services
241 | Compressed Air
242 | Blower Air
243 | Oxygen Plant
250 | Fuels
251 | Fuel Storage & Distribution
253 | Refuelling Bay
260 | Electrical Services
261 | Electrical Services - General
262 | Plant HV Distribution
263 | Plant Sub Stations
264 | Plant Control System
265 | Plant Security System'
266 | Fire Control System
300 | Infrustructure
310 | Infrustructure - General
320 | Environmental
330 | Water & Sewerage
331 | Raw Water Supply
332 | Potable Water Supply
333 | Water Treatment & Disposal
340 | Power Supply
350 | Tailings Den
351 | Tailings Storage Dam
352 | Tailings Pipeline
353 | Decant System
360 | Buildings - Admin & Security
370 | Buildings - Plant
380 | Pernament Accommodation
390
400 | Mining
410 | Mining - General
420 | Mine Establishment
430 | Mining Pre-Production
440 | Mining Consultants
450 | Mining Facilities Shared
460 | Mine Mobile Equipment (Heavy)
470 | Mine Mobile Equipment (Light)
480 | Under Ground Surface Mining Infrustructure
490 | Open Pit Mining Infrustructure
500 | Management Costs
510 | EPCM
520
530 | Specialist Consultants - Design
540 | Specialist Consultants - Construction
550 | Vendor Representatives
560
570
580
590
600 | Owners Costs
610 | Owners Costs - General
620 | Pre-Production Labour
630 | Pre-Production Other
640 | Spares Part Process Plant
650 | Fees/Taxes/Duties
660 | Environmental, Social, Land Acquisitions and Resettlement
670 | Mobile Plant Equipment
680 | Ouagadougou Office Expenses
690 | Mine Site Office Expenses
700
710
720
730
740
750
760
770
780
800 | Owners Costs
810 | Owners Costs Human Resources
820 | Owners Costs Constracts
830 | Owners Cost - Construction
840 | Owners Cost - General
850 | Owners Cost First Fills
860 | Owners Cost Mining Establishment
900 | Owners Operations Costs
910 | Owenrs Operations Costs - General

## Pivot Ref - Do Not Print (hidden)
Size | Qty | Valve Class | A/M | Reference | New/Spare | Supplier
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 1 | B03S1 | SOV | 25B03S1-SOV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
80 | 1 | F01L4 | SOV | 80F01L4-SOV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
100 | 1 | F01L4 | FCV | 100F01L4-FCV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
200 | 1 | F01L4 | FCV | 200F01L4-FCV | New | -
200 | 1 | K01L3 | SOV | 200K01L3-SOV | New | -
600 | 1 | K01L3 | SOV | 600K01L3-SOV | New | -
200 | 1 | K01L3 | SOV | 200K01L3-SOV | New | -
150 | 1 | K01L3 | SOV | 150K01L3-SOV | New | -
600 | 1 | K01L3 | SOV | 600K01L3-SOV | New | -
600 | 1 | K01L3 | SOV | 600K01L3-SOV | New | -
200 | 1 | K01L3 | SOV | 200K01L3-SOV | New | -
150 | 1 | K01L3 | SOV | 150K01L3-SOV | New | -
600 | 1 | K01L3 | SOV | 600K01L3-SOV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
80 | 1 | F01L4 | FCV | 80F01L4-FCV | New | -
250 | 1 | K01L3 | SOV | 250K01L3-SOV | New | -
250 | 1 | K01L3 | SOV | 250K01L3-SOV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
50 | 1 | K01L3 | SOV | 50K01L3-SOV | New | -
50 | 1 | K01L3 | SOV | 50K01L3-SOV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
80 | 1 | F01L4 | SOV | 80F01L4-SOV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 1 | D01L2 | FCV | 25D01L2-FCV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
150 | 1 | F01V1 | SOV | 150F01V1-SOV | New | -
100 | 1 | B01V1 | SOV | 100B01V1-SOV | New | -
100 | 1 | F01L6 | SOV | 100F01L6-SOV | New | -
100 | 1 | F01L4 | SOV | 100F01L4-SOV | New | -
80 | 1 | F01L6 | SOV | 80F01L6-SOV | New | -
50 | 1 | PRV | MAN | 50PRV-MAN | New | -
150 | 1 | B01S1 | SOV | 150B01S1-SOV | New | -
100 | 1 | B01S1 | SOV | 100B01S1-SOV | New | -
100 | 1 | F01L5 | SOV | 100F01L5-SOV | New | -
100 | 1 | F01L4 | SOV | 100F01L4-SOV | New | -
80 | 1 | F01L5 | SOV | 80F01L5-SOV | New | -
50 | 1 | PRV | MAN | 50PRV-MAN | New | -
100 | 1 | F01L6 | SOV | 100F01L6-SOV | New | -
80 | 1 | F01L5 | SOV | 80F01L5-SOV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
80 | 1 | F01L5 | SOV | 80F01L5-SOV | New | -
80 | 1 | F01L5 | SOV | 80F01L5-SOV | New | -
80 | 1 | F01L5 | SOV | 80F01L5-SOV | New | -
50 | 1 | B03S1 | SOV | 50B03S1-SOV | New | -
50 | 1 | B03S1 | SOV | 50B03S1-SOV | New | -
100 | 1 | F01L4 | SOV | 100F01L4-SOV | New | -
100 | 1 | F01L4 | SOV | 100F01L4-SOV | New | -
100 | 1 | F01L5 | SOV | 100F01L5-SOV | New | -
100 | 1 | F01L5 | SOV | 100F01L5-SOV | New | -
80 | 1 | F01L5 | SOV | 80F01L5-SOV | New | -
100 | 1 | F01L5 | SOV | 100F01L5-SOV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
50 | 1 | B03S1 | SOV | 50B03S1-SOV | New | -
50 | 1 | B03S1 | SOV | 50B03S1-SOV | New | -
80 | 1 | F01L5 | SOV | 80F01L5-SOV | New | -
80 | 1 | F01L5 | SOV | 80F01L5-SOV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
50 | 1 | F01L5 | SOV | 100F01L5-SOV | New | -
50 | 1 | F01L5 | SOV | 100F01L5-SOV | New | -
50 | 1 | F01L5 | SOV | 100F01L5-SOV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
200 | 1 | K01L3 | SOV | 200K01L3-SOV | New | -
500 | 1 | K01L3 | SOV | 500K01L3-SOV | New | -
150 | 1 | K01L3 | SOV | 150K01L3-SOV | New | -
100 | 1 | K01L3 | SOV | 100K01L3-SOV | New | -
500 | 1 | K01L3 | SOV | 500K01L3-SOV | New | -
500 | 1 | K01L3 | SOV | 500K01L3-SOV | New | -
150 | 1 | K01L3 | SOV | 150K01L3-SOV | New | -
100 | 1 | K01L3 | SOV | 100K01L3-SOV | New | -
500 | 1 | K01L3 | SOV | 500K01L3-SOV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
100 | 1 | F01L4 | SOV | 100F01L4-SOV | New | -
25 | 1 | B03S1 | SOV | 25B03S1-SOV | New | -
25 | 1 | B03S1 | SOV | 25B03S1-SOV | New | -
25 | 1 | PRV | MAN | 25PRV-MAN | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 1 | B03S1 | SOV | 25B03S1-SOV | New | -
50 | 1 | F01L4 | SOV | 50F01L4-SOV | New | -
25 | 1 | PRV | MAN | 25PRV-MAN | New | -
25 | 1 | B03S1 | SOV | 25B03S1-SOV | New | -
50 | 1 | F01L4 | SOV | 50F01L4-SOV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 1 | B03S1 | SOV | 25B03S1-SOV | New | -
25 | 1 | B03S1 | SOV | 25B03S1-SOV | New | -
40 | 1 | B03S1 | SOV | 40B03S1-SOV | New | -
40 | 1 | B03S1 | SOV | 40B03S1-SOV | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
50 | 1 | PCV | MAN | 50PCV-MAN | New | -
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | 1 | #REF! | #REF! | #REF! | #REF! | #REF!
50 | 1 | B03S3 | SOV | 50B03S3-SOV | New | -

## Pivot Table - Do Not Print (hidden)
Row Labels | Sum of Qty | Spares
B01S1 | 2
100 | 1
150 | 1
B01V1 | 1 | 1
100 | 1
B03S1 | 13 | 2
25 | 7
50 | 4
40 | 2
D01L2 | 1 | 2
25 | 1
F01L4 | 12 | 1
50 | 2 | 1
80 | 3
100 | 6 | 50
200 | 1 | 30
F01L5 | 15 | 2
50 | 3
80 | 8 | 4
100 | 4 | 2
F01L6 | 3
80 | 1
100 | 2
K01L3 | 22
50 | 2 | 2
100 | 2 | 3
150 | 4
200 | 4 | 1
250 | 2 | 2
500 | 4 | 1
600 | 4 | 1
PRV | 4
25 | 2
50 | 2
PCV | 1 | 2
50 | 1 | 1
#REF! | 757 | 2
#REF! | 757
F01V1 | 1 | 4
150 | 1 | 5
Grand Total | 832
2
2
1
5
4
4
2
1
1
1
1
4
2
1
1
1
1
2
2
1
2
1
2
2
2
1