## Revisions
PROCESS CONTROL TABLES
REVISION HISTORY
KCGM GROWTH PROJECT
2000-F19-LST-PR-10001
NORTHERN STAR RESOURCES LIMITED
Revision
Date
2024-05-20
2024-09-09
2025-01-22
Document Changes
- Vendor Data TBC highlighted or red-text
- Vendor Data TBC highlighted or red-text
A for Internal Review
- Vendor Data TBC highlighted or red-text
B for Client Review
0 for Design

## 1. Analogue Input
KCGM GROWTH PROJECT
ANALOGUE INPUT
[6 empty] | Range |  |  | Process Switchpoints | [5 empty] | Alarms
Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | Trend (sec) | Min | Max | Unit | P_LL |  |  |  |  | P_HH | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Comments | Rev
ZS19411A/B | ZI19411 | 2000-F19-PID-PR-10007 | F19-CR-431 Hoist Position | F19CR431 Hoist Position | 1 | 0 | 8330 | mm |  | 5 | [13 empty] | Calculate position using outputs from quadrature output encoders: ZS19411A/B (see Digital Input tab) Refer to 2000-ME067-M02-10000 End points to be calibrated during commissioning. Hoist movement distance/counts ratio to be confirmed during commissioning. | B
ZS19412A/B | ZI19412 | 2000-F19-PID-PR-10007 | F19-CR-431 Trolley Position | F19CR431 TrolleyPosition | 1 | 0 | 14273 | mm |  | 90 | [13 empty] | Calculate position using outputs from quadrature output encoders: ZS19412A/B (see Digital Input tab) Refer to 2000-ME067-M02-10000 End points to be calibrated during commissioning. Trolley movement distance/counts ratio to be confirmed during commissioning. | B
ET19429 | EI19429 | 2000-F19-PID-PR-10007 | F19-BLC-401 Voltage Transducer | F19BLC401 Voltage | 1 | 0 | 300 | V DC | [10 empty] | 285 | 5 |  |  |  | 4-20 mA | A
IT19430 | II19430 | 2000-F19-PID-PR-10007 | F19-BLC-401 Current Transducer | F19BLC401 Current | 1 | 0 | 50 | A DC | [10 empty] | 47.5 | 5 |  |  |  | 4-20 mA | A
LIT19755 | LI19755 | 2000-F19-PID-PR-10006 | F19-BN-61A Ball Charging Bin 1 Level | F19BN61A Level | 1 | 0 | 100 | % |  | 75 | 5 | 90 | 5 |  |  |  | 30 | 5 | 97 | 5 |  |  |  | Hopper 1 Level Transmitter (North) 0-100% 4-20 mA | A
LIT19756 | LI19756 | 2000-F19-PID-PR-10006 | F19-BN-61B Ball Charging Bin 2 Level | F19BN61B Level | 1 | 0 | 100 | % | [8 empty] | 30 | 5 | 97 | 5 |  |  |  | Hopper 2 Level Transmitter (Middle) 0-100% 4-20 mA | A
LIT19757 | LI19757 | 2000-F19-PID-PR-10006 | F19-BN-61C Ball Charging Bin 3 Level | F19BN61C Level | 1 | 0 | 100 | % | [8 empty] | 30 | 5 | 97 | 5 |  |  |  | Hopper 3 Level Transmitter (South) 0-100% 4-20 mA | A
WIT19401 | WI19401 | 2000-F19-PID-PR-10007 | F19-BLC-401 Load Cell | F19BLC401 Load Cell | 1 | 0 | 3200 | kg |  | 100 | 5 | [7 empty] | 2880 | 5 | 3040 | 5 |  | Vendor Reference : U1_LC U1 Load Cell Transmitter 0-3200 kg 4-20 mA Alarm setpoints to be confirmed during commissioning | B

## 3. Digital Input
KCGM GROWTH PROJECT
DIGITAL INPUT
DIGITAL INSTRUMENTS (DI)
Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Source | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev
ZS19411A | ZI19411A | 2000-F19-PID-PR-10007 | F19-CR-431 Hoist Encoder A | F19CR431 Hoist Enc. A | Low | High |  | Hardwired to PCS |  |  |  | Vendor Reference : V_ENC_A VERTICAL ENCODER A Hoist encoder Channel A signal. Output position value to ZI19411 Incremental encoder. Refer to 2000-ME067-M02-10000 | B
ZS19411B | ZI19411B | 2000-F19-PID-PR-10007 | F19-CR-431 Hoist Encoder B | F19CR431 Hoist Enc. B | Low | High |  | Hardwired to PCS |  |  |  | Vendor Reference : V_ENC_B VERTICAL ENCODER B Hoist encoder Channel B signal. Output position value to ZI19411 Incremental encoder. Refer to 2000-ME067-M02-10000 | B
ZS19412A | ZI19412A | 2000-F19-PID-PR-10007 | F19-CR-431 Trolley Encoder A | F19CR431 Tro. Enc. A | Low | High |  | Hardwired to PCS |  |  |  | Vendor Reference : H_ENC_A HORIZONTAL ENCODER A Trolley encoder Channel A signal. Output position value to ZI19412 Incremental encoder. Refer to 2000-ME067-M02-10000 | B
ZS19412B | ZI19412B | 2000-F19-PID-PR-10007 | F19-CR-431 Trolley Encoder B | F19CR431 Tro. Enc. B | Low | High |  | Hardwired to PCS |  |  |  | Vendor Reference : H_ENC_B HORIZONTAL ENCODER B Trolley encoder Channel B signal. Output position value to ZI19412 Incremental encoder. Refer to 2000-ME067-M02-10000 | B
HS19420A | HS19420AAUT | 2000-F19-PID-PR-10007 | F19-BLC-401 Local Automatic Mode | F19BLC401 Local Auto | Inactive | Active |  | Hardwired to PCS |  |  |  | e Local Mode operating in Auto. Allows for Auto-Start (HS19420DSTT) via LCP. Refer to 2000-ME067-M02-10000 | B
HS19420B | HS19420BAUT | 2000-F19-PID-PR-10007 | F19-BLC-401 Remote Automatic Mode | F19BLC401 Remote Auto | Inactive | Active |  | Hardwired to PCS |  |  |  | e Remote Mode operating in Auto. A inl l Mow iss f o tar A ).uto-Start remotely via DCS (see BLC_REM_STRT/STOP c b Refer to 2000-ME067-M02-10000 | B
HS19420C | HS19420CMAN | 2000-F19-PID-PR-10007 | F19-BLC-401 Local Manual Mode | F19BLC401 Local Manual | Inactive | Active |  | Hardwired to PCS |  |  |  | e Local Mode operating in Manual. Allows for manual controls via LCP (see HS19420FFWD, HS19420GFST, HS19420HREV, HS19420JUP, HS19420KFST and HS19420MDWN in Digital Input tab). Refer to 2000-ME067-M02-10000 | B
HS19420D | HS19420DSTT | 2000-F19-PID-PR-10007 | F19-BLC-401 LCP Auto-Start Push Button | F19BLC401 LCP AutoStart | Inactive | Active |  | Hardwired to PCS |  |  |  | o N/O push button on LCP to start auto ball loading. Refer to 2000-ME067-M02-10000 ) | B
HS19420E | HS19420ESTP | 2000-F19-PID-PR-10007 | F19-BLC-401 LCP Stop Pushbutton | F19BLC401 Stop | Inactive | Active |  | Hardwired to PCS |  |  |  | Vendor Reference: STOP S3 Stop N/O push button on LCP to stop the auto ball loading sequence at the end of the current cycle. Refer to 2000-ME067-M02-10000 A , l | B
HS19420F | HS19420FFWD | 2000-F19-PID-PR-10007 | F19-CR-431 LCP Trolley Forward Manual Pushbutton | F19CR431 Tro. Fwd | Inactive | Active |  | Hardwired to PCS |  |  |  | N/O local push button on LCP drives trolley forward towards north when signal is high via output XC19428B Refer to 2000-ME067-M02-10000 | B
HS19420G | HS19420GFST | 2000-F19-PID-PR-10007 | F19-CR-431 LCP Trolley Fast Manual Pushbutton | F19CR431 Tro. Fast | Inactive | Active |  | Hardwired to PCS |  |  |  | e y Fast The HS19420FFWD and HS19420HREV buttons on LCP are two step action buttons. The first action will drive the trolley forward (HS19420FFWD) or reverse (HS19420HREV). The secondary action will energise HS19420GFST and therefore output XC19428D. Refer to 2000-ME067-M02-10000 | B
HS19420H | HS19420HREV | 2000-F19-PID-PR-10007 | F19-CR-431 LCP Trolley Reverse Pushbutton | F19CR431 Tro. Rev | Inactive | Active |  | Hardwired to PCS |  |  |  | N/O local push button on LCP drives trolley in reverse towards south when signal is high via output XC19428C Refer to 2000-ME067-M02-10000 | B
HS19420J | HS19420JUP | 2000-F19-PID-PR-10007 | F19-CR-431 LCP Hoist Up Pushbutton | F19CR431 Hoist Up | Inactive | Active |  | Hardwired to PCS |  |  |  | s t N/O hoist up push button on LCP will raise hoist when signal is high via output XC19428E Refer to 2000-ME067-M02-10000 | B
HS19420K | HS19420KFST | 2000-F19-PID-PR-10007 | F19-CR-431 LCP Hoist Fast Pushbutton | F19CR431 Hoist Fast | Inactive | Active |  | Hardwired to PCS |  |  |  | The hoist up (HS19420JUP) and down (HS19420MDWN) push buttons on LCP, are two step action buttons. The secondary action HS19420KFST and therefore output XC19428G Refer to 2000-ME067-M02-10000 | B
HS19420M | HS19420MDWN | 2000-F19-PID-PR-10007 | F19-CR-431 LCP Hoist Down | F19CR431 Hoist Down | Inactive | Active |  | Hardwired to PCS |  |  |  | s t N/O hoist down push button on LCP will lower hoist when signal is high via output XC19428F Refer to 2000-ME067-M02-10000 | B
XS19421 | XA19421 | 2000-F19-PID-PR-10007 | F19-BLC-401 Emergency Stop Feedback | F19BLC401 EStop | Alarm | Normal | Alarm | Hardwired to PCS |  | 0 |  | CONTACT N/C emergency stop push button shuts down power to magnet and hoist/trolley system Refer to 2000-ME067-M02-10000 | B
XS19422 | XA19422 | 2000-F19-PID-PR-10007 | F19-BLC-401 Circuit Breaker Trip Feedback | F19BLC401 CB Trip | Healthy | Alarm | Alarm | Hardwired to PCS |  | 3 |  | r Auxiliary NO contact for Trans CB, Lift AC CB, Dump AC CB or Lift DC CB Refer to 2000-ME067-M02-10000 | B
XS19423 | XA19423 | 2000-F19-PID-PR-10007 | F19-BLC-401 Earth Trip | F19BLC401 Earth Trip | Normal | Alarm | Alarm | Hardwired to PCS |  | 3 |  | The Bender relay will open its ELD-K1 contact on fault as an advisory to the DCS. Refer to 2000-ME067-M02-10000 | B
ZS19410 | ZI19410 | 2000-F19-PID-PR-10007 | F19-CR-431 Upper Advisory Limit | F19CR431 Upper Adv Limit | Active (at upper limit) | Inactive (Below upper limit) |  | Hardwired to PCS |  |  |  | r t A N/C limit switch opens when hoist has reached upper limit Used as vertical home position to zero traverse enconder (ZI19411) in F19-SEQ-0004. Refer to 2000-ME067-M02-10000 Reduce to 1 second debounce | 0
XS19424 | XA19424 | 2000-F19-PID-PR-10007 | F19-CR-431 Trolley Fault | F19CR431 Trolley Fault | Normal | Fault | Fault | Hardwired to PCS |  | 3 |  | Fault is detected P13 will be low. Refer to 2000-ME067-M02-10000 | B
XS19425 | XA19425 | 2000-F19-PID-PR-10007 | F19-CR-431 Hoist Fault | F19CR431 Hoist Fault | Normal | Fault | Fault | Hardwired to PCS |  | 3 |  | t a Fault is detected P14 will be low. Refer to 2000-ME067-M02-10000 | B
ZS19404 | ZA19404 | 2000-F19-PID-PR-10007 | F19-CR-431 Bunker 1 End of Travel | F19CR431 Bunker 1 EOT | Normal (ZS19404 Closed, normal travel limits) | Alarm (ZS19404 Open, exceeded normal travel limits) | Alarm (ZS19404 Open, exceeded normal travel limits) | Hardwired to PCS |  | 1 |  | l y N/C limit switch opens when travel has exceeded normal limits. Refer to 2000-ME067-M02-10000 | B
ZS19409 | ZI19409 | 2000-F19-PID-PR-10007 | F19-CR-431 Bunker 1 Position Limit Switch | F19CR431 Bunker 1 LS | Inactive | Active |  | Hardwired to PCS |  |  |  | N/O Proximity limit switch closes when in position. Used as horizontal home position to zero traverse enconder (ZI19412) in F19-SEQ-0004. Refer to 2000-ME067-M02-10000 Reduce to 1 second debounce | 0
ZS19401 | ZI19401 | 2000-F19-PID-PR-10007 | F19-CR-431 Hopper 1 Position Limit Switch | F19CR431 Hopper 1 LS | Inactive | Active |  | Hardwired to PCS |  |  |  | r N/O Proximity limit switch closes when in position. Refer to 2000-ME067-M02-10000 Reduce to 1 second debounce | B
ZS19402 | ZI19402 | 2000-F19-PID-PR-10007 | F19-CR-431 Hopper 2 Position Limit Switch | F19CR431 Hopper 2 LS | Inactive | Active |  | Hardwired to PCS |  |  |  | r N/O Proximity limit switch closes when in position. Refer to 2000-ME067-M02-10000 Reduce to 1 second debounce | B
ZS19408 | ZI19408 | 2000-F19-PID-PR-10007 | F19-CR-431 Bunker 2 Position Limit Switch | F19CR431 Bunker 2 LS | Inactive | Active |  | Hardwired to PCS |  |  |  | N/O Proximity limit switch closes when in position. Refer to 2000-ME067-M02-10000 Reduce to 1 second debounce | B
ZS19403 | ZI19403 | 2000-F19-PID-PR-10007 | F19-CR-431 Hopper 3 Position Limit Switch | F19CR431 Hopper 3 LS | Inactive | Active |  | Hardwired to PCS |  |  |  | r N/O Proximity limit switch closes when in position. Refer to 2000-ME067-M02-10000 Reduce to 1 second debounce | B
ZS19406 | ZI19406 | 2000-F19-PID-PR-10007 | F19-CR-431 Maintenance Position Limit Switch | F19CR431 Mntenance LS | Inactive | Active |  | Hardwired to PCS |  |  |  | a N/O Proximity limit switch closes when in position. Refer to 2000-ME067-M02-10000 Reduce to 1 second debounce | B
ZS19405 | ZA19405 | 2000-F19-PID-PR-10007 | F19-CR-431 Maintenance End of Travel | F19CR431 Mntenance EOT | Normal (ZS19405 Closed, normal travel limits) | Alarm ZS19405 Open, exceeded normal travel limits | Alarm ZS19405 Open, exceeded normal travel limits | Hardwired to PCS |  | 1 |  | a E l visory N/C limit switch opens when travel has exceeded normal limits. Refer to 2000-ME067-M02-10000 | B
XS19426 | XA19426 | 2000-F19-PID-PR-10007 | F19-CR-431 Running Feedback | F19CR431 Running FB | Inactive (KM1 Contactor Deenergised) | Active (KM1 Contactor Energised) | Inactive (KM1 Contactor Deenergised) | Hardwired to PCS |  | 3 |  | / N/O contact feedback from contactor in Trolley/Hoist control panel. Refer to 2000-ME067-M02-10000 KM1 Contactor energised by: • Locally by pressing START on the pendant OR • Remotely by energising XC19428H (RL18). | B
XY19427A | XC19427A | 2000-F19-PID-PR-10007 | F19MG405 Lift DC | Inactive As per F19-SEQ-0003 | Active As per F19-SEQ-0003 |  |  |  |  | Vendor Reference: RL1_LIFT_DC RL1 Lift DC Relay Configures the DC circuit for lift polarity. | A
XY19427B | XC19427B | 2000-F19-PID-PR-10007 | F19MG405 Dump DC | Inactive As per F19-SEQ-0003 | Active As per F19-SEQ-0003 |  |  |  |  | Vendor Reference: RL2_DUMP_DC RL2 Dump DC Relay Configures the DC circuit for Dump polarity. | A
XY19427C | XC19427C | 2000-F19-PID-PR-10007 | F19MG405 Lift AC Red. | Inactive As per F19-SEQ-0003 | Active As per F19-SEQ-0003 |  |  |  |  | Vendor Reference: RL3_LIFT_AC_RED RL3 Reduced Lift AC Relay Closes the Reduced power contactor on the transformer secondary. | A
XY19427D | XC19427D | 2000-F19-PID-PR-10007 | F19MG405 Dump AC | Inactive As per F19-SEQ-0003 | Active As per F19-SEQ-0003 |  |  |  |  | Vendor Reference: RL4_DUMP_AC RL4 Dump AC Relay Closes the Dump power contactor on the transformer secondary. | A
XY19427E | XC19427E | 2000-F19-PID-PR-10007 | F19MG405 Lift AC Full | Inactive As per F19-SEQ-0003 | Active As per F19-SEQ-0003 |  |  |  |  | Vendor Reference: RL5_LIFT_AC_FUL RL5 Full Lift AC Relay Closes the Full power contactor on the transformer secondary. | A
XY19427F | XC19427F | 2000-F19-PID-PR-10007 | F19BLC401 Standby Idle | Inactive | Active if (else inactive): F19CR431_MXDUTY = Inactive AND XC19427H, XC19427K AND XC19428A = Inactive AND XA19421, XA19422, XA19423, XA19424 AND XA19425 = Inactive AND F19-CR-431 AND F19-BLC-401 Drive Healthy, E- Stop Inactive AND MCC Healthy |  |  |  |  | Vendor Reference: RL6_IDLE RL6 Standby Idle Standby Idle must be energised to enable local earth leak testing. Hoist and Trolley is in the home position and all fault conditions are healthy. | A
XY19427G | XC19427G | 2000-F19-PID-PR-10007 | F19BLC401 Power On | Inactive | Active |  |  |  |  | Vendor Reference: RL7_PWR RL7 Power On Energises local indication and enables release of mechanical latches | A
XY19427H | XC19427H | 2000-F19-PID-PR-10007 | F19MG405 Fault | Inactive | Alarm F19-MG-405 Magnet Fault | Alarm F19-MG-405 Magnet Fault |  | 3 |  | Vendor Reference: RL8_MAG_FLT RL8 Magnet Fault Energises local indication of Magnet Fault Status. | 0
XY19427J | XC19427J | 2000-F19-PID-PR-10007 | F19BLC401 Dump Cycle | Inactive As per F19-SEQ-0003 | Active As per F19-SEQ-0003 |  |  |  |  | Vendor Reference: RL9_DMP_CYC RL9 Dump Cycle in Progress Energises local indication for duration of dump and back emf discharge cycle. | A
XY19427K | XC19427K | 2000-F19-PID-PR-10007 | F19CR431 Tro. Overload | Inactive | Alarm F19-CR-431 Trolley Motor 1 OR 2 VSD Fault | Alarm F19-CR-431 Trolley Motor 1 OR 2 VSD Fault |  | 3 |  | Vendor Reference: RL10_TRO_FLT RL10 Trolley Fault Energises local indication of Trolley fault as signalled by Trolley/Hoist control panel. | 0
XY19428A | XC19428A | 2000-F19-PID-PR-10007 | F19CR431 Hoist Overload | Inactive | Alarm F19-CR-431 Hoist Motor VSD Fault | Alarm F19-CR-431 Hoist Motor VSD Fault |  | 3 |  | Vendor Reference: RL11_HST_FLT RL11 Hoist Fault Energises local indication of Trolley fault as signalled by Trolley/Hoist control panel. | 0
XY19428B | XC19428B | 2000-F19-PID-PR-10007 | F19CR431 Trolley Fwd | Inactive | Active if (else inactive): Auto: 'HS19420AAUT OR HS19420BAUT Active' AND As per Sequence F19-SEQ-0003 OR F19-SEQ- 0004 OR Manual: HS19420CMAN Active AND HS19420FFWD Active |  |  |  |  | Vendor Reference: RL12_TRO_FWD RL12 Trolley Forward Energising XC19428B closes N/O contact in Trolley/Hoist control panel acting on Trolley Forward contactor. Ensure YA19401 Beacon is ACTIVATED whilst F19-CR-431 Trolley driving forward. Force inactive as priority (2 second delay) if: • XC19428E OR XC19428F Active OR • XC19428C Active OR • ZA19404 Active OR | 0
XY19428C | XC19428C | 2000-F19-PID-PR-10007 | F19CR431 Trolley Rev | Inactive | Active if (else inactive): Auto: 'HS19420AAUT OR HS19420BAUT Active' AND As per Sequence F19-SEQ-0003 OR F19-SEQ- 0004 OR Manual: HS19420CMAN Active AND HS19420HREV Active |  |  |  |  | Vendor Reference: RL13_TRO_REV RL13 Trolley Reverse Energising XC19428C closes N/O contact in Trolley/Hoist control panel acting on Trolley Reverse contactor. Ensure YA19401 Beacon is ACTIVATED whilst F19-CR-431 Trolley driving reverse. Force inactive as priority (2 second delay) if: • XC19428E OR XC19428F Active OR • XC19428B Active OR • ZA19405 Active OR • [ZI19412.PV >= ABS_H_ENC_HPR3.SV + ABS_H_ENC_HPR3_Y.SV] AND [F19-BLC-401 Magnet | 0
XY19428D | XC19428D | 2000-F19-PID-PR-10007 | F19CR431 Trolley Fast | Inactive | Active if (else inactive): Auto: 'HS19420AAUT OR HS19420BAUT' Active AND As per Sequence F19-SEQ-0003 OR F19-SEQ- 0004 OR Manual: HS19420CMAN Active AND HS19420GFST Active AND 'XC19428B OR XC19428C' Active |  |  |  |  | Vendor Reference: RL14_TRO_FST RL14 Trolley Fast Energising XC19428D closes N/O contact in Trolley/Hoist control panel acting on Trolley Fast contactor. | A
XY19428E | XC19428E | 2000-F19-PID-PR-10007 | F19CR431 Hoist Up | Inactive | Active if (else inactive): Auto: 'HS19420AAUT OR HS19420BAUT' Active AND As per Sequence F19-SEQ-0003 OR F19-SEQ- 0004 OR Manual: HS19420CMAN Active AND HS19420JUP Active |  |  |  |  | Vendor Reference: RL15_HST_UP RL15 Hoist Up Energising XC19428E closes N/O contact in Trolley/Hoist control panel acting on Hoist Up contactor. Force inactive as priority (2 second delay) if: • XC19428B OR XC19428C Active OR • XC19428F Active OR • ZI19410 Inactive | A
XY19428F | XC19428F | 2000-F19-PID-PR-10007 | F19CR431 Hoist Down | Inactive | Active if (else inactive): Auto: HS19420AAUT OR HS19420BAUT' Active AND As per Sequence F19-SEQ-0003 OR F19-SEQ- 0004 OR Manual: HS19420CMAN Active AND HS19420MDWN Active AND |  |  |  |  | Vendor Reference: RL16_HST_DWN RL16 Hoist Down Energising XC19428F closes N/O contact in Trolley/Hoist control panel acting on Hoist Down contactor. Force inactive as priority (2 second delay) if: • XC19428B OR XC19428C Active OR • XC19428E Active OR • [ZI19411.PV >= ABS_V_ENC_BNKL.SV AND [ZI19412.PV within ABS_H_ENC_BKR1.SV ± ABS_H_ENC_TLR OR ZI19409 Active OR ZI19412.PV within ABS_H_ENC_BKR2.SV ± ABS_H_ENC_TLR OR ZI19408 Active]] OR • [ZI19411.PV >= ABS_V_ENC_DMP1.SV AND [ZI19412.PV within ABS_H_ENC_HPR1.SV ± ABS_H_ENC_TLR OR ZI19401 Active OR ZI19412.PV within ABS_H_ENC_HPR2.SV ± ABS_H_ENC_TLR OR ZI19402 Active OR ZI19412.PV within ABS_H_ENC_HPR3.SV ± ABS_H_ENC_TLR OR ZI19403 Active]] OR • [ZI19411.PV >= ABS_V_ENC_LWR.SV AND [ZI19412.PV within ABS_H_ENC_MNT.SV ± ABS_H_ENC_TLR OR ZI19406 Active]] OR • [[ZI19412.PV not within ABS_H_ENC_BKR1.SV ± ABS_H_ENC_TLR OR ZI19409 Inactive] AND [ZI19412.PV not within ABS_H_ENC_HPR1.SV ± ABS_H_ENC_TLR OR ZI19401 Inactive] AND [ZI19412.PV not within ABS_H_ENC_HPR2.SV ± ABS_H_ENC_TLR OR ZI19402 Inactive] AND [ZI19412.PV not within ABS_H_ENC_BKR2.SV ± ABS_H_ENC_TLR OR ZI19408 Inactive] AND [ZI19412.PV not within ABS_H_ENC_HPR3.SV ± ABS_H_ENC_TLR OR ZI19403 Inactive] AND [ZI19412.PV not within ABS_H_ENC_MNT.SV ± ABS_H_ENC_TLR OR ZI19406 Inactive]] | 0
XY19428G | XC19428G | 2000-F19-PID-PR-10007 | F19CR431 Hoist Fast | Inactive | Active if (else inactive): Auto: 'HS19420AAUT OR HS19420BAUT' Active AND As per Sequence F19-SEQ-0003 OR F19-SEQ- 0004 OR Manual: HS19420CMAN Active AND HS19420KFST Active AND 'XC19428E OR XC19428F' Active |  |  |  |  | Vendor Reference: RL17_HST_FST RL17 Hoist Fast Energising XC19428G closes N/O contact in Trolley/Hoist control panel acting on Hoist Fast contactor. | A
XY19428H | XC19428H | 2000-F19-PID-PR-10007 | F19BLC401 System Start | Inactive | Active if (else inactive): As per F19-SEQ-0004 OR Locally by pressing START on the pendant OR Remotely energised by CRO (include PB on DCS) |  |  |  |  | Vendor Reference: RL18_SYS_SRT RL18 Trolley/Hoist System Start Energising XC19428H closes N/O contact in Trolley/Hoist control panel acting on System Start relay. Designed for momentary action with a 3 second off delay. Sounds Trolley Horn. Activated the HORN/BEACON for 5 seconds. Energising XC19428H will energise KA1 and therefore latch KM1 contactor. | B
XY19428J | XC19428J | 2000-F19-PID-PR-10007 | SAG Bunker Traffic Light | ZI19409 Active (Red) | ZI19409 Inactive (Green) |  |  |  |  | Vendor Reference: RL19_BNK1_IL RL19 Bunker 1 Traffic Light Energise XC19428J when ZI19409 'Bunker 1' INACTIVE, illuminating the traffic light green. De-Energise XC19428J when ZI19409 'Bunker 1' ACTIVE, illuminating the traffic light red. | A
XY19428K | XC19428K | 2000-F19-PID-PR-10007 | Ball Bunker TrafficLight | ZI19408 Active (Red) | ZI19408 Inactive (Green) |  |  |  |  | Vendor Reference: RL20_BNK2_IL RL20 Bunker 2 Traffic Light Energise XC19428K when ZI19408 'Bunker 2' INACTIVE, illuminating the traffic light green. De-Energise XC19428K when ZI19408 'Bunker 2' ACTIVE, illuminating the traffic light red. | A

## 5. Totalisers
KCGM GROWTH PROJECT
TOTALISERS
Reset Period
Tag Source | Tag Name | Type | P&ID | Description | Abbreviated Description (Faceplate) | Units | Shift | Day | Cont | Comments | Rev
WIT19401 | WQI19401A | WQI | 2000-F19-PID-PR-10007 | F13-BN-61A Mill Ball Transfer Totaliser | F13-BN-61A Totaliser | t | X | X | X | Totalise as per F19-SEQ-0003 Step 24 | A

## 6. OnOff Valves
KCGM GROWTH PROJECT
ONOFF VALVES
Permissives and Trips
Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open | Close | Bypass | Reset Required | Comments | Rev

## 7. Control Valves
KCGM GROWTH PROJECT
CONTROL VALVES
Permissive and Trips
Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open | Close | Bypass | Reset Required | Comments | Rev

## 8. PID Cont
KCGM GROWTH PROJECT
PID CONT
[5 empty] | Modes |  |  |  | Setpoint |  |  | Range |  |  | Process Switchpoints |  | Alarms |  |  | Controlled/Manipulated Variable
Tag Source | Tag Name | P&ID | Abbreviated Description (Faceplate) | Normal Operating Mode | Manual | Auto | Cascade | Process Value Tag | Min | Max | Unit | Min | Max | Unit | P_LL | P_HH | A_LL | A_HH | Alarm Masking Conditions | Range Min | Range Max | Lower Limit | Upper Limit | Unit | Destination Description | Destination (Output) Tag | Direct / Reverse Acting | P | I | D | Comment | Rev

## 9. Drives
KCGM GROWTH PROJECT
DRIVES
Interlocks
Tag Name | P&ID | Name | Drive Type | Speed Min | Speed Max | Speed Units | SP Lower Limit | SP Upper Limit | Current Max | Manual | Auto | Start Condition (Auto Mode) | Stop Condition (Auto Mode) | # | Description (Unhealthy Interlocks and Healthy Start Permissives) | Delay On | Delay Off | Start Permissive | Process | Critical | Hardwired to Drive | Bypass | Reset Required | Comments | Rev
F19-CR-431_T | - | BALL CHARGING MAGNET SYSTEM TROLLEY | N/A | [6 empty] | X | X | XC19428B (Fwd) Active OR XC19428C (Rev) Active NOTE: Incorporate a delay (F19BLC401_T1 Misc tab) between activating XC19428B/C and energising the drive. | XC19428B (Fwd) Inactive AND XC19428C (Rev) Inactive NOTE: Deenergising this drive will start F19BLC401_T2 |  |  | 0 0 0 0 0 0 0 0 0 0 5 5 3 0 0 0 |  |  |  | X X X X X X X X X X X X X X X X | X |  | X X
[14 empty] | 1 | F19-CR-431_T Comms Failure | [9 empty] | A
[14 empty] | 2 | F19-CR-431_T Fail to Start / Stop | [9 empty] | 0
[14 empty] | 3 | F19-CR-431_T Drive Fault | [9 empty] | 0
[14 empty] | 4 | F19-CR-431_T E-Stop | [9 empty] | 0
[14 empty] | 5 | F19-CR-431_T MCC Unhealthy | [9 empty] | A
[14 empty] | 6 | F19-CR-431_T Drive Out of Service | [9 empty] | 0
[14 empty] | 7 | F19-CR-431_T Drive Ready | [9 empty] | 0
[14 empty] | 8 | XA19421 Alarm Trolley Duty Cycle Exceeded ZI19410 Active XC19428B & C Active XC19428E/F Active XC19427K Active ZA19404 Alarm ZA19405 Alarm Trolley Loaded Outside Limit | [8 empty] | Emergency Stop active Logic: F19CR431_MXDUTY Active F19-CR-431 Trolley motor => Max Duty Cycle Logic: ZI19410 Active AND [XC19428B OR XC19428C Active] F19-CR-431 Hoist not at Upper Advisory Limit and Trolley Forward or Reverse relay active Logic: XC19428B Active AND XC19428C Active F19-CR-431 Reverse and Forward Relays active simultaneously Logic: XC19428E Active OR XC19428F Active F19-CR-431 Hoist Up or Down Relays active F19-CR-431 Trolley Overload Logic: ZA19404 Active AND XC19428B Active F19-CR-431 Bunker 1 End of Travel Limit active Logic: ZA19405 Active AND XC19428C Active F19-CR-431 Maintenance End of Travel Limit active Logic: [ZI19412.PV >= ABS_H_ENC_HPR3.SV + ABS_H_ENC_HPR3_Y.SV] AND XC19428C = Active F19-CR-431 Trolley Reverse to de-energise if: • Trolley is travelling past Hopper 3 (toward maintenance bay) Refer to page 16, Table 1 of 2000-ME067-ME02-10000 | A A A A A A A A A
9
10
11
12
13
14
15
16
F19-CR-431_H | - | BALL CHARGING MAGNET SYSTEM HOIST | N/A | [6 empty] | X | X | XC19428E (Up) Active OR XC19428F (Down) Active | XC19428E (Up) Inactive AND XC19428F (Down) Inactive |  |  | 0 0 0 0 0 0 0 0 5 5 3 0 3 5 |  | X | X | X X X X X X X X X X X X | X | X X
[14 empty] | 1 | F19-CR-431_H Comms Failure | [9 empty] | A
[14 empty] | 2 | F19-CR-431_H Fail to Start / Stop | [9 empty] | 0
[14 empty] | 3 | F19-CR-431_H Drive Fault | [9 empty] | 0
[14 empty] | 4 | F19-CR-431_H E-Stop | [9 empty] | 0
[14 empty] | 5 | F19-CR-431_H MCC Unhealthy | [9 empty] | A
[14 empty] | 6 | F19-CR-431_H Drive Out of Service | [9 empty] | 0
[14 empty] | 7 | F19-CR-431_H Drive Ready | [9 empty] | 0
[14 empty] | 8 | XA19421 Alarm XC19428B/C Active XC19428E & F Active XC19428A Alarm F19BLC401_T2 Elapsed WI19401 >= A_HH Hoist Horizontal Out of Range | [8 empty] | Emergency Stop active Logic: XC19428B Active OR XC19428C Active F19-CR-431 Reverse or Forward Relay active Logic: XC19428E Active AND XC19428F Active F19-CR-431 Hoist Up and Down Relays active simultaneously F19-CR-431 Hoist Overload F19-CR-431 Post-Movement Traverse Pause Timer must elapse prior to energising hoist F19-BLC-401 Load Cell Logic: • XC19428F Active AND • [[ZI19412.PV not within ABS_H_ENC_BKR1.SV ± ABS_H_ENC_TLR OR ZI19409 Inactive] AND [ZI19412.PV not within ABS_H_ENC_HPR1.SV ± ABS_H_ENC_TLR OR ZI19401 Inactive] AND [ZI19412.PV not within ABS_H_ENC_HPR2.SV ± ABS_H_ENC_TLR OR ZI19402 Inactive] AND [ZI19412.PV not within ABS_H_ENC_BKR2.SV ± ABS_H_ENC_TLR OR ZI19408 Inactive] AND [ZI19412.PV not within ABS_H_ENC_HPR3.SV ± ABS_H_ENC_TLR OR ZI19403 Inactive] AND [ZI19412.PV not within ABS_H_ENC_MNT.SV ± ABS_H_ENC_TLR OR ZI19406 Inactive]] Hoist can only be lowered within specific horizontal trolley positions. Refer to page 16, Table 1 of 2000-ME067-ME02-10000 | A 0 0 A A A 0
9
10
11
12
13
14
[14 empty] | 15 | Hoist Vertical Out of Range |  |  |  |  | X |  |  |  | Logic: • XC19428F Active AND • [ZI19411.PV >= ABS_V_ENC_BNKL.SV + ABS_V_ENC_TLR AND [ZI19412.PV within ABS_H_ENC_BKR1.SV ± ABS_H_ENC_TLR OR ZI19409 Active OR ZI19412.PV within ABS_H_ENC_BKR2.SV ± ABS_H_ENC_TLR OR ZI19408 Active]] OR • [ZI19411.PV >= ABS_V_ENC_DMP1.SV + ABS_V_ENC_TLR AND [ZI19412.PV within ABS_H_ENC_HPR1.SV ± ABS_H_ENC_TLR OR ZI19401 Active OR ZI19412.PV within ABS_H_ENC_HPR2.SV ± ABS_H_ENC_TLR OR ZI19402 Active OR ZI19412.PV within ABS_H_ENC_HPR3.SV ± ABS_H_ENC_TLR OR ZI19403 Active]] OR • ZI19411.PV >= ABS_V_ENC_LWR.SV + ABS_V_ENC_TLR AND [ZI19412.PV within ABS_H_ENC_MNT.SV ± ABS_H_ENC_TLR OR ZI19406 Active] Hoist can only be lowered to heights specific to the trolley's designated position. Refer to page 16, Table 1 of 2000-ME067-ME02-10000
F19-MG-405 | - | BALL CHARGING MAGNET | N/A | [7 empty] | X | As per F19-SEQ-0003 | As per F19-SEQ-0003 |  |  | 0 0 0 0 0 0 0 0 0 0 |  | X |  | X X X X X X X X X | X | X
[14 empty] | 1 | F19-MG-405 Comms Failure | [9 empty] | A
[14 empty] | 2 | F19-MG-405 Fail to Start / Stop | [9 empty] | 0
[14 empty] | 3 | F19-MG-405 Drive Fault | [9 empty] | 0
[14 empty] | 4 | F19-MG-405 E-Stop | [9 empty] | 0
[14 empty] | 5 | F19-MG-405 MCC Unhealthy | [9 empty] | A
[14 empty] | 6 | F19-MG-405 Drive Out of Service | [9 empty] | 0
[14 empty] | 7 | F19-MG-405 Drive Ready | [9 empty] | 0
[14 empty] | 8 | XA19421 Alarm Magnet Duty Cycle Exceeded Horizontal Magnet Energise Limit | [8 empty] | Emergency Stop active Logic: Logic (Healthy): ZI19412.PV < ABS_H_ENC_HPR3.SV + ABS_H_ENC_HPR3_Y.SV F19-CR-431 Magnet cannot be energised when trolley is past Hopper 3 (toward Maintenance bay) | A A A
9
10

## 10. Sequence
KCGM GROWTH PROJECT
SEQUENCE
SEQUENCES
Seq No. | Seq Description | Step | Action | Tag / Item | Description | Next Step Delay (s) | Step Advance Condition | Comments | Rev | Equipment Permissives | Recovery Seq. No if Step Faults
PLEASE REFER TO SEQUENCE FLOWCHART DOCUMENT (2000-F19-LST-PR-10002)

## 11. Calculation
KCGM GROWTH PROJECT
CALCULATION
|  |  | Unit | Inputs |  |  |  | Operator Input | Calc. Value | Manual Input
Tag Name | P&ID | Description (Software Tag Only) |  | # | Tag | Unit | Description |  |  | Nom | Min | Max | Calculation | Comments | Rev
F19-CALC-0001 |  | F19CR431 Duty Cycle | % | 1 | F19CR431 _ON | On / Off | F19-CR-431 Trolley Running | [5 empty] | Calculate the rolling hourly RUNTIME of the trolley FORWARD motor to
|  |  |  | 2 |  | % | F19-CR-431 Fwd Dty Cycle Req. | X |  | 60 |  |  | Calculate Min Off Time per Hour Calculate Max On Time per Hour
|  |  |  | 3 4 5 |  | Minutes Minutes Minutes | F19-CR-431 FWD Min Off Time F19-CR-431 FWD Max On Time F19-CR-431 FWD Actual On Time |  | X X X |  |  |  | w r 9 C | m | A
F19-CALC-0003 |  | F19MG405 Duty Cycle | % | 1 | F19MG405_ON | On / Off | F19MG405 Drive On/Off | [5 empty] | Calculate the rolling 20 MINUTE RUNTIME of the MAGNET drive to ensure
|  |  |  | 2 |  | % | F19MG405 Duty Cycle Req. | X |  | 75 |  |  | Calculate Min Off Time per 20 minutes
|  |  |  | 3 4 5 |  | Minutes Minutes Minutes | F19MG405 Min OffTime F19MG405 Max On Time F19MG405 Actual Runtime per Hour |  | X X X |  |  |  | Calculate Max On Time per 20 minutes 5_ a ) s ll 4 05 drive. 9 M | m | A

## 12. Misc
KCGM GROWTH PROJECT
MISC
MISC. INSTRUMENTS AND CONTROLLERS
Tag Name | P&ID | Description | Normal State | Alarm State | Hardwired (y/n) | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev
F19BLC401_SEQ_ON | - | F19BLC401 Seq Auto En | Active |  | N |  | - |  | Memory bit is used as a condition to enable auto looping of F19-SEQ-0003. Activate and latch if: Deactivate/unlatch if: • HS19420CMAN is active OR • F19BLC401_HOME is active MNO anT uE a: )Deactivating/unlatching via BLC_REM_STOP or HS19420ESTP can be done in all modes (Local Auto, Remote Auto, Local l | B
BLC_REM_STRT | - | F19BLC401 Rem AutoStart | Inactive |  | N |  | - |  | Pushbutton on the DCS to start auto ball loading. See F19BLC401_SEQ_ON. Activates F19BLC401_SEQ_ON (Misc tab) in Remote Auto mode (HS19420BAUT) only | B
BLC_REM_STOP | - | F19BLC401 Rem AutoStop | Inactive |  | N |  | - |  | Pushbutton on the DCS to stop auto ball loading. See F19BLC401_SEQ_ON. Deactivates and unlatches F19BLC401_SEQ_ON (Misc tab) in all modes (Local Auto, Remote Auto, Local Manual) | B
F19BN61A_SEQ_ON | - | F19BN61 Seq Auto En | Active |  | N |  | - |  | Memory bit is used as a condition to enable auto looping of F19-SEQ-0003. | B
F19BLC401_HOME | - | F19BLC401 Homing Alarm | Inactive | Homing Request Alarm | N |  | 10 |  | A homing request alarm is initiated on the DCS when: • KM1 contactor running feedback (XI19426) is inactive in remote/local auto mode (HS19420AAUT/B) OR • The F19-SEQ-0003 is stopped in remote/local auto mode (HS19420AAUT/B) and standby idle (XC19427F) is inactive OR • There is a mismatch between the upper advisory limit (ZI19410) and vertical encoder (ZI19411) i.e., when ZI19410 is inactive, ZI19411 • e h between the bunker 1 limit (ZI19409) and horizontal encoder (ZI19412) i.e., when ZI19409 is active, ZI19412 • 4 S 9 A ve OR HS19420BAUT Active] OR • [F19-SEQ-0003 Not Running AND [HS19420AAUT Active OR HS19420BAUT Active]] AND XC19427F Inactive OR | B
F19CR431_MXDUTY | - | F19CR431 Max Duty | Inactive | Alarm | N |  | 0 |  | REFER TO F19-CALC-0001 1 ) | B
F19MG405_MXDUTY | - | F19MG405 Max Duty | Inactive | Alarm | N |  | 0 |  | REFER TO F19-CALC-0003 | B
MAGNET_WARNING | - | F19MG405 Load Warning | Timer PT = 10 Minutes | Timer Elapsed | N |  | 0 |  | This is to ensure the CRO can investigate the long loading duration before the Magnet duty cycle is complete. | B
ABS_V_ENC_TLR | - | F19CR431 HoistTolernce | Setpoint |  | N |  | - |  | Hoist vertical encoder position tolerance. Used in Hoist Drive interlocks (see Drives tab) Nominal: 5mm Lower Limit: 0mm Upper Limit: 100mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value | B
ABS_H_ENC_TLR | - | F19CR431 TrolleyTolernce | Setpoint |  | N |  | - |  | Trolley horizontal encoder position tolerance. Used in Hoist Drive interlocks (see Drives tab) Nominal: 20mm Lower Limit: 0mm Upper Limit: 100mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value | B
ABS_H_ENC_BKR1 | - | F19CR431 Bkr. 1 Pos. | Setpoint |  | N |  | - |  | Bunker 1 Absolute Position ZI19409 Should be active at this trolley position Used in F19-SEQ-0003 and Hoist Drive interlocks (see Drives tab) Nominal: 0mm Lower Limit: N/A Upper Limit: N/A Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_H_ENC_BKR1_X | - | F19CR431 Bkr. 1 X Dist | Setpoint |  | N |  | - |  | Bunker 1 - X Distance Distance before Bunker 1 Absolute Position that trolley normal travel relay de-energises in F19-SEQ-0003. Used in F19-SEQ-0003 Nominal: 50mm Lower Limit: 0mm Upper Limit: 1000mm a 1 ) n i . Include in graphic which allows the adjustment of the above Nominal setpoint. Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_H_ENC_BKR1_Y | - | F19CR431 Bkr. 1 Y Dist | Setpoint |  | N |  | - |  | Bunker 1 - Y Distance Distance after Bunker 1 Abosolute Position that trolley fast travel relay energises in F19-SEQ-0003. Used in F19-SEQ-0003 Nominal: 67mm Lower Limit: 0mm Upper Limit: 1000mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_H_ENC_BKR1_Z | - | F19CR431 Bkr. 1 Z Dist | Setpoint |  | N |  | - |  | Bunker 1 - Z Distance Distance before Bunker 1 Absolute Position that trolley fast travel relay de-energises in F19-SEQ-0003. Used in F19-SEQ-0003 Nominal: 225mm Lower Limit: 0mm Upper Limit: 1000mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_H_ENC_HPR1 | - | F19CR431 Hpr. 1 Pos. | Setpoint |  | N |  | - |  | Hopper 1 Absolute Position ZI19401 Should be active at this trolley position Used in F19-SEQ-0003 and Hoist Drive interlocks (see Drives tab) Nominal: 1800mm Lower Limit: 1700mm Upper Limit: 1900mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_H_ENC_HPR1_X | - | F19CR431 Hpr. 1 X Dist | Setpoint |  | N |  | - |  | Hopper 1 - X Distance Distance before Hopper 1 Absolute Position that trolley normal travel relay de-energises in F19-SEQ-0003. Used in F19-SEQ-0003 Nominal: 50mm Lower Limit: 0mm Upper Limit: 1000mm rs 1 ) n 0 Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_H_ENC_HPR1_Y | - | F19CR431 Hpr. 1 Y Dist | Setpoint |  | N |  | - |  | Hopper 1 - Y Distance Distance after Hopper 1 Absolute Position that trolley fast travel relay energises in F19-SEQ-0003. Used in F19-SEQ-0003 Nominal: 67mm Lower Limit: 0mm Upper Limit: 1000mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_H_ENC_HPR1_Z | - | F19CR431 Hpr. 1 Z Dist | Setpoint |  | N |  | - |  | Hopper 1 - Z Distance Distance before Hopper 1 Absolute Position that trolley fast travel relay de-energises in F19-SEQ-0003. Used in F19-SEQ-0003 Nominal: 225mm Lower Limit: 0mm Upper Limit: 1000mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_H_ENC_HPR2 | - | F19CR431 Hpr. 2 Pos. | Setpoint |  | N |  | - |  | Hopper 2 Absolute Position ZI19402 Should be active at this trolley position Used in Hoist Drive interlocks (see Drives tab) Nominal: 5800mm Lower Limit: 5700mm Upper Limit: 5900mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_H_ENC_BKR2 | - | F19CR431 Bkr. 2 Pos. | Setpoint |  | N |  | - |  | Bunker 2 Absolute Position. ZI19408 Should be active at this trolley position Used in Hoist Drive interlocks (see Drives tab) Nominal: 7670mm Lower Limit: 7570mm Upper Limit: 7770mm Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges at DCS . Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_H_ENC_HPR3 | - | F19CR431 Hpr. 3 Pos. | Setpoint |  | N |  | - |  | Hopper 3 Absolute Position ZI19403 Should be active at this trolley position Used in Hoist Drive interlocks (see Drives tab) Nominal: 9800mm Lower Limit: 9700mm Upper Limit: 9900mm Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges at DCS . Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_H_ENC_MNT | - | F19CR431 Maint. Pos. | Setpoint |  | N |  | - |  | Maintenance Absolute Position ZI19406 Should be active at this trolley position Used in Hoist Drive interlocks (see Drives tab) Nominal: 14173mm Lower Limit: 14073mm Upper Limit: 14273mm Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges at DCS . Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_V_ENC_DMP1 | - | F19CR431 Hoist Dump 1 | Setpoint |  | N |  | - |  | Dump 1 Absolute Position Used in Hoist Drive interlocks (see Drives tab) Nominal: 560mm Lower Limit: 460mm Upper Limit: 660mm Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges at DCS . Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_V_ENC_DMP2 | - | F19CR431 Hoist Dump 2 | Setpoint |  | N |  | - |  | Dump 2 Absolute Position Used in F19-SEQ-0003 Nominal: 300mm Lower Limit: 200mm Upper Limit: 400mm Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges at DCS . Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_V_ENC_CHT | - | F19CR431 Hoist Chute | Setpoint |  | N |  | - |  | Chute Absolute Position Used in F19-SEQ-0003 Nominal: 5740mm Lower Limit: 5453 mm Upper Limit: 6027 mm Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges at DCS . Requires Engineer login to change value Refer to 2000-ME067-M02-10000 | B
ABS_V_ENC_BNKL | - | F19CR431 Hoist Bunker | Setpoint |  | N |  | - |  | Bunker Limit Absolute Position Used in Hoist Drive interlocks (see Drives tab) Nominal: 7980mm Lower Limit: 7880mm Upper Limit: 8080mm Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges from the DCS Distance to be confirmed during commissioning. Requires Engineer login to adjust timer Refer to 2000-ME067-M02-10000 | B
ABS_V_ENC_LWR | - | F19CR431 Hoist Lower | Setpoint |  | N |  | - |  | Lower Limit Absolute Position Used in Hoist Drive interlocks (see Drives tab) Nominal: 8230mm Lower Limit: 8130mm Upper Limit: 8330mm Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges from the DCS Distance to be confirmed during commissioning. Requires Engineer login to adjust timer Refer to 2000-ME067-M02-10000 | B
F19BLC401_T1 | - | F19CR431 PreMovePause | Timer PT = 1 seconds |  | N |  | - |  | Trolley Pre-movement Pause. Timer to begin when a Trolley FWD (XC19428B) or REV (XC19428C) start command is called. Trolley will energise after the Pre- movement Pause timer has elapsed (see Drives tab) Nominal: 1s Lower Limit:0s Upper Limit:60s Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer Refer to 2000-ME067-M02-10000 | B
F19BLC401_T2 | - | F19CR431 PostMovePause | Timer PT = 1 seconds |  | N |  | - |  | Trolley Post-movement Pause Timer to begin when the Trolley FWD (XC19428B) or REV (XC19428C) relay de-energises. This is to allow for any horizontal sway to stop prior to lowering the hoist (interlock on Hoist included in Drives tab). Nominal: 1s Lower Limit:0s Upper Limit:60s Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer Refer to 2000-ME067-M02-10000 | B
F19BLC401_T3 | - | F19CR431 EndCyclePause | Timer PT = 1 seconds |  | N |  | - |  | End of Cycle Pause For use in F19-SEQ-0003 Nominal: 1s Lower Limit:0s Upper Limit:600s Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer Refer to 2000-ME067-M02-10000 | B
F19BLC401_KT1 | - | F19BLC401 LiftRiseTime | Timer PT = 6 seconds |  | N |  | - |  | Lift Current Rise Timer For use in F19-SEQ-0003 Nominal: 6s Lower Limit:0s Upper Limit:10s Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer Refer to 2000-ME067-M02-10000 | B
F19BLC401_KT2 | - | F19BLC401 SwtchRiseTme | Timer PT = 4 seconds |  | N |  | - |  | Switch Current Rise Timer For use in F19-SEQ-0003 Nominal: 4s Lower Limit:0s Upper Limit:10s Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer Refer to 2000-ME067-M02-10000 | B
F19BLC401_KT3 | - | F19BLC401 LiftBackEMF | Timer PT = 7 seconds |  | N |  | - |  | Lift Back EMF Timer For use in F19-SEQ-0003 Nominal: 7s Lower Limit:0s Upper Limit:10s Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer Refer to 2000-ME067-M02-10000 | B
F19BLC401_KT4 | - | F19BLC401 DumpRiseTme | Timer PT = 3 seconds |  | N |  | - |  | Dump Current Rise Timer For use in F19-SEQ-0003 Nominal: 3s Lower Limit:0s Upper Limit:10s Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer Refer to 2000-ME067-M02-10000 | B
F19BLC401_KT5 | - | F19BLC401 DumpBackEMF | Timer PT = 3 seconds |  | N |  | - |  | Dump Back EMF Timer For use in F19-SEQ-0003 Nominal: 3s Lower Limit:0s Upper Limit:10s Include in graphic which allows the adjustment of the above Nominal setpoint and lower / upper ranges from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer Refer to 2000-ME067-M02-10000 | B

## 13. Alarm Database
KCGM GROWTH PROJECT
ALARM DATABASE
ALARM DATABASE
Tag Name | P&ID | Abbreviated Description (Faceplate) | Type | Alarm State | Alarm Value | Alarm Units | On Delay (sec) | Alarm Masking Condition | Impact | Urgency | Priority | Operator Response | Rev
LI19755 | 2000-F19-PID-PR-10006 | F19BN61A Level | Analogue |  | 30 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Ensure the Ball Charging System is in auto, healthy and that the SAG Mill Ball Bunker is stocked with mill balls. Ensure metering system is in auto, healthy and not faulted. | B
LI19755 | 2000-F19-PID-PR-10006 | F19BN61A Level | Analogue |  | 97 | % | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Rapid (>5 to <15 minutes) | Low |  | B
LI19756 | 2000-F19-PID-PR-10006 | F19BN61B Level | Analogue |  | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check bin level in the field. Bin should not be in use. | B
LI19756 | 2000-F19-PID-PR-10006 | F19BN61B Level | Analogue |  | 97 | % | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check bin level in the field. Bin should not be in use. | B
LI19757 | 2000-F19-PID-PR-10006 | F19BN61C Level | Analogue |  | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check bin level in the field. Bin should not be in use. | B
LI19757 | 2000-F19-PID-PR-10006 | F19BN61C Level | Analogue |  | 97 | % | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check bin level in the field. Bin should not be in use. | B
WI19401 | 2000-F19-PID-PR-10007 | F19-BLC-401 Load Cell | Analogue |  | 2880 | kg | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check Hoist is not entangled or in contact with surrounding structure. Attempt to lower and de- energise magnet. Run homing sequence if required. | B
WI19401 | 2000-F19-PID-PR-10007 | F19-BLC-401 Load Cell | Analogue | A_HH | 3040 | kg | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator to check Hoist is not entangled or in contact with surrounding structure. Attempt to lower and de- energise magnet and rehome, else advise Maintenance to action when practical. Interlock bypass required. | B
EI19429 | 2000-F19-PID-PR-10007 | F19BLC401 Voltage | Analogue |  | 285 | V DC | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | High magnet voltage. Advise Maintenance to investigate if high alarm persists. | B
II19430 | 2000-F19-PID-PR-10007 | F19BLC401 Current | Analogue |  | 47.5 | A DC | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | High magnet current. Advise Maintenance to investigate if high alarm persists. | B
XA19421 | 2000-F19-PID-PR-10007 | F19BLC401 EStop | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Advise Field Operator to investigate area immediately. Reset E- stop and reenergise system if safe to do so. | B
XA19422 | 2000-F19-PID-PR-10007 | F19BLC401 CB Trip | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Electrician to investigate and reset tripped breaker. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | B
XA19423 | 2000-F19-PID-PR-10007 | F19BLC401 Earth Trip | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Electrician to investigate and reset fault condition. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | B
XA19424 | 2000-F19-PID-PR-10007 | F19CR431 Trolley Fault | Digital | Fault |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Electrician to investigate and reset fault condition. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | B
XA19425 | 2000-F19-PID-PR-10007 | F19CR431 Hoist Fault | Digital | Fault |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Electrician to investigate and reset fault condition. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | B
ZA19404 | 2000-F19-PID-PR-10007 | F19CR431 Bunker 1 EOT | Digital | Alarm (ZS19404 Open, exceeded normal travel limits) |  |  | 1 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Trolley over travelled. Advise Field Operator to check in field. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | B
ZA19405 | 2000-F19-PID-PR-10007 | F19CR431 Mntenance EOT | Digital | Alarm ZS19405 Open, exceeded normal travel limits |  |  | 1 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Trolley over travelled. Advise Field Operator to check in field. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | B
XA19426 | 2000-F19-PID-PR-10007 | F19CR431 Running FB | Digital | Inactive (KM1 Contactor Deenergised) |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Running feedback lost. Remotely/locally restart. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | B
F19BLC401_HOME | - | F19BLC401 Homing Alarm | Digital Misc | Homing Request Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | CRO to start auto homing sequence. | B
F19CR431_MXDUTY | - | F19CR431 Max Duty | Digital Misc | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | At max duty cycle. Check if trolley is held on a sequence transition. Check limit switches are in correct position. Check encoder is reading correctly (conduct auto homing if not to recalibrate). | B
F19MG405_MXDUTY | - | F19MG405 Max Duty | Digital Misc | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | At max duty cycle. Magnet will only trip if unloaded. Check if magnet is held on a sequence transition. | B
MAGNET_WARNING | - | F19MG405 Load Warning | Digital Misc | Timer Elapsed |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | F19-MG-405 approaching max duty cycle whilst loaded. CRO to advise Field Operator to investigate immediately. System likely out of Sequence. | B
XC19427H | 2000-F19-PID-PR-10007 | F19MG405 Fault | Digital Output | Alarm F19-MG-405 Magnet Fault |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Restart remotely if possible, else Advise Electrician to reset and monitor for recurring issues. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | B
XC19427K | 2000-F19-PID-PR-10007 | F19CR431 Trolley O/load | Digital Output | Alarm F19-CR-431 Trolley Motor 1 OR 2 VSD Fault |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Restart remotely if possible, else Advise Electrician to reset and monitor for recurring issues. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | B
XC19428A | 2000-F19-PID-PR-10007 | F19CR431 Hoist Overload | Digital Output | Alarm F19-CR-431 Hoist Motor VSD Fault |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Restart remotely if possible, else Advise Electrician to reset and monitor for recurring issues. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | B