## Revisions
PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION,
REVISION HISTORY
KCGM GROWTH PROJECT
2000-F22-LST-PR-10101
NORTHERN STAR RESOURCES LIMITED
Revision | Document Changes | Date
A - Issued for Internal Review | - Vendor data TBC highlighted or red text | 2024-08-05
B - Issued for Tender | - Vendor data TBC highlighted or red text | 2024-08-23
C - Issued for Client Review | - Vendor data TBC highlighted or red text | 2024-11-20
0 - Issued for Design | - Vendor data TBC highlighted or red text | 2025-04-16
1 - Post FAT Updates | - Vendor data TBC highlighted or red text | 2026-09-01
- F22 Mercury Abatement HAZOP actions incorporated
- Revision 1 changes highlighted in orange
- Strikethrough indicates removal from design

## 1. Analogue Input
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION, ELECTROWINNING & GOLD ROOM (AREA F22 & F66) | [39 empty] | Urgent (Critical Failure) | #REF!
|  |  |  | 2000-F22-LST-PR-10101 | [39 empty] | High (Fault/Error) | #REF!
|  |  |  | ANALOGUE INSTRUMENTS | [39 empty] | Low (Warning) | #REF!
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [11 empty] | C1 Sign Off |  | C2 Sign Off |  |  |  |  | Information/Event (Journal) | #REF!
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Controller (Y/N) | Comments | Rev | OK | Date | OK | Date | Comments - Don’t comment in C2 column | Change Date | Change Reference | - | #REF!
|  |  |  | LT22140 | LI22140 | 2000-F21-PID-PR-10002 | F22-HP-445 CIL4 Loaded Carbon Transfer Vessel Level Indicating Transmitter | F22HP445 Lvl | 1 | 0 | 100 | % | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95 | 5 | - | N |  | 1 | [5 empty] | 2026-01-21 | LIT should be LT
|  |  |  | TT22013 | TI22013 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Temperature Indicating Transmitter | F22PR411 Top | 1 | 0 | 200 | °C | - | - | - | - | - | - | 90 | 5 | - | 120 | 5 | - | - | - | - | - | 150 | 5 | 160 | 3 | - | N |  | C
|  |  |  | PIT22015 | PI22015 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Pressure Indicating Transmitter | F22PR411 Top | 1 | -50 | 600 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 450 | 5 | 490 | 3 | - | N |  | 0
|  |  |  | FIT22025 | FI22025 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Hydrochloric Acid Flow Indicating Transmitter | F22PR411 HCl | 1 | 0 | 20 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | 10 | 0.1 | 3 | - | - | A_Lo Mask: F72PP424 is NOT RUNNING Enable 10s delay mask on pump start-up A_Hi Mask: XV22024 is Open | N | Note: the A_Hi is to pick up a 'passing' valve i.e. flow registerd past the valve when it is closed (hence why alarm is masked when the valve is registered open). | 0
|  |  |  | PIT22033 | PI22033 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Reagent Addition Manifold Pressure Indicating Transmitter | F22PR411 Press 2 | 1 | 0 | 600 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | C
|  |  |  | AIT22027 | AI22027 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column HCN Gas Analyser Indicating Transmitter | Elution HCN | 1 | 0 | 30 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | 0
|  |  |  | PIT22049 | PDI22049 | 2000-F22-PID-PR-10001 | F22-FI-411 CIL4 Elution Filter Pressure Differential Indicating Transmitter | F22FI411 DP | 1 | 0 | 100 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 60 | 3 | - | - | - | N |  | 0
|  |  |  | PIT22050 | PDI22050 | 2000-F22-PID-PR-10001 | F22-FI-412 CIL4 Elution Filter Pressure Differential Indicating Transmitter | F22FI412 DP | 1 | 0 | 100 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 60 | 3 | - | - | - | N |  | 0
|  |  |  | TIT22031 | TI22031 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Pregnant Eluate Temperature Indicating Transmitter | F22PR411 Inlet | 1 | 0 | 200 | °C | - | - | - | 90 | 5 | - | - | - | - | - | - | - | - | - | - | - | 150 | 5 | 160 | 3 | - | N |  | 1 | [5 empty] | 2025-07-23 | Updated as per KAN-2085
|  |  |  | PIT22081 | PI22081 | 2000-F22-PID-PR-10002 | F22-HE-412 CIL4 Elution Recovery Heat Exchanger Pregnant Eluate Return Pressure Indicating Transmitter | F22HE412 Hot In | 1 | 0 | 600 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | C
|  |  |  | TIT22082 | TI22082 | 2000-F22-PID-PR-10002 | F22-HE-412 CIL4 Elution Recovery Heat Exchanger Pregnant Eluate Return Temperature Indicating Transmitter | F22HE412 Hot In | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | A
|  |  |  | TT22101 | TI22101 | 2000-F22-PID-PR-10002 | F22-HE-411 CIL4 Elution Primary Heat Exchanger Pregant Eluate Discharge Temperature Transmitter | F22PR411 Eluate | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | A
|  |  |  | TT22108 | TI22108 | 2000-F22-PID-PR-10002 | F22-HT-411 CIL4 Elution Heater Temperature Transmitter | F22HT411 Oil | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | A
|  |  |  | TT22097 | TI22097 | 2000-F22-PID-PR-10002 | F22-HT-411 CIL4 Elution Heater Eluate Temperature Transmitter | F22HT411 Eluate | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | 0
|  |  |  | PT22098 | PI22098 | 2000-F22-PID-PR-10002 | F22-HT-411 CIL4 Elution Heater Eluate Pressure Transmitter | F22HT411 Eluate | 1 | 0 | 1200 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | 0
|  |  |  | TIT22122 | TI22122 | 2000-F22-PID-PR-10002 | F22-HE-412 CIL4 Elution Recovery Heat Exchanger Discharge Temperature Indicating Transmitter | F22HE412 Hot Out | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 85 | 5 | 95 | 5 | - | N |  | A
|  |  |  | LIT22143 | LI22143 | 2000-F22-PID-PR-10002 | F22-TK-442 CIL4 Lean Eluate Tank Level Indicating Transmitter | F22TK442 Level | 1 | 0 | 100 | % | - | - | - | - | - | - | 85 | 3 | - | - | - | - | 5 | 5 | 10 | 5 | 90 | 5 | 97 | 5 | - | N |  | A
|  |  |  | LIT22146 | LI22146 | 2000-F22-PID-PR-10002 | F22-TK-446 Eluate Expansion Tank Level Indicating Transmitter | F22TK446 Level | 1 | 0 | 100 | % | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | A
|  |  |  | LIT22152 | LI22152 | 2000-F22-PID-PR-10002 | F22-TK-441 CIL4 Elution Water Tank Level Indicating Transmitter | F22TK441 Level | 1 | 0 | 100 | % | - | 10 | 3 | 30 | 3 | - | 90 | 3 | - | - | - | - | 5 | 5 | 10 | 5 | 92 | 5 | 95 | 5 | - | N |  | A
|  |  |  | TIT22167 | TI22167 | 2000-F22-PID-PR-10002 | CIL4 Elution Pumps Discharge Temperature Indicating Transmitter | F22HE412 Cold In | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | A
|  |  |  | PIT22166 | PI22166 | 2000-F22-PID-PR-10002 | CIL4 Elution Pumps Discharge Pressure Indicating Transmitter | F22HE412 Cold In | 1 | 0 | 1200 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | 180 | 5 | 200 | 5 | 750 | 5 | 800 | 3 | A_LL mask: F22PW441 is NOT RUNNING AND F22PW444 IS NOT RUNNING A_Lo mask: F22PW441 is NOT RUNNING AND F22PW444 is NOT RUNNING Enable 10s delay mask on pump start-up | N |  | C
|  |  |  | PIT22171 | PI22171 | 2000-F22-PID-PR-10002 | F22-HE-411 CIL4 Elution Primary Heat Exchanger Discharge Pressure Indicating Transmitter | F22HE411 Cold In | 1 | 0 | 1200 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | 180 | 5 | 200 | 5 | 750 | 5 | 800 | 3 | A_LL mask: F22PW441 is NOT RUNNING AND F22PW444 IS NOT RUNNING A_Lo mask: F22PW441 is NOT RUNNING AND F22PW444 is NOT RUNNING Enable 10s delay mask on pump start-up | N |  | C
|  |  |  | TIT22172 | TI22172 | 2000-F22-PID-PR-10002 | F22-HE-411 CIL4 Elution Primary Heat Exchanger Discharge Temperature Indicating Transmitter | F22HE411 Cold In | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | A
|  |  |  | FIT22182 | FI22182 | 2000-F22-PID-PR-10002 | Elution Cyanide Feed Flow Indicating Transmitter | CIL4 Elution CN | 1 | 0 | 10 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | 10 | - | - | - | - | (F72PP675 is NOT RUNNING AND F72PP676 is NOT RUNNING) OR XV22181 is Closed Enable 10s delay mask on pump start-up | N |  | 0
|  |  |  | FIT22192 | FI22192 | 2000-F22-PID-PR-10002 | Elution Caustic Feed Flow Indicating Transmitter | CIL4Elution NaOH | 1 | 0 | 10 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 10 | - | - | - | - | (F72PP673 is NOT RUNNING AND F72PP674 is NOT RUNNING) OR XV22191 is Closed Enable 10s delay mask on pump start-up | N |  | 0
|  |  |  | F22-CALC-0001 | PDI22081 | 2000-F22-PID-PR-10002 | F22HE412 Hot Side Differential Pressure | F22HE412 DP1 | 1 | 0 | 100 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 20 | 3 | - | - | - | N |  | 0
|  |  |  | F22-CALC-0002 | PDI22166 | 2000-F22-PID-PR-10002 | F22HE412 Cold Side Differential Pressure | F22HE412 DP2 | 1 | 0 | 100 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 20 | 3 | - | - | - | N |  | 0
|  |  |  | F22-CALC-0003 | PDI22098 | 2000-F22-PID-PR-10002 | F22HE411 Cold Side Differential Pressure | F22HE411 DP1 | 1 | 0 | 100 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 20 | 3 | - | - | - | N |  | 0
|  |  |  | TI22280AS | TI22280A | 2000-F22-PID-PR-10005 | F22-KN-411 Zone 1 Temperature | F22KN411 Z1 Temp | 1 | 0 | 800 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft signals via modbus | 0
|  |  |  | TI22281AS | TI22281A | 2000-F22-PID-PR-10005 | F22-KN-411 Zone 2 Temperature | F22KN411 Z2 Temp | 1 | 0 | 800 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft signals via modbus | 0
|  |  |  | TI22282AS | TI22282A | 2000-F22-PID-PR-10005 | F22-KN-411 Zone 3 Temperature | F22KN411 Z3 Temp | 1 | 0 | 800 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft signals via modbus | 0
|  |  |  | LT22189 | LI22189 | 2000-F22-PID-PR-10005 | F22-HP-431 CIL4 Carbon Regeneration Kiln Feed HopperLevel Level Indicating Transmitter | F22HP431 Level | 1 | 0 | 100 | % | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10 | 5 | 90 | 5 | 95 | 5 | - | N |  | 1 | [5 empty] | 2026-01-21 | LIT should be LT
|  |  |  | FIT22196 | FI22196 | 2000-F22-PID-PR-10005 | F22-PP-490 CIL4 Barren Carbon Pump Feed Flow Indicating Transmitter | F22PP490 Suction | 1 | 0 | 100 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 30 | 5 | 80 | 5 | - | - | A_Lo Mask: F24PW406 is NOT RUNNING AND F24PW407 is NOT RUNNING | N |  | 1 | [6 empty] | PP to PW
|  |  |  | PIT22195 | PI22195 | 2000-F22-PID-PR-10005 | F22-PP-490 CIL4 Barren Carbon Pump Feed Pressure Indicating Transmitter | F22PP490 Suction | 1 | 0 | 300 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 50 | 5 | 200 | 5 | - | - | A_Lo Mask: F24PW406 is NOT RUNNING AND F24PW407 is NOT RUNNING | N |  | 1 | [6 empty] | PP to PW
|  |  |  | AIT22052 | AI22052 | 2000-F22-PID-PR-10005 | F22-KN-411 CIL4 Carbon Regeneration Kiln Area Mercury Analyser Indicating Transmitter | F22KN411 Mercury | 1 | 0 | 100 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 25 | 3 | - | N | Logic: Include 120 second (system limit) off delay on A_HH | 1 | [5 empty] | 2025-09-16 | change of units https://pastech-2955.atlassian.net/browse/KAN-2045
|  |  |  | AIT22232 | AI22232 | 2000-F22-PID-PR-10007 | F22-ST-401 Kiln Mercury Abatement Discharge Stack Mercury Analyser Indicating Transmitter | F22ST401 Mercury | 1 | 0 | 100 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 25 | 3 | - | N | Logic: Include 120 second (system limit) off delay on A_HH | 1 | [5 empty] | 2025-09-16 | change of units https://pastech-2955.atlassian.net/browse/KAN-2045
|  |  |  | AIT22252 | AI22252 | 2000-F22-PID-PR-10007 | F22-PS-453 Mercury Abatement Area Sump Pump Mercury Analyser Indicating Transmitter | F22PS453 Mercury | 1 | 0 | 100 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 25 | 3 | - | N | Logic: Include 120 second (system limit) off delay on A_HH | 1 | [5 empty] | 14/05/2025 16/09/2025 | Updated as per HAZOP 02/05/2025 https://pastech-2955.atlassian.net/browse/KAN-2045
|  |  |  | FIT22223 | FI22223 | 2000-F22-PID-PR-10007 | F22-HE-401 Kiln Mercury Abatement Off-Gas Cooler Cooling Water Inlet Flow Indicating Transmitter | F22HE401 In Flow | 1 | 0 | 100 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | 1 | [5 empty] | 2025-05-02 | Removed as per HAZOP 02/05/2025
|  |  |  | TIT22234 | TI22234 | 2000-F22-PID-PR-10007 | F22-HE-401 Kiln Mercury Abatement Off-Gas Cooler Cooling Water Return Temperature Indicating Transmitter | F22HE401 Return | 1 | 0 | 50 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 25 | 5 | 30 | 5 | - | N |  | 0
|  |  |  | TIT22224 | TI22224 | 2000-F22-PID-PR-10007 | F22-TK-420 Kiln Mercury Abatement Knock Out Box Kiln Off Gas Inlet Temperature Indicating Transmitter | F22TK420 In T | 1 | 0 | 300 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 220 | 5 | 230 | 5 | - | N |  | 0
|  |  |  | PIT22225 | PI22225 | 2000-F22-PID-PR-10007 | F22-TK-420 Kiln Mercury Abatement Knock Out Box Kiln Off Gas Inlet Pressure Indicating Transmitter | F22TK420 In P | 1 | 0 | 10 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.5 | 5 | 1 | 5 | - | N |  | 0
|  |  |  | TIT22226 | TI22226 | 2000-F22-PID-PR-10007 | F22-TK-420 Kiln Mercury Abatement Knock Out Box Kiln Off Gas Outlet Temperature Indicating Transmitter | F22TK420 Out T | 1 | 0 | 300 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 105 | 5 | 110 | 5 | - | N |  | 0
|  |  |  | PIT22227 | PI22227 | 2000-F22-PID-PR-10007 | F22-TK-420 Kiln Mercury Abatement Knock Out Box Kiln Off Gas Outlet Pressure Indicating Transmitter | F22TK420 Out P | 1 | 0 | 10 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.5 | 5 | 1 | 5 | - | N |  | 0
|  |  |  | PIT22229 | PI22229 | 2000-F22-PID-PR-10007 | F22-HE-401 Kiln Mercury Abatement Off-Gas Cooler Kiln Off Gas Outlet Pressure Indicating Transmitter | F22HE401 Out P | 1 | 0 | 10 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.5 | 5 | 1 | 5 | - | N |  | 0
|  |  |  | TIT22230 | TI22230 | 2000-F22-PID-PR-10007 | F22-HE-401 Kiln Mercury Abatement Off-Gas Cooler Cooling Water Inlet Temperature Indicating Transmitter | F22HE401 In T1 | 1 | 0 | 50 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 20 | 5 | 25 | 5 | - | N |  | 0
|  |  |  | TIT22221 | TI22221 | 2000-F22-PID-PR-10007 | F22-HE-401 Kiln Mercury Abatement Off-Gas Cooler Cooling Water Inlet Temperature Indicating Transmitter | F22HE401 In T2 | 1 | 0 | 50 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 20 | 5 | 25 | 5 | - | N |  | 1 | [5 empty] | 2025-07-03 | Updated as per KAN-2046
|  |  |  | PIT22222 | PI22222 | 2000-F22-PID-PR-10007 | F22-HE-401 Kiln Mercury Abatement Off-Gas Cooler Cooling Water Inlet Pressure Indicating Transmitter | F22HE401 In P | 1 | 0 | 300 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | 60 | 5 | - | - | 200 | 5 | 210 | 5 | A_LL Mask: F22-PW-591 is NOT RUNNING AND F22-PW-592 is NOT RUNNING | N |  | 1 | [5 empty] | 2025-07-03 | Updated as per KAN-2046
|  |  |  | TIT22235 | TI22235 | 2000-F22-PID-PR-10007 | F22-TK-421 Kiln Mercury Abatement Demister Vessel Outlet Temperature Indicating Transmitter | F22TK421 Out T | 1 | 0 | 50 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 30 | 5 | 35 | 5 | - | N |  | 0
|  |  |  | PIT22236 | PI22236 | 2000-F22-PID-PR-10007 | F22-TK-421 Kiln Mercury Abatement Demister Vessel Outlet Pressure Indicating Transmitter | F22TK421 Out P | 1 | 0 | 10 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.5 | 5 | 1 | 5 | - | N |  | 0
|  |  |  | TIT22237 | TI22237 | 2000-F22-PID-PR-10007 | F22-TK-422 Kiln Mercury Abatement Adsorption Vessel Outlet Temperature Indicating Transmitter | F22TK422 Out T | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93 | 5 | 100 | 5 | - | N |  | 0
|  |  |  | PIT22238 | PI22238 | 2000-F22-PID-PR-10007 | F22-TK-422 Kiln Mercury Abatement Adsorption Vessel Outlet Pressure Indicating Transmitter | F22TK422 Out P | 1 | 0 | 10 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.5 | 5 | 1 | 5 | - | N |  | 0
|  |  |  | TE22240 | TI22240 | 2000-F22-PID-PR-10007 | F22-HT-401 Kiln Mercury Abatement Exhaust Heater Temperature | F22HT401 Out T | 1 | -200 | 2000 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Modbus tag : 2000-SPC-CS-11001_AI | 1 | [5 empty] | 2/05/2025 14/4/26 | Updated as per HAZOP 02/05/2025 FC : updated range as per vendor doc and add comment re: modbus tag
|  |  |  | F22-CALC-0004 | TDI22240 | 2000-F22-PID-PR-10007 | F22-HT-401 Temperature Differential | F22HT401 Diff. T | 1 | 0 | 50 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12 | 5 | - | - | - | - |  | N |  | 1 | [5 empty] | 2025-05-02 | Updated as per HAZOP 02/05/2025
|  |  |  | F22-CALC-0005 | PDI22225 | 2000-F22-PID-PR-10007 | F22-TK-420 Pressure Differential | F22TK420 Diff. P | 1 | 0 | 10 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.5 | 5 | - | - |  | N |  | 1 | [5 empty] | 2025-05-12 | Updated as per HAZOP 02/05/2025
|  |  |  | F22-CALC-0006 | PDI22229 | 2000-F22-PID-PR-10007 | F22-TK-421 Pressure Differential | F22TK421 Diff. P | 1 | 0 | 10 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.5 | 5 | - | - |  | N |  | 1 | [5 empty] | 2025-05-12 | Updated as per HAZOP 02/05/2025
|  |  |  | F22-CALC-0007 | PDI22236 | 2000-F22-PID-PR-10007 | F22-TK-422 Pressure Differential | F22TK422 Diff. P | 1 | 0 | 10 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2.5 | 5 | - | - |  | N |  | 1 | [5 empty] | 2025-05-12 | Updated as per HAZOP 02/05/2025
|  |  |  | LIT22242 | LI22242 | 2000-F22-PID-PR-10008 | F22-TK-484 Kiln Abatement System Cooling Water Tank Level Indicating Transmitter | F22TK484 Level | 1 | 0 | 100 | % | - | - | - | 50 | 5 | - | 90 | 5 | - | - | - | - | 5 | 5 | 10 | 5 | 95 | 5 | 97 | 5 | - | N |  | B
|  |  |  | TIT22243 | TI22243 | 2000-F22-PID-PR-10008 | F22-TK-484 Kiln Abatement System Cooling Water Tank Temperature Indicating transmitter | F22TK484 Temp | 1 | 0 | 50 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 25 | 5 | - | - | - | N |  | 0
|  |  |  | LIT66404 | LI66404 | 2000-F66-PID-PR-10001 | F66-TK-461 CIL4 Eluate Circulation Tank 1 Level Indicator Transmitter | F66TK461 Level | 1 | 0 | 100 | % | - | - | - | 10 | 3 | - | 80 | 3 | - | - | - | - | 5 | 5 | 10 | 5 | 90 | 5 | 95 | 5 | - | N |  | A
|  |  |  | LIT66405 | LI66405 | 2000-F66-PID-PR-10001 | F66-TK-471 CIL4 Eluate Circulation Tank 2 Level Indicator Transmitter | F66TK471 Level | 1 | 0 | 100 | % | - | - | - | 10 | 3 | - | 80 | 3 | - | - | - | - | 5 | 5 | 10 | 5 | 90 | 5 | 95 | 5 | - | N |  | A
|  |  |  | FIT66406 | FI66406 | 2000-F66-PID-PR-10001 | F66-PP-461/462 CIL4 Electrowinning Pump 1/2 Discharge 1 Flow Indicating Transmitter | CIL4 Preg Eluate | 1 | 0 | 100 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | 20 | 5 | 40 | 5 | - | - | - | - | Alarm if: ((F66-PP-461 Running AND XV66415 Open) OR (F66-PP-462 Running AND XV66417 Open)) for 10 seconds | N | Nominal 45 - 48 m3/h flowrate per E/W cell | 1
|  |  |  | FIT66419 | FI66419 | 2000-F66-PID-PR-10001 | F66-PP-461/462 CIL4 Electrowinning Pump 1/2 Discharge 2 Flow Indicating Transmitter | CIL4 Brn Eluate | 1 | 0 | 100 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | 20 | 5 | 40 | 5 | - | - | - | - | Alarm if: ((F66-PP-461 Running AND XV66416 Open) OR (F66-PP-462 Running AND XV66418 Open)) for 10 seconds | N |  | 1
|  |  |  | II66444S | II66444S | 2000-F66-PID-PR-10002 | F66-ER-411A CIL4 Electrowinning Cell 1 Rectifier 1 Measured Current | F66ER411A Rect1MeasAmp | 1 | 0 | 2500 | A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600 | 5 | - | - | 2000 | 5 | - | N |  | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
|  |  |  | XI66444S | XI66444S | 2000-F66-PID-PR-10002 | F66-ER-411A CIL4 Electrowinning Cell 1 Rectifier 1 Measured Voltage | F66ER411A Rect1MeasVolt | 1 | 0 | 4.5 | V | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | 5 | - | - | 4.4 | 5 | - | N |  | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
|  |  |  | II66445S | II66445S | 2000-F66-PID-PR-10002 | F66-ER-411B CIL4 Electrowinning Cell 1 Rectifier 2 Measured Current | F66ER411B Rect1MeasAmp | 1 | 0 | 2500 | A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600 | 5 | - | - | 2000 | 5 | - | N |  | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
|  |  |  | XI66445S | XI66445S | 2000-F66-PID-PR-10002 | F66-ER-411B CIL4 Electrowinning Cell 1 Rectifier 2 Measured Voltage | F66ER411B Rect1MeasVolt | 1 | 0 | 4.5 | V | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | 5 | - | - | 4.4 | 5 | - | N |  | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
|  |  |  | II66446S | II66446S | 2000-F66-PID-PR-10002 | F66-ER-412A CIL4 Electrowinning Cell 1 Rectifier 1 Measured Current | F66ER412A Rect1MeasAmp | 1 | 0 | 2500 | A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600 | 5 | - | - | 2000 | 5 | - | N |  | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
|  |  |  | XI66446S | XI66446S | 2000-F66-PID-PR-10002 | F66-ER-412A CIL4 Electrowinning Cell 1 Rectifier 1 Measured Voltage | F66ER412A Rect1MeasVolt | 1 | 0 | 4.5 | V | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | 5 | - | - | 4.4 | 5 | - | N |  | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
|  |  |  | II66447S | II66447S | 2000-F66-PID-PR-10002 | F66-ER-412B CIL4 Electrowinning Cell 1 Rectifier 2 Measured Current | F66ER412B Rect1MeasAmp | 1 | 0 | 2500 | A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600 | 5 | - | - | 2000 | 5 | - | N |  | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
|  |  |  | XI66447S | XI66447S | 2000-F66-PID-PR-10002 | F66-ER-412B CIL4 Electrowinning Cell 1 Rectifier 2 Measured Voltage | F66ER412B Rect1MeasVolt | 1 | 0 | 4.5 | V | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | 5 | - | - | 4.4 | 5 | - | N |  | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
|  |  |  | AIT22002 | AI22002 | 2000-F23-PID-PR-10001 | F22-BX-405 Final Tails Collection Box Area HCN Gas Analyser Indicating Transmitter | Elution Tail HCN | 1 | 0 | 30 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | 0
|  |  |  | PIT22037 | PI22037 | 2000-F24-PID-PR-10031 | F22-RA-411 Elution Air Receiver Discharge Pressure Transmitter | F22RA411 Press | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600 | 5 | 980 | 5 | - | - | - | N |  | 1 | [5 empty] | 27/05/2025 14/04/26 | Missed on P&ID, air receiver for F22 area. Press. To Press FC : updated range to 0 - 1000 and 980 for hi
|  |  |  | UT22006 | TI22006 | - | F22-SR-001 Carbon Regen and Elution 415V Switchroom Switchroom Temperature/Humidity Transmitter | F22SR001 Temp | 1 | 0 | 50 | ℃ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 30 | 600 | - | - | - | N |  | C
|  |  |  | UT22007 | TI22007 | - | F22-SR-001 Carbon Regen and Elution 415V Switchroom Transformer (F22-TR-030) Temperature/Humidity Transmitter | F22TR030 Temp | 1 | 0 | 50 | ℃ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 30 | 600 | - | - | - | N |  | C
|  |  |  | UT22008 | TI22008 | - | F22-SR-001 Carbon Regen and Elution 415V Switchroom Transformer (F22-TR-031) Temperature/Humidity Transmitter | F22TR031 Temp | 1 | 0 | 50 | ℃ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 30 | 600 | - | - | - | N |  | C
|  |  |  | FIT22017 | FI22017 | 2000-F22-PID-PR-10001 | F22-BX-405 Final Tails Collection Box Acid Wash Feed Flow Switch High | F22BX405 Flow | 1 | 0 | 150 | m3/h | [16 empty] | 3 | 10 |  |  | Mask if XV22051 Open |  | A_Hi = Valve passing alarm. Setpoint TBC during commissioning | 1 | [5 empty] | 31/01/2025 9/02/2025 | CR-062 P_Hi moved to A_Hi
|  |  |  | FIT22018 | FI22018 | 2000-F22-PID-PR-10001 | F22-HE-412 CIL4 Elution Recovery Heat Exchanger Pregnant Eluate Feed Flow Switch High | F22HE412 Flow | 1 | 0 | 150 | m3/h | [16 empty] | 3 | 10 |  |  | Mask if XV22054 Open |  | A_Hi = Valve passing alarm. Setpoint TBC during commissioning | 1 | [5 empty] | 31/01/2025 9/02/2025 | CR-062 P_Hi moved to A_Hi
|  |  |  | DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE | [28 empty] | -
[25 empty] | 70 |  | 70 |  | 70 |  | 70
280
|  |  |  | 75 | 75

## 2. Analogue Output
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION, ELECTROWINNING & GOLD ROOM (AREA F22 & F66) | [17 empty] | Urgent (Critical Failure)
|  |  |  | 2000-F22-LST-PR-10101 | [17 empty] | High (Fault/Error)
|  |  |  | ANALOGUE OUTPUT | [17 empty] | Low (Warning)
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  |  |  | C1 Sign Off |  | C2 Sign Off |  |  |  |  | Information/Event (Journal)
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | Comments | Rev | OK | Date | OK | Date | Comments - Don’t comment in C2 column | Change Date | Change Reference | -
|  |  |  | TC22131 | TIC22131.SP | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Pregnant Eluate Temperature Indicating Transmitter | CIL4 Elution Temp. Ctrl | 1 | 0 | 150 | °C | Setpoint to be sent to the Elution Heater Burner management control system (vendor PLC). | 1 | [5 empty] | 2025-07-04 | Updated as per KAN-2085
|  |  |  | IC66440S | IC66440 | 2000-F66-PID-PR-10002 | F66-ER-411A CIL4 Electrowinning Cell 1 Rectifier 1 Current Feedback | F66ER411A Rect1AmpFdbck | 1 | 0 | 2500 | A | Remote current setpoint input from PCS when rectifier is operating remotely in "DC Current Mode". 2550 A is maximum peak current, determined by bus bar limitation. | 0
|  |  |  | XC66440S | XC66440 | 2000-F66-PID-PR-10002 | F66-ER-411A CIL4 Electrowinning Cell 1 Rectifier 1 Voltage Feedback | F66ER411A Rect1VoltFdbk | 1 | 0 | 4.5 | V | Voltage limit input from PCS when rectifier is operating remotely in "DC Current Mode". 5 V maximum limit recommended by vendor. | 0
|  |  |  | IC66441S | IC66441 | 2000-F66-PID-PR-10002 | F66-ER-411B CIL4 Electrowinning Cell 1 Rectifier 2 Current Feedback | F66ER411B Rect1AmpFdbck | 1 | 0 | 2500 | A | Remote current setpoint input from PCS when rectifier is operating remotely in "DC Current Mode". 2550 A is maximum peak current, determined by bus bar limitation. | 0
|  |  |  | XC66441S | XC66441 | 2000-F66-PID-PR-10002 | F66-ER-411B CIL4 Electrowinning Cell 1 Rectifier 2 Voltage Feedback | F66ER411B Rect1VoltFdbk | 1 | 0 | 4.5 | V | Voltage limit input from PCS when rectifier is operating remotely in "DC Current Mode". 5 V maximum limit recommended by vendor. | 0
|  |  |  | IC66442S | IC66442 | 2000-F66-PID-PR-10002 | F66-ER-412A CIL4 Electrowinning Cell 2 Rectifier 1 Current Feedback | F66ER412A Rect1AmpFdbck | 1 | 0 | 2500 | A | Remote current setpoint input from PCS when rectifier is operating remotely in "DC Current Mode". 2550 A is maximum peak current, determined by bus bar limitation. | 0
|  |  |  | XC66442S | XC66442 | 2000-F66-PID-PR-10002 | F66-ER-412A CIL4 Electrowinning Cell 2 Rectifier 1 Voltage Feedback | F66ER412A Rect1VoltFdbk | 1 | 0 | 4.5 | V | Voltage limit input from PCS when rectifier is operating remotely in "DC Current Mode". 5 V maximum limit recommended by vendor. | 0
|  |  |  | IC66443S | IC66443 | 2000-F66-PID-PR-10002 | F66-ER-412B CIL4 Electrowinning Cell 2 Rectifier 2 Current Feedback | F66ER412B Rect1AmpFdbck | 1 | 0 | 2500 | A | Remote current setpoint input from PCS when rectifier is operating remotely in "DC Current Mode". 2550 A is maximum peak current, determined by bus bar limitation. | 0
|  |  |  | XC66443S | XC66443 | 2000-F66-PID-PR-10002 | F66-ER-412B CIL4 Electrowinning Cell 2 Rectifier 2 Voltage Feedback | F66ER412B Rect1VoltFdbk | 1 | 0 | 4.5 | V | Voltage limit input from PCS when rectifier is operating remotely in "DC Current Mode". 5 V maximum limit recommended by vendor. | 0
[5 empty] | 0 | 0 | 0 | [6 empty] | A
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 9 | 9

## 4. Digital Output
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION, ELECTROWINNING & GOLD ROOM (AREA F22 & F66) |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)* | [15 empty] | Urgent (Critical Failure) | Urgent (Critical Failure) | 0
|  |  |  | 2000-F22-LST-PR-10101 | [19 empty] | High (Fault/Error) | High (Fault/Error) | 0
|  |  |  | DIGITAL OUTPUTS | [19 empty] | Low (Warning) | Low (Warning) | 0
[17 empty] | C1 Sign Off |  | C2 Sign Off |  |  |  |  | Information/Event (Journal) | Information/Event (Journal) | 0
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date | Comments - Don’t comment in C2 column | Change Date | Change Reference |  | - | 0
|  |  |  | YY22001 | YA22001 | 2000-F22-PID-PR-10001 | CIL 4 Elution Area Common Alarm Siren/Beacon | Elution Area Alarm | Off | On | - |  | - | - | Alarm will trigger and activate an audible siren in the field if any of the Elution and/or Acid Wash sequences go into a fault state. If a Fault state in F22-SEQ-0001 to F22-SEQ-0008 is triggered. Activate YA22001 If F22-SEQ-0001 to F22-SEQ-0008 are Healthy. Deactivate YA22001 | B
|  |  |  | YY22027 | YA22027 | 2000-F22-PID-PR-10001 | F22PR411 CIL4 Elution & Acid Wash Column Area HCN Gas Siren Signal | Elution HCN Alarm | Off | On | - |  | - | - | Siren and Beacon If ASHH22027 = Inactive for 3 seconds: Activate YA22027 If ASHH22027 = Active for 10 minutes: Deactivate YA22027 | 0
|  |  |  | YY22002 | YA22002 | 2000-F23-PID-PR-10001 | F22-BX-405 Final Tails Collection Box Area HCN Alarm Signal | Elution Tail HCN Alarm | Off | On | - |  | - | - | Siren and Beacon If ASHH22002 = Inactive for 3 seconds: Activate YA22002 If ASHH22002 = Active for 10 minutes: Deactivate YA22002 | 0
|  |  |  | XY22116 | HS22116 | 2000-F22-PID-PR-10002 | F22HT411-CPN CIL4 Elution Heater Control Panel Remote Start | F22HT411 Start | - | - | - |  | - | - | Logic: Deactivating HS22116 will initiate a stop on the elution heater | A
|  |  |  | XY22117 | HS22117 | 2000-F22-PID-PR-10002 | F22HT411-CPN CIL4 Elution Heater Control Panel Reset | F22HT411 Reset | - | - | - |  | - | - |  | 0
|  |  |  | XY22118 | HS22118 | 2000-F22-PID-PR-10002 | F22HT411-CPN CIL4 Elution Heater Control Panel Remote Mode Select | F22HT411 Remote | - | - | - |  | - | - |  | 0
|  |  |  | HS22250S | HS22250 | 2000-F22-PID-PR-10008 | F22-CU-406 Kiln Mercury Abatement Chiller Start/Stop | F22CU406 Start / Stop | - | - | - |  | - | - |  | B
|  |  |  | XS22292S | XS22292 | 2000-F22-PID-PR-10005 | F22-KN-411 CIL4 Carbon Regeneration Kiln Start | F22KN411 Start | - | - | - |  | - | - | True = Start ; False = Not Start | 1 | [5 empty] | 2025-06-09 | Updated as per client review comment
|  |  |  | XS22293S | XS22293 | 2000-F22-PID-PR-10005 | F22-KN-411 CIL4 Carbon Regeneration Kiln Stop | F22KN411 Stop | - | - | - |  | - | - | True = Stop ; False = Not Stop | 1 | [5 empty] | 2025-06-09 | Updated as per client review comment
|  |  |  | XS22294S | XS22294 | 2000-F22-PID-PR-10005 | F22-KN-411 CIL4 Carbon Regeneration Kiln Reset | F22KN411 Reset | - | - | - |  | - | - |  | 0
|  |  |  | YY22053 | YA22053 | 2000-F22-PID-PR-10005 | F22-KN-411 CIL4 Carbon Regeneration Kiln Mercury Siren/Beacon | F22KN411 Mercury | Off | On | - |  | - | - | Siren and Beacon If AIT22052 ≥ A_HH for 3 seconds: Activate YA22053 If AIT22052 < A_HH for 10 minutes: Deactivate YA22053 | 0
|  |  |  | YY22253 | YA22253 | 2000-F22-PID-PR-10007 | F22-PS-453 Mercury Abatement Area Sump Pump Siren/Beacon | F22PS453 Mercury | Off | On | - |  | - | - | Siren and Beacon If AIT22252 ≥ A_HH for 3 seconds: Activate YA22253 If AIT22252 < A_HH for 10 minutes: Deactivate YA22253 | 1 | [5 empty] | 2025-05-14 | Updated as per HAZOP 02/05/2025
|  |  |  | YY22233 | YA22233 | 2000-F22-PID-PR-10007 | F22-ST-401 Kiln Mercury Abatement Discharge Stack Mercury Siren/Beacon | F22ST401 Mercury | Off | On | - |  | - | - | Siren and Beacon If AIT22232 ≥ A_HH for 3 seconds: Activate YA22233 If AIT22232 < A_HH for 10 minutes: Deactivate YA22233 | 0
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 13 | 13

## 5. Totalisers
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION, ELECTROWINNING & GOLD ROOM (AREA F22 & F66)
2000-F22-LST-PR-10101
TOTALISERS
[11 empty] | Reset Period |  |  |  |  | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | Type | P&ID | Description | Abbreviated Description (Faceplate) | Units | Shift | Day | Cont | Comments | Rev | OK | Date | OK | Date | Comments - Don’t comment in C2 column
|  |  |  | FQ22023 | FQI22023 | FQI | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Scheme Water Flow Totaliser | CIL4 Elution Water Flow | m3 | X | X | X |  | A
|  |  |  | FQ22025 | FQI22025 | FQI | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Hydrochloric Acid Flow Totaliser | CIL4 Elution HCl Flow | m3 | X | X | X |  | A
|  |  |  | FQ22182 | FQI22182 | FQI | 2000-F22-PID-PR-10002 | Elution Cyanide Feed Flow Totaliser | CIL4 Elution CN Flow | m3 | X | X | X |  | A
|  |  |  | FQ22192 | FQI22192 | FQI | 2000-F22-PID-PR-10002 | Elution Caustic Feed Flow Totaliser | CIL4 Elution NaOH Flow | m3 | X | X | X |  | A
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 4 | 4
[8 empty] | 4 | [6 empty] | #NAME?

## 3. Digital Input
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION, ELECTROWINNING & GOLD ROOM (AREA F22 & F66) |  |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)* | [15 empty] | Urgent (Critical Failure) | #REF!
|  |  |  | 2000-F22-LST-PR-10101 | [20 empty] | High (Fault/Error) | #REF!
|  |  |  | DIGITAL INPUTS | [20 empty] | Low (Warning) | #REF!
[18 empty] | C1 Sign Off |  | C2 Sign Off |  |  |  |  | Information/Event (Journal) | #REF!
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Source | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date | Comments - Don’t comment in C2 column | Change Date | Change Reference |  | #REF!
|  |  |  | LSH22137 | LAH22137 | 2000-F21-PID-PR-10002 | F22-PR-413 CIL4 Loaded Carbon Transfer Vessel Level Switch High | F22HP445 Full | Normal | Alarm | Alarm | Hardwired |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | LSH22012 | LAH22012 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Level Switch High | F22PR411 Full | Normal | Alarm | Alarm | Hardwired |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | LSH22071 | LAH22071 | 2000-F22-PID-PR-10001 | F22-PS-451 CIL4 Elution Area Sump Pump Level Switch High | F22PS451 Hi | Normal | Alarm | Alarm | Hardwired |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | FSH22019 | FAH22019 | 2000-F22-PID-PR-10001 | F21-FD-431 CIL4 Feed Distribution Box Spillage Feed Flow Switch High | Misdirect Flow 3 | Normal | Alarm | Alarm | Hardwired |  | 3 | XV22072 Open | Flowswitch purpose is to detect misdirected flow i.e. if upstream valve is passing/failing to close properly. | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | FSH22020 | FAH22020 | 2000-F22-PID-PR-10001 | F22-BX-405 Final Tails Collection Box Spillage Feed Flow Switch High | Misdirect Flow 4 | Normal | Alarm | Alarm | Hardwired |  | 3 | XV22073 Open | Flowswitch purpose is to detect misdirected flow i.e. if upstream valve is passing/failing to close properly. | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | ASHH22027 | AAHH22027 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column HCN Gas Switch | Elution HCN | Alarm | Normal | Alarm | Hardwired |  | 3 | - | Logic: Include 10 minute off delay on AAHH22027 | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | ASHH22002 | AAHH22002 | 2000-F23-PID-PR-10001 | F22-BX-405 Final Tails Collection Box Area HCN Gas Switch | Elution Tail HCN | Alarm | Normal | Alarm | Hardwired |  | 3 | - | Logic: Include 10 minute off delay on AAHH22002 | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | PDSH22104 | PDAH22104 | 2000-F22-PID-PR-10002 | F22-PP-460 CIL4 Elution Heater Thermal Oil Pump Differential Pressure Switch | F22PP460 Diff. | Normal | Alarm | Alarm | Hardwired |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | PSH22104 | PAH22104 | 2000-F22-PID-PR-10002 | F22-PP-460 CIL4 Elution Heater Thermal Oil Pump Pressure Switch | F22PP460 Press. | Normal | Alarm | Alarm | Hardwired |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | TSH22107 | TAH22107 | 2000-F22-PID-PR-10002 | F22-ST-411 CIL4 Elution Heater Exhaust Stacker Temperature Switch High | F22ST411 Stack | Alarm | Normal | Alarm | Hardwired |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | TSH22109 | TAH22109 | 2000-F22-PID-PR-10002 | F22-HT-411 CIL4 Elution Heater Temperature Switch High | F22HT411 Oil | Alarm | Normal | Alarm | Hardwired |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | LSL22113 | LAL22113 | 2000-F22-PID-PR-10002 | F22-TK-444 CIL4 Elution Heater Oil Expansion Tank Level Switch Low | F22TK444 Oil | Alarm | Normal | Alarm | Hardwired |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | XS22114 | XA22114 | 2000-F22-PID-PR-10002 | F22HT411-CPN CIL4 Elution Heater Control Panel Fault | F22HT411 Fault | Normal | Alarm | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | XS22115 | XI22115 | 2000-F22-PID-PR-10002 | F22HT411-CPN CIL4 Elution Heater Control Panel Healthy/Running | F22HT411 Running | Normal | Active | - | Hardwired |  | - | - |  | A
|  |  |  | XS22119 | XI22119 | 2000-F22-PID-PR-10002 | F22HT411-CPN CIL4 Elution Heater Ready | F22HT411 Ready | Normal | Active | - | Hardwired |  | - | - |  | 0
|  |  |  | PSL22125 | PAL22125 | 2000-F22-PID-PR-10002 | F22FN411 CIL4 Elution Heater Burner Fan Low Pressure Switch | F22FN411 Low | Normal | Alarm | Alarm | Hardwired |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | XS22285 | XA22285 | 2000-F22-PID-PR-10005 | F22-KN-411 CIL4 Carbon Regeneration Kiln Common Alarm Fault | F22KN411 Fault | Normal | Alarm | Alarm | Hardwired |  | 0 | - | Part of ME017 - F22-KN-411 CIL4 Carbon Regeneration Kiln | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | XS22286 | XI22286 | 2000-F22-PID-PR-10005 | F22-KN-411 CIL4 Carbon Regeneration Kiln E-Stop Healthy | F22KN411 E-Stop | Normal | Active | - | Hardwired |  | - | - | Part of ME017 - F22-KN-411 CIL4 Carbon Regeneration Kiln | 1 | [6 empty] | 22-KN-41 changed to 22-KN-411
|  |  |  | XS22287 | XI22287 | 2000-F22-PID-PR-10005 | F22-KN-411 CIL4 Carbon Regeneration Kiln DC Emergency Drive On | F22KN411 E Drive | Normal | Active | - | Hardwired |  | - | - | Part of ME017 - F22-KN-411 CIL4 Carbon Regeneration Kiln | 0
|  |  |  | XS22288 | XA22288 | 2000-F22-PID-PR-10005 | F22-KN-411 CIL4 Carbon Regeneration Kiln Outlet Hopper Hi Temp/Full | F22KN411 Quench | Normal | Alarm | Alarm | Hardwired |  | 0 | - | Part of ME017 - F22-KN-411 CIL4 Carbon Regeneration Kiln | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | XS22289 | XI22289 | 2000-F22-PID-PR-10005 | F22-KN-411 CIL4 Carbon Regeneration Kiln Terminal Cooling Fan Running | F22KN411 Fan | Normal | Active | - | Hardwired |  | - | - | Part of ME017 - F22-KN-411 CIL4 Carbon Regeneration Kiln | 0
|  |  |  | XS22290 | XI22290 | 2000-F22-PID-PR-10005 | F22-KN-411 CIL4 Carbon Regeneration Kiln Kiln Rotation Drive On | F22KN411 Rotate | Normal | Active | - | Hardwired |  | - | - | Part of ME017 - F22-KN-411 CIL4 Carbon Regeneration Kiln | 0
|  |  |  | XS22291 | XI22291 | 2000-F22-PID-PR-10005 | F22-KN-411 CIL4 Carbon Regeneration Kiln Kiln Screw Feeder On | F22KN411 Feeder | Normal | Active | - | Hardwired |  | - | - | Part of ME017 - F22-KN-411 CIL4 Carbon Regeneration Kiln | 0
|  |  |  | LSL22297 | LAL22297 | 2000-F22-PID-PR-10005 | F22-KN-411 CIL4 Carbon Regeneration Kiln Input Hopper Carbon Level Switch | F22FS413 Level | Normal | Alarm | Alarm | Soft Tag |  | 3 | - |  | 1 | [5 empty] | 15/07/2025 14/04/26 | Updated as per KAN-2046 FC:Reinstated. Info is still required even if it comes across comms
|  |  |  | LSH22205 | LAH22205 | 2000-F22-PID-PR-10005 | F22-TK-446 CIL4 Carbon Quench Tank Level Switch High | F22HP446 Carbon | Normal | Alarm | Alarm | Hardwired |  | 5 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | LSHH22206 | LAHH22206 | 2000-F22-PID-PR-10005 | F22-TK-446 CIL4 Carbon Quench Tank Level Switch High High | F22HP446 Water | Alarm | Normal | Alarm | Hardwired |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | LSH22211 | LAH22211 | 2000-F22-PID-PR-10005 | F22-PS-452 Regen Kiln Area Sump Pump Level Switch High | F22PS452 Hi | Normal | Alarm | Alarm | Hardwired |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | ZSC22244 | ZIC22244 | 2000-F22-PID-PR-10008 | F22-PW-591 Kiln Abatement System Cooling Water Pump 1 Suction Valve Position Switch Closed | F22PW591 Suc Cls | Normal | Active | - | Hardwired |  | - | - |  | B
|  |  |  | ZSO22244 | ZIO22244 | 2000-F22-PID-PR-10008 | F22-PW-591 Kiln Abatement System Cooling Water Pump 1 Suction Valve Position Switch Open | F22PW591 Suc Opn | Normal | Active | - | Hardwired |  | - | - |  | B
|  |  |  | ZSC22245 | ZIC22245 | 2000-F22-PID-PR-10008 | F22-PW-591 Kiln Abatement System Cooling Water Pump 1 Discharge Valve Position Switch Closed | F22PW591 Dis Cls | Normal | Active | - | Hardwired |  | - | - |  | B
|  |  |  | ZSO22245 | ZIO22245 | 2000-F22-PID-PR-10008 | F22-PW-591 Kiln Abatement System Cooling Water Pump 1 Discharge Valve Position Switch Open | F22PW591 Dis Opn | Normal | Active | - | Hardwired |  | - | - |  | B
|  |  |  | ZSC22246 | ZIC22246 | 2000-F22-PID-PR-10008 | F22-PW-592 Kiln Abatement System Cooling Water Pump 2 Suction Valve Position Switch Closed | F22PW592 Suc Cls | Normal | Active | - | Hardwired |  | - | - |  | B
|  |  |  | ZSO22246 | ZIO22246 | 2000-F22-PID-PR-10008 | F22-PW-592 Kiln Abatement System Cooling Water Pump 2 Suction Valve Position Switch Open | F22PW592 Suc Opn | Normal | Active | - | Hardwired |  | - | - |  | B
|  |  |  | ZSC22247 | ZIC22247 | 2000-F22-PID-PR-10008 | F22-PW-592 Kiln Abatement System Cooling Water Pump 2 Discharge Valve Position Switch Closed | F22PW592 Dis Cls | Normal | Active | - | Hardwired |  | - | - |  | B
|  |  |  | ZSO22247 | ZIO22248 | 2000-F22-PID-PR-10008 | F22-PW-592 Kiln Abatement System Cooling Water Pump 2 Discharge Valve Position Switch Open | F22PW592 Dis Opn | Normal | Active | - | Hardwired |  | - | - |  | B
|  |  |  | FSL22248 | FAL22248 | 2000-F22-PID-PR-10008 | F22-PW-591/592 Kiln Abatement System Cooling Water Pumps Discharge Flow Switch Low Low | F22CU406 Lo Water FLo | Normal | Alarm | Alarm | Hardwired |  | 3 | F22-PW-591 is NOT RUNNING AND F22-PW-592 is NOT RUNNING |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | XS22250 | XA22250C | 2000-F22-PID-PR-10008 | F22-CU-406 Kiln Mercury Abatement Chiller Fault | F22CU406 Fault | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | XS22250A | XI22250A | 2000-F22-PID-PR-10008 | F22-CU-406 Kiln Mercury Abatement Chiller Running | F22CU406 Running | Normal | Active | - | Hardwired |  | - | - |  | B
|  |  |  | XS22250B | XI22250B | 2000-F22-PID-PR-10008 | F22-CU-406 Kiln Mercury Abatement Chiller Ready | F22CU406 Ready | Normal | Active | - | Hardwired |  | - | - |  | B
|  |  |  | FSL22261 | FAL22261 | 2000-F24-PID-PR-10003 | F22-PP-490 CIL4 Barren Carbon Pump Gland Water Flow Switch Low | F22PP490 GW Lo | Alarm | Normal | Alarm | Hardwired |  | 3 | F22-PP-490 is NOT RUNNING Enable 10s delay mask on pump start-up |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | HS66451 | HS_66451 | 2000-F66-PID-PR-10001 | F66-PW-461/462 CIL4 Electrowinning Pump 1/2 Pregnant Eluate Sample Command Pushbutton | CIL4 EW Pregnant | Normal | Active | - | Hardwired |  | - | - | Field pushbutton on LCP. Pressing this button for > 1 second, will open SV66451 for 20 seconds (Configurable, TBC during commissioning) | B
|  |  |  | HS66542 | HS_66542 | 2000-F66-PID-PR-10001 | F66-PW-461/462 CIL4 Electrowinning Pump 1/2 Barren Eluate Sample Command Pushbutton | CIL4 EW Barren | Normal | Active | - | Hardwired |  | - | - | Field pushbutton on LCP. Pressing this button for > 1 second, will open SV66452 for 20 seconds (Configurable, TBC during commissioning) | B
|  |  |  | FSL66455 | FAL66455 | 2000-F66-PID-PR-10002 | F66-EW-411 Low Flow Switch 1 | F66EC411 Flow 1 | Normal | Alarm | Alarm | Hardwired |  | 3 | F66-PW-461 is NOT RUNNING AND F66-PW-462 is NOT RUNNING |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | FSL66456 | FAL66456 | 2000-F66-PID-PR-10002 | F66-EW-411 Low Flow Switch 2 | F66EC411 Flow 2 | Normal | Alarm | Alarm | Hardwired |  | 3 | F66-PW-461 is NOT RUNNING AND F66-PW-462 is NOT RUNNING |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | FSL66457 | FAL66457 | 2000-F66-PID-PR-10002 | F66-EW-412 Low Flow Switch 1 | F66EC412 Flow 1 | Normal | Alarm | Alarm | Hardwired |  | 3 | F66-PW-461 is NOT RUNNING AND F66-PW-462 is NOT RUNNING |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | FSL66458 | FAL66458 | 2000-F66-PID-PR-10002 | F66-EW-412 Low Flow Switch 2 | F66EC412 Flow 2 | Normal | Alarm | Alarm | Hardwired |  | 3 | F66-PW-461 is NOT RUNNING AND F66-PW-462 is NOT RUNNING |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | - | ACID_USE | - | Elution Acid in Use | Elution Acid | Normal | Active | - | Soft Tag |  | - |  | Used as a flag in sequence to indicate when acid solution is in use in area | 0
|  |  |  | - | ELUATE_USE | - | Elution Eluate in Use | Elution Eluate | Normal | Active | - | Soft Tag |  | - |  | Used as a flag in sequence to indicate when eluate solution is in use in area | 0
|  |  |  | F22DCS412PS1 | F22DCS412_PS1 | - | F22-DCS-412 PS1 24VDC HEALTHY | F22DCS412 PS1 24VDC OK | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22DCS412PS2 | F22DCS412_PS2 | - | F22-DCS-412 PS2 24VDC HEALTHY | F22DCS412 PS2 24VDC OK | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22SW030PS | F22SW030_PS | - | F22-SW-030 ACB SHUNT TRIP 24VDC OK | F22SW030 ACBShunt 24V OK | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22SW030AF | F22SW030_AF | - | F22-SW-030 ARC FLASH DETECTION SYSTEM ALARM | F22SW030 Arc Flash | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22SW030OP | F22SW030_OP | - | F22-SW-030 CIRCUIT BREAKER OPENED | F22SW030 Breaker Open | Active | Normal | - | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22SW030CL | F22SW030_CL | - | F22-SW-030 CIRCUIT BREAKER CLOSED | F22SW030 Breaker Close | Active | Normal | - | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22SW030TRP | F22SW030_TRP | - | F22-SW-030 CIRCUIT BREAKER TRIPPED | F22SW030 Breaker Trip | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22SR001ESTP | F22SR001_ESTP | - | F22-SR-001 SWITCHROOM EMERGENCY SHUTDOWN DCS INPUT | F22SR001 Estop | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22SW030PS1 | F22SW030_PS1 | - | F22-SW-030 PS1 24VDC HEALTHY | F22SW030 PS1 24VDC OK | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22SW030PS2 | F22SW030_PS2 | - | F22-SW-030 PS2 24VDC HEALTHY | F22SW030 PS2 24VDC OK | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22SW031PS | F22SW031_PS | - | F22-SW-031 ACB SHUNT TRIP 24VDC OK | F22SW031 ACBShunt 24V OK | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22SW031AF | F22SW031_AF | - | F22-SW-031 ARC FLASH DETECTION SYSTEM ALARM | F22SW031 Arc Flash | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22SW031OP | F22SW031_OP | - | F22-SW-031 CIRCUIT BREAKER OPENED | F22SW031 Breaker Open | Active | Normal | - | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22SW031CL | F22SW031_CL | - | F22-SW-031 CIRCUIT BREAKER CLOSED | F22SW031 Breaker Close | Active | Normal | - | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22SW031TRP | F22SW031_TRP | - | F22-SW-031 CIRCUIT BREAKER TRIPPED | F22SW031 Breaker Trip | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22SW030SD | F22SW030_SD | - | F22-SW-030 INCOMER SURGE DIVERTER OK | F22SW030 Surge Diverter | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22SW031PS1 | F22SW031_PS1 | - | F22-SW-031 PS1 24VDC HEALTHY | F22SW031 PS1 24VDC OK | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22SW031PS2 | F22SW031_PS2 | - | F22-SW-031 PS2 24VDC HEALTHY | F22SW031 PS2 24VDC OK | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22FIP001ALM | F22FIP001_ALM | - | F22-FIP-001 Alarm | F22FIP001 Alarm | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22FIP001ISL | F22FIP001_ISL | - | F22-FIP-001 Isolated | F22FIP001 Isolate | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22FIP001FLT | F22FIP001_FLT | - | F22-FIP-001 Fault | F22FIP001 Fault | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22SW031SD | F22SW031_SD | - | F22-SW-031 INCOMER SURGE DIVERTER OK | F22SW031 Surge Diverter | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22SW131Q1CL | F22SW131_Q1CL | - | F22-SW-131 Mains Supply CB Closed | F22SW131 Main CB | Active | Normal | - | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22SW131Q1OP | F22SW131_Q1OP | - | F22-SW-131 Mains Supply CB Tripped | F22SW131 MainCB Open | Inactive | Active | - | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22SW131Q2CL | F22SW131_Q2CL | - | F22-SW-131 Generator Supply CB Closed | F22SW131 Gen CB | Active | Normal | - | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22SW131Q2OP | F22SW131_Q2OP | - | F22-SW-131 Generator Supply CB Tripped | F22SW131 GenCB Open | Inactive | Active | - | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22SW131SD | F22SW131_SD | - | F22-SW-131 Surge Diverter Ok | F22SW131 Surge Diverter | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-05-07 | Tag Name can not be same as Tag Source
|  |  |  | F22RIO001PS1 | F22RIO001_PS1 | - | F22-RIO-001 PS1 24VDC HEALTHY | F22RIO001 PS1 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22RIO001PS2 | F22RIO001_PS2 | - | F22-RIO-001 PS2 24VDC HEALTHY | F22RIO001 PS2 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22RIO002PS1 | F22RIO002_PS1 | - | F22-RIO-002 PS1 24VDC HEALTHY | F22RIO002 PS1 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | F22RIO002PS2 | F22RIO002_PS2 | - | F22-RIO-002 PS2 24VDC HEALTHY | F22RIO002 PS2 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | ZSC22004 | ZAC22004 | - | F22-TR-030 CARBON REGEN AND ELUTION 415V MCC 1 TRANSFORMER Enclosure Door Position Switch Closed | F22TR030 415VMCC Door CL | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-07-08 | State 0/1 updated to align with submitted control documents
|  |  |  | ZSC22005 | ZAC22005 | - | F22-TR-031 CARBON REGEN AND ELUTION 415V MCC 2 TRANSFORMER Enclosure Door Position Switch Closed | F2TR031 415VMCC Door CL | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2026-04-29 | Abbreviated description
|  |  |  | LSH22009 | LAH22009 | - | F22-GE-131 CARBON REGEN AND ELUTION EMERGENCY SUPPLY 415V GENERATOR FUEL LEVEL SWITCH HIGH | F22GE131 LVL Hi | Normal | Alarm | Alarm | Hardwired |  | 0 | - |  | 0
|  |  |  | LSL22009 | LAL22009 | - | CARBON REGEN AND ELUTION EMERGENCY SUPPLY 415V GENERATOR FUEL LEVEL SWITCH LOW | F22GE131 LVL Lo | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 0
|  |  |  | AS22175 | AA22175 | 2000-F22-PID-PR-10002 | CIL4 ELUTION AREA OIL TRAP SUMP HYDROCARBON LEAK DETECTOR | Elution Oil Leak | Normal | Alarm | Alarm | Hardwired |  | 0 | - |  | 0
|  |  |  | FSH22263 | FAH22263 | 2000-F24-PID-PR-10028 | F22-SE-470 CIL4 LOADED CARBON SCREEN AREA SAFETY SHOWER FLOW SWITCH HIGH | F22SE470 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22264 | FAH22264 | 2000-F24-PID-PR-10028 | F22-SE-471 CIL4 - LOADED CARBON TRANSFER VESSEL UPPER SAFETY SHOWER FLOW SWITCH HIGH | F22SE471 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22265 | FAH22265 | 2000-F24-PID-PR-10028 | F22-SE-472 CIL4 - LOADED CARBON TRANSFER VESSEL LOWER SAFETY SHOWER FLOW SWITCH HIGH | F22SE472 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22266 | FAH22266 | 2000-F24-PID-PR-10028 | F22-SE-473 CIL4 - CIL4 REGEN KILN DEWATERING SCREEN AREA SAFETY SHOWER FLOW SWITCH HIGH | F22SE473 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22267 | FAH22267 | 2000-F24-PID-PR-10028 | F22-SE-474 CIL4 - CIL4 ELUTION & ACID WASH COLUMN AREA UPPER SAFETY SHOWER FLOW SWITCH HIGH | F22SE474 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22268 | FAH22268 | 2000-F24-PID-PR-10028 | F22-SE-475 CIL4 - CIL4 ELUTION & ACID WASH COLUMN AREA MIDDLE SAFETY SHOWER FLOW SWITCH HIGH | F22SE475 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22269 | FAH22269 | 2000-F24-PID-PR-10028 | F22-SE-476 CIL4 - CIL4 ELUTION & ACID WASH COLUMN AREA LOWER SAFETY SHOWER FLOW SWITCH HIGH | F22SE476 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22270 | FAH22270 | 2000-F24-PID-PR-10028 | F22-SE-477 CIL4 - CIL4 ELUTION & ACID WASH COLUMN BUND AREA SAFETY SHOWER FLOW SWITCH HIGH | F22SE477 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22271 | FAH22271 | 2000-F24-PID-PR-10028 | F22-SE-478 CIL4 - CIL4 ELUTION PUMP AREA SAFETY SHOWER FLOW SWITCH HIGH | F22SE478 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22272 | FAH22272 | 2000-F24-PID-PR-10028 | F22-SE-479 CIL4 - CIL4 ELUTION HEATER AREA SAFETY SHOWER FLOW SWITCH HIGH | F22SE479 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22273 | FAH22273 | 2000-F24-PID-PR-10028 | F22-SE-480 CIL4 - CIL4 CARBON REGENERATION KILN UPPER SAFETY SHOWER FLOW SWITCH HIGH | F22SE480 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22274 | FAH22274 | 2000-F24-PID-PR-10028 | F22-SE-481 CIL4 - CIL4 CARBON REGENERATION KILN LOWER SAFETY SHOWER FLOW SWITCH HIGH | F22SE481 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22275 | FAH22275 | 2000-F24-PID-PR-10028 | F22-SE-482 CIL4 - MERCURY ABATEMENT AREA SAFETY SHOWER FLOW SWITCH HIGH | F22SE482 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22276 | FAH22276 | 2000-F24-PID-PR-10028 | F22-SE-505 MERCURY ABATEMENT AREA SAFETY SHOWER 2 FLOW SWITCH HIGH | F22SE505 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-08-18 10:44 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH22277 | FAH22277 | 2000-F24-PID-PR-10028 | F22-SE-506 MERCURY ABATEMENT AREA SAFETY SHOWER 3 FLOW SWITCH HIGH | F22SE506 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-08-18 10:44 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH66435 | FAH66435 | 2000-F24-PID-PR-10005 | F66-SE-433 ILR ELECTROWINNING AREA SAFETY SHOWER FLOW SWITCH HIGH | F66SE433 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH66436 | FAH66436 | 2000-F24-PID-PR-10005 | F66-SE-437 ELUATE CIRCULATION TANKS PLATFORM SAFETY SHOWER FLOW SWITCH HIGH | F66SE437 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH66437 | FAH66437 | 2000-F24-PID-PR-10005 | F66-SE-438 CIL4 ELECTROWINNING AREA SAFETY SHOWER FLOW SWITCH HIGH | F66SE438 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH66438 | FAH66438 | 2000-F24-PID-PR-10005 | F66-SE-467 GOLDROOM SAFETY SHOWER FLOW SWITCH HIGH | F66SE467 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 | - |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | F22TR030WTH | F22TR030_WTH | - | F22-TR-030 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F22TR030 Temp Hi | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-08-19 | CR-034
|  |  |  | F22TR031WTH | F22TR031_WTH | - | F22-TR-031 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F22TR031 Temp Hi | Alarm | Normal | Alarm | Hardwired |  | 0 | - |  | 1 | [5 empty] | 2025-08-19 | CR-034
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 105 | 105

## 6. OnOff Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION, ELECTROWINNING & GOLD ROOM (AREA F22 & F66)
2000-F22-LST-PR-10101
OPEN-CLOSE VALVES
[14 empty] | Permissives and Trips | [12 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position (Loss of Power) | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open Interlock | Close Interlock | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date | Comments - Don’t comment in C2 column | Change Date | Change Reference
|  |  |  | XV21136 | 2000-F21-PID-PR-10002 | F22-SC-421 CIL4 Loaded Carbon Screen Spray Water Valve | F22SC421 Spray | Detail 7 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22138 | 2000-F21-PID-PR-10002 | F22-PR-413 CIL4 Loaded Carbon Transfer Vessel Scheme Water Valve | F22HP445 Motive | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22011 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Loaded Carbon Feed Valve | F22PR411 Carbon | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | OP1 | TI22013 ≤ P_Hi AND TI22031 ≤ P_Lo | - | 0 | - | X | - | - | - | - | - | Valve can not open when column is under high temperature and pressure; to prevent flashing of column contents. | 1 | [5 empty] | 2025-07-23 | Update to TI22031 P_Lo condition
|  |  |  | XV22016 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Eluate Discharge Valve | F22PR411 Top Out | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22051 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Acid Rinse Water Discharge Valve | F22PR411 HCl Out | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | OP1 | TI22013 ≤ P_Hi AND TI22031 ≤ P_Lo | - | 0 | - | X | - | - | - | - | - | Valve can not open when column is under high temperature and pressure; to prevent flashing of column contents. | 1 | [5 empty] | 2025-07-23 | Update to TI22031 P_Lo condition
|  |  |  | XV22054 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Pregnant Eluate Discharge Valve | F22PR411 PregOut | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22057 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Barren Carbon Discharge Valve | F22PR411 C Out | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | OP1 | TI22013 ≤ P_Hi AND TI22031 ≤ P_Lo | - | 0 | - | X | - | - | - | - | - | Valve can not open when column is under high temperature and pressure; to prevent flashing of column contents. | 1 | [5 empty] | 2025-07-23 | Update to TI22031 P_Lo condition
|  |  |  | XV22026 | 2000-F22-PID-PR-10001 | F22-PW-403 CIL 4 Carbon Eductor Pump Discharge Valve | F22PW403 Discharge | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | ` | [5 empty] | 2026-02-16 | Dchrge to Discharge
|  |  |  | XV22061 | 2000-F22-PID-PR-10001 | F22-FD-420 CIL4 Regen Kiln Dewatering Screen Feed Box Barren Carbon Feed Valve | CIL4 C to Regen | Detail 3 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22062 | 2000-F22-PID-PR-10001 | F22-FD-433 CIL4 Carbon Sizing Screen Feed Box Barren Carbon Feed Valve | CIL4 C to CIL4 | Detail 3 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22022 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Scheme Water Feed Valve | F22PR411 Rinse | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22024 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Hydrochloric Acid Feed Valve | F22PR411 HCl | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22030 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Pregnant Eluate Feed Valve | F22PR411 Btm In | Detail 8 | FO | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2025-04-30 | Mistake - updated to match P&ID
|  |  |  | XV22034 | 2000-F22-PID-PR-10001 | F22-PR-411 CIL4 Elution & Acid Wash Column Reagent Addition Manifold Drain Valve | F22PR411 Drain | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | OP1 | TI22013 ≤ P_Hi AND TI22031 ≤ P_Lo | - | 0 | - | X | - | - | - | - | - | Valve can not open when column is under high temperature and pressure; to prevent flashing of column contents. | 1 | [5 empty] | 2025-07-23 | Update to TI22031 P_Lo condition
|  |  |  | XV22021 | 2000-F22-PID-PR-10001 | F22-PW-442 CIL4 Carbon Eductor Pump Suction Valve | F22PW403 Suction | Detail 9 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22072 | 2000-F22-PID-PR-10001 | F22-PS-451 CIL4 Elution Area Sump Pump CIL4 Feed Distribution Box Valve | Sump to CIL4 | Detail 8 | FC | X | X | ELUATE_USE is ACTIVE | ACID_USE is ACTIVE | - | ACID_USE is ACTIVE | - | 0 | - | - | - | - | X | X | - | ELUATE_USE set by sequences. Refer 2000-F22-LST-PR-10102 for details. When ELUATE_USE is active, indicates that Eluate Solution is in use within the Elution Area, resulting in sump pump discharge valve line-up changing appropriately to handle potential spillage. | 0
|  |  |  | XV22073 | 2000-F22-PID-PR-10001 | F22-PS-451 CIL4 Elution Area Sump Pump Final Tails Tank Valve | Sump to Tails | Detail 7 | FO | X | X | ACID_USE is ACTIVE | ELUATE_USE is ACTIVE | - | - | - | - | - | - | - | - | - | - | - | ACID_USE set by sequences. Refer 2000-F22-LST-PR-10102 for details. When ACID_USE is active, indicates that Acid Solution is in use within the Elution Area, resulting in sump pump discharge valve line-up changing appropriately to handle potential spillage. | 0
|  |  |  | XV22151 | 2000-F22-PID-PR-10002 | F22-TK-441 CIL4 Elution Water Tank Scheme Water Feed Valve | F22TK441 H2O In | Detail 8 | FC | X | X | LI22152 ≤ P_Lo | LI22152 ≥ P_Hi | CT1 | LI22152 ≥ A_HH | - | 3 | - | - | - | - | X | X | - | CIL4 Elution Water Tank level unable to accept water. | A
|  |  |  | XV22142 | 2000-F22-PID-PR-10002 | F22-TK-442 CIL4 Lean Eluate Tank Scheme Water Feed Valve | F22TK442 H2O In | Detail 8 | FC | X | X | - | - | CT1 | LI22143 ≥ A_HH | - | 3 | - | - | - | - | X | X | - | CIL4 Lean Eluate Tank unable to accept water. | A
|  |  |  | XV22181 | 2000-F22-PID-PR-10002 | Elution Cyanide Feed Valve | CIL4 NaCN | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22191 | 2000-F22-PID-PR-10002 | Elution Caustic Feed Valve | CIL4 NaOH | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22144 | 2000-F22-PID-PR-10002 | F22-TK-442 CIL4 Lean Eluate Tank Discharge Valve | F22TK442 Outlet | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22153 | 2000-F22-PID-PR-10002 | F22-TK-441 CIL4 Elution Water Tank Discharge Valve | F22TK441 Outlet | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22147 | 2000-F22-PID-PR-10002 | F22-TK-446 Eluate Expansion Tank Outlet Valve | F22TK446 Outlet | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22141 | 2000-F22-PID-PR-10002 | F22-TK-442 CIL4 Lean Eluate Tank Feed Valve | F22TK442 El In | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22145 | 2000-F22-PID-PR-10002 | F22-TK-446 Eluate Expansion Tank Intake Valve | F22TK446 El In | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22124 | 2000-F22-PID-PR-10002 | F22-TK-443 CIL4 Pregnant Eluate Tank Feed Valve | CIL4 Preg Eluate | Detail 8 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22161 | 2000-F22-PID-PR-10002 | F22-PW-441 CIL4 Elution Water Pump 1 Suction Valve | F22PW441 Suction | Detail 9 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22162 | 2000-F22-PID-PR-10002 | F22-PW-441 CIL4 Elution Water Pump 1 Discharge Valve | F22PW441 Discharge | Detail 9 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2026-02-16 | Dschrge to Discharge
|  |  |  | XV22163 | 2000-F22-PID-PR-10002 | F22-PW-444 CIL4 Elution Water Pump 2 Suction Valve | F22PW444 Suction | Detail 9 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22164 | 2000-F22-PID-PR-10002 | F22-PW-444 CIL4 Elution Water Pump 2 Discharge Valve | F22PW444 Discharge | Detail 9 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2026-02-16 | Dschrge to Discharge
|  |  |  | XV22194 | 2000-F22-PID-PR-10005 | F22-PP-490 CIL4 Barren Carbon Pump Feed Valve | F22PP490 H2O In | Detail 7 | FO | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2025-04-30 | Mistake - updated to match P&ID
|  |  |  | XV22201 | 2000-F22-PID-PR-10005 | F22-TK-446 CIL4 Carbon Quench Tank Discharge Valve | F22HP446 C Out | Detail 4 | FC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | CT1 | F22-PP-490 is Not Running | - | - | - | - | - | - | X | X | - |  | 1 | [5 empty] | 2025-05-16 | Addition to logic
|  |  |  | XV22202 | 2000-F22-PID-PR-10005 | F22-PP-490 CIL4 Barren Carbon Pump Drain Valve | F22PP490 Drain | Detail 3 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV22207 | 2000-F22-PID-PR-10005 | F22-HP-446 CIL4 Carbon Quench Hopper Scheme Water Valve | F22HP446 Scheme | Detail 9 | FL | X | X | LSHH22206 is INACTIVE | LSHH22206 is ACTIVE AND 30 second timer elapsed | - | - | - | - | - | - | - | - | - | - | - |  | 0
|  |  |  | XV22251 | 2000-F22-PID-PR-10005 | F22-HP-431 CIL4 Carbon Regeneration Hopper Discharge Valve | F22HP431 Discharge | Detail 4 | FC | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2026-02-16 | Dschrge to Discharge
|  |  |  | XV22231 | 2000-F22-PID-PR-10007 | F22-HE-401 Kiln Mercury Abatement Chiller Quick Cool Valve | F22HE401 Cool | Detail 7 | FO | X | X | TIC22228 > A_HH | TIC22228 < A_Hi | - | - | - | - | - | - | - | - | - | - | - |  | 0 | [5 empty] | 2025-03-17 | Actioned as per F22 HAZOP
|  |  |  | XV22241 | 2000-F22-PID-PR-10008 | F22-TK-484 Kiln Abatement System Cooling Water Tank Inlet Valve | F22TK484 H2O In | Detail 7 | FC | X | X | LI22242 ≤ P_Lo | LI22242 ≥ P_Hi | CT1 | LI22242 ≥ A_HH | - | 3 | - | - | - | - | X | X | - |  | B
|  |  |  | SV22260 | 2000-F24-PID-PR-10014 | F22-PP-490 CIL4 Barren Carbon Pump Gland Water Valve | F22PP490 Gland | Detail 11 | FO | X | X | F22PP490 is RUNNING |  | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2026-04-14 | FC : updated as per PL-679
|  |  |  | XV66401 | 2000-F66-PID-PR-10001 | F66-TK-461 CIL4 Eluate Circulation Tank 1 Caustic Addition Valve | F66TK461 NaOH | Detail 8 | FC | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV66408 | 2000-F66-PID-PR-10001 | F66-TK-471 CIL4 Eluate Circulation Tank 2 Caustic Addition Valve | F66TK471 NaOH | Detail 8 | FC | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV66402 | 2000-F66-PID-PR-10001 | F66-TK-461 CIL4 Eluate Circulation Tank 1 Pregnant Eluate Valve | F66TK461 Preg El | Detail 9 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | CT1 | XV66403 is Open | - | 3 | - | - | - | - | X | X | - | Only one CIL4 Eluate Circulation Tank can receive feed from the elution circuit at any one time. Tank selection will be via sequence. | A
|  |  |  | XV66403 | 2000-F66-PID-PR-10001 | F66-TK-471 CIL4 Eluate Circulation Tank 2 Pregnant Eluate Valve | F66TK471 Preg El | Detail 9 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | CT1 | XV66402 is Open | - | 3 | - | - | - | - | X | X | - | Only one CIL4 Eluate Circulation Tank can receive feed from the elution circuit at any one time. Tank selection will be via sequence. | A
|  |  |  | XV66409 | 2000-F66-PID-PR-10001 | F66-TK-461 CIL4 Eluate Circulation Tank 1 Pregnant Solution Valve | F66TK461 Return | Detail 9 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | CT1 | XV66410 is Open | - | 3 | - | - | - | - | X | X | - | Eluate return from electrowinning cells can only discharge into one tank at any time. | A
|  |  |  | XV66410 | 2000-F66-PID-PR-10001 | F66-TK-471 CIL4 Eluate Circulation Tank 2 Pregnant Solution Valve | F66TK471 Return | Detail 9 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | CT1 | XV66409 is Open | - | 3 | - | - | - | - | X | X | - | Eluate return from electrowinning cells can only discharge into one tank at any time. | A
|  |  |  | XV66415 | 2000-F66-PID-PR-10001 | F66-PW-461 CIL4 Electrowinning Pump 1 Pregnant Eluate Discharge Valve | F66PW461 PregOut | Detail 9 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | CT1 | XV66417 is Open | - | 3 | - | - | - | - | X | X | - | Only one pregnant eluate discharge valve can be opened. | A
|  |  |  | XV66416 | 2000-F66-PID-PR-10001 | F66-PW-461 CIL4 Electrowinning Pump 1 Barren Eluate Discharge Valve | F66PW461 Brn Out | Detail 9 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | CT1 | XV66418 is Open | - | 3 | - | - | - | - | X | X | - | Only one barren eluate discharge valve can be opened. | A
[12 empty] | - | - | CT2 | LI66650 ≥ A_HH | - | 3 | - | - | - | - | X | X | - | Barren Eluate Tank level unable to accept barren eluate. | A
[12 empty] | - | - | OP1 | LI66650 < A_Hi | - | 5 | - | X | - | - | - | X | - | Barren Eluate Tank level able to accept barren eluate. | A
|  |  |  | XV66417 | 2000-F66-PID-PR-10001 | F66-PW-462 CIL4 Electrowinning Pump 2 Pregnant Eluate Discharge Valve | F66PW462 PregOut | Detail 9 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | CT1 | XV66415 is Open | - | 3 | - | - | - | - | X | X | - | Only one pregnant eluate discharge valve can be opened. | A
|  |  |  | XV66418 | 2000-F66-PID-PR-10001 | F66-PW-462 CIL4 Electrowinning Pump 2 Barren Eluate Discharge Valve | F66PW462 Brn Out | Detail 9 | FL | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES | CT1 | XV66416 is Open | - | 3 | - | - | - | - | X | X | - | Only one barren eluate discharge valve can be opened. | A
[12 empty] | - | - | CT2 | LI66650 ≥ A_HH | - | 3 | - | - | - | - | X | X | - | Barren Eluate Tank level unable to accept barren eluate. | A
[12 empty] | - | - | OP1 | LI66650 < A_Hi | - | 5 | - | X | - | - | - | X | - | Barren Eluate Tank level able to accept barren eluate. | A
|  |  |  | SV66451 | 2000-F66-PID-PR-10001 | F66-PW-461/462 CIL4 Electrowinning Pump 1/2 Pregnant Eluate Sample Valve | Preg El Sample | Detail 11 | FC |  | X | HS66451 Active for 1 second | SV66451 open for 20 seconds | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2026-06-05 | https://pastech-2955.atlassian.net/browse/KAN-2719
|  |  |  | SV66452 | 2000-F66-PID-PR-10001 | F66-PW-461/462 CIL4 Electrowinning Pump 1/2 Barren Eluate Sample Valve | Brn El Sampler | Detail 11 | FC |  | X | HS66452 Active for 1 second | SV66452 open for 20 seconds | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2026-06-05 | https://pastech-2955.atlassian.net/browse/KAN-2719
|  |  |  | XV66411 | 2000-F66-PID-PR-10002 | F66-EC-411 CIL4 Electrowinning Cell 1 Sludge Discharge Valve 1 | F66EC411 Sldge 1 | Detail 12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Valve operated manually by field operator within the goldroom | A
|  |  |  | XV66412 | 2000-F66-PID-PR-10002 | F66-EC-411 CIL4 Electrowinning Cell 1 Sludge Discharge Valve 2 | F66EC411 Sldge 2 | Detail 12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Valve operated manually by field operator within the goldroom | A
|  |  |  | XV66413 | 2000-F66-PID-PR-10002 | F66-EC-412 CIL4 Electrowinning Cell 2 Sludge Discharge Valve 1 | F66EC412 Sldge 1 | Detail 12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Valve operated manually by field operator within the goldroom | A
|  |  |  | XV66414 | 2000-F66-PID-PR-10002 | F66-EC-412 CIL4 Electrowinning Cell 2 Sludge Discharge Valve 2 | F66EC412 Sldge 2 | Detail 12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Valve operated manually by field operator within the goldroom | A
|  |  |  | XV66421 | 2000-F66-PID-PR-10003 | F66-TK-460 Gravity Electrowinning Tank Caustic Addition Valve | F66TK460 NaOH | Detail 8 | FC | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | B
-
|  |  |  | DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE | [11 empty] | -
52
1

## 7. Control Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION, ELECTROWINNING & GOLD ROOM (AREA F22 & F66)
2000-F22-LST-PR-10101
CONTROL VALVES
[14 empty] | Permissive and Trips | [12 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open Interlock | Close Interlock | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date | Comments - Don’t comment in C2 column
|  |  |  | PCV22121 | 2000-F22-PID-PR-10002 | F22-HE-412 CIL4 Elution Recovery Heat Exchanger Discharge Pressure Control Valve | CIL4 Elution PCV | Detail 1 | FO | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - | Refer to PID Controller FIC-22121 | A
|  |  |  | TCV22228 | 2000-F22-PID-PR-10007 | F22-HE-401 Kiln Mercury Abatement Off-Gas Cooler Cooling Water Inlet Temperature Control Valve | F22HE401 Cooling TCV | Detail 1 | FO | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - | Refer to PID Controller TIC-22228 | A
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
2

## 8. PID Cont
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION, ELECTROWINNING & GOLD ROOM (AREA F22 & F66) | [60 empty] | High | Urgent (Critical Failure) | 0
|  |  |  | 2000-F22-LST-PR-10101 | [60 empty] | Med | High (Fault/Error) | 0
|  |  |  | PID Controllers | [60 empty] | Low | Low (Warning) | 0
[10 empty] | Modes |  |  |  | Setpoint |  |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [7 empty] | Alarm Priority |  |  |  |  | Controlled/Manipulated Variable | [10 empty] | Comment | Rev | C1 Sign Off |  | C2 Sign Off |  |  |  |  | n/a | Information/Event (Journal) | 0
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Controller Description | Abbreviated Description (Faceplate) | Normal Operating Mode | Manual | Auto | Cascade | Process Value Tag | Min | Max | Unit | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | A_LL | A_Lo | A_Hi | A_HH | Alarm Masking Conditions | Range Min | Range Max | Lower Limit | Upper Limit | Unit | Destination Description | Destination (Output) Tag | Direct / Reverse Acting | P | I | D |  |  | OK | Date | OK | Date | Comments - Don’t comment in C2 column | Change Date | Change Reference
|  |  |  | PIT22121 | PIC-22121 | 2000-F22-PID-PR-10002 | F22-HE-412 CIL4 Elution Recovery Heat Exchanger Discharge Pressure Indicating Transmitter | CIL4 Elution Press. Ctrl | Automatic | X | X | - | PIT22121 | 230 | 430 | kPa | 0 | 600 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | 200 | 5 | 220 | 5 | 450 | 5 | 490 | 3 |  |  |  |  | A_LL mask: F22PW441 is NOT RUNNING AND F22PW444 IS NOT RUNNING A_Lo mask: F22PW441 is NOT RUNNING AND F22PW444 is NOT RUNNING Enable 10s delay mask on pump start-up | 20 | 100 | 20 | 100 | % Open | CIL4 Elution PCV | F22-PCV-22121 | Direct | TBC | TBC | TBC |  | C
|  |  |  | FIT22165 | FIC-22165 | 2000-F22-PID-PR-10002 | CIL4 Elution Pumps Discharge Flow Indicating Transmitter | CIL4 Elution Flow Ctrl | Automatic | X | X | - | FIT22165 | 60 | 90 | m3/h | 0 | 100 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | 32 | 5 | 50 | 5 | - | - | - | - |  |  |  |  | A_LL mask: F22PW441 is NOT RUNNING AND F22PW444 IS NOT RUNNING A_Lo mask: F22PW441 is NOT RUNNING AND F22PW444 is NOT RUNNING Enable 10s delay mask on pump start-up | 0 | 100 | 0 | 100 | % Speed | CIL4 Elution Pumps | F22-PW-441 VSD OR F22-PW-444 VSD | Reverse | TBC | TBC | TBC | Flow control loop tuning to be slow acting in comparison to PIC-22121 to prevent conflicting control. | 1 | [5 empty] | 2026-02-17 | Typo in Destination VSD
|  |  |  | TIT22228 | TIC-22228 | 2000-F22-PID-PR-10007 | F22-HE-401 Kiln Mercury Abatement Off-Gas Cooler Kiln Off Gas Outlet Temperature Indicating Transmitter | F22HE401 Cooling Ctrl | Automatic | X | X | - | TIT22228 | 0 | 30 | °C | 0 | 50 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 30 | 5 | 35 | 5 |  |  |  |  | - | 0 | 100 | 0 | 100 | % Open | F22HE401 Cooling TCV | F22-TCV-22228 | Direct | TBC | TBC | TBC |  | 0
|  |  |  | FIT22023 | FIC-22023 | 2000-F22-PID-PR-10001 | F22-PW-403 CIL4 Carbon Eductor Pump Flow Indicating Transmitter | F22PW403 Flow | Automatic | X | X | - | FIT22023 | 0 | 100 | m3/h | 0 | 100 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | 40 | 5 | 50 | 5 | - | - | - | - |  |  |  |  | F22PW403 is NOT RUNNING Enable 10s delay mask on pump start-up | 0 | 100 | 0 | 100 | % Speed | CIL4 Carbon Eductor Pump | F22-PW-403 VSD | Reverse | TBC | TBC | TBC |  | 1 | [5 empty] | 2026-04-13 | FC : updated as per PL683
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 3 | 3

## 9. Drives
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION, ELECTROWINNING & GOLD ROOM (AREA F22 & F66)
2000-F22-LST-PR-10101
DRIVE INTERLOCKS AND CONTROL
[15 empty] | Description (Unhealthy Interlocks) |  |  |  | Interlocks | [6 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Name | Drive Type | Speed Min | Speed Max | Speed Units | SP Lower Limit | SP Upper Limit | Current Max | Manual | Auto | Start Condition (Auto Mode) | Stop Condition (Auto Mode) | # |  | Delay On | Delay Off | Start Permissive | Process | Critical | Hardwired to Drive | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date | Comments - Don’t comment in C2 column | Change Date | Change Reference
F22-PS-451 | 2000-F22-PID-PR-10001 | CIL4 Elution Area Sump Pump | DOL | - | - | - | - | - | TBC | X | X | LSH22071 is ACTIVE | LSH22071 INACTIVE for 600 seconds |  | Drive Operation | [9 empty] | 0
[14 empty] | 1 | F22-PS-451 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F22-PS-451 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F22-PS-451 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F22-PS-451 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F22-PS-451 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F22-PS-451 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F22-PS-451 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | XV22072 Closed AND XV22073 Closed | 5 |  |  | X |  |  | X |  | Pump Discharge Valves are Closed | A
F22-PS-452 | 2000-F22-PID-PR-10005 | Regen Kiln Area Sump Pump | DOL | - | - | - | - | - | TBC | X | X | LSH22211 is ACTIVE | LSH22211 INACTIVE for 600 seconds |  | Drive Operation | [9 empty] | 0
[14 empty] | 1 | F22-PS-452 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F22-PS-452 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F22-PS-452 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F22-PS-452 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F22-PS-452 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F22-PS-452 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F22-PS-452 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F22-PS-453 | 2000-F22-PID-PR-10005 | Mercury Abatement Area Sump Pump | DOL | - | - | - | - | - | TBC | X | X | LSH22239 is ACTIVE | LSH22239 INACTIVE for 600 seconds |  | Drive Operation | [9 empty] | C
[14 empty] | 1 | F22-PS-453 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F22-PS-453 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F22-PS-453 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F22-PS-453 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F22-PS-453 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F22-PS-453 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F22-PS-453 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F22-PP-490 | 2000-F22-PID-PR-10005 | CIL4 Barren Carbon Pump | VSD | 0 | 100 | % | 40 | 100 | TBC | X | X | F22-SEQ-0009 | F22-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-06-17 | Updated as per KAN-2050
[14 empty] | 1 | F22-PP-490 Comms Failure | 0 |  |  |  | X |  |  |  |  | 1 | [5 empty] | 2025-06-17 | Updated as per KAN-2051
[14 empty] | 2 | F22-PP-490 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 1 | [5 empty] | 2025-06-17 | Updated as per KAN-2051
[14 empty] | 3 | F22-PP-490 Drive Fault | 0 |  |  |  | X |  |  |  |  | 1 | [5 empty] | 2025-06-17 | Updated as per KAN-2051
[14 empty] | 4 | F22-PP-490 E-Stop | 0 |  |  |  | X | X |  |  |  | 1 | [5 empty] | 2025-06-17 | Updated as per KAN-2051
[14 empty] | 5 | F22-PP-490 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 1 | [5 empty] | 2025-06-17 | Updated as per KAN-2051
[14 empty] | 6 | F22-PP-490 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 1 | [5 empty] | 2025-06-17 | Updated as per KAN-2051
[14 empty] | 7 | F22-PP-490 Drive Ready | 0 |  |  |  | X |  |  |  |  | 1 | [5 empty] | 2025-06-17 | Updated as per KAN-2051
[14 empty] | 8 | SV22260 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve is in auto or open | C
[14 empty] | 8 | FSL22261 is INACTIVE AND F22-PP-490 RUNNING | 600 |  |  | X |  |  | X |  | Low Gland Water Flow | 1 | [5 empty] | 2025-06-17 | Updated as per KAN-2051 FSL polarity changed (inactive)
[14 empty] | 9 | XV22194 Closed | 3 |  |  | X |  |  | X |  | Suction Valve is Closed | A
[14 empty] | 11 | F21-SC-420 is NOT RUNNING | 10 |  |  | X |  |  | X |  | CIL4 Carbon Sizing Screen is Not Running | A
F22-PW-403 | 2000-F22-PID-PR-10001 | CIL4 Carbon Eductor Pump | VSD | 0 | 100 | % | 40 | 100 | TBC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-06-17 | Updated as per KAN-2050
[14 empty] | 1 | F22-PW-403 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F22-PW-403 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F22-PW-403 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F22-PW-403 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F22-PW-403 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F22-PW-403 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F22-PW-403 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | XV22021 Closed | 3 |  |  | X |  |  | X |  | Suction Valve is Closed | A
[14 empty] | 9 | FIC22023 ≤ A_LL AND F22-PW-403 RUNNING | 300 |  |  | X |  |  | X |  | CIL4 Carbon Eductor Pump Flow is Low-Low | 0
[14 empty] | 10 | LI22152 ≤ A_LL | 300 |  |  | X |  |  | X |  | CIL4 Elution Water Tank Level is Low-Low | A
F22-PW-441 | 2000-F22-PID-PR-10002 | CIL4 Elution Pump 1 | VSD | 0 | 100 | % | 40 | 100 | TBC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES |  | Drive Operation | [9 empty] | A
[14 empty] | 1 | F22-PW-441 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F22-PW-441 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F22-PW-441 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F22-PW-441 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F22-PW-441 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F22-PW-441 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F22-PW-441 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | XV22161 Closed | 0 |  |  | X |  |  | X |  | Suction Valve is Closed | A
[14 empty] | 9 | XV22162 Closed | 0 |  |  | X |  |  | X |  | Discharge Valve is Closed | A
[14 empty] | 10 | XV22030 Closed | 0 |  |  | X |  |  | X |  | CIL4 Elution & Acid Wash Column Eluate Inlet Valve is Closed | B
[14 empty] | 11 | PI22015 ≥ A_HH | 3 |  |  | X |  |  | X |  | High High CIL4 Elution & Acid Wash Column Pressure | C
[14 empty] | 12 | PI22166 ≥ A_HH | 1 |  |  | X |  |  | X |  | High High CIL4 Elution Pump Discharge Pressure | C
[14 empty] | 13 | FI22165 ≤ A_LL AND F22-PW-441 RUNNING | 300 |  |  | X |  |  | X |  | Discharge Flow is Low-Low | C
[14 empty] | 14 | F22PW444 RUNNING | 3 |  |  | X |  |  | X |  | CIL4 Elution Pump 2 Running | 1 | [5 empty] | 2025-07-25 | Updated as per KAN-2146
F22-PW-444 | 2000-F22-PID-PR-10002 | CIL4 Elution Pump 2 | VSD | 0 | 100 | % | 40 | 100 | TBC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES |  | Drive Operation | [9 empty] | A
[14 empty] | 1 | F22-PW-444 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F22-PW-444 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F22-PW-444 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F22-PW-444 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F22-PW-444 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F22-PW-444 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F22-PW-444 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | XV22163 Closed | 0 |  |  | X |  |  | X |  | Suction Valve is Closed | A
[14 empty] | 9 | XV22164 Closed | 0 |  |  | X |  |  | X |  | Discharge Valve is Closed | A
[14 empty] | 10 | XV22030 Closed | 0 |  |  | X |  |  | X |  | CIL4 Elution & Acid Wash Column Eluate Inlet Valve is Closed | B
[14 empty] | 11 | PI22015 ≥ A_HH | 3 |  |  | X |  |  | X |  | CIL4 Elution & Acid Wash Column Pressure | 0
[14 empty] | 12 | PI22166 ≥ A_HH | 1 |  |  | X |  |  | X |  | High High CIL4 Elution Pump Discharge Pressure | 0
[14 empty] | 13 | FI22165 ≤ A_LL AND F22-PW-444 RUNNING | 300 |  |  | X |  |  | X |  | Discharge Flow is Low-Low | C
[14 empty] | 14 | F22PW441 RUNNING | 3 |  |  | X |  |  | X |  | CIL4 Elution Pump 1 Running | 1 | [5 empty] | 2025-07-25 | Updated as per KAN-2146
F22-SC-421 | 2000-F21-PID-PR-10002 | CIL4 Loaded Carbon Screen | DOL | - | - | - | - | - | TBC | X | X | F21-SEQ-0003 | F21-SEQ-0003 |  | Drive Operation | [9 empty] | A
[14 empty] | 1 | F22-SC-421 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F22-SC-421 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F22-SC-421 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F22-SC-421 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F22-SC-421 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F22-SC-421 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F22-SC-421 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | XS24673A Inactive | 0 |  |  |  | X |  |  |  | Linear heat detector alarm activated through F22-FIP-401 Refer to F24-LST-PR-10001 for the fire alam system details. | 1 | [5 empty] | 2025-08-06 | state was incorrectly set as active. Inverted. Interlock is part of NOVD142 & CR-013
F22-SC-423 | 2000-F22-PID-PR-10005 | CIL4 Regen Kiln Dewatering Screen | DOL | - | - | - | - | - | TBC | X | X | F22-SEQ-0008 | F22-SEQ-0008 |  | Drive Operation | [9 empty] | A
[14 empty] | 1 | F22-SC-423 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F22-SC-423 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F22-SC-423 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F22-SC-423 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F22-SC-423 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F22-SC-423 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F22-SC-423 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F22-HT-411 | 2000-F22-PID-PR-10002 | CIL4 Elution Heater | PLC | - | - | - | - | - | - | - | - | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES |  | Drive Operation | [9 empty] | 0
[14 empty] | 1 | F22-HT-411 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 1 | [5 empty] | 6/5/26 Updated as per PL-733
[14 empty] | 2 | F22-HT-411 Drive Fault | 0 |  |  |  | X |  |  |  | Hardwired Signal XA22114 | 1 | [5 empty] | 6/5/26 Updated as per PL-733
[14 empty] | 3 | F22-HT-411 Drive Ready | 0 |  |  |  | X |  |  |  | Hardwired Signal XS22119 | 1 | [5 empty] | 6/5/26 Updated as per PL-733
[14 empty] | 4 | F22-PW-441 is NOT RUNNING AND F22-PW-444 is NOT RUNNING | 3 |  |  | X |  |  | X |  | Deactivate HS22116 - CIL4 Elution Pumps are not running | 0
[14 empty] | 5 | PSL24671 Inactive | 3 |  |  | X |  |  | X |  | Deactivate HS22116 - Fire check valve alarm activated. 3 seconds damper applied to prevent trip due to thermal expansion Refer to F24-LST-PR-10001 for the fire alam system details. | 1 | [5 empty] | 2026-04-13 | updated to be inactive as per PL-688
[14 empty] | 6 | F22-PP-460 is NOT RUNNING | 0 |  |  | X |  |  | X |  | Deactivate HS22116 - CIL4 Elution Heater Thermal Oil Pump is not running | 0
F22-PP-460 | 2000-F22-PID-PR-10002 | CIL4 Elution Heater Thermal Oil Pump | DOL | - | - | - | - | - | TBC | X | X | MULTIPLE SEQUENCES | MULTIPLE SEQUENCES |  | Drive Operation | [9 empty] | A
[14 empty] | 1 | F22-PP-460 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F22-PP-460 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F22-PP-460 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F22-PP-460 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F22-PP-460 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F22-PP-460 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F22-PP-460 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | PSL24671 Inactive | 3 |  |  | X |  |  | X |  | Fire check valve alarm activated. 3 seconds damper applied to prevent trip due to thermal expansion Refer to F24-LST-PR-10001 for the fire alam system details. | 1 | [5 empty] | 2026-04-13 | updated to be inactive as per PL-688
F22-KN-411 | 2000-F22-PID-PR-10005 | CIL4 Carbon Regeneration Kiln Package | PLC | - | - | - | - | - | - | - | - |  |  |  | Drive Operation | [9 empty] | 0
[14 empty] | 1 | TIC22228 > A_HH | 60 |  |  | X |  |  | X |  | Initiate remote stop (XS22293) and prevent start (XS22292) until cleared | 0
[14 empty] | 2 | TI22243 > A_Hi | 600 |  |  | X |  |  | X |  | Initiate remote stop (XS22293) and prevent start (XS22292) until cleared | 0
[14 empty] | 3 | TI22235 > A_HH | 300 |  |  | X |  |  | X |  | Initiate remote stop (XS22293) and prevent start (XS22292) until cleared | 0
[14 empty] | 4 | TDI22240 < A_Lo AND XS22292 Active | 120 |  |  | X |  |  | X |  | Initiate remote stop (XS22293) and prevent start (XS22292) until cleared | 1 | [5 empty] | 2025-05-13 | Updated as per HAZOP 02/05/2025
[14 empty] | 5 | F22-FN-401 is NOT RUNNING | 3 |  |  | X |  |  | X |  | Initiate remote stop (XS22293) and prevent start (XS22292) until cleared | 0
F22-KN-411A | - | CIL4 Carbon Regeneration Kiln Heater Z11 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411A Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411A Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411A Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411A E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411A MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411A Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411A Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411B | - | CIL4 Carbon Regeneration Kiln Heater Z12 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411B Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411B Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411B Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411B E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411B MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411B Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411B Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411C | - | CIL4 Carbon Regeneration Kiln Heater Z13 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411C Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411C Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411C Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411C E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411C MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411C Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411C Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411D | - | CIL4 Carbon Regeneration Kiln Heater Z14 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411D Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411D Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411D Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411D E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411D MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411D Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411D Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411E | - | CIL4 Carbon Regeneration Kiln Heater Z15 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411E Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411E Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411E Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411E E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411E MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411E Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411E Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411F | - | CIL4 Carbon Regeneration Kiln Heater Z16 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411F Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411F Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411F Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411F E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411F MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411F Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411F Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411G | - | CIL4 Carbon Regeneration Kiln Heater Z17 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411G Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411G Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411G Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411G E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411G MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411G Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411G Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411H | - | CIL4 Carbon Regeneration Kiln Heater Z18 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411H Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411H Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411H Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411H E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411H MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411H Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411H Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411I | - | CIL4 Carbon Regeneration Kiln Heater Z21 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411I Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411I Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411I Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411I E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411I MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411I Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411I Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411J | - | CIL4 Carbon Regeneration Kiln Heater Z22 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411J Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411J Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411J Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411J E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411J MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411J Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411J Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411K | - | CIL4 Carbon Regeneration Kiln Heater Z23 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411K Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411K Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411K Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411K E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411K MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411K Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411K Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411L | - | CIL4 Carbon Regeneration Kiln Heater Z24 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411L Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411L Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411L Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411L E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411L MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411L Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411L Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411M | - | CIL4 Carbon Regeneration Kiln Heater Z25 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411M Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411M Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411M Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411M E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411M MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411M Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411M Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411N | - | CIL4 Carbon Regeneration Kiln Heater Z26 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411N Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411N Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411N Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411N E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411N MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411N Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411N Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411O | - | CIL4 Carbon Regeneration Kiln Heater Z31 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411O Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411O Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411O Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411O E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411O MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411O Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411O Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411P | - | CIL4 Carbon Regeneration Kiln Heater Z32 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411P Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411P Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411P Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411P E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411P MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411P Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411P Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-KN-411Q | - | CIL4 Carbon Regeneration Kiln Heater Z33 | [12 empty] | Drive Operation | [8 empty] | Local mode control only | 0 | bar: DOL to X
[14 empty] | 1 | F22-KN-411Q Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F22-KN-411Q Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F22-KN-411Q Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F22-KN-411Q E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F22-KN-411Q MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F22-KN-411Q Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F22-KN-411Q Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F22-CU-406 | 2000-F22-PID-PR-10007 | Kiln Mercury Abatement Chiller | FE | - | - | - | - | - | TBC | X | X |  |  |  | Drive Operation | [9 empty] | A
[14 empty] | 1 | F22-CU-406 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F22-CU-406 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F22-CU-406 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F22-CU-406 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F22-CU-406 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F22-CU-406 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F22-CU-406 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F22-PW-591 | 2000-F22-PID-PR-10008 | Kiln Abatement System Cooling Water Pump 1 | DOL | - | - | - | - | - | TBC | X | X |  |  |  | Drive Operation | [9 empty] | B
[14 empty] | 1 | F22-PW-591 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F22-PW-591 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F22-PW-591 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F22-PW-591 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F22-PW-591 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F22-PW-591 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F22-PW-591 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | HV22244 Closed | 3 |  |  | X |  |  | X |  | Suction Valve is Closed | 1 | [5 empty] | 2026-02-17 | XV changed to HV
[14 empty] | 9 | HV22245 Closed | 3 |  |  | X |  |  | X |  | Discharge Valve is Closed | 1 | [5 empty] | 2026-02-17 | XV changed to HV
[14 empty] | 10 | LI22242 ≤ A_LL | 300 |  |  | X |  |  | X |  | Kiln Abatement System Cooling Water Tank Level Low-Low | B
[14 empty] | 11 | FSL22248 is ACTIVE | 300 |  |  | X |  |  | X |  | Low Discharge Flow | 0
F22-PW-592 | 2000-F22-PID-PR-10008 | Kiln Abatement System Cooling Water Pump 2 | DOL | - | - | - | - | - | TBC | X | X |  |  |  | Drive Operation | [9 empty] | B
[14 empty] | 1 | F22-PW-592 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F22-PW-592 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F22-PW-592 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F22-PW-592 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F22-PW-592 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F22-PW-592 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F22-PW-592 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | HV22246 Closed | 3 |  |  | X |  |  | X |  | Suction Valve is Closed | 1 | [5 empty] | 2026-02-17 | XV changed to HV
[14 empty] | 9 | HV22247 Closed | 3 |  |  | X |  |  | X |  | Discharge Valve is Closed | 1 | [5 empty] | 2026-02-17 | XV changed to HV
[14 empty] | 10 | LI22242 ≤ A_LL | 300 |  |  | X |  |  | X |  | Kiln Abatement System Cooling Water Tank Level Low-Low | B
[14 empty] | 11 | FSL22248 is ACTIVE | 300 |  |  | X |  |  | X |  | Low Discharge Flow | 0
F22-FN-401 | 2000-F22-PID-PR-10007 | Kiln Mercury Abatement Exhaust Fan | DOL | - | - | - | - | - | TBC | X | X | F22FN401_ES |  |  | Drive Operation | [8 empty] | Refer to Misc tab for function on F22_E_POWER | 1 | [5 empty] | 2025-07-29 | Updated as per 2000-F00-TQY-PR-10537
[14 empty] | 1 | F22-FN-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F22-FN-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F22-FN-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F22-FN-401 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F22-FN-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F22-FN-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F22-FN-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F66-PW-461 | 2000-F66-PID-PR-10001 | CIL4 Electrowinning Pump 1 | DOL | - | - | - | - | - | TBC | X | X | F22-SEQ-0010 | F22-SEQ-0010 |  | Drive Operation | [9 empty] | A
[14 empty] | 1 | F66-PP-461 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F66-PP-461 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F66-PP-461 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F66-PP-461 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F66-PP-461 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F66-PP-461 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F66-PP-461 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | FI66406 ≤ A_LL AND F66-PP-461 RUNNING AND XV66415 NOT CLOSED | 300 |  |  | X |  |  | X |  | Discharge Flow is Low | 1
[14 empty] | 9 | FI66419 ≤ A_LL AND F66-PP-461 RUNNING AND XV66416 NOT CLOSED | 300 |  |  | X |  |  | X |  | Discharge Flow is Low | 1
[14 empty] | 10 | XV66415 Closed AND XV66416 Closed | 3 |  |  | X |  |  | X |  | Pump Discharge Valves are Closed | A
F66-PW-462 | 2000-F66-PID-PR-10001 | CIL4 Electrowinning Pump 2 | DOL | - | - | - | - | - | TBC | X | X | F22-SEQ-0011 | F22-SEQ-0011 |  | Drive Operation | [9 empty] | A
[14 empty] | 1 | F66-PP-462 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F66-PP-462 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F66-PP-462 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F66-PP-462 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F66-PP-462 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F66-PP-462 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F66-PP-462 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | FI66406 ≤ A_LL AND F66-PP-462 RUNNING AND XV66417 NOT CLOSED | 300 |  |  | X |  |  | X |  | Discharge Flow is Low | 1
[14 empty] | 9 | FI66419 ≤ A_LL AND F66-PP-462 RUNNING AND XV66418 NOT CLOSED | 300 |  |  | X |  |  | X |  | Discharge Flow is Low | 1
[14 empty] | 9 | XV66417 Closed AND XV66418 Closed | 3 |  |  | X |  |  | X |  | Pump Discharge Valves are Closed | A
F66-ER-411A | 2000-F66-PID-PR-10002 | CIL4 Electrowinning Cell 1 Rectifier 1 | FE | - | - | - | - | - | TBC | X | X | F22-SEQ-0010 & 0011 | F22-SEQ-0010 & 0011 | 1 | F66-ER-411A Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F66-ER-411A Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F66-ER-411A Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F66-ER-411A E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F66-ER-411A MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F66-ER-411A Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F66-ER-411A Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | II66444 ≥ A_HH | 3 |  |  | X |  |  | X |  | Rectifier maximum current | A
[14 empty] | 9 | F66-PW-461 is NOT RUNNGING AND F66-PW-462 is NOT RUNNING | 3 |  |  | X |  |  | X |  | CIL4 Electrowinning Pumps not running | 0
[14 empty] | 10 | XI66444 ≥ A_HH | 3 |  |  | X |  |  | X |  | Rectifier maximum voltage | A
F66-ER-411B | 2000-F66-PID-PR-10002 | CIL4 Electrowinning Cell 1 Rectifier 2 | FE | - | - | - | - | - | TBC | X | X | F22-SEQ-0010 & 0011 | F22-SEQ-0010 & 0011 | 1 | F66-ER-411B Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F66-ER-411B Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F66-ER-411B Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F66-ER-411B E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F66-ER-411B MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F66-ER-411B Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F66-ER-411B Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | II66445 ≥ A_HH | 3 |  |  | X |  |  | X |  | Rectifier maximum current | A
[14 empty] | 9 | F66-PW-461 is NOT RUNNGING AND F66-PW-462 is NOT RUNNING | 3 |  |  | X |  |  | X |  | CIL4 Electrowinning Pumps not running | 0
[14 empty] | 10 | XI66445 ≥ A_HH | 3 |  |  | X |  |  | X |  | Rectifier maximum voltage | A
F66-ER-411A | 2000-F66-PID-PR-10002 | CIL4 Electrowinning Cell 2 Rectifier 1 | FE | - | - | - | - | - | TBC | X | X | F22-SEQ-0010 & 0011 | F22-SEQ-0010 & 0011 | 1 | F66-ER-412A Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F66-ER-412A Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F66-ER-412A Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F66-ER-412A E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F66-ER-412A MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F66-ER-412A Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F66-ER-412A Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | II66446 ≥ A_HH | 3 |  |  | X |  |  | X |  | Rectifier maximum current | A
[14 empty] | 9 | F66-PW-461 is NOT RUNNGING AND F66-PW-462 is NOT RUNNING | 3 |  |  | X |  |  | X |  | CIL4 Electrowinning Pumps not running | 0
[14 empty] | 10 | XI66446 ≥ A_HH | 3 |  |  | X |  |  | X |  | Rectifier maximum voltage | A
F66-ER-411B | 2000-F66-PID-PR-10002 | CIL4 Electrowinning Cell 2 Rectifier 2 | FE | - | - | - | - | - | TBC | X | X | F22-SEQ-0010 & 0011 | F22-SEQ-0010 & 0011 | 1 | F66-ER-412B Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F66-ER-412B Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F66-ER-412B Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F66-ER-412B E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F66-ER-412B MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F66-ER-412B Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F66-ER-412B Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | II66447 ≥ A_HH | 3 |  |  | X |  |  | X |  | Rectifier maximum current | A
[14 empty] | 9 | F66-PW-461 is NOT RUNNGING AND F66-PW-462 is NOT RUNNING | 3 |  |  | X |  |  | X |  | CIL4 Electrowinning Pumps not running | 0
[14 empty] | 10 | XI66447 ≥ A_HH | 3 |  |  | X |  |  | X |  | Rectifier maximum voltage | A
39
Notes:
1. "VSD UNHEALTHY" encompasses the following conditions: VSD Modbus Comms Not Healthy, General fault, Main Circuit Breaker Not Closed and Drive Circuit Breaker Not Closed.
2. "DOL UNHEALTHY" encompasses the following conditions: DOL Modbus Comms Not Healthy, General Fault, Main Circuit Breaker Not Closed and Drive Circuit Breaker Not Closed

## 10. Sequence
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION, ELECTROWINNING & GOLD ROOM (AREA F22 & F66)
2000-F22-LST-PR-10101
SEQUENCES
Seq No. | Seq Description | Step | Action | Tag / Item | Description | Next Step Delay (s) | Step Advance Condition | Comments | Rev | Equipment Permissives | Recovery Seq. No if Step Faults
PLEASE REFER TO SEQUENCE FLOWCHART DELIVERABLE DOCUMENTS
0

## 11. Calculation
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION, ELECTROWINNING & GOLD ROOM (AREA F22 & F66)
2000-F22-LST-PR-10101
CALCULATIONS
|  |  | Unit | Inputs |  |  |  | Operator Input | Calc. Value | Manual Input | [5 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Description (Software Tag Only) |  | # | Tag | Unit | Description |  |  | Nom | Min | Max | Calculation | Comments | Rev | OK | Date | OK | Date | Comments - Don’t comment in C2 column | Change Date | Change Reference
F22-CALC-0001 | 2000-F22-PID-PR-10002 | F22HE412 DP1 | kPa | 1 | PI22081.PV | kPa | F22HE412 Heater Hot Side In Pressure | [5 empty] | PDI22081 = ¦ PI22081.PV - PIC22121.PV ¦ |  | 0
|  |  |  | 2 | PIC22121.PV | kPa | F22HE412 Heater Hot Side Out Pressure | [7 empty] | 0
|  |  |  | 3 | PDI22081 | kPa | F22HE412 Hot Side Differential Pressure |  | X | [5 empty] | 0
F22-CALC-0002 | 2000-F22-PID-PR-10002 | F22HE412 DP2 | kPa | 1 | PI22166.PV | kPa | F22HE412 Heater Cold Side In Pressure | [5 empty] | PDI22166 = ¦ PI22166.PV - PI22098.PV ¦ |  | 0
|  |  |  | 2 | PI22098.PV | kPa | F22HE412 Heater Cold Side Out Pressure | [7 empty] | 0
|  |  |  | 3 | PDI22166 | kPa | F22HE412 Cold Side Differential Pressure |  | X | [5 empty] | 0
F22-CALC-0003 | 2000-F22-PID-PR-10002 | F22HE411 DP1 | kPa | 1 | PI22098.PV | kPa | F22HE411 Cold Side In Pressure | [5 empty] | PDI22098 = ¦ PI22098.PV - PI22171.PV ¦ |  | 0
|  |  |  | 2 | PI22171.PV | kPa | F22HE411 Cold Side Out Pressure | [7 empty] | 0
|  |  |  | 3 | PDI22098 | kPa | F22HE411 Cold Side Differential Pressure |  | X | [5 empty] | 0
F22-CALC-0004 | 2000-F22-PID-PR-10007 | F22HT401 Diff. T | ° C | 1 | TDI22240 | ° C | F22HT401 Temperature Differential |  | X |  |  |  | TDI22240 = TI22240.PV - TI22235.PV |  | 1 | [5 empty] | 2025-05-02 | Updated as per HAZOP 02/05/2025
|  |  |  | 2 | TI22235.PV | ° C | F22TK421 Outlet Temperature | [7 empty] | 1 | [5 empty] | 2025-05-02 | Updated as per HAZOP 02/05/2025
|  |  |  | 3 | TI22240.PV | ° C | F22HT401 Outlet Temperature | [7 empty] | 1 | [5 empty] | 2025-05-02 | Updated as per HAZOP 02/05/2025
F22-CALC-0005 | 2000-F22-PID-PR-10007 | F22-TK-420 Diff. P | kPa | 1 | PDI22225 | kPa | F22TK420 Pressure Differential |  | X |  |  |  | PDI22225 = PI22225.PV - PI22227.PV |  | 1 | [5 empty] | 2025-05-02 | Updated as per HAZOP 02/05/2025
|  |  |  | 2 | PI22225.PV | kPa | F22TK420 Inlet Pressure | [7 empty] | 1 | [5 empty] | 2025-05-02 | Updated as per HAZOP 02/05/2025
|  |  |  | 3 | PI22227.PV | kPa | F22TK420 Outlet Pressure | [7 empty] | 1 | [5 empty] | 2025-05-02 | Updated as per HAZOP 02/05/2025
F22-CALC-0006 | 2000-F22-PID-PR-10007 | F22-TK-421 Diff. P | kPa | 1 | PDI22229 | kPa | F22TK421 Pressure Differential |  | X |  |  |  | PDI22229 = PI22229.PV - PI22236.PV |  | 1 | [5 empty] | 2025-05-02 | Updated as per HAZOP 02/05/2025
|  |  |  | 2 | PI22229.PV | kPa | F22TK421 Inlet Pressure | [7 empty] | 1 | [5 empty] | 2025-05-02 | Updated as per HAZOP 02/05/2025
|  |  |  | 3 | PI22236.PV | kPa | F22TK421 Outlet Pressure | [7 empty] | 1 | [5 empty] | 2025-05-02 | Updated as per HAZOP 02/05/2025
F22-CALC-0007 | 2000-F22-PID-PR-10007 | F22-TK-422 Diff. P | kPa | 1 | PDI22236 | kPa | F22TK422 Pressure Differential |  | X |  |  |  | PDI22236 = PI22236.PV - PI22238.PV |  | 1 | [5 empty] | 2025-05-02 | Updated as per HAZOP 02/05/2025
|  |  |  | 2 | PI22236.PV | kPa | F22TK422 Inlet Pressure | [7 empty] | 1 | [5 empty] | 2025-05-02 | Updated as per HAZOP 02/05/2025
|  |  |  | 3 | PI22238.PV | kPa | F22TK422 Outlet Pressure | [7 empty] | 1 | [5 empty] | 2025-05-02 | Updated as per HAZOP 02/05/2025
7 | 7

## 12. Misc
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION, ELECTROWINNING & GOLD ROOM (AREA F22 & F66)
2000-F22-LST-PR-10101
MISC. INSTRUMENTS AND CONTROLLERS
[11 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Description | Normal State | Alarm State | Hardwired (y/n) | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date | Comments - Don’t comment in C2 column | Change Date | Change Reference
HS22165 | 2000-F22-PID-PR-10002 | Elution Pump Duty Select | Operator Selection |  | N |  |  |  | Selector of duty pump to be controlled by FIC-22165 Faceplate Selection: • F21-PW-441 OR • F22-PW-444 | 1 | [5 empty] | 2025-07-23 | Updated as per KAN-2146
F22FN401_ES | - | F22FN401 Emergency Start | Logic |  | N |  |  |  | if F22-GE-131 = running and If F22SW131Q2CL = active: pulse F22FN401 to auto and pulse F22FN401 start | 1 | [5 empty] | 30/07/2025 2/10/2025 | New addition based on 2000-F00-TQY-PR-10537_1 Updated CR-010
1

## 13. Alarm Database
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CIL4 CARBON TREATMENT, ELUTION, ELECTROWINNING & GOLD ROOM (AREA F22 & F66)
2000-F22-LST-PR-10101
ALARM DATABASE
[14 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Abbreviated Description (Faceplate) | Type | Alarm State | Alarm Value | Alarm Units | On Delay (sec) | Alarm Masking Condition | Impact | Urgency | Priority | Operator Response | Rev | OK | Date | OK | Date | Comments - Don’t comment in C2 column | Change Date | Change Reference
TI22013 | 2000-F22-PID-PR-10001 | F22PR411 Top | Analogue | A_Hi | 150 | °C | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate the elution circuit | C
TI22013 | 2000-F22-PID-PR-10001 | F22PR411 Top of Column | Analogue | A_HH | 160 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate the elution circuit | C
FIC22023 | 2000-F22-PID-PR-10001 | F22PW403 Flow | Analogue | A_Lo | 50 | % | 5 | F22PW403 is NOT RUNNING Enable 10s delay mask on pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate F22-PW-403 | 1
LI22140 | 2000-F22-PID-PR-10001 | F22HP445 Lvl | Analogue | A_HH | 95 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate F22-HP-445 | 0
PI22015 | 2000-F22-PID-PR-10001 | F22PR411 Top of Column | Analogue | A_Hi | 450 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate elution circuit for obstruction. Potential blockage in elution filters | C
PI22015 | 2000-F22-PID-PR-10001 | F22PR411 Top of Column | Analogue | A_HH | 490 | kPa | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate elution circuit for obstruction. Potential blockage in elution filters | C
FI22025 | 2000-F22-PID-PR-10001 | F22PR411 HCl Flow | Analogue | A_Lo | 2 | m3/h | 10 | F72PP424 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | C
FI22025 | 2000-F22-PID-PR-10001 | F22PR411 HCl Flow | Analogue | A_Hi | 0.1 | m3/h | 3 | XV22024 is Open | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to check XV22024 for leaks/failure | 0
PDI22049 | 2000-F22-PID-PR-10001 | F22FI411 DP | Analogue | A_Hi | 60 | kPa | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to check filter/strainer for debris | 0
PDI22050 | 2000-F22-PID-PR-10001 | F22FI412 DP | Analogue | A_Hi | 60 | kPa | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to check filter/strainer for debris | 0
TI22031 | 2000-F22-PID-PR-10001 | F22PR411 Column Bottom | Analogue | A_Hi | 150 | °C | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate the elution circuit | C
TI22031 | 2000-F22-PID-PR-10001 | F22PR411 Column Bottom | Analogue | A_HH | 160 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate the elution circuit | C
PIC22121 | 2000-F22-PID-PR-10002 | F22HE412 Hot-Side Out | Analogue | A_LL | 200 | kPa | 5 | F22PW441 is NOT RUNNING AND F22PW444 is NOT RUNNING | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate elution heater circuit. Potential loss of containment. | A
PIC22121 | 2000-F22-PID-PR-10002 | F22HE412 Hot-Side Out | Analogue | A_Lo | 220 | kPa | 5 | F22PW441 is NOT RUNNING AND F22PW444 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate elution heater circuit | A
PIC22121 | 2000-F22-PID-PR-10002 | F22HE412 Hot-Side Out | Analogue | A_Hi | 450 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate elution heater circuit | A
PIC22121 | 2000-F22-PID-PR-10002 | F22HE412 Hot-Side Out | Analogue | A_HH | 490 | kPa | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate elution heater circuit. Potential blockage. | A
TI22122 | 2000-F22-PID-PR-10002 | F22HE412 Hot-Side Out | Analogue | A_Hi | 85 | °C | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | A
TI22122 | 2000-F22-PID-PR-10002 | F22HE412 Hot-Side Out | Analogue | A_HH | 95 | °C | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate. Solution at risk of flashing at high temperatures | A
LI22143 | 2000-F22-PID-PR-10002 | F22TK442 Level | Analogue | A_LL | 5 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
LI22143 | 2000-F22-PID-PR-10002 | F22TK442 Level | Analogue | A_Lo | 10 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | A
LI22143 | 2000-F22-PID-PR-10002 | F22TK442 Level | Analogue | A_Hi | 90 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | A
LI22143 | 2000-F22-PID-PR-10002 | F22TK442 Level | Analogue | A_HH | 97 | % | 5 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Operator to investigate | C
LI22152 | 2000-F22-PID-PR-10002 | F22TK441 Level | Analogue | A_LL | 5 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
LI22152 | 2000-F22-PID-PR-10002 | F22TK441 Level | Analogue | A_Lo | 10 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | A
LI22152 | 2000-F22-PID-PR-10002 | F22TK441 Level | Analogue | A_Hi | 92 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | C
LI22152 | 2000-F22-PID-PR-10002 | F22TK441 Level | Analogue | A_HH | 95 | % | 5 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Operator to investigate | A
FIC22165 | 2000-F22-PID-PR-10002 | CIL4 Elution Flow | Analogue | A_Lo | 50 | m3/h | 5 | F22PW441 is NOT RUNNING AND F22PW444 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | A
FIC22165 | 2000-F22-PID-PR-10002 | CIL4 Elution Flow | Analogue | A_LL | 32 | m3/h | 5 | F22PW441 is NOT RUNNING AND F22PW444 is NOT RUNNING | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate. Potential loss of containment or flashing of eluate solution. | A
PI22166 | 2000-F22-PID-PR-10002 | F22HE412 Cold -Side In | Analogue | A_LL | 180 | kPa | 5 | F22PW441 is NOT RUNNING AND F22PW444 is NOT RUNNING | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate elution heater circuit. Potential loss of containment. | C
PI22166 | 2000-F22-PID-PR-10002 | F22HE412 Cold -Side In | Analogue | A_Lo | 200 | kPa | 5 | F22PW441 is NOT RUNNING AND F22PW444 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate elution heater circuit | C
PI22166 | 2000-F22-PID-PR-10002 | F22HE412 Cold -Side In | Analogue | A_Hi | 750 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate elution heater circuit | C
PI22166 | 2000-F22-PID-PR-10002 | F22HE412 Cold -Side In | Analogue | A_HH | 800 | kPa | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate elution heater circuit. Potential blockage. | C
PI22171 | 2000-F22-PID-PR-10002 | F22HE411 Cold-Side In | Analogue | A_LL | 180 | kPa | 5 | F22PW441 is NOT RUNNING AND F22PW444 is NOT RUNNING | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate elution heater circuit. Potential loss of containment. | C
PI22171 | 2000-F22-PID-PR-10002 | F22HE411 Cold-Side In | Analogue | A_Lo | 200 | kPa | 5 | F22PW441 is NOT RUNNING AND F22PW444 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate elution heater circuit | C
PI22171 | 2000-F22-PID-PR-10002 | F22HE411 Cold-Side In | Analogue | A_Hi | 750 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate elution heater circuit | C
PI22171 | 2000-F22-PID-PR-10002 | F22HE411 Cold-Side In | Analogue | A_HH | 800 | kPa | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate elution heater circuit. Potential blockage. | C
FI22182 | 2000-F22-PID-PR-10002 | CIL4 Elution CN Flow | Analogue | A_Lo | 2 | m3/h | 10 | (F72PP675 is NOT RUNNING AND F72PP676 is NOT RUNNING) OR ZSC22181 is ACTIVE | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate Cyanide delivery circuit to CIL4 Elution Pumps | C
FI22192 | 2000-F22-PID-PR-10002 | CIL4 Elution NaOH Flow | Analogue | A_Lo | 1 | m3/h | 10 | (F72PP673 is NOT RUNNING AND F72PP674 is NOT RUNNING) OR ZSC22191 is ACTIVE | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate Caustic delivery circuit to CIL4 Elution Pumps | C
PDI22081 | 2000-F22-PID-PR-10002 | F22HE412 DP1 | Analogue | A_Hi | 20 | kPa | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to observe heat exchangers, possible internal inspection required | 0
PDI22166 | 2000-F22-PID-PR-10002 | F22HE412 DP2 | Analogue | A_Hi | 20 | kPa | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to observe heat exchangers, possible internal inspection required | 0
PDI22098 | 2000-F22-PID-PR-10002 | F22HE411 DP1 | Analogue | A_Hi | 20 | kPa | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to observe heat exchangers, possible internal inspection required | 0
LI22189 | 2000-F22-PID-PR-10005 | F22HP431 Level | Analogue | A_Lo | 10 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging | No action required | C
LI22189 | 2000-F22-PID-PR-10005 | F22HP431 Level | Analogue | A_Hi | 90 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Vessel approaching high-high level. Operator to investigate instrument reading is accurate | C
LI22189 | 2000-F22-PID-PR-10005 | F22HP431 Level | Analogue | A_HH | 95 | % | 5 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Filling of vessel to be stopper. Operator to investigate instrument reading is accurate | C
FI22196 | 2000-F22-PID-PR-10005 | F22PP490 Suction | Analogue | A_Lo | 30 | m3/h | 5 | A_Lo Mask: F24PP406 is NOT RUNNING AND F24PP407 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to inspect CIL4 Barren Carbon Pump | 0
FI22196 | 2000-F22-PID-PR-10005 | F22PP490 Suction | Analogue | A_Hi | 80 | m3/h | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to inspect CIL4 Barren Carbon Pump | 0
PI22195 | 2000-F22-PID-PR-10005 | F22PP490 Suction | Analogue | A_Lo | 50 | kPa | 5 | A_Lo Mask: F24PP406 is NOT RUNNING AND F24PP407 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate raw water line to the CIL4 Barren Carbon Pump | C
PI22195 | 2000-F22-PID-PR-10005 | F22PP490 Suction | Analogue | A_Hi | 200 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate raw water line to the CIL4 Barren Carbon Pump | C
TI22234 | 2000-F22-PID-PR-10007 | F22HE401 Cooling Return | Analogue | A_Hi | 25 | °C | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
TI22234 | 2000-F22-PID-PR-10007 | F22HE401 Cooling Return | Analogue | A_HH | 30 | °C | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate mercury abatement chiller. Consider stopping kiln operation if temperatures do not fall | A
TI22224 | 2000-F22-PID-PR-10007 | F22TK420 Exhaust Inlet | Analogue | A_Hi | 220 | °C | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
TI22224 | 2000-F22-PID-PR-10007 | F22TK420 Exhaust Inlet | Analogue | A_HH | 230 | °C | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate. Consider stopping kiln operation if temperatures do not fall | A
PI22225 | 2000-F22-PID-PR-10007 | F22TK420 Exhaust Inlet | Analogue | A_Hi | 0.5 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
PI22225 | 2000-F22-PID-PR-10007 | F22TK420 Exhaust Inlet | Analogue | A_HH | 1 | kPa | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate. Consider stopping kiln operation if pressure remains high | A
TI22226 | 2000-F22-PID-PR-10007 | F22TK420 Exhaust Outlet | Analogue | A_Hi | 105 | °C | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
TI22226 | 2000-F22-PID-PR-10007 | F22TK420 Exhaust Outlet | Analogue | A_HH | 110 | °C | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate. Consider stopping kiln operation if temperatures do not fall | A
PI22227 | 2000-F22-PID-PR-10007 | F22TK420 Exhaust Outlet | Analogue | A_Hi | 0.5 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
PI22227 | 2000-F22-PID-PR-10007 | F22TK420 Exhaust Outlet | Analogue | A_HH | 1 | kPa | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate. Consider stopping kiln operation if pressure remains high | A
TIC22228 | 2000-F22-PID-PR-10007 | F22HE401 Exhaust Outlet | Analogue | A_Hi | 30 | °C | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate chilled water system and kiln | A
TIC22228 | 2000-F22-PID-PR-10007 | F22HE401 Exhaust Outlet | Analogue | A_HH | 35 | °C | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Temperature is above normal operating conditions. Investigate circuit before kiln stops due to interlock | A
PI22229 | 2000-F22-PID-PR-10007 | F22HE401 Exhaust Outlet | Analogue | A_Hi | 0.5 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
PI22229 | 2000-F22-PID-PR-10007 | F22HE401 Exhaust Outlet | Analogue | A_HH | 1 | kPa | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate. Consider stopping kiln operation if pressure remains high | A
TI22230 | 2000-F22-PID-PR-10007 | F22HE401 Cool Water In | Analogue | A_Hi | 20 | °C | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
TI22230 | 2000-F22-PID-PR-10007 | F22HE401 Cool Water In | Analogue | A_HH | 25 | °C | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate mercury abatement chiller. Consider stopping kiln operation if temperatures do not fall | A
TI22221 | 2000-F22-PID-PR-10007 | F22HE401 Cooling Inlet | Analogue | A_Hi | 20 | °C | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | 1 | [5 empty] | 2025-07-03 | Updated as per KAN-2046
TI22221 | 2000-F22-PID-PR-10007 | F22HE401 Cooling Inlet | Analogue | A_HH | 25 | °C | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate mercury abatement chiller. Consider stopping kiln operation if temperatures do not fall | 1 | [5 empty] | 2025-07-03 | Updated as per KAN-2046
PI22222 | 2000-F22-PID-PR-10007 | F22HE401 Cooling Inlet | Analogue | A_Lo | 60 | kPa | 5 | F22-PW-591 is NOT RUNNING AND F22-PW-592 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | 1 | [5 empty] | 2025-07-03 | Updated as per KAN-2046
PI22222 | 2000-F22-PID-PR-10007 | F22HE401 Cooling Inlet | Analogue | A_Hi | 200 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | 1 | [5 empty] | 2025-07-03 | Updated as per KAN-2046
PI22222 | 2000-F22-PID-PR-10007 | F22HE401 Cooling Inlet | Analogue | A_HH | 210 | kPa | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate. Consider stopping kiln operation if pressure remains high | 1 | [5 empty] | 2025-07-03 | Updated as per KAN-2046
TI22235 | 2000-F22-PID-PR-10007 | F22TK421 Exhaust Outlet | Analogue | A_Hi | 30 | °C | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
TI22235 | 2000-F22-PID-PR-10007 | F22TK421 Exhaust Outlet | Analogue | A_HH | 35 | °C | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Temperature is above normal operating conditions. Investigate circuit before kiln stops due to interlock | A
PI22236 | 2000-F22-PID-PR-10007 | F22TK421 Exhaust Outlet | Analogue | A_Hi | 0.5 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
PI22236 | 2000-F22-PID-PR-10007 | F22TK421 Exhaust Outlet | Analogue | A_HH | 1 | kPa | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate. Consider stopping kiln operation if pressure remains high | A
TI22237 | 2000-F22-PID-PR-10007 | F22TK422 Exhaust Outlet | Analogue | A_Hi | 93 | °C | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
TI22237 | 2000-F22-PID-PR-10007 | F22TK422 Exhaust Outlet | Analogue | A_HH | 100 | °C | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate. Consider stopping kiln operation if temperatures do not fall | A
PI22238 | 2000-F22-PID-PR-10007 | F22TK422 Exhaust Outlet | Analogue | A_Hi | 0.5 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
PI22238 | 2000-F22-PID-PR-10007 | F22TK422 Exhaust Outlet | Analogue | A_HH | 1 | kPa | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate. Consider stopping kiln operation if pressure remains high | A
TDI22240 | 2000-F22-PID-PR-10007 | F22HT401 Diff. T | Analogue | A_Lo | 12 | °C | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Prolonged alarm will cause kiln to stop. Operator to investigate mercury abatement duct heater. | 1 | [5 empty] | 2025-05-12 | Updated as per HAZOP 02/05/2025
PDI22225 | 2000-F22-PID-PR-10007 | F22TK420 Diff. P | Analogue | A_Hi | 0.5 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate mercury abatement knock-out box. Filtration may be in need of replacement. | 1 | [5 empty] | 2025-05-12 | Updated as per HAZOP 02/05/2025
PDI22229 | 2000-F22-PID-PR-10007 | F22TK421 Diff. P | Analogue | A_Hi | 0.5 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate mercury abatement demister vessel. Filtration may be in need of replacement. | 1 | [5 empty] | 2025-05-12 | Updated as per HAZOP 02/05/2025
PDI22236 | 2000-F22-PID-PR-10007 | F22TK422 Diff. P | Analogue | A_Hi | 2.5 | kPa | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate mercury abatement SIC vessel. SIC Carbon may be in need of replacement. | 1 | [5 empty] | 2025-05-12 | Updated as per HAZOP 02/05/2025
LI22242 | 2000-F22-PID-PR-10008 | F22TK484 Level | Analogue | A_LL | 5 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate chiller circuit | C
LI22242 | 2000-F22-PID-PR-10008 | F22TK484 Level | Analogue | A_Lo | 10 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate chiller circuit | C
LI22242 | 2000-F22-PID-PR-10008 | F22TK484 Level | Analogue | A_Hi | 95 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate chiller circuit | C
LI22242 | 2000-F22-PID-PR-10008 | F22TK484 Level | Analogue | A_HH | 97 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate chiller circuit | C
TI22243 | 2000-F22-PID-PR-10008 | F22TK484 Temp | Analogue | A_HH | 25 | °C | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate chiller circuit before kiln stops due to interlock. Prolinged temperature approaching 40 deg C is not suitable for chiller tank materials of construction. | 0
LI66404 | 2000-F66-PID-PR-10001 | F66TK461 Level | Analogue | A_LL | 5 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
LI66404 | 2000-F66-PID-PR-10001 | F66TK461 Level | Analogue | A_Lo | 10 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | A
LI66404 | 2000-F66-PID-PR-10001 | F66TK461 Level | Analogue | A_Hi | 90 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | A
LI66404 | 2000-F66-PID-PR-10001 | F66TK461 Level | Analogue | A_HH | 95 | % | 5 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Operator to investigate | A
LI66405 | 2000-F66-PID-PR-10001 | F66TK471 Level | Analogue | A_LL | 5 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate | A
LI66405 | 2000-F66-PID-PR-10001 | F66TK471 Level | Analogue | A_Lo | 10 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | A
LI66405 | 2000-F66-PID-PR-10001 | F66TK471 Level | Analogue | A_Hi | 90 | % | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | A
LI66405 | 2000-F66-PID-PR-10001 | F66TK471 Level | Analogue | A_HH | 95 | % | 5 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Operator to investigate | A
FI66406 | 2000-F66-PID-PR-10001 | CIL4 Pregnant Eluate | Analogue | A_Lo | 40 | m3/h | 5 | F66PP461 is NOT RUNNING AND F66PP462 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | A
FI66406 | 2000-F66-PID-PR-10001 | CIL4 Pregnant Eluate | Analogue | A_LL | 20 | m3/h | 5 | F66PP461 is NOT RUNNING AND F66PP462 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate circuit before pumps stop due to interlock | A
FI66419 | 2000-F66-PID-PR-10001 | CIL4 Brn Eluate | Analogue | A_Lo | 40 | m3/h | 5 | Alarm if: ((F66-PP-461 Running AND XV66415 Open) OR (F66-PP-462 Running AND XV66417 Open)) for 10 seconds | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | 1
FI66419 | 2000-F66-PID-PR-10001 | CIL4 Brn Eluate | Analogue | A_LL | 20 | m3/h | 5 | Alarm if: ((F66-PP-461 Running AND XV66416 Open) OR (F66-PP-462 Running AND XV66418 Open)) for 10 seconds | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate circuit before pumps stop due to interlock | 1
II66444S | 2000-F66-PID-PR-10002 | F66ER411A Amp | Analogue | A_Lo | 600 | A | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate solution conductivity, dissolved oxygen, pH | C
II66444S | 2000-F66-PID-PR-10002 | F66ER411A Amp | Analogue | A_HH | 2000 | A | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Rectifier tripped. Operator to investigate issue in the equipment | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
II66445S | 2000-F66-PID-PR-10002 | F66ER411B Amp | Analogue | A_Lo | 600 | A | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate solution conductivity, dissolved oxygen, pH | C
II66445S | 2000-F66-PID-PR-10002 | F66ER411B Amp | Analogue | A_HH | 2000 | A | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Rectifier tripped. Operator to investigate issue in the equipment | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
XI66444S | 2000-F66-PID-PR-10002 | F66ER411A Volt | Analogue | A_Lo | 2 | V | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate issue and escalate to maintenance if needed | C
XI66444S | 2000-F66-PID-PR-10002 | F66ER411A Volt | Analogue | A_HH | 4.4 | V | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Rectifier tripped. Operator to investigate issue in the equipment | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
XI66445S | 2000-F66-PID-PR-10002 | F66ER411B Volt | Analogue | A_Lo | 2 | V | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate issue and escalate to maintenance if needed | C
XI66445S | 2000-F66-PID-PR-10002 | F66ER411B Volt | Analogue | A_HH | 4.4 | V | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Rectifier tripped. Operator to investigate issue in the equipment | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
II66446S | 2000-F66-PID-PR-10002 | F66ER412A Amp | Analogue | A_Lo | 600 | A | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate solution conductivity, dissolved oxygen, pH | C
II66446S | 2000-F66-PID-PR-10002 | F66ER412A Amp | Analogue | A_HH | 2000 | A | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Rectifier tripped. Operator to investigate issue in the equipment | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
II66447S | 2000-F66-PID-PR-10002 | F66ER412B Amp | Analogue | A_Lo | 600 | A | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate solution conductivity, dissolved oxygen, pH | C
II66447S | 2000-F66-PID-PR-10002 | F66ER412B Amp | Analogue | A_HH | 2000 | A | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Rectifier tripped. Operator to investigate issue in the equipment | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
XI66446S | 2000-F66-PID-PR-10002 | F66ER412A Volt | Analogue | A_Lo | 2 | V | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate issue and escalate to maintenance if needed | C
XI66446S | 2000-F66-PID-PR-10002 | F66ER412A Volt | Analogue | A_HH | 4.4 | V | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Rectifier tripped. Operator to investigate issue in the equipment | 1 | [5 empty] | 2026-08-05 | Changed to HH to align with F14/66. No change to DCS
XI66447S | 2000-F66-PID-PR-10002 | F66ER412B Volt | Analogue | A_Lo | 2 | V | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate issue and escalate to maintenance if needed | C
XI66447S | 2000-F66-PID-PR-10002 | F66ER412B Volt | Analogue | A_HH | 4.4 | V | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Rectifier tripped. Operator to investigate issue in the equipment | 1
AI22052 | 2000-F22-PID-PR-10005 | F22KN411 Mercury | Analogue | A_HH | 25 | ppm | 3 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Mercury detected in area. Siren/Beacon to activate to alert field personnel to evacuate area. | 0
AI22232 | 2000-F22-PID-PR-10007 | F22ST401 Mercury | Analogue | A_HH | 25 | ppm | 3 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Mercury detected in area. Siren/Beacon to activate to alert field personnel to evacuate area. | 1 | [5 empty] | 2025-05-14 | Abbreviated Description was incorrect
AI22252 | 2000-F22-PID-PR-10007 | F22PS453 Mercury | Analogue | A_HH | 25 | ppm | 3 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Mercury detected in area. Siren/Beacon to activate to alert field personnel to evacuate area. | 1 | [5 empty] | 2025-05-14 | Updated as per HAZOP 02/05/2025
PI22037 | 2000-F24-PID-PR-10031 | F22RA411 Press | Analogue | A_Lo | 900 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate air receiver and compressed air distribution. | 1 | [5 empty] | 2025-05-27 | Missed on P&ID, air receiver for F22 area.
PI22037 | 2000-F24-PID-PR-10031 | F22RA411 Press | Analogue | A_Hi | 1300 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate air receiver and compressed air distribution. | 1 | [5 empty] | 2025-05-27 | Missed on P&ID, air receiver for F22 area.
LAH22137 | 2000-F21-PID-PR-10001 | F22HP445 Full | Digital | Alarm | - | - | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging |  | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
LAH22012 | 2000-F22-PID-PR-10001 | F22PR411 Full | Digital | Alarm | - | - | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging |  | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
LAH22071 | 2000-F22-PID-PR-10001 | F22PS451 High | Digital | Alarm | - | - | 3 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Operator to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
PDAH22104 | 2000-F22-PID-PR-10002 | F22PP460 Diff. | Digital | Alarm | - | - | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate. Potential blockage within thermal oil lines. | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
PAH22104 | 2000-F22-PID-PR-10002 | F22PP460 Press. | Digital | Alarm | - | - | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate. Potential blockage within thermal oil lines. | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
TAH22107 | 2000-F22-PID-PR-10002 | F22ST411 Stack | Digital | Alarm | - | - | 3 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low |  | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
TAH22109 | 2000-F22-PID-PR-10002 | F22HT411 Oil | Digital | Alarm | - | - | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate Eluter Heater BMS. | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
LAL22113 | 2000-F22-PID-PR-10002 | F22TK444 Oil | Digital | Alarm | - | - | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Elution Heater in need of oil fill | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
XA22114 | 2000-F22-PID-PR-10002 | F22HT411 Fault | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect heater control panel | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
PAL22125 | 2000-F22-PID-PR-10002 | F22FN411 Low | Digital | Alarm | - | - | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate elution heater burner fan | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
XA22288 | 2000-F22-PID-PR-10005 | F22KN411 Quench | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Kiln stopped due to full quench hopper | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
XA22285 | 2000-F22-PID-PR-10005 | F22KN411 Fault | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect kiln control panel | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
LAL22297 | 2000-F22-PID-PR-10005 | F22FS413 Level | Digital | Alarm | - | - | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging |  | 1 | [5 empty] | 2025-07-15 | Updated as per KAN-2046
LAH22205 | 2000-F22-PID-PR-10005 | F22HP446 Carbon | Digital | Alarm | - | - | 3 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Not Urgent (>30 minutes) | Logging |  | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
LAHH22206 | 2000-F22-PID-PR-10005 | F22HP446 Water | Digital | Alarm | - | - | 3 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Not Urgent (>30 minutes) | Logging |  | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
LAH22211 | 2000-F22-PID-PR-10005 | F22PS452 High Lvl | Digital | Alarm | - | - | 3 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Operator to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
XA22250C | 2000-F22-PID-PR-10008 | F22CU406 Fault | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate maercury abatement chiller | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
FAL22248 | 2000-F22-PID-PR-10008 | F22CU406 Lo Water FLo | Digital | Alarm | - | - | 3 | F22-PW-591 is NOT RUNNING AND F22-PW-592 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate maercury abatement chiller | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
FAL22261 | 2000-F24-PID-PR-10003 | F22PP490 GW Low | Digital | Alarm | - | - | 3 | F22-PP-490 is NOT RUNNING Enable 10s delay mask on pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
FI22017 | 2000-F22-PID-PR-10001 | F22BX405 Flow | Analogue | A_Hi | 3 | m3/h | 10 | Mask if XV22051 Open | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Misdirected flow detected. Operator to investigate function of valve | 1 | [5 empty] | 2025-01-31 | CR-062
FI22018 | 2000-F22-PID-PR-10001 | F22HE412 Flow | Analogue | A_Hi | 3 | m3/h | 10 | Mask if XV22054 Open | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Misdirected flow detected. Operator to investigate function of valve | 1 | [5 empty] | 2025-01-31 | CR-062
FAH22019 | 2000-F22-PID-PR-10001 | Misdirect Flow 3 | Digital | Alarm | - | - | 3 | XV22072 Open | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Misdirected flow detected. Operator to investigate function of valve | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
FAH22020 | 2000-F22-PID-PR-10001 | Misdirect Flow 4 | Digital | Alarm | - | - | 3 | XV22073 Open | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Misdirected flow detected. Operator to investigate function of valve | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
AAHH22027 | 2000-F22-PID-PR-10001 | Elution HCN | Digital | Alarm | - | - | 3 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | HCN detected in area. Siren/Beacon to activate to alert field personnel to evacuate area. | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
AAHH22002 | 2000-F23-PID-PR-10001 | Elution Tail HCN | Digital | Alarm | - | - | 3 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | HCN detected in area. Siren/Beacon to activate to alert field personnel to evacuate area. | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
FAL66455 | 2000-F66-PID-PR-10002 | F66EC411 Flow 1 | Digital | Alarm | - | - | 3 | F66-PW-461 is NOT RUNNING AND F66-PW-462 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Obstruction detected. Operator to investigate electrowinning cells | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
FAL66456 | 2000-F66-PID-PR-10002 | F66EC411 Flow 2 | Digital | Alarm | - | - | 3 | F66-PW-461 is NOT RUNNING AND F66-PW-462 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Obstruction detected. Operator to investigate electrowinning cells | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
FAL66457 | 2000-F66-PID-PR-10002 | F66EC412 Flow 1 | Digital | Alarm | - | - | 3 | F66-PW-461 is NOT RUNNING AND F66-PW-462 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Obstruction detected. Operator to investigate electrowinning cells | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
FAL66458 | 2000-F66-PID-PR-10002 | F66EC412 Flow 2 | Digital | Alarm | - | - | 3 | F66-PW-461 is NOT RUNNING AND F66-PW-462 is NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Obstruction detected. Operator to investigate electrowinning cells | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
LAH22009 | - | F22GE131 LVL Hi | Digital | Alarm | - | - | 0 | - | None | Rapid (>5 to <15 minutes) | Logging | High fuel level in generator fuel reservoir. Operator to radio local field operator to cease re-fuelling. | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
LAL22009 | - | F22GE131 LVL Lo | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operational risk for backup power. Operator to organise re-fuelling. | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
AA22175 | 2000-F22-PID-PR-10002 | Elution Oil Leak | Digital | Alarm | - | - | 0 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Operator to assess elution heater bund for potential oil spill | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22DCS412_PS1 | - | F22DCS412 PS1 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22DCS412_PS2 | - | F22DCS412 PS2 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW030_PS | - | F22SW030 ACB 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW030_AF | - | F22SW030 Arc Flash | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW030_TRP | - | F22SW030 Breaker Trip | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SR001_ESTP | - | F22SR001 Emergency Shut | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW030_PS1 | - | F22SW030 PS1 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW030_PS2 | - | F22SW030 PS2 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW031_PS | - | F22SW031 ACB 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW031_AF | - | F22SW031 Arc Flash | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW031_OP | - | F22SW031 Breaker Open | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) | Logging | No response required. | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW031_TRP | - | F22SW031 Emergency Shut | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW030_SD | - | F22SW030 Surge Diverter | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW031_PS1 | - | F22SW031 PS1 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW031_PS2 | - | F22SW031 PS2 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22FIP001_ALM | - | F22FIP001 Alarm | Digital | Alarm | - | - | 0 | - | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm. Follow site specific Fire Emergency Plan. | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22FIP001_ISL | - | F22FIP001 Isolate | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) | Logging | Fire alarm. Follow site specific Fire Emergency Plan. | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22FIP001_FLT | - | F22FIP001 Fault | Digital | Alarm | - | - | 0 | - | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm fault. Follow site specific Fire Emergency Plan. | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW031_SD | - | F22SW031 Surge Diverter | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22SW131_SD | - | F22SW131 Surge Diverter | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22RIO001_PS1 | - | F22RIO001PS1 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22RIO001_PS2 | - | F22RIO001PS2 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22RIO002_PS1 | - | F22RIO002PS1 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
F22RIO002_PS2 | - | F22RIO002PS2 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-05-12 | Tag Source changed to Tag Name
TI22006 | - | F22SR001 Switchroom Temp | Analogue | A_Hi | 30 | ℃ | 600 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate air conditioning and cause of high room temperatures. | C
TI22007 | - | F22TR030 Trans Temp | Analogue | A_Hi | 30 | ℃ | 600 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate air conditioning and cause of high room temperatures. | C
TI22008 | - | F22TR031 Trans Temp | Analogue | A_Hi | 30 | ℃ | 600 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate air conditioning and cause of high room temperatures. | C
ZAC22004 | - | F22TR030 415VMCC Door CL | Digital | Alarm | - | - | 0 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Restricted work area potential safety breach/issue | C
ZAC22005 | - | F22TR030 415VMCC Door CL | Digital | Alarm | - | - | 0 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Restricted work area potential safety breach/issue | C
FAH22263 | 2000-F24-PID-PR-10028 | F22SE470 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22264 | 2000-F24-PID-PR-10028 | F22SE471 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22265 | 2000-F24-PID-PR-10028 | F22SE472 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22266 | 2000-F24-PID-PR-10028 | F22SE473 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22267 | 2000-F24-PID-PR-10028 | F22SE474 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22268 | 2000-F24-PID-PR-10028 | F22SE475 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22269 | 2000-F24-PID-PR-10028 | F22SE476 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22270 | 2000-F24-PID-PR-10028 | F22SE477 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22271 | 2000-F24-PID-PR-10028 | F22SE478 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22272 | 2000-F24-PID-PR-10028 | F22SE479 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22273 | 2000-F24-PID-PR-10028 | F22SE480 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22274 | 2000-F24-PID-PR-10028 | F22SE481 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22275 | 2000-F24-PID-PR-10028 | F22SE482 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22276 | 2000-F24-PID-PR-10028 | F22SE505 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-08-18 10:44 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH22277 | 2000-F24-PID-PR-10028 | F22SE506 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-08-18 10:44 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH66435 | 2000-F24-PID-PR-10005 | F66SE433 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH66436 | 2000-F24-PID-PR-10005 | F66SE437 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH66437 | 2000-F24-PID-PR-10005 | F66SE438 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH66438 | 2000-F24-PID-PR-10005 | F66SE467 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
F22TR030_WTH | - | F22TR030 Temp Hi | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrican to investigate high transformer winding temperature alarm | 1 | [5 empty] | 2025-08-19 | CR-034
F22TR031_WTH | - | F22TR031 Temp Hi | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrican to investigate high transformer winding temperature alarm | 1 | [5 empty] | 2025-08-19 | CR-034