## Revisions
PROCESS CONTROL TABLES
REVISION HISTORY
KCGM GROWTH PROJECT
2000-F30-LST-PR-10201
NORTHERN STAR RESOURCES LIMITED
Revision
Date
A
7/03/2024
B
12/03/2024
C
15/03/2024
Updated as per clients comments
0
Minor Corrections
3/07/2024
1
24/07/2024
Preliminary Revision - DDC Automation. Updated PID tab
Document Changes
Preliminary Revision - DDC Automation
Preliminary Revision - DDC Automation
Updated as per client comments

## 1. Analogue Input
KCGM GROWTH PROJECT
ANALOGUE INPUT
[9 empty] | Range |  |  | Process Switchpoints |  |  | Alarms | [7 empty] | Alarm Priority
Tag Source | Tag Name | Parent Equipment | Graphic | P&ID | Description |  | Abbreviated Description (Faceplate) | Trend (sec) | Min | Max | Unit | P_LL | P_HH |  | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | A_LL | A_Lo | A_Hi | A_HH | Alarm Masking Conditions |  | Controller (Y/N) | Comments | Rev
DYS010202WTR.SV | DYS010501WTR | n/a | n/a | n/a | Density of Water |  | Density of Water |  | 1.00 | 2.00 | KG/L |  |  |  | 1 |  | 1 |  | 2 |  | 2 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
DYS010202FOR.SV | DYS010501FOR | n/a | n/a | n/a | Density of Fimiston ORE |  | Density of Fimiston ORE |  | 0.00 | 5.00 | KG/L |  |  |  | 0 |  | 0 |  | 5 |  | 5 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
DYS010202CON.SV | DYS010501CON | n/a | n/a | n/a | Density of Fimiston CON |  | Density of Fimiston CON |  | 0.00 | 5.00 | KG/L |  |  |  | 0 |  | 0 |  | 5 |  | 5 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z021111 | TI30200B | n/a | .GR0046 | n/a | SUB 38 ROOM TEMPERATURE |  | SUB 38 ROOM TEMPERATURE |  | 0.0 | 100.0 | DEGC |  |  |  | 0 |  | 0 |  | 29 |  | 34 |  | User (6) | User (6) | User (6) | User (6) |  | 4 |  |  | 1 | NO
%Z024106 | II75260 | 75PW13A | .GR0032 | 75-PI-0461 | BoreWaterPmp75PW13A Amp | s | BoreWaterPmp75PW13A Amps |  | 0.0 | 224.0 | AMPS |  |  |  | 0 |  | 0 |  | 224 |  | 224 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z024107 | II75261 | 75PW13B | .GR0032 | 75-PI-0461 | BoreWaterPmp75PW13B Amp | s | BoreWaterPmp75PW13B Amps |  | 0.0 | 224.0 | AMPS |  |  |  | 0 |  | 0 |  | 224 |  | 224 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z021106 | FI30315 | n/a | .GR0320 .GR0331 | 30-PI-0312 | Flot Thknr#2Under Flow |  | Flot Thknr#2Under Flow |  | 0.000 | 1000.000 | M3/H |  |  |  | 0 |  | 0 |  | 1000 |  | 1000 |  | Logging | Logging | Logging | Logging |  | 4 |  |  | 1 | HOUR
%Z021101 | AI30320 | n/a | n/a | 30-PI-0313 | CIL2 Tk Lime pH Probe 1 |  | CIL2 Tk Lime pH Probe 1 |  | 7.00 | 10.00 | pH |  |  |  | 0 |  | 0 |  | 10 |  | 10 |  | Medium | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%Z024116 | JI30376 | 30-SW-31 | .GR0044 | n/a | 30-SW-31 MCCPower Supply |  | 30-SW-31 MCCPower Supply |  | 0.000 | 2000.000 | KW |  |  |  | 0 |  | 0 |  | 2000 |  | 2000 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
MI30337.P08 | MI30337A | n/a | n/a | 30-PI-0312 | Floc Usage |  | Floc Usage |  | 0.0 | 90000.0 | G/T |  |  |  | 0 |  | 0 |  | 90000 |  | 90000 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z021107 | FI30333 | n/a | .GR0320 .GR0705 | 30-PI-0313 | CIL2 LIME FLOW |  | CIL2 LIME FLOW |  | 0.0 | 40.0 | M3/H |  |  |  | 0 |  | 0 |  | 40 |  | 40 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
| PI81RA33 | n/a | .GR0301 | n/a | Plant Air Receiver |  | Plant Air Receiver |  | 0.0 | 1000.0 | KPA |  |  |  | 0 |  | 0 |  | 1000 |  | 1000 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z025113 %Z021112 | II3048 PI81304 | 75PW72A 81CM61 | .GR0032 GR0051 | n/a n/a | Gland Water Pump 75PW72A InstAir Comp81CM61 |  | Gland Water Pump 75PW72A InstAir Comp81CM61 |  | 0.0 0.0 | 100.0 1000.0 | AMPS KPA |  |  |  | 0 550 |  | 0 580 |  | 100 1000 |  | 100 1000 | e | Medium Medium | Medium Medium | Medium Medium | Medium Medium |  | 4 4 |  |  | 1 1 | NO HOUR
%Z024115 | FI81312 | 81RA33 | .GR0051 | n/a | Plant Air Air Flow |  | Plant Air Air Flow |  | 0.0 | 1000.0 | M3/H |  |  |  | 0 |  | 0 |  | 1000 |  | 1000 | r | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z021101 | AI30382 | n/a | .GR0320 | n/a | CIL2 2nd Stream Cyanide |  | CIL2 2nd Stream Cyanide |  | 0.0 | 500.0 | PPM |  |  |  | 0 |  | 0 |  | 500 |  | 500 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z021108 | FI30338 | n/a | .GR0320 .GR0672 | 30-PI-0008 | CIL2 BARREN ELUATE FLOW |  | CIL2 BARREN ELUATE FLOW |  | 0.0 | 100.0 | M3/H |  |  |  | 0 |  | 0 |  | 100 |  | 100 | a | Medium | Medium | Medium | Medium |  | 1 |  |  | 1 | NO
%Z064105 | FI30638 | n/a | .GR0330 .GR0672 | 2000-F30-PID-PR-10008 | CIL3 BARREN ELUATE FLOW |  | CIL3 BARREN ELUATE FLOW |  | 0.0 | 100.0 | M3/H |  |  |  | 0 |  | 0 |  | 100 |  | 100 | s | Medium | Medium | Medium | Medium |  | 1 |  |  | 1 | NO
%Z021109 | FI30384 | n/a | .GR0300 .GR0320 | 30-PI-0701 | CIL2 Slurry Flow frm MTC |  | CIL2 Slurry Flow frm MTC |  | 0.0 | 400.0 | M3/H |  |  |  | 0 |  | 0 |  | 400 |  | 400 | nt | Medium | Medium | Medium | Medium |  | 1 |  |  | 1 | NO
%Z022108 | AI30393A | TK32A | GR0320 | 30-PI-0313 | CIL2 TK32A pH |  | CIL2 TK32A pH |  | 7.00 | 14.00 | pH |  |  |  | 7 |  | 8.60000038 |  | 9.19999981 |  | 14 | i | Logging | Logging | Logging | Logging |  | 3 |  |  | 1 | NO
%Z022109 | AI30393B | TK32A | GR0320 | 30-PI-0313 | CIL2 TK32A Disolved Oxy |  | CIL2 TK32A Disolved Oxy |  | 0.00 | 40.00 | PPM |  |  |  | 0 |  | 0 |  | 100 |  | 100 | o | Logging | Logging | Logging | Logging |  | 3 |  |  | 1 | NO
%Z022110 | AI30393C | TK32B | GR0320 | 30-PI-0313 | CIL2 TK32B pH |  | CIL2 TK32B pH |  | 7.00 | 14.00 | pH |  |  |  | 8.3000002 |  | 8.60000038 |  | 9.19999981 |  | 14 |  | Logging | Logging | Logging | Logging |  | 3 |  |  | 1 | NO
%Z022111 | AI30393D | TK32B | GR0320 | 30-PI-0313 | CIL2 TK32B Dissolved Oxy |  | CIL2 TK32B Dissolved Oxy |  | 0.00 | 40.00 | PPM |  |  |  | 0 |  | 0 |  | 100 |  | 100 | p | Logging | Logging | Logging | Logging |  | 3 |  |  | 1 | NO
%Z021114 | AI30394A | n/a | .GR0310 | n/a | CIL1 Tails Free CN |  | CIL1 Tails Free CN |  | 0.00 | 3000.00 | PPM |  |  |  | 0 |  | 0 |  | 3000 |  | 3000 |  | Low | Low | Low | Low |  | 1 |  |  | 1 | NO
%Z021115 | AI30394B | n/a | .GR0310 | n/a | CIL1 Tails WAD CN |  | CIL1 Tails WAD CN |  | 0.00 | 3000.00 | PPM |  |  |  | 0 |  | 0 |  | 3000 |  | 3000 |  | Low | Low | Low | Low |  | 1 |  |  | 1 | NO
%Z022114 | AI30394C | TK63 | .GR0341 | n/a | Tails Free CN |  | Tails Free CN |  | 0.00 | 1500.00 | PPM |  |  |  | 0 |  | 0 |  | 1500 |  | 1500 |  | Low | Low | Low | Low |  | 1 |  |  | 1 | NO
%Z022115 | AI30394D | TK63 | .GR0341 | n/a | Tails WAD CN |  | Tails WAD CN |  | 0.00 | 1500.00 | PPM |  |  |  | 0 |  | 0 |  | 1500 |  | 1500 | m | Low | Low | Low | Low |  | 1 |  |  | 1 | NO
%Z061105 | AI30693A | TK62A | GR0330 | 2000-F30-PID-PR-10008 | CIL3 TK62A pH |  | CIL3 TK62A pH |  | 7.00 | 14.00 | pH |  |  |  | 8.35999966 |  | 8.60000038 |  | 9.19999981 |  | 14 |  | Logging | Logging | Logging | Logging |  | 3 |  |  | 1 | NO
%Z062113 | AI30693B | TK62A | GR0330 | 2000-F30-PID-PR-10008 | CIL3 TK62A Disolved Oxy |  | CIL3 TK62A Disolved Oxy |  | 0.00 | 40.00 | PPM |  |  |  | 0 |  | 0 |  | 100 |  | 100 | r | Logging | Logging | Logging | Logging |  | 3 |  |  | 1 | NO
%Z061109 | AI30693C | TK62B | GR0330 | 2000-F30-PID-PR-10008 | CIL3 TK62B pH |  | CIL3 TK62B pH |  | 7.00 | 14.00 | pH |  |  |  | 8.30000019 |  | 8.60000038 |  | 9.19999981 |  | 14 | a | Logging | Logging | Logging | Logging |  | 3 |  |  | 1 | NO
%Z062114 | AI30693D | TK62B | GR0330 | 2000-F30-PID-PR-10008 | CIL3 TK62B Dissolved Oxy |  | CIL3 TK62B Dissolved Oxy |  | 0.00 | 40.00 | PPM |  |  |  | 0 |  | 0 |  | 100 |  | 100 | l | Logging | Logging | Logging | Logging |  | 3 |  |  | 1 | NO
%Z025114 | PI75502 | 75PP19A/B | .GR0033 | n/a | Carbon TFX Cyanide Water |  | Carbon TFX Cyanide Water |  | 0.0 | 1000.0 | KPA |  |  |  | 0 |  | 150 |  | 650 |  | 750 |  | Medium | Medium | Medium | Medium |  | 1 |  |  | 1 | HOUR
%Z025110 | FI65331 | n/a | .GR0649 | 65-PI-1004 | Water To Carbon Attrit |  | Water To Carbon Attrit |  | 0.0 | 150.0 | M3/H |  |  |  | 0 |  | 0 |  | 100 |  | 100 | a | Medium | Medium | Medium | Medium |  | 3 |  |  | 1 | HOUR
| LI65332 | 65TK70 | .GR0649 | 65-PI-1004 | Carbon Attrition Tk Levl |  | Carbon Attrition Tk Levl |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  | Medium | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%Z025112 | II65339 | 65PP70 | .GR0649 | 65-PI-1004 | 65PP70 Mtr Current |  | 65PP70 Mtr Current |  | 0.0 | 60.0 | AMPS |  |  |  | 0 |  | 0 |  | 60 |  | 60 |  | Medium | Medium | Medium | Medium |  | 3 |  |  | 1 | HOUR
%Z061116 | II30665 | 30SC62M | .GR0320 | n/a | CIL3 Screen 30SC62M Amps |  | CIL3 Screen 30SC62M Amps |  | 0.0 | 100.0 | AMPS |  |  |  | 0 |  | 0 |  | 100 |  | 100 | m | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z061110 | II30660 | 30SC62B | .GR0320 | 2000-F30-PID-PR-10008 | CIL3 Screen 30SC62B Amps |  | CIL3 Screen 30SC62B Amps |  | 0.0 | 100.0 | AMPS |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z061111 | II30661 | 30SC62C | .GR0320 | 2000-F30-PID-PR-10008 | CIL3 Screen 30SC62C Amps |  | CIL3 Screen 30SC62C Amps |  | 0 | 100 | AMPS |  |  |  | 0 |  | 0 |  | 100 |  | 100 | r | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z061113 | II30662 | 30SC62D | .GR0320 | 2000-F30-PID-PR-10009 | CIL3 Screen 30SC62D Amps |  | CIL3 Screen 30SC62D Amps |  | 0 | 100 | AMPS |  |  |  | 0 |  | 0 |  | 100 |  | 100 | i | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z061114 | II30663 | 30SC62E | .GR0320 | 2000-F30-PID-PR-10009 | CIL3 Screen 30SC62E Amps |  | CIL3 Screen 30SC62E Amps |  | 0 | 100 | AMPS |  |  |  | 0 |  | 0 |  | 100 |  | 100 | f | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z061115 | II30664 | 30SC62F | .GR0320 | 2000-F30-PID-PR-10009 | CIL3 Screen 30SC62F Amps |  | CIL3 Screen 30SC62F Amps |  | 0 | 100 | AMPS |  |  |  | 0 |  | 0 |  | 100 |  | 100 | n | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z024101 | II75262 | 75PW63A | .GR0033 | 75-PI-0461 | Cn Water Pmp75PW63A Amps |  | Cn Water Pmp75PW63A Amps |  | 0 | 400 | AMPS |  |  |  | 0 |  | 0 |  | 400 |  | 400 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z024102 | II75263 | 75PW63B | .GR0033 | 75-PI-0461 | Cn Water Pmp75PW63B Amps |  | Cn Water Pmp75PW63B Amps |  | 0.0 | 400.0 | AMPS |  |  |  | 0 |  | 0 |  | 400 |  | 400 | o | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z063108 | NI30601 | TH61 | .GR0302 | 2000-F30-PID-PR-10001 | Thickener #3 Torque |  | Thickener #3 Torque |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 40 |  | 50 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
LI30606AVG.CPV | LI30606 | TH61 | .GR0302 | 2000-F30-PID-PR-10001 | Thickener #3 Bed Level |  | Thickener #3 Bed Level |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 40 |  | 70 | c | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z063109 | ZI30610 | TH61 | .GR0302 | 2000-F30-PID-PR-10001 | Thickener #3 Rake Height |  | Thickener #3 Rake Height |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 40 |  | 50 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z063101 | II30611 | 30PP61A | .GR0302 | 2000-F30-PID-PR-10001 | Thickener #3U/F PpA Amps |  | Thickener #3U/F PpA Amps |  | 0.0 | 200.0 | AMPS |  |  |  | 0 |  | 0 |  | 190 |  | 200 | : | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z063102 | II30612 | 30PP61B | .GR0302 | 2000-F30-PID-PR-10001 | Thickener #3U/F PpB Amps |  | Thickener #3U/F PpB Amps |  | 0.0 | 200.0 | AMPS |  |  |  | 0 |  | 0 |  | 190 |  | 200 | e | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z063111 | FI30616 | 30TH61 | n/a | 2000-F30-PID-PR-10001 | Thickener #3 Floc Flow |  | Thickener #3 Floc Flow |  | 0.0 | 8000.0 | L/HR |  |  |  | 600 |  | 600 |  | 8000 |  | 8000 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z062115 | FI30650 | n/a | .GR0302 | 2000-F30-PID-PR-10001 | Thknr #3 U/FDilute Water |  | Thknr #3 U/FDilute Water |  | 0.0 | 200.0 | M3/H |  |  |  | 0 |  | 0 |  | 135 |  | 150 | t | Medium e | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MI30637.P08 | MI30637A | n/a | n/a | 2000-F30-PID-PR-10001 | FLOC USAGE |  | FLOC USAGE |  | 0.0 | 50.0 | G/T |  |  |  | 0 |  | 0 |  | 50 |  | 50 | o | Logging | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%Z065109 | AI30637 | n/a | .GR0330 | 2000-F30-PID-PR-10008 | CIL3 CyanideAnalyser |  | CIL3 CyanideAnalyser |  | 0 | 500 | PPM |  |  |  | 0 |  | 0 |  | 1000 |  | 1000 |  | Medium g | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z064108 | FI30655 | n/a | .GR0302 | 2000-F30-PID-PR-10001 | THICK 3 FLOC WATER ADD |  | THICK 3 FLOC WATER ADD |  | 0.0 | 100.0 | M3/H |  |  |  | 0 |  | 0 |  | 90 |  | 100 | N | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z072110 | FI30808 | 30PP61A | GR0302 | n/a | n/a |  | 30PP61A Gland Water Flow |  | 0.0 | 100.0 | L/M |  |  |  | 10 |  | 0 |  | 100 |  | 100 |  | n Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z065101 | II75611A | 75PW62A | .GR0032 | 75-PI-0461 | Circuit WatrPump A Amps |  | Circuit WatrPump A Amps |  | 0.0 | 80.0 | AMPS |  |  |  | 33 |  | 35 |  | 80 |  | 80 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z065102 | JI75610A | 75PW62A | .GR0032 | 75-PI-0461 | Circuit WatrPump A Pwr |  | Circuit WatrPump A Pwr |  | 0.0 | 500.0 | KW |  |  |  | 0 |  | 0 |  | 500 |  | 500 | l | a Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z065103 | II75611B | 75PW62B | .GR0032 | 75-PI-0461 | Circuit WatrPump B Amps |  | Circuit WatrPump B Amps |  | 0.0 | 80.0 | AMPS |  |  |  | 30 |  | 30 |  | 80 |  | 80 | a | Medium r | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z065104 | JI75610B | 75PW62B | .GR0032 | 75-PI-0461 | Circuit WatrPump B Pwr |  | Circuit WatrPump B Pwr |  | 0.0 | 500.0 | KW |  |  |  | 0 |  | 0 |  | 500 |  | 500 | r | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z065107 | II75620A | 75PW17A | .GR0031 | 75-PI-0461 | Bore Water Pump 17A Amp |  | Bore Water Pump 17A Amp |  | 0.0 | 300.0 | AMPS |  |  |  | 0 |  | 0 |  | 170 |  | 182 |  | Medium n | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z065108 | II75620B | 75PW17B | .GR0031 | 75-PI-0461 | Bore Water Pump 17B Amp |  | Bore Water Pump 17B Amp |  | 0.0 | 300.0 | AMPS |  |  |  | 0 |  | 0 |  | 170 |  | 182 | e | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z065108 | II75620B | 30SW62A | .GR0044 | n/a | 30SW62A 415VPower Supply |  | 30SW62A 415VPower Supply |  | 0 | 1800 | KW |  |  |  | 0 |  | 0 |  | 1800 |  | 1800 |  | Medium i | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z062112 | JI30676B | 30SW62B | .GR0044 | n/a | 30SW62B 415VPower Supply |  | 30SW62B 415VPower Supply |  | 0.0 | 1800.0 | KW |  |  |  | 0 |  | 0 |  | 1400 |  | 1500 | n | Medium h | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z062110 | JI30677 | 30SW61 | .GR0044 | n/a | 30SW61 3.3kVPower Supply |  | 30SW61 3.3kVPower Supply |  | 0 | 1500 | KW |  |  |  | 0 |  | 0 |  | 1500 |  | 1500 |  | Medium t | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z024109 | FI75280 | n/a | .GR0032 .GR0301 | 75-PI-0461 | Bore Water No1 Pps Flow |  | Bore Water No1 Pps Flow |  | 0.0 | 1000.0 | M3/H |  |  |  | 0 |  | 0 |  | 1000 |  | 1000 | e | Medium i | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z072109 | AI30637B | 30TK62F | GR0330 | n/a | CIL3 Cyanide Conc. B |  | CIL3 Cyanide Conc. B |  | 0.0 | 500.0 | PPM |  |  |  | 0 |  | 0 |  | 500 |  | 500 | G | w Logging | Logging | Logging | Logging |  | 3 |  |  | 1 | NO
%Z061108 | AI30620B | 30TK62A | n/a | 2000-F30-PID-PR-10008 | CIL3 Leach Tank pH #2 |  | CIL3 Leach Tank pH #2 |  | 8.00 | 10.00 | pH |  |  |  | 0 |  | 0 |  | 14 |  | 14 |  | Medium | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%Z061107 | AI30635 | 30TK62B | n/a | 2000-F30-PID-PR-10008 | CIL3 DisolveOxygen |  | CIL3 DisolveOxygen |  | 0.00 | 30.00 | PPM |  |  |  | 0 |  | 0 |  | 40 |  | 40 |  | Medium | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%Z062101 | II30625 | 30AG62A 30AG62B 30AG62C 30AG62D 30AG62E 30AG62F | .GR0330 | 2000-F30-PID-PR-10008 | CIL3 Agitatr30AG62A Amps |  | CIL3 Agitatr30AG62A Amps |  | 0.0 | 200.0 | AMPS |  |  |  | 50 |  | 50 |  | 200 |  | 200 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z062102 | II30626 |  | .GR0330 | 2000-F30-PID-PR-10008 | CIL3 Agitatr30AG62B Amps |  | CIL3 Agitatr30AG62B Amps |  | 0.0 | 200.0 | AMPS |  |  |  | 50 |  | 50 |  | 200 |  | 200 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z062103 | II30627 |  | .GR0330 | 2000-F30-PID-PR-10008 | CIL3 Agitatr30AG62C Amps |  | CIL3 Agitatr30AG62C Amps |  | 0.0 | 200.0 | AMPS |  |  |  | 50 |  | 50 |  | 200 |  | 200 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z062104 | II30628 |  | .GR0330 | 2000-F30-PID-PR-10009 | CIL3 Agitatr30AG62D Amps |  | CIL3 Agitatr30AG62D Amps |  | 0.0 | 200.0 | AMPS |  |  |  | 50 |  | 50 |  | 200 |  | 200 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z062105 | II30629 |  | .GR0330 | 2000-F30-PID-PR-10009 | CIL3 Agitatr30AG62E Amps |  | CIL3 Agitatr30AG62E Amps |  | 0.0 | 200.0 | AMPS |  |  |  | 50 |  | 50 |  | 200 |  | 200 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z062106 | II30630 |  | .GR0330 | 2000-F30-PID-PR-10009 | CIL3 Agitatr30AG62F Amps |  | CIL3 Agitatr30AG62F Amps |  | 0.0 | 200.0 | AMPS |  |  |  | 50 |  | 50 |  | 200 |  | 200 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z061103 | FI30633 | n/a | .GR0330 .GR0705 | n/a | CIL3 LIME FLOW |  | CIL3 LIME FLOW |  | 0.0 | 40.0 | M3/H |  |  |  | 0 |  | 0 |  | 40 |  | 40 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z072108 | AI30621B | n/a | n/a | n/a | CIL3 pH Filtrate |  | CIL3 pH Filtrate |  | 8.00 | 10.00 | pH |  |  |  | 8 |  | 8 |  | 10 |  | 10 |  | Logging | Logging | Logging | Logging |  | 3 |  |  | 1 | NO
%Z064111 | FI30615 | n/a | .GR0330 .GR0331 | 2000-F30-PID-PR-10001 | CIL3 Feed Flow |  | CIL3 Feed Flow |  | 0.0 | 1000.0 | M3/H |  |  |  | 100 |  | 150 |  | 900 |  | 1000 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z064110 | DI30613 | n/a | TRENDS 1 | 2000-F30-PID-PR-10001 | CIL3 Feed Density |  | CIL3 Feed Density |  | 0.0 | 80.0 | %SOL |  |  |  | 45 |  | 0 |  | 70 |  | 100 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z062113 | AI30621A | 30TK62A | n/a | n/a | CIL3 TK62A Disolved Oxy |  | CIL3 TK62A Disolved Oxy |  | 0.00 | 40.00 | PPM |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  | Logging | Logging | Logging | Logging |  | 3 |  |  | 1 | NO
%Z071101 | TI30760A | 30PP62A | .GR0341 | n/a | FTails PP62ABear Tmp DE |  | FTails PP62ABear Tmp DE |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 150 |  | 150 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071102 | TI30760B | 30PP62A | .GR0341 | n/a | FTails PP62ABear Tmp NDE |  | FTails PP62ABear Tmp NDE |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 150 |  | 150 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071103 | TI30761A | 30PP62A | .GR0341 | n/a | FTails PP62AWind Tmp Red |  | FTails PP62AWind Tmp Red |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 140 |  | 149.899994 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071104 | TI30761B | 30PP62A | .GR0341 | n/a | FTails PP62AWind Tmp Wht |  | FTails PP62AWind Tmp Wht |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 140 |  | 149.899994 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071105 | TI30761C | 30PP62A | .GR0341 | n/a | FTails PP62AWind Tmp Blu |  | FTails PP62AWind Tmp Blu |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 140 |  | 149.899994 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071106 | TI30762A | 30PP62B | .GR0341 | n/a | FTails PP62BBear Tmp DE |  | FTails PP62BBear Tmp DE |  | 0.0 | 200.0 | DEG |  |  |  | 0 |  | 0 |  | 200 |  | 200 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071107 | TI30762B | 30PP62B | .GR0341 | n/a | FTails PP62BBear Tmp NDE |  | FTails PP62BBear Tmp NDE |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 150 |  | 150 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071108 | TI30763A | 30PP62B | .GR0341 | n/a | FTails PP62BWind Tmp Red |  | FTails PP62BWind Tmp Red |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 140 |  | 149.899994 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071109 | TI30763B | 30PP62B | .GR0341 | n/a | FTails PP62BWind Tmp Wht |  | FTails PP62BWind Tmp Wht |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 140 |  | 149.899994 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071110 | TI30763C | 30PP62B | .GR0341 | n/a | FTails PP62BWind Tmp Blu |  | FTails PP62BWind Tmp Blu |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 140 |  | 149.899994 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071111 | TI30764A | 30PP62C | .GR0341 | n/a | FTails PP62CBear Tmp DE |  | FTails PP62CBear Tmp DE |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 150 |  | 150 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071112 | TI30764B | 30PP62C | .GR0341 | n/a | FTails PP62CBear Tmp NDE |  | FTails PP62CBear Tmp NDE |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 150 |  | 150 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071114 | TI30765B | 30PP62C | .GR0341 | n/a | FTails PP62CWind Tmp Wht |  | FTails PP62CWind Tmp Wht |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 140 |  | 149.899994 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071115 | TI30765C | 30PP62C | .GR0341 | n/a | FTails PP62CWind Tmp Blu |  | FTails PP62CWind Tmp Blu |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 140 |  | 149.899994 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071113 | TI30765A | 30PP62C | .GR0341 | n/a | FTails PP62CWind Tmp Red |  | FTails PP62CWind Tmp Red |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 140 |  | 149.899994 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z071116 | FI30727A | 30PP62A | GR0341 | 30-PI-1011 | FTails Pmp A Gland Water |  | FTails Pmp A Gland Water |  | 0.0 | 100.0 | L/MIN |  |  |  | 10 |  | 15 |  | 65 |  | 65 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z065114 | TI30766 | 30PP62A | .GR0341 | n/a | FTails PP62AVSD TEMP |  | FTails PP62AVSD TEMP |  | 0.0 | 100.0 | DEG |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051101 | TI30753A | 30PP62D | .GR0341 | n/a | FTails PP62dBear Tmp DE |  | FTails PP62dBear Tmp DE |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 150 |  | 150 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051102 | TI30753B | 30PP62D | .GR0341 | n/a | FTails PP62DBear Tmp NDE |  | FTails PP62DBear Tmp NDE |  | 0.0 | 150.0 | DEG |  |  |  | 0 |  | 0 |  | 150 |  | 150 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051104 | TI30754B | 30PP62D | .GR0341 | n/a | FTails PP62DWind Tmp Wht |  | FTails PP62DWind Tmp Wht |  | 0.0 | 180.0 | DEG |  |  |  | 0 |  | 0 |  | 150 |  | 160 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051105 | TI30754C | 30PP62D | .GR0341 | n/a | FTails PP62DWind Tmp Blu |  | FTails PP62DWind Tmp Blu |  | 0.0 | 180.0 | DEG |  |  |  | 0 |  | 0 |  | 150 |  | 160 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051103 | TI30754A | 30PP62D | .GR0341 | n/a | FTails PP62DWind Tmp Red |  | FTails PP62DWind Tmp Red |  | 0.0 | 180.0 | DEG |  |  |  | 0 |  | 0 |  | 150 |  | 160 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051106 | FI30727B | 30PP62B | GR0341 | 30-PI-1011 | FTails Pmp B Gland Water |  | FTails Pmp B Gland Water |  | 0.0 | 100.0 | L/MIN |  |  |  | 10 |  | 15 |  | 45 |  | 45 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051107 | FI30727D | 30PP62B | GR0341 | 30-PI-1011 | FTails Pmp D Gland Water |  | FTails Pmp D Gland Water |  | 0.0 | 100.0 | L/MIN |  |  |  | 10 |  | 15 |  | 45 |  | 55 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z063104 | LI30800 |  | .GR0037 TRENDS 6 | n/a | LAST CHANCE POND LEVEL |  | LAST CHANCE POND LEVEL |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 65 |  | 70 |  | 95 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z064104 | PI30740 | n/a | .GR0341 .GR0331 .GR0343 | 30-PI-1011 | TailsA Line 400A Pressur |  | TailsA Line 400A Pressur |  | 0.0 | 1200.0 | KPA |  |  |  | 0 |  | 0 |  | 980 |  | 1150 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z064107 | PI30741 | n/a | .GR0341 .GR0331 .GR0343 | 30-PI-1011 | TailsC Line 400C Pressur |  | TailsC Line 400C Pressur |  | 0 | 1200 | KPA |  |  |  | 0 |  | 0 |  | 1100 |  | 1150 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z064101 | PI30739 | n/a | .GR0341 .GR0331 .GR0343 | 30-PI-1011 | TailsB Line 315 Pressure |  | TailsB Line 315 Pressure |  | 0.0 | 1200.0 | KPA |  |  |  | 0 |  | 0 |  | 1150 |  | 1195 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z064106 | FI30742 | n/a | .GR0341 .GR0331 .GR0343 TRENDS 4 | 30-PI-1011 | TailsA Line 400A Flow |  | TailsA Line 400A Flow |  | 0.0 | 1500.0 | M3/H |  |  |  | 350 |  | 400 |  | 1500 |  | 1500 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z064109 | FI30743 | n/a | .GR0341 .GR0331 .GR0343 TRENDS 4 | 30-PI-1011 | TailsC Line 400C Flow |  | TailsC Line 400C Flow |  | 0.0 | 1600.0 | M3/H |  |  |  | 350 |  | 400 |  | 1600 |  | 1600 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z064103 | FI30738 | n/a | .GR0341 .GR0331 .GR0343 TRENDS 4 | 30-PI-1011 | TailsB Line 315 Flow |  | TailsB Line 315 Flow |  | 0.0 | 1200.0 | M3/H |  |  |  | 350 |  | 400 |  | 1200 |  | 1200 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
PI30740SUB.CPV | PI30740D | n/a | .GR0341 .GR0343 | 30-PI-1011 | TailsA Line 400A Pressure |  | TailsA Line 400A Pressure |  | -600.0 | 600.0 | KPA |  |  |  | -600 |  | -600 |  | 600 |  | 600 |  | Logging | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
PI30739SUB.CPV | PI30739D | n/a | .GR0341 .GR0343 | 30-PI-1011 | TailsB Line 315 Pressure |  | TailsB Line 315 Pressure |  | -600 | 600 | KPA |  |  |  | -600 |  | -600 |  | 600 |  | 600 |  | Logging | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
PI30741SUB.CPV | PI30741D | n/a | .GR0341 .GR0343 | 30-PI-1011 | TailsC Line 400C Pressur |  | TailsC Line 400C Pressur |  | -600.000 | 600.000 | KPA |  |  |  | -600 |  | -600 |  | 600 |  | 600 |  | Logging | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
FI30742SUB.CPV | FI30742D | n/a | .GR0341 .GR0343 | 30-PI-1011 | TailsA Line 400A Flow |  | TailsA Line 400A Flow |  | -750.000 | 750.000 | M3/H |  |  |  | -750 |  | -750 |  | 750 |  | 750 |  | Logging | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
FI30738SUB.CPV | FI30738D | n/a | .GR0341 .GR0343 | 30-PI-1011 | TailsB Line 315 Flow |  | TailsB Line 315 Flow |  | -400.0 | 400.0 | M3/H |  |  |  | -400 |  | -400 |  | 400 |  | 400 |  | Logging | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
FI30743SUB.CPV | FI30743D | n/a | .GR0341 .GR0343 | 30-PI-1011 | TailsC Line 400C Flow |  | TailsC Line 400C Flow |  | -750.0 | 750.0 | M3/H |  |  |  | -750 |  | -750 |  | 750 |  | 750 |  | Logging | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
FI30741SUB.CPV | FI30741 | n/a | .GR0341 | n/a | TAILSA LINE DIFFERENCE |  | TAILSA LINE DIFFERENCE |  | -100.0 | 100.0 | % |  |  |  | -300 |  | -290 |  | 290 |  | 300 |  | Logging | Logging | Logging | Logging |  | 5 |  |  | 1 | HOUR
FI30744SUB.CPV | FI30744 | n/a | .GR0341 | n/a | TAILSC LINE DIFFERENCE |  | TAILSC LINE DIFFERENCE |  | -100.0 | 100.0 | % |  |  |  | -300 |  | -290 |  | 290 |  | 300 |  | Logging | Logging | Logging | Logging |  | 5 |  |  | 1 | HOUR
TAILSLEAKCALC.CPV | FA30741HH | n/a | n/a | n/a | TAILSA LINE DIFF ALARM |  | TAILSA LINE DIFF ALARM |  | 0.0 | 10.0 | % |  |  |  | 0 |  | 0 |  | 10 |  | 10 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | SEC
TAILSLEAKCALC.CPV1 | FA30744HH | n/a | n/a | n/a | TAILSC LINE DIFF ALARM |  | TAILSC LINE DIFF ALARM |  | 0.0 | 10.0 | % |  |  |  | 0 |  | 0 |  | 10 |  | 10 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | SEC
FI30741 | FA30741CTP | n/a | n/a | n/a | TAILSA DIFF ALRM COUNT |  | TAILSA DIFF ALRM COUNT |  | 0.0 | 1000000.0 | % |  |  |  | 0 |  | 0 |  | 1000000 |  | 1000000 |  | Logging | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
FI30744 | FA30744CTP | n/a | n/a | n/a | TAILSC DIFF ALRM COUNT |  | TAILSC DIFF ALRM COUNT |  | 0.0 | 1000000.0 | % |  |  |  | 0 |  | 0 |  | 1000000 |  | 1000000 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | NO
FI30739SUB.CPV | FI30739 | n/a | .GR0341 | n/a | TAILSB LINE DIFFERENCE |  | TAILSB LINE DIFFERENCE |  | -100.0 | 100.0 | % |  |  |  | -300 |  | -290 |  | 290 |  | 300 |  | Logging | Logging | Logging | Logging |  | 5 |  |  | 1 | HOUR
FI30739 | FA30739CTP | n/a | n/a | n/a | TAILSB DIFF ALRM COUNT |  | TAILSB DIFF ALRM COUNT |  | 0.0 | 1000000.0 | % |  |  |  | 0 |  | 0 |  | 1000000 |  | 1000000 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | NO
TAILSLEAKCALC.CPV2 | FA30739HH | n/a | n/a | n/a | TAILSB LINE DIFF ALARM |  | TAILSB LINE DIFF ALARM |  | 0.0 | 10.0 | % |  |  |  | 0 |  | 0 |  | 10 |  | 10 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | SEC
TAILSLEAKCALD.CPV | FA30742HH | n/a | n/a | n/a | TAILSA LINE DIFF ALARM |  | TAILSA LINE DIFF ALARM |  | 0.0 | 10.0 | % |  |  |  | 0 |  | 0 |  | 10 |  | 10 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | SEC
TAILSLEAKCALD.CPV1 | FA30743HH | n/a | n/a | n/a | TAILSC LINE DIFF ALARM |  | TAILSC LINE DIFF ALARM |  | 0.0 | 10.0 | % |  |  |  | 0 |  | 0 |  | 10 |  | 10 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | SEC
TAILSLEAKCALD.CPV2 | FA30738HH | n/a | n/a | n/a | TAILSB LINE DIFF ALARM |  | TAILSB LINE DIFF ALARM |  | 0.0 | 10.0 | % |  |  |  | 0 |  | 0 |  | 10 |  | 10 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | SEC
TAILSLEAKCALE.CPV | PA30740HH | n/a | n/a | n/a | TAILSA LINE DIFF ALARM |  | TAILSA LINE DIFF ALARM |  | 0.0 | 10.0 | % |  |  |  | 0 |  | 0 |  | 10 |  | 10 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | SEC
TAILSLEAKCALE.CPV1 | PA30741HH | n/a | n/a | n/a | TAILSC LINE DIFF ALARM |  | TAILSC LINE DIFF ALARM |  | 0.0 | 10.0 | % |  |  |  | 0 |  | 0 |  | 10 |  | 10 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | SEC
TAILSLEAKCALE.CPV2 | PA30739HH | n/a | n/a | n/a | TAILSB LINE DIFF ALARM |  | TAILSB LINE DIFF ALARM |  | 0.0 | 10.0 | % |  |  |  | 0 |  | 0 |  | 10 |  | 10 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | SEC
FI30742D | FA30742CTP | n/a | n/a | n/a | TAILSA DIFF ALRM COUNT |  | TAILSA DIFF ALRM COUNT |  | 0.000 | 1000000.000 | % |  |  |  | 0 |  | 0 |  | 1000000 |  | 1000000 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | NO
FI30738D | FA30738CTP | n/a | n/a | n/a | TAILSB DIFF ALRM COUNT |  | TAILSB DIFF ALRM COUNT |  | 0.00 | 1000000.00 | % |  |  |  | 0 |  | 0 |  | 1000000 |  | 1000000 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | NO
FI30743D | FA30743CTP | n/a | n/a | n/a | TAILSC DIFF ALRM COUNT |  | TAILSC DIFF ALRM COUNT |  | 0.0 | 1000000.0 | % |  |  |  | 0 |  | 0 |  | 1000000 |  | 1000000 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | NO
PI30739D | PA30740CTP | n/a | n/a | n/a | TAILSA DIFF ALRM COUNT |  | TAILSA DIFF ALRM COUNT |  | 0.0 | 1000000.0 | % |  |  |  | 0 |  | 0 |  | 1000000 |  | 1000000 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | NO
PI30740D | PA30739CTP | n/a | n/a | n/a | TAILSB DIFF ALRM COUNT |  | TAILSB DIFF ALRM COUNT |  | 0.0 | 1000000.0 | % |  |  |  | 0 |  | 0 |  | 1000000 |  | 1000000 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | NO
PI30741D | PA30741CTP | n/a | n/a | n/a | TAILSC DIFF ALRM COUNT |  | TAILSC DIFF ALRM COUNT |  | 0.0 | 1000000.0 | % |  |  |  | 0 |  | 0 |  | 1000000 |  | 1000000 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | NO
FI30742D PI30740D | FPA30741CTP | n/a | n/a | n/a | TAILSA DIFF ALRM COUNT |  | TAILSA DIFF ALRM COUNT |  | 0.0 | 1000000.0 | % |  |  |  | 0 |  | 0 |  | 1000000 |  | 1000000 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | NO
FI30738D PI30739D | FPA30739CTP | n/a | n/a | n/a | TAILSB DIFF ALRM COUNT |  | TAILSB DIFF ALRM COUNT |  | 0.0 | 1000000.0 | % |  |  |  | 0 |  | 0 |  | 1000000 |  | 1000000 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | NO
FI30743D PI30741D | FPA30744CTP | n/a | n/a | n/a | TAILSC DIFF ALRM COUNT |  | TAILSC DIFF ALRM COUNT |  | 0.0 | 1000000.0 | % |  |  |  | 0 |  | 0 |  | 1000000 |  | 1000000 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | NO
TAILSLEAKCALF.CPV | FPA30741HH | n/a | n/a | n/a | TAILSA LINE DIFF ALARM |  | TAILSA LINE DIFF ALARM |  | 0.0 | 10.0 | % |  |  |  | 0 |  | 0 |  | 10 |  | 10 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | SEC
TAILSLEAKCALF.CPV1 | FPA30744HH | n/a | n/a | n/a | TAILSC LINE DIFF ALARM |  | TAILSC LINE DIFF ALARM |  | 0.0 | 10.0 | % |  |  |  | 0 |  | 0 |  | 10 |  | 10 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | SEC
TAILSLEAKCALF.CPV2 | FPA30739HH | n/a | n/a | n/a | TAILSB LINE DIFF ALARM |  | TAILSB LINE DIFF ALARM |  | 0.0 | 10.0 | % |  |  |  | 0 |  | 0 |  | 10 |  | 10 |  | Logging | Logging | Logging | Logging |  | 7 |  |  | 1 | SEC
%Z025116 | II75711 | 75PW71A | .GR0031 | 75-PI-1500 | 75PW71A Mtr Current |  | 75PW71A Mtr Current |  | 0.0 | 200.0 | AMPS |  |  |  | 0 |  | 0 |  | 150 |  | 200 |  | Medium | Medium | Medium | Medium |  | 2 |  |  | 1 | NO
%Z025102 | TI75710A | 75PW71A | .GR0032 | n/a | 75PW71A Mtr Temp - Red |  | 75PW71A Mtr Temp - Red |  | 0.0 | 200.0 | DEG |  |  |  | 0 |  | 0 |  | 100 |  | 120 |  | Medium | Medium | Medium | Medium |  | 2 |  |  | 1 | NO
%Z025103 | TI75710B | 75PW71A | .GR0032 | n/a | 75PW71A Mtr Temp - White |  | 75PW71A Mtr Temp - White |  | 0.0 | 200.0 | DEG |  |  |  | 0 |  | 0 |  | 100 |  | 120 |  | Medium | Medium | Medium | Medium |  | 2 |  |  | 1 | NO
%Z025104 | TI75710C | 75PW71A | .GR0032 | n/a | 75PW71A Mtr Temp - Blue |  | 75PW71A Mtr Temp - Blue |  | 0.0 | 200.0 | DEG |  |  |  | 0 |  | 0 |  | 100 |  | 120 |  | Medium | Medium | Medium | Medium |  | 2 |  |  | 1 | NO
%Z025115 | II75709 | 75PW71B | .GR0032 | 75-PI-1500 | 75PW71B Mtr Current |  | 75PW71B Mtr Current |  | 0.0 | 200.0 | AMPS |  |  |  | 0 |  | 0 |  | 200 |  | 200 |  | Medium | Medium | Medium | Medium |  | 2 |  |  | 1 | NO
%Z025105 | TI75708A | 75PW71B | .GR0032 | n/a | 75PW71B Mtr Temp - Red |  | 75PW71B Mtr Temp - Red |  | 0.0 | 200.0 | DEG |  |  |  | 0 |  | 0 |  | 145 |  | 155 |  | Medium | Medium | Medium | Medium |  | 2 |  |  | 1 | NO
%Z025106 | TI75708B | 75PW71B | .GR0032 | n/a | 75PW71B Mtr Temp - White |  | 75PW71B Mtr Temp - White |  | 0.0 | 200.0 | DEG |  |  |  | 0 |  | 0 |  | 145 |  | 155 |  | Medium | Medium | Medium | Medium |  | 2 |  |  | 1 | NO
%Z025107 | TI75708C | 75PW71B | .GR0032 | n/a | 75PW71B Mtr Temp - Blue |  | 75PW71B Mtr Temp - Blue |  | 0.0 | 200.0 | DEG |  |  |  | 0 |  | 0 |  | 145 |  | 155 |  | Medium | Medium | Medium | Medium |  | 2 |  |  | 1 | NO
%Z025101 | PDI75721 | n/a | .GR0031 | 75-PI-1500 | FluidisWtrFiltDiff Press |  | FluidisWtrFiltDiff Press |  | 0.0 | 200.0 | KPA |  |  |  | 0 |  | 0 |  | 15 |  | 20 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z072102 | SI30785 | 30CS61A | .GR0340 | n/a | Tails Sampler Prim Speed |  | Tails Sampler Prim Speed |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z072103 | II30786 | 30CS61A | .GR0340 | n/a | Tails Sampler Prim Amps |  | Tails Sampler Prim Amps |  | 0.0 | 10.0 | AMPS |  |  |  | 0 |  | 0 |  | 20 |  | 20 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z072104 | LI30782 | 30HP75 | .GR0340 | n/a | Tails Smplr Prim Hpr Lvl |  | Tails Smpler Prim Hpr Lvl |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z022101 | JQ30325 | 30AG32A | GR0320 | n/a | CIL2 Agitatr30AG32A |  | CIL2 Agitatr30AG32A |  | 0.0 | 100.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z022102 | JQ30326 | 30AG32B | GR0320 | n/a | CIL2 Agitatr30AG32B |  | CIL2 Agitatr30AG32B |  | 0.0 | 100.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z022104 | JQ30328 | 30AG32D | GR0320 | n/a | CIL2 Agitatr30AG32D |  | CIL2 Agitatr30AG32D |  | 0.0 | 100.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z022106 | JQ30330 | 30AG32F | GR0320 | n/a | CIL2 Agitatr30AG32F |  | CIL2 Agitatr30AG32F |  | 0.0 | 100.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  | Medium | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z022105 | JQ30329 | 30AG32E | GR0320 | n/a | CIL2 Agitatr30AG32E | CIL2 Agitatr30AG32E |  | 0.0 | 100.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z022103 | JQ30327 | 30AG32C | GR0320 | n/a | CIL2 Agitatr30AG32C | CIL2 Agitatr30AG32C |  | 0.0 | 100.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
JQ30744CMUL.CPV | JQ30744C | 30PP62C | GR0341 | n/a | FTails Pump C Motor | FTails Pump C Motor |  | 0.0 | 450.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
JQ3086BMUL.CPV | JQ3086B | 30PP62D | GR0341 | n/a | FTails Pump D Motor | FTails Pump D Motor |  | 0.0 | 450.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z062101 | JQ30625 | 30AG62A | GR0330 | n/a | CIL3 Agitatr30AG62A | CIL3 Agitatr30AG62A |  | 0.0 | 100.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z062102 | JQ30626 | 30AG62B | GR0330 | n/a | CIL3 Agitatr30AG62B | CIL3 Agitatr30AG62B |  | 0.0 | 100.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z062103 | JQ30627 | 30AG62C | GR0330 | n/a | CIL3 Agitatr30AG62C | CIL3 Agitatr30AG62C |  | 0.0 | 100.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z062104 | JQ30628 | 30AG62D | GR0330 | n/a | CIL3 Agitatr30AG62D | CIL3 Agitatr30AG62D |  | 0.0 | 100.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z062105 | JQ30629 | 30AG62E | GR0330 | n/a | CIL3 Agitatr30AG62E | CIL3 Agitatr30AG62E |  | 0.0 | 100.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z062106 | JQ30630 | 30AG62F | GR0330 | n/a | CIL3 Agitatr30AG62F | CIL3 Agitatr30AG62F |  | 0.0 | 100.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z025112 | JQ65339 | 65PP70 | GR0649 | n/a | 65PP70 Motor | 65PP70 Motor |  | 0.0 | 100.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
JQ30744AMUL.CPV | JQ30744A | 30PP62A | GR0341 | n/a | FTails Pump A Motor | FTails Pump A Motor |  | 0.0 | 450.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
JQ30744BMUL.CPV | JQ30744B | 30PP62B | GR0341 | n/a | FTails Pump B Motor | FTails Pump B Motor |  | 0.0 | 450.0 | KW |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | HOUR
%Z063113 | SI30745 | 30PP62C | .GR0341 | n/a | FTails Pmp CMotorSpeedIn | FTails Pmp CMotorSpeedIn |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%Z062107 | II30744A | 30PP62A | .GR0341 | 30-PI-1011 | FTails Pmp AMotor Amps | FTails Pmp AMotor Amps |  | 0.0 | 687.0 | AMPS |  |  |  | 0 |  | 0 |  | 687 |  | 687 |  |  | Low |  | Low | Low | Low |  | 4 |  |  | 1 | NO
%Z062108 | II30744B | 30PP62B | .GR0341 | 30-PI-1011 | FTails Pmp BMotor Amps | FTails Pmp BMotor Amps |  | 0.0 | 687.0 | AMPS |  |  |  | 0 |  | 0 |  | 687 |  | 687 |  |  | Low |  | Low | Low | Low |  | 4 |  |  | 1 | NO
%Z062109 %Z065116 | II30744C SI30745B | 30PP62C 30PP62B | .GR0341 .GR0341 | 30-PI-1011 n/a | FTails Pmp CMotor Amps FTails Pmp BMotorSpeedIn | FTails Pmp CMotor Amps FTails Pmp BMotorSpeedIn |  | 0.0 0.0 | 687.0 100.0 | AMPS % |  |  |  | 0 0 |  | 0 0 |  | 687 100 |  | 8 1 | 00 00 |  | L | Low ogging | Low Logging | Low Logging | Low Logging |  | 4 4 |  |  | 1 1 | NO NO
%Z072106 | FI30727C | 30PP62C | .GR0341 | 30-PI-1011 | FTails Pmp C Gland Flow | FTails Pmp C Gland Flow |  | 0.0 | 100.0 | L/MIN |  |  |  | 10 |  | 15 |  | 35 |  |  | 45 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z065115 | SI30745A | 30PP62A | .GR0341 | n/a | FTails Pmp AMotorSpeedIn | FTails Pmp AMotorSpeedIn |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 1 | 00 i | e | L | ogging | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%Z061104 | LI30719A | TK63 | .GR0341 | n/a | FTails Tank Level Radar | FTails Tank Level Radar |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 1 | 00 |  | L | ogging | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%Z063103 | LI30719 | TK63 | .GR0341 | 30-PI-1011 | FTails Tank Level USonic | FTails Tank Level USonic |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 1 | H 00 | s | L | ogging | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%Z065113 | SI30745D | 30PP62D | .GR0341 | n/a | FTails Pmp DMotorSpeedIn | FTails Pmp DMotorSpeedIn |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 1 | 00 i | i | L | ogging | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%Z072112 | II30777 | 30PP62A | .GR0341 | 30-PI-1011 | TailsGlndPmpA Motor Amps | TailsGlndPmpA Motor Amps |  | 0.0 | 10.0 | AMPS |  |  |  | 0 |  | 0 |  | 10 |  |  | 10 | v | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z072115 | II30781 | 30PP62B | .GR0341 | 30-PI-1011 | TailsGlndPmpB Motor Amps | TailsGlndPmpB Motor Amps |  | 0.0 | 10.0 | AMPS |  |  |  | 0 |  | 0 |  | 10 |  |  | 10 H |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z072111 | SI30777 | 30PP62A | .GR0341 | 30-PI-1011 | TailsGlndPmpA Motor Spd | TailsGlndPmpA Motor Spd |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 1 | 00 | e | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z072114 | SI30781 | 30PP62B | .GR0341 | 30-PI-1011 | TailsGlndPmpB Motor Spd | TailsGlndPmpB Motor Spd |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 1 | 00 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z024103 | AI30371A | n/a | GR0800 | n/a | HCN Monitor Elution | HCN Monitor Elution |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | 25 d | r | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z024104 | AI30371B | n/a | GR0800 | n/a | HCN Monitor Elution | HCN Monitor Elution |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | 25 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z024105 | AI30371C | n/a | GR0800 | n/a | HCN Monitor Elution | HCN Monitor Elution |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | 25 n | e | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z024108 | AI30371D | n/a | GR0800 | n/a | HCN Monitor Elution | HCN Monitor Elution |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | 25 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z021105 | AI30372A | TK32A | GR0800 | n/a | HCN Monitor CIL2 Tk32A | HCN Monitor CIL2 Tk32A |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | 25 a | s | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z021110 | AI30372B | TK32B | GR0800 | n/a | HCN Monitor CIL2 Tk32B | HCN Monitor CIL2 Tk32B |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | 25 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z021116 | AI30372C | TK32F | GR0800 | n/a | HCN Monitor CIL2 Tk32F | HCN Monitor CIL2 Tk32F |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | 25 i | a | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051108 | AI30671A | TK62A | GR0800 | n/a | HCN Monitor CIL3 Tk62A | HCN Monitor CIL3 Tk62A |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | 25 | e | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051109 | AI30671B | TK62B | GR0800 | n/a | HCN Monitor CIL3 Tk62B | HCN Monitor CIL3 Tk62B |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | H 25 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051110 | AI30671C | TK62F | GR0800 | n/a | HCN Monitor CIL3 Tk62F | HCN Monitor CIL3 Tk62F |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | 25 | l | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051111 | AI30672D | n/a | GR0800 | n/a | HCN Monitor Carb Screen | HCN Monitor Carb Screen |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | 25 | P | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051112 | AI30672A | n/a | GR0800 | n/a | HCN Monitor Carb Screen | HCN Monitor Carb Screen |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | e 25 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051113 | AI30672B | n/a | GR0800 | n/a | HCN Monitor Carb Screen | HCN Monitor Carb Screen |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | 25 r |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z051114 | AI30672C | n/a | GR0800 | n/a | HCN Monitor Carb Screen | HCN Monitor Carb Screen |  | 0.0 | 25.0 | ppm |  |  |  | 0 |  | 0 |  | 10 |  |  | 25 | . | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,1] | AI651022A | n/a | GR0718 | n/a | Kiln 3/4 Feed Mercury | Kiln 3/4 Feed Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | e 75 | t | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,2] | AI651022B | n/a | GR0718 | n/a | Kiln 3/4 Centre Mercury | Kiln 3/4 Centre Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 h | n | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,3] | AI651022C | n/a | GR0718 | n/a | Kiln 3/4 Dschrg Mercury | Kiln 3/4 Dschrg Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 | i | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,4] | AI651022D | n/a | GR0718 | n/a | Kiln 4 Mercury | Kiln 4 Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,5] | AI651022E | n/a | GR0718 | n/a | Kiln 3 Mercury | Kiln 3 Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | w 75 | o | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,6] | AI651022F | n/a | GR0718 | n/a | Scrbr Lvl 2 Mercury | Scrbr Lvl 2 Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,7] | AI651022G | n/a | GR0718 | n/a | Scrbr Lvl 3 Mercury | Scrbr Lvl 3 Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 | p | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,8] | AI651022H | n/a | GR0718 | n/a | Mercury Cabinet | Mercury Cabinet |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | e 75 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,9] | AI651022I | n/a | GR0718 | n/a | Kiln 3/4 Platfrm Mercury | Kiln 3/4 Platfrm Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 c | e | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,10] | AI651022J | n/a | GR0718 | n/a | Rd Hpr Dschrg Mercury | Rd Hpr Dschrg Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,11] | AI651022K | n/a | GR0718 | n/a | Kiln 3 Dewtr Mercury | Kiln 3 Dewtr Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 n |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,12] | AI651022L | n/a | GR0718 | n/a | Kiln 4 Dewtr Mercury | Kiln 4 Dewtr Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 | m | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,13] | AI651022M | n/a | n/a | n/a | nknown location Mercury (possible spare | Unknown location Mercury (possible spare?) |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 a |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,14] | AI651022N | n/a | n/a | n/a | nknown location Mercury (possible spare | Unknown location Mercury (possible spare?) |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 t | a | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,15] | AI651022O | n/a | n/a | n/a | nknown location Mercury (possible spare | Unknown location Mercury (possible spare?) |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[1,16] | AI651022P | n/a | n/a | n/a | nknown location Mercury (possible spare | Unknown location Mercury (possible spare?) |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 s | s | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,1] | AI78151A | n/a | GR0179 | n/a | Crbn Filt ID Fan Mercury | Crbn Filt ID Fan Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 n |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,2] | AI78151B | n/a | GR0179 | n/a | RTO ID Fans Mercury | RTO ID Fans Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 | e | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,3] | AI78151C | n/a | GR0179 | n/a | RTO Feed Fans Mercury | RTO Feed Fans Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 i |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,4] | AI78151D | n/a | GR0179 | n/a | RTO Inlet Mercury | RTO Inlet Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 | h | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,5] | AI78151E | n/a | GR0179 | n/a | Crbn Filters Mercury | Crbn Filters Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 e |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,6] | AI78151F | n/a | GR0179 | n/a | Sub 78 Mercury | Sub 78 Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 l | t | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,7] | AI78151G | n/a | GR0179 | n/a | Kiln 5 Centre Mercury | Kiln 5 Centre Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 | t | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,8] | AI78151H | n/a | GR0179 | n/a | Kiln 5 Feed Mecury | Kiln 5 Feed Mecury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | p 75 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,9] | AI78151I | n/a | GR0179 | n/a | Kiln 5 Dschrg Mercury | Kiln 5 Dschrg Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 i | a | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,10] | AI78151J | n/a | GR0179 | n/a | Kiln 5 Platform Mercury | Kiln 5 Platform Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 t |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,11] | AI78151K | n/a | GR0179 | n/a | Dewtr Dschrg Mercury | Dewtr Dschrg Mercury |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 l |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,12] | AI78151L | n/a | n/a | n/a | nknown location Mercury (possible spare | Unknown location Mercury (possible spare?) |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 u | e | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,13] | AI78151M | n/a | n/a | n/a | nknown location Mercury (possible spare | Unknown location Mercury (possible spare?) |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 | r | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,14] | AI78151N | n/a | n/a | n/a | nknown location Mercury (possible spare | Unknown location Mercury (possible spare?) |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | M 75 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,15] | AI78151O | n/a | n/a | n/a | nknown location Mercury (possible spare | Unknown location Mercury (possible spare?) |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 | a | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[2,16] | AI78151P | n/a | n/a | n/a | nknown location Mercury (possible spare | Unknown location Mercury (possible spare?) |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  |  | 75 |  | M | edium | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[3,1] MERCURYSFC.MERCURY[3,2] | AI66858A AI66858B | n/a n/a | GR0720 GR0720 | n/a n/a | Retort Room Entrance Retort Carbon Column Dis | Retort Room Entrance Retort Carbon Column Dis |  | 0.0 0.0 | 100.0 100.0 | ug/M3 ug/M3 |  |  |  | 0 0 |  | 0 0 |  | 25 25 |  | 75 75 |  |  | Medium Medium |  | Medium Medium | Medium Medium | Medium Medium |  | 4 4 |  |  | 1 1 | NO NO
MERCURYSFC.MERCURY[3,3] | AI66858C | n/a | GR0720 | n/a | Retort Room Rear | Retort Room Rear |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  | 75 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[3,4] | AI66858D | n/a | GR0720 | n/a | Mixing Station | Mixing Station |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  | 75 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[3,5] | AI66858E | n/a | GR0720 | n/a | Slag Tray | Slag Tray |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  | 75 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[3,6] | AI66858F | n/a | GR0720 | n/a | Cathode Wash Bay | Cathode Wash Bay |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  | 75 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[3,7] | AI66858G | n/a | GR0720 | n/a | Mezzanine Level | Mezzanine Level |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  | 75 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[3,8] | AI66858H | n/a | GR0720 | n/a | Carbon Filter Discharge | Carbon Filter Discharge |  | 0.0 | 100.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  | 75 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
MERCURYSFC.MERCURY[3,1] | AI66816 | n/a | .GR0693 | n/a | Retort Room Entrance | Retort Room Entrance |  | 0.0 | 1000.0 | ug/M3 |  |  |  | 0 |  | 0 |  | 25 |  | 75 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0041 | VI30969B | 30PP77A | GR0734 | n/a | NDE VIBRATION PP77A | NDE VIBRATION PP77A |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 25.3999996 |  | 25.3999996 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0039 | VI30969A | 30PP77A | GR0734 | n/a | DE VIBRATION PP77A | DE VIBRATION PP77A |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 25.3999996 |  | 25.3999996 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0045 | VI30976B | 30PP77B | GR0734 | n/a | NDE SPM PP77B | NDE SPM PP77B |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 25.3999996 |  | 25.3999996 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0043 | VI30976A | 30PP77B | GR0734 | n/a | DE SPM PP77B | DE SPM PP77B |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 25.3999996 |  | 25.3999996 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0049 | VI30977B | 30PP77B | GR0734 | n/a | NDE VIBRATION PP77B | NDE VIBRATION PP77B |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 25.3999996 |  | 25.3999996 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0047 | VI30977A | 30PP77B | GR0734 | n/a | DE VIBRATION PP77B | DE VIBRATION PP77B |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 25.3999996 |  | 25.3999996 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0053 | VI30975B | 30PP77A | GR0734 | n/a | NDE VIBRATION GEARBOX PP | NDE VIBRATION GEARBOX PP |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 25.3999996 |  | 25.3999996 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0051 | VI30975A | 30PP77A | GR0734 | n/a | DE VIBRATION GEARBOX PP7 | DE VIBRATION GEARBOX PP7 |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 25.3999996 |  | 25.3999996 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0029 | PI30904 | 30PP77A | GR0731 | 75-PI-5301 | DSCH PRESSURE F30-PP77A | DSCH PRESSURE F30-PP77A |  | 0.0 | 1900.0 | KPA |  |  |  | 0 |  | 0 |  | 1900 |  | 1900 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0027 | PI30902 | 30PP77A | GR0731 | 75-PI-5301 | SUCT PRESSURE F30-PP77A | SUCT PRESSURE F30-PP77A |  | -100.0 | 1000.0 | KPA |  |  |  | 150 |  | 180 |  | 1000 |  | 1000 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0033 | PI30903 | 30PP77B | GR0731 | 75-PI-5301 | SUCT PRESSURE F30-PP77B | SUCT PRESSURE F30-PP77B |  | -100.0 | 1000.0 | KPA |  |  |  | 150 |  | 180 |  | 1000 |  | 1000 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%WW0031 | FI30908 | 30PP77A | GR0731 | 75-PI-5301 | FLOW METER F30-PP77A | FLOW METER F30-PP77A |  | 0.0 | 1500.0 | M3/H |  |  |  | 0 |  | 0 |  | 1500 |  | 1500 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0037 | FI30909 | 30PP77B | GR0731 | 75-PI-5301 | FLOW METER F30-PP77B | FLOW METER F30-PP77B |  | 0.0 | 1500.0 | M3/H |  |  |  | 0 |  | 0 |  | 1500 |  | 1500 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0035 | PI30905 | 30PP77B | GR0731 | 75-PI-5301 | DSCH PRESSURE F30-PP77B | DSCH PRESSURE F30-PP77B |  | 0.0 | 1900.0 | KPA |  |  |  | 0 |  | 0 |  | 1900 |  | 1900 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%WW0057 | VI30983B | 30PP77B | GR0734 | 75-PI-5308 | NDE VIBRATN GEARBX PP77B | NDE VIBRATN GEARBX PP77B |  | 0.0 | 100.0 | MM/S |  |  |  | 0 |  | 0 |  | 6 |  | 8 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0055 | VI30983A | 30PP77B | GR0734 | 75-PI-5308 | DE VIBRATION G/BOX PP77B | DE VIBRATION G/BOX PP77B |  | 0.0 | 100.0 | MM/S |  |  |  | 0 |  | 0 |  | 6 |  | 8 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0061 | TI30971B | 30PP77A | GR0734 | 75-PI-5308 | NDE TEMPMOT BEARNG PP77A | NDE TEMPMOT BEARNG PP77A |  | -50.0 | 150.0 | DEGC |  |  |  | -50 |  | -50 |  | 90 |  | 95 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0059 | TI30971A | 30PP77B | GR0734 | 75-PI-5308 | DE SPM PP77B | DE SPM PP77B |  | -50.0 | 150.0 | DEGC |  |  |  | -50 |  | -50 |  | 90 |  | 95 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0063 | TI30972 | 30PP77A | GR0734 | 75-PI-5308 | GBOX BEARNG TEMP PP77A | GBOX BEARNG TEMP PP77A |  | -50.0 | 150.0 | DEGC |  |  |  | -50 |  | -50 |  | 90 |  | 95 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0069 | TI30979B | 30PP77B | GR0734 | 75-PI-5308 | NDETEMP MOT BEARNG PP77B | NDETEMP MOT BEARNG PP77B |  | -50.0 | 150.0 | DEGC |  |  |  | -50 |  | -50 |  | 90 |  | 95 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0067 | TI30979A | 30PP77B | GR0734 | 75-PI-5308 | DE TEMP MOT BEARNG PP77B | DE TEMP MOT BEARNG PP77B |  | -50.0 | 150.0 | DEGC |  |  |  | -50 |  | -50 |  | 90 |  | 95 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0071 | TI30980 | 30PP77B | GR0734 | 75-PI-5308 | GBOX BEARNG TEMP PP77B | GBOX BEARNG TEMP PP77B |  | -50.0 | 150.0 | DEGC |  |  |  | -50 |  | -50 |  | 90 |  | 95 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0077 | FI30921 | 30PP77A | GR0733 | 75-PI-5303 | SEAL WATER FLOW PP-77A | SEAL WATER FLOW PP-77A |  | 0.0 | 50.0 | L/M |  |  |  | 8 |  | 10 |  | 30 |  | 35 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0075 | PI30920 | 30PP77A/B | GR0733 | 75-PI-5303 | SEAL WATER PRESSURE | SEAL WATER PRESSURE |  | 0.0 | 2000.0 | KPA |  |  |  | -75 |  | -50 |  | 150 |  | 200 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0081 | LI30912 | n/a | .GR0731 .GR0735 | 75-PI-5301 | LEVEL SUMP | LEVEL SUMP |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0079 | FI30922 | 30PP77B | GR0733 | n/a | SEAL WATER FLOW PP-77B | SEAL WATER FLOW PP-77B |  | 0.0 | 50.0 | L/M |  |  |  | 8 |  | 10 |  | 30 |  | 35 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0083 | LI30915 | F30TK77 | GR0732 | 75-PI-5303 | FIM 2 SEAL WATER TK LVL | FIM 2 SEAL WATER TK LVL |  | 0.0 | 100.0 | % |  |  |  | 10 |  | 70 |  | 97 |  | 99 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0241 | VI30985B | 30PP78A | GR0744 | 75-PI-5309 | NDE VIBRATION PP78A | NDE VIBRATION PP78A |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 6 |  | 8 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0239 | VI30985A | 30PP78A | GR0744 | 75-PI-5309 | DE VIBRATION PP78A | DE VIBRATION PP78A |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 6 |  | 8 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0245 | VI30992B | 30PP78B | GR0744 | 75-PI-5309 | NDE SPM PP78B | NDE SPM PP78B |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 6 |  | 8 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0243 | VI30992A | 30PP78B | GR0744 | 75-PI-5309 | DE SPM PP78B | DE SPM PP78B |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 6 |  | 8 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0249 | VI30993B | 30PP78B | GR0744 | 75-PI-5309 | NDE VIBRATION PP78B | NDE VIBRATION PP78B |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 6 |  | 8 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0247 | VI30993A | 30PP78B | GR0744 | 75-PI-5309 | DE VIBRATION PP78B | DE VIBRATION PP78B |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 6 |  | 8 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0253 | VI30991B | 30PP78A | GR0744 | 75-PI-5308 | NDE VIBRATION GEARBOX PP | NDE VIBRATION GEARBOX PP |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 6 |  | 8 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0251 | VI30991A | 30PP78A | GR0744 | 75-PI-5308 | DE VIBRATION GBOX PP78A | DE VIBRATION GBOX PP78A |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 6 |  | 8 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0229 | PI30936 | 30PP78A | GR0741 | 75-PI-5302 | DSCH PRESSURE F30-PP78A | DSCH PRESSURE F30-PP78A |  | 0.0 | 1900.0 | KPA |  |  |  | 0 |  | 0 |  | 1400 |  | 1550 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%WW0227 | PI30934 | 30PP78A | GR0741 | 75-PI-5302 | SUCT PRESSURE F30-PP78A | SUCT PRESSURE F30-PP78A |  | -100.0 | 1000.0 | KPA |  |  |  | 150 |  | 180 |  | 1000 |  | 1000 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%WW0233 | PI30935 | 30PP78B | GR0741 | 75-PI-5302 | SUCT PRESSURE F30-PP78B | SUCT PRESSURE F30-PP78B |  | -100.0 | 1000.0 | KPA |  |  |  | 150 |  | 180 |  | 1000 |  | 1000 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%WW0231 | FI30940 | 30PP78A | GR0741 .GR0744 .GR0745 | 75-PI-5302 | FLOW METER F30-PP78A | FLOW METER F30-PP78A |  | 0.0 | 1500.0 | M3/H |  |  |  | 0 |  | 0 |  | 1500 |  | 1500 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0237 | FI30941 | 30PP78B | GR0741 .GR0744 .GR0745 | 75-PI-5302 | FLOW METER F30-PP78B | FLOW METER F30-PP78B |  | 0.0 | 1500.0 | M3/H |  |  |  | 0 |  | 0 |  | 1500 |  | 1500 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0235 | PI30937 | 30PP78B | GR0741 | 75-PI-5302 | DSCH PRESSURE F30-PP78B | DSCH PRESSURE F30-PP78B |  | 0.0 | 1900.0 | KPA |  |  |  | 0 |  | 0 |  | 1900 |  | 1900 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%WW0257 | VI30999B | 30PP78B | GR0744 | 75-PI-5309 | NDE VIBRATN GBOX PP78B | NDE VIBRATN GBOX PP78B |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 6 |  | 8 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0255 | VI30999A | 30PP78B | GR0744 | 75-PI-5309 | DE VIB GBOX PP78B | DE VIB GBOX PP78B |  | 0.0 | 25.4 | MM/S |  |  |  | 0 |  | 0 |  | 6 |  | 8 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0261 | TI30987B | 30PP78A | GR0744 | 75-PI-5309 | NDE TEMP MT. BRNG PP78A | NDE TEMP MT. BRNG PP78A |  | -50.0 | 150.0 | DEGC |  |  |  | 0 |  | 0 |  | 90 |  | 95 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0259 | TI30987A | 30PP78B | GR0744 | 75-PI-5309 | DE SPM PP78B | DE SPM PP78B |  | -50.0 | 150.0 | DEGC |  |  |  | 0 |  | 0 |  | 90 |  | 95 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0263 | TI30988 | 30PP78A | GR0744 | 75-PI-5309 | DETEMP GBOX BEARNG PP78A | DETEMP GBOX BEARNG PP78A |  | -50.0 | 150.0 | DEGC |  |  |  | 0 |  | 0 |  | 90 |  | 95 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0269 | TI30995B | 30PP78B | GR0744 | 75-PI-5309 | NDETEMP MOT BEARNG PP78B | NDETEMP MOT BEARNG PP78B |  | -50.0 | 150.0 | DEGC |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0267 | TI30995A | 30PP78B | GR0744 | 75-PI-5309 | DE TEMP MOT BEARNG PP78B | DE TEMP MOT BEARNG PP78B |  | -50.0 | 150.0 | DEGC |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0271 | TI30996 | 30PP78A | GR0744 | 75-PI-5309 | DE TEMP GBOX BRNG PP78A | DE TEMP GBOX BRNG PP78A |  | -50.0 | 150.0 | DEGC |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0277 | FI30953 | 30PP78A | GR0743 | 75-PI-5304 | SEAL WATER FLOW PP-78A | SEAL WATER FLOW PP-78A |  | 0.0 | 50.0 | L/M |  |  |  | 8 |  | 10 |  | 28 |  | 30 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0275 | PI30952 | 30PP78A/B | GR0743 | 75-PI-5304 | SEAL WATER PRESSURE | SEAL WATER PRESSURE |  | 0.0 | 2000.0 | KPA |  |  |  | -75 |  | -50 |  | 150 |  | 200 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%WW0281 | LI30944 | n/a | GR0741 .GR0745 | 75-PI-5302 | LEVEL SUMP | LEVEL SUMP |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0279 | FI30954 | 30PP78B | GR0743 | 75-PI-5304 | SEAL WATER FLOW PP-78B | SEAL WATER FLOW PP-78B |  | 0.0 | 50.0 | L/M |  |  |  | 8 |  | 10 |  | 28 |  | 30 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%WW0283 | LI30947 | F30TK78 | GR0742 | 75-PI-5304 | KALTAILS SEAL WTR TK LVL | KALTAILS SEAL WTR TK LVL |  | 0.0 | 100.0 | % |  |  |  | 40 |  | 70 |  | 100 |  | 100 |  |  | High |  | High | High | High |  | 4 |  |  | 1 | NO
%WW0431 | PI30XXX | n/a | n/a | n/a | KT Amiad Inlet Pressure | KT Amiad Inlet Pressure |  | 0.0 | 100.0 | KPA |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%WW0433 | PI30XX2 | n/a | n/a | n/a | KT Amiad Outlet Pressure | KT Amiad Outlet Pressure |  | 0.0 | 100.0 | KPA |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%WW0627 | PI301110 | n/a | GR0751 | n/a | FIM 1 Booster Sctn Press | FIM 1 Booster Sctn Press |  | -101.0 | 1670.0 | KPA |  |  |  | 50 |  | 75 |  | 1670 |  | 1670 |  |  | Medium |  | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%WW0629 | PI301111 | n/a | GR0751 | n/a | FIM 1 Booster Dsch Press | FIM 1 Booster Dsch Press |  | 0.0 | 1670.0 | KPA |  |  |  | 0 |  | 0 |  | 1300 |  | 1400 |  |  | Medium |  | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%WW0631 | PI301114 | 30PP79 | GR0751 | n/a | FIM 1 Boost Glnd Wtr Prs | FIM 1 Boost Glnd Wtr Prs |  | 0.0 | 2500.0 | KPA |  |  |  | 750 |  | 900 |  | 2500 |  | 2500 |  |  | Medium |  | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%WW0635 | FI301113 | 30PP79 | GR0751 | n/a | FIM 1 Boost Glnd Wtr Flw | FIM 1 Boost Glnd Wtr Flw |  | 0.0 | 50.0 | M3/H |  |  |  | 2 |  | 3 |  | 50 |  | 50 |  |  | Medium |  | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%WW0633 | LI75135 | F30TK78 | GR0751 | n/a | FIM 1 Boost Glnd Wtr Tk | FIM 1 Boost Glnd Wtr Tk |  | 0.0 | 100.0 | % |  |  |  | 10 |  | 40 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%WW0623 | SI30PP79 | 30PP79 | GR0751 | n/a | FIM 1 Boost Pmp Spd Fdbk | FIM 1 Boost Pmp Spd Fdbk |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%WW0625 | II30PP79 | 30PP79 | GR0751 | n/a | FIM 1 Booster Pump Amps | FIM 1 Booster Pump Amps |  | 0.0 | 941.0 | A |  |  |  | 0 |  | 0 |  | 941 |  | 941 |  |  | Medium |  | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%WW0637 | TI301115A | 30PP79 | GR0751 | n/a | FIM 1 Boost Wndg A Temp | FIM 1 Boost Wndg A Temp |  | -50.0 | 150.0 | DEGC |  |  |  | -50 |  | -50 |  | 100 |  | 150 |  |  | Medium |  | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%WW0639 | TI301115B | 30PP79 | GR0751 | n/a | FIM 1 Boost Wndg B Temp | FIM 1 Boost Wndg B Temp |  | -50.0 | 150.0 | DEGC |  |  |  | -50 |  | -50 |  | 100 |  | 150 |  |  | Medium |  | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%WW0641 | TI301115C | 30PP79 | GR0751 | n/a | FIM 1 Boost Wndg C Temp | FIM 1 Boost Wndg C Temp |  | -50.0 | 150.0 | DEGC |  |  |  | -50 |  | -50 |  | 100 |  | 150 |  |  | Medium |  | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%WW0643 | TI301115G | 30PP79 | GR0751 | n/a | FIM 1 Boost DE Brng Tmp | FIM 1 Boost DE Brng Tmp |  | -50.0 | 150.0 | DEGC |  |  |  | -50 |  | -50 |  | 80 |  | 150 |  |  | Medium |  | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%WW0645 | TI301115H | 30PP79 | GR0751 | n/a | FIM 1 Boost NDE Brng Tmp | FIM 1 Boost NDE Brng Tmp |  | -50.0 | 150.0 | DEGC |  |  |  | -50 |  | -50 |  | 80 |  | 150 |  |  | Medium |  | Medium | Medium | Medium |  | 3 |  |  | 1 | NO
%Z022116 | FI30342 | n/a | TRENDS 1 | n/a | Thk2 Bypass Flowmeter | Thk2 Bypass Flowmeter |  | 0.0 | 1000.0 | M3/H |  |  |  | 0 |  | 0 |  | 1000 |  | 1000 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z064114 | FI30641 | n/a | TRENDS 1 | n/a | Thk3 Bypass Flowmeter | Thk3 Bypass Flowmeter |  | 0.0 | 1000.0 | M3/H |  |  |  | 0 |  | 0 |  | 1000 |  | 1000 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z072105 | 30PP75AMPS | 30PP75 | GR0340 | 30-PI-1000 | CarbonRecov Pump AMPS | CarbonRecov Pump AMPS |  | 0.0 | 80.0 | AMPS |  |  |  | 0 |  | 0 |  | 80 |  | 80 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z025108 | AI30386 | n/a | n/a | n/a | CIL2 Wind Direction | CIL2 Wind Direction |  | 0.0 | 360.0 | DEG |  |  |  | 0 |  | 0 |  | 360 |  | 360 |  |  | Medium |  | Medium | Medium | Medium |  | 2 |  |  | 1 | NO
%Z025109 | AI30387 | n/a | n/a | n/a | CIL2 Wind Speed | CIL2 Wind Speed |  | 0.0 | 50.0 | M/S |  |  |  | 0 |  | 0 |  | 50 |  | 50 |  |  | Medium |  | Medium | Medium | Medium |  | 2 |  |  | 1 | NO
AI30387MUL.CPV | AI30387A | n/a | n/a | n/a | CIL2 Wind Speed | CIL2 Wind Speed |  | 0.0 | 180.0 | KM/H |  |  |  | 0 |  | 0 |  | 180 |  | 180 |  |  | Medium |  | Medium | Medium | Medium |  | 2 |  |  | 1 | NO
%Z022107 | PI25354 | 25CM31C | GR0051 | n/a | FLOTS AIR COMP 31C | FLOTS AIR COMP 31C |  | 0.0 | 1000.0 | KPA |  |  |  | 400 |  | 450 |  | 780 |  | 800 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z022101 | II30325 | 30AG32A | GR0320 | 30-PI-0313 | CIL2 Agitatr30AG32A Amps | CIL2 Agitatr30AG32A Amps |  | 0.0 | 150.0 | AMPS |  |  |  | 50 |  | 50 |  | 150 |  | 150 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z022102 | II30326 | 30AG32B | GR0320 | 30-PI-0313 | CIL2 Agitatr30AG32B Amps | CIL2 Agitatr30AG32B Amps |  | 0.00 | 150.00 | AMPS |  |  |  | 50 |  | 65 |  | 150 |  | 150 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z022103 | II30327 | 30AG32C | GR0320 | 30-PI-0313 | CIL2 Agitatr30AG32C Amps | CIL2 Agitatr30AG32C Amps |  | 0 | 150 | AMPS |  |  |  | 50 |  | 50 |  | 150 |  | 150 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z022104 | II30328 | 30AG32D | GR0320 | 30-PI-0313 | CIL2 Agitatr30AG32D Amps | CIL2 Agitatr30AG32D Amps |  | 0.000 | 150.000 | AMPS |  |  |  | 10 |  | 45 |  | 150 |  | 150 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z022105 | II30329 | 30AG32E | GR0320 | 30-PI-0313 | CIL2 Agitatr30AG32E Amps | CIL2 Agitatr30AG32E Amps |  | 0.0 | 150.0 | AMPS |  |  |  | 50 |  | 50 |  | 150 |  | 150 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z022106 | II30330 | 30AG32F | GR0320 | 30-PI-0313 | CIL2 Agitatr30AG32F Amps | CIL2 Agitatr30AG32F Amps |  | 0.00 | 150.00 | AMPS |  |  |  | 30 |  | 50 |  | 150 |  | 150 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z024110 | II30654 | 30SC34B | GR0320 | 30-PI-0313 | CIL2 Screen 30SC34B Amps | CIL2 Screen 30SC34B Amps |  | 0.00 | 75.00 | AMPS |  |  |  | 0 |  | 0 |  | 75 |  | 75 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z024111 | II30655 | 30SC34C | GR0320 | 30-PI-0313 | CIL2 Screen 30SC34C Amps | CIL2 Screen 30SC34C Amps |  | 0.0 | 75.0 | AMPS |  |  |  | 0 |  | 0 |  | 75 |  | 75 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z024112 | II30656 | 30SC34D | GR0320 | 30-PI-0313 | CIL2 Screen 30SC34D Amps | CIL2 Screen 30SC34D Amps |  | 0.0 | 75.0 | AMPS |  |  |  | 0 |  | 0 |  | 75 |  | 75 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z024113 | II30657 | 30SC34E | GR0320 | 30-PI-0313 | CIL2 Screen 30SC34E Amps | CIL2 Screen 30SC34E Amps |  | 0.0 | 75.0 | AMPS |  |  |  | 0 |  | 0 |  | 75 |  | 75 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z024114 | II30658 | 30SC34F | GR0320 | 30-PI-0313 | CIL2 Screen 30SC34F Amps | CIL2 Screen 30SC34F Amps |  | 0.0 | 75.0 | AMPS |  |  |  | 0 |  | 0 |  | 75 |  | 75 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
N/A | II30659 | 30SC34M | GR0320 | n/a | CIL2 Screen 30SC34M Amps | CIL2 Screen 30SC34M Amps |  | 0.0 | 75.0 | AMPS |  |  |  | 0 |  | 0 |  | 75 |  | 75 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
FI30615.PV | AI30631 | n/a | n/a | n/a |  | CIL3 Feed Flow |  | 0.0 | 1000.0 | M3/H |  |  |  | 0 |  | 0 |  | 950 |  | 1000 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
%Z065105 | LI75601 | 75TK61 | n/a | 75-PI-0461 | Cct Wtr Pp 75TK61 Level | Cct Wtr Pp 75TK61 Level |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
DYS010202CON.SV | STEVEMCL | n/a | n/a | n/a |  |  |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
04004PV02.PV | 05018PV02 | n/a | n/a | n/a |  |  |  | 0 | 65535 | (None) |  |  |  | 0 |  | 0 |  | 65535 |  | 65535 |  |  | User (8) |  | User (8) | User (8) | User (8) |  | 4 |  |  | 1 | NO
05018CI03.PV | 05018PV03 | n/a | n/a | n/a |  |  |  | 0.0 | 65535.0 | (None) |  |  |  | 0 |  | 0 |  | 65535 |  | 65535 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
03003PV03.PV | 05018PV04 | n/a | n/a | n/a |  |  |  | 0 | 65535 | (None) |  |  |  | 0 |  | 0 |  | 65535 |  | 65535 |  |  | User (8) |  | User (8) | User (8) | User (8) |  | 4 |  |  | 1 | NO
07021PV07.PV | 05018PV05 | n/a | n/a | n/a |  |  |  | 0 | 65535 | (None) |  |  |  | 0 |  | 0 |  | 65535 |  | 65535 |  |  | User (8) |  | User (8) | User (8) | User (8) |  | 4 |  |  | 1 | NO
05018CI06.PV | 05018PV06 | n/a | n/a | n/a |  |  |  | 0 | 65535 | (None) |  |  |  | 0 |  | 0 |  | 65535 |  | 65535 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
05018CI08.PV | 05018PV08 | n/a | n/a | n/a |  |  |  | 0 | 65535 | (None) |  |  |  | 0 |  | 0 |  | 65535 |  | 65535 |  |  | Medium |  | Medium | Medium | Medium |  | 4 |  |  | 1 | NO
02060PV07.PV | 05018PV07 | n/a | n/a | n/a |  |  |  | 0 | 65535 | (None) |  |  |  | 0 |  | 0 |  | 65535 |  | 65535 |  |  | User (8) |  | User (8) | User (8) | User (8) |  | 4 |  |  | 1 | NO
%WW0099 | 30PP77ASTEPNO | n/a | n/a | n/a |  |  |  | 0.0 | 100.0 | (None) |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%WW0101 | 30PP77BSTEPNO | n/a | n/a | n/a |  |  |  | 0.0 | 100.0 | (None) |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%WW0299 | 30PP78ASTEPNO | n/a | .GR0743 | n/a |  |  |  | 0.0 | 100.0 | (None) |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%WW0301 | 30PP78BSTEPNO | n/a | n/a | n/a |  |  |  | 0.0 | 100.0 | (None) |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO
%WW0621 | 30PP79SEQNO | n/a | .GR0341 .GR0751 | n/a |  |  |  | 0.0 | 100.0 | % |  |  |  | 0 |  | 0 |  | 100 |  | 100 |  |  | Logging |  | Logging | Logging | Logging |  | 4 |  |  | 1 | NO

## 2. Analogue Output
KCGM GROWTH PROJECT
ANALOGUE OUTPUT
Range
Tag Source | Tag Name | Parent Equipment | P&ID | Abbreviated Description (Faceplate) | Trend (sec) | Min | Max | Unit | Comments | Rev
AO %Z021104 | FY30378 | AV30322 | 2000-F30-PID-PR-10005 | FC30378 OUTPUTTO FY30378 |  | 0 | 100 | % |  | 0
%Z061102 | AY30622 | AV30622 | 2000-F30-PID-PR-10008 | CIL3 Cyanide Flow Vlv |  | 0 | 100 | % |  | 0
%Z061106 | AY30620 | AV30620 | 2000-F30-PID-PR-10008 | CIL3 Lime Addn Vlv |  | 0 | 100 | % |  | 0
%Z062116 | FT30650 | FV30650 | 2000-F30-PID-PR-10001 | Thick #3 Dilute Valve |  | 0 | 100 | % |  | 0
%Z063105 | SY30746A | 30PP62A | 2000-F30-PID-PR-10014 | Tails Pp A Speed Output |  | 0 | 100 | % |  | 0
%Z063106 | SY30746B | 30PP62B | 2000-F30-PID-PR-10014 | Tails Pp B Speed Output |  | 0 | 100 | % |  | 0
%Z063107 | SY30746C | 30PP62C | 2000-F30-PID-PR-10014 | Tails Pp C Speed Output |  | 0 | 100 | % |  | 0
%Z063115 | SY30607A | 30PP61A | 2000-F30-PID-PR-10001 | FTailsThk3UFPpA Spd Out |  | 0 | 100 | % |  | 0
%Z063116 | SY30607B | 30PP61B | 2000-F30-PID-PR-10001 | FTailsThk3UFPpA Spd Out |  | 0 | 100 | % |  | 0
%Z064113 | FY30684 | 70PP21A/B | 2000-F30-PID-PR-10008 | CIL3 PBNO3 Addn Output |  | 0 | 100 | % |  | 0
%Z065112 | SY30745D | 30PP62D | n/a | FinalTailsPp30PP62DSpeed |  | 0 | 100 | % |  | 0
%Z072101 | SY30787 | 30SC61A | n/a | TailsSamplerPriCuttr Spd |  | 0 | 100 | % |  | 0
%Z072107 | FY30719 | FV30719 | n/a | Tails HopperWtr Addition |  | 0 | 100 | % |  | 0
%Z072113 | SY30779 | 75PW68A | n/a | FTails Gland Water Pump A Speed |  | 0 | 100 | % |  | 0
%Z072116 | SY30782 | 75PW68B | n/a | FTails Gland Water Pump B Speed |  | 0 | 100 | % |  | 0

## 3. Digital Input
KCGM GROWTH PROJECT
DIGITAL INPUT
DIGITAL INSTRUMENTS INPUT
Tag Source | Tag Name | Parent Equipment | Graphics | P&ID | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Source | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev
%Z023129 | 30XE63BYP | 30XE63 | GR0046 | N/A | Sub 38 UPS Bypass Swtch | NORMAL | BYPASS | BYPASS |  |  |  |  | Direct | 0
%Z023130 | 30XE63ALM | 30XE63 | GR0046 | N/A | Sub 38 UPS Fault Alarm | OK | FAULT | FAULT |  |  |  |  | Direct | 0
%Z023131 | 30XE63BLO | 30XE63 | GR0046 | N/A | Sub 38 UPS Battery Low | OK | LOW | LOW |  |  |  |  | Direct | 0
%Z023132 | 30XE63BON | 30XE63 | GR0046 | N/A | Sub 38 UPS Battery On | OFF | ON | ON |  |  |  |  | Direct | 0
%Z023418 | 75FI01ZSH | 70FI01 | n/a | 75-PI-1500 | 75FI01 Fwd Limit Switch | OFF | ON | n/a |  |  |  |  | Direct | 0
DI %Z023419 | 75FI01ZSL | 70FI01 | n/a | 75-PI-1500 | 75FI01 RvrseLimit Switch | OFF | ON | n/a |  |  |  |  | Direct | 0
%Z023427 | AIT30394E | n/a | n/a | N/A | CynProbe Critical Alm | OFF | ON | ON |  |  |  |  | Direct | 0
%Z023428 | AIT30394F | n/a | n/a | N/A | CynProbe Warning Alm | OFF | ON | ON |  |  |  |  | Direct | 0
%Z031423 | PSH81301DB | 81-RA-32 | GR0051 | N/A | Pressure Switch High | HI | OK | HI |  |  |  |  | Reverse | 0
%Z031424 | PSL81301DB | 81-RA-32 | GR0051 | N/A | Pressure Switch Low | HI | OK | HI |  |  |  |  | Reverse | 0
%Z031429 | LSHH30340 | 30PS31 | GR0320 | 30-PI-0313 | DRIVE LEVEL SWITCH HIGH | OFF | ON | ON |  |  |  |  | Direct | 0
%Z031432 | LSHH30341 | 30PS32A | GR0320 | 30-PI-0313 | DRIVE LEVEL SWITCH HIGH | OFF | ON | ON |  |  |  |  | Direct | 0
%Z032109 | TSH30370 | 30TR31 | n/a | N/A | TRANSFORMER Opn INPUT | OFF | ON | ON |  |  |  |  | Direct | 0
%Z032110 | TSHH30370 | 30TR31 | n/a | N/A | TRANSFORMER Cls INPUT | OFF | ON | ON |  |  |  |  | Direct | 0
%Z032123 | 30SW31EAV | 30SW31 | GR0044 | N/A | EMERG PWR AVAIL INPUT | NAVAIL | AVAIL | NAVAIL |  |  |  |  | Direct | 0
%Z032124 | 30SW31EBC | 30SW31 | GR0044 | N/A | EMERG PWR CBClsD INPUT | Open | Closed | OPEN |  |  |  |  | Direct | 0
%Z032125 | 30SW31NBC | 30SW31 | GR0044 | N/A | NORM PWR CB ClsD INPUT | Open | Closed | OPEN |  |  |  |  | Direct | 0
%Z032126 | 30SW31NAV | 30SW31 | GR0044 | N/A | NORM PWR AVAIL INPUT | NAVAIL | AVAIL | OPEN |  |  |  |  | Direct | 0
%Z032127 | 30SW31ESWAUT-N | n/a | n/a | N/A | Emerg SwitchInAuto Input | OFF | ON | ON |  |  |  |  | Direct | 0
%Z032131 | LSH65359 | VL-34 | GR0651 | N/A | LEVEL SW HIGH INPUT | HI | OK | HI |  |  |  |  | Direct | 0
%Z032132 | LSH30385 | 30TK32A | GR0320/ GR0331 | N/A | LEVEL SW HIGH INPUT | HI | OK | HI |  |  |  |  | Direct | 0
%Z032205 | HS30391 | n/a | n/a | N/A | CIL2 HCNWarnLight Switch | OFF | ON | ON |  |  |  |  | Direct | 0
%Z032206 | 30FDP3803-1 | SUB38 | GR0046 | N/A | SUB38 VESDA Alert Input | OFF | ON | ON |  |  |  |  | Direct | 0
%Z032207 | 30FDP3803-2 | SUB38 | GR0046 | N/A | SUB38 VESDA Action Input | OFF | ON | ON |  |  |  |  | Direct | 0
%Z032208 | 30FDP3803-3 | SUB38 | GR0046 | N/A | SUB38 VESDA Fire 1 Input | OFF | ON | ON |  |  |  |  | Direct | 0
%Z032209 | 30FDP3803-FLT | SUB38 | GR0046 | N/A | SUB38 VESDA Fault Input | OFF | ON | ON |  |  |  |  | Direct | 0
%Z032211 | 30XE32BYP | 30XE32 | GR0046 | N/A | SUB38 RECLS UPS BYP | NORMAL | BYPASS | BYPASS |  |  |  |  | Direct | 0
%Z032212 | 30XE32ALM | 30XE32 | GR0046 | N/A | SUB38 RECLS UPS FLT | OK | FAULT | FAULT |  |  |  |  | Direct | 0
%Z032213 | 30XE32BLO | 30XE32 | GR0046 | N/A | SUB38 RECLS UPS BATT LO | OK | LOW | LOW |  |  |  |  | Direct | 0
%Z032214 | 30XE32BON | 30XE32 | GR0046 | N/A | SUB38 RECLS UPS BATT ON | OFF | ON | ON |  |  |  |  | Direct | 0
%Z052109 | LSH30623 | 30TK62A | GR0330 | 2000-F30-PID-PR-10008 | 30TK62A Level Sw High | OFF | ON | OFF |  |  |  |  | Direct | 0
%Z052126 | LSH30624 | 30TK62B | GR0330 | 2000-F30-PID-PR-10008 | CIL 3 30TK62B LevelSw Hi | OFF | ON | OFF |  |  |  |  | Direct | 0
%Z052127 | 30SW62NAV | 30SW62 | GR0044 | N/A | 415V Normal Supply Avail | NAVAIL | AVAIL | NAVAIL |  |  |  |  | Direct | 0
%Z052128 | 30SW62EAV | 30SW62 | GR0044 | N/A | 415V Emerg Supply Avail | NAVAIL | AVAIL | NAVAIL |  |  |  |  | Direct | 0
%Z052129 | 30SW62NBC | 30SW62 | GR0044 | N/A | 415V Normal Supply Sel | Open | Closed | OPEN |  |  |  |  | Direct | 0
%Z052130 | 30SW62EBC | 30SW62 | GR0044 | N/A | 415V Emerg Supply Sel | Open | Closed | OPEN |  |  |  |  | Direct | 0
%Z052131 | 30BC61ALM | 30BC61 | n/a | N/A | TrippngSply BattChgFlt | OFF | ON | ON |  |  |  |  | Direct | 0
%Z052327 | ZSO30783 | KV30783 | GR0341 | N/A | Tails Gland PW66A Disch | OFF | ON | ON |  |  |  |  | Direct | 0
%Z052328 | ZSC30783 | KV30783 | GR0341 | N/A | Tails Gland PW66A Disch | OFF | ON | ON |  |  |  |  | Direct | 0
%Z052329 | ZSO30784 | KV30784 | GR0341 | N/A | Tails Gland PW66B Disch | OFF | ON | ON |  |  |  |  | Direct | 0
%Z052330 | ZSC30784 | KV30784 | GR0341 | N/A | Tails Gland PW66B Disch | OFF | ON | ON |  |  |  |  | Direct | 0
%Z052332 | HS30648OP | 30SM62 | n/a | N/A | CIL3 Tails Sampler OpnPB | OFF | ON | ON |  |  |  |  | Direct | 0
%Z053120 | HS30704A | 30SL61A | GR0340 | 30-PI-0440 | SaftyScrn61A Pullwire | OK | PULLWIRE | PULLWIRE |  |  |  |  | Direct | 0
%Z053121 | ZS30703A | 30SL61A | GR0340 | 30-PI-0440 | SaftyScrn61A BeltDrift | OK | BELT DRIFT | BELT DRIFT |  |  |  |  | Direct | 0
%Z053201 | HS30706A | 30SL61B | GR0340 | 30-PI-0440 | SaftyScrn61B Pullwire | OK | PULLWIRE | PULLWIRE |  |  |  |  | Direct | 0
%Z053202 | ZS30705A | 30SL61B | GR0340 | 30-PI-0440 | SaftyScrn61B BeltDrift | OK | BELT DRIFT | BELT DRIFT |  |  |  |  | Direct | 0
%Z053221 | ZS30707A | 30SL61C | GR0340 | 30-PI-0440 | SaftyScrn61C BeltDrift | OK | BELT DRIFT | BELT DRIFT |  |  |  |  | Direct | 0
%Z053301 | HS30710A | 30SL61D | GR0340 | 30-PI-0440 | SaftyScrn61D Pullwire | OK | PULLWIRE | PULLWIRE |  |  |  |  | Direct | 0
%Z053302 | ZS30709A | 30SL61D | GR0340 | 30-PI-0440 | SaftyScrn61D BeltDrift | OK | BELT DRIFT | BELT DRIFT |  |  |  |  | Direct | 0
%Z053313 | 30SC62MSTP1 | 30SC62 | n/a | N/A | CIL2 MAINT SCREEN | OFF | ON | ON |  |  |  |  | Direct | 0
%Z053314 | HS30708A | 30SL61C | GR0340 | 30-PI-0440 | SaftyScrn61C Pullwire | OK | PULLWIRE | PULLWIRE |  |  |  |  | Direct | 0
%Z053405 | ZSL30603 | 30TH61 | GR0302 | 2000-F30-PID-PR-10001 | FlotTailThk3Rake Lo | OK | RAKEDWN | RAKEDWN |  |  |  |  | Direct | 0
%Z053406 | ZSH30603 | 30TH61 | GR0302 | 2000-F30-PID-PR-10001 | FlotTailThk3Rake HI | OK | RAKEUP | RAKEUP |  |  |  |  | Direct | 0
%Z053407 | NSHH30602 | 30TH61 | GR0302 | 2000-F30-PID-PR-10001 | FlotTailThk3Torque HiHi | OK | HIHI | HIHI |  |  |  |  | Direct | 0
%Z053408 | LSL30604 | 30TH61 | GR0302 | 2000-F30-PID-PR-10001 | FlotTailThk3HydOil Lo | OK | HYDRAULIC OIL LO | HYDRAULIC OIL LO |  |  |  |  | Direct | 0
%Z053409 | LSL30605 | 30TH61 | GR0302 | 2000-F30-PID-PR-10001 | FlotTailThk3GB Oil Lo | OK | GEARBOX OIL LO | GEARBOX OIL LO |  |  |  |  | Direct | 0
%Z054121 | SSL30619 | 30TH61 | GR0302 | N/A | Thcknr 3 Rake Pulse | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054122 | 80CB64ZSC | 80CB64 | GR0042 | N/A | 80CB64 Closed Input | OFF | ON | OFF |  |  |  |  | Direct | 0
%Z054123 | 80CB64ZSO | 80CB64 | GR0042 | N/A | 80CB64 Open Input | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054124 | 80CB64LINE | 80CB64 | GR0042 | N/A | 80CB64 Line Earth Fault | OFF | ON | ON |  |  |  |  | Reverse | 0
%Z054125 | 80CB64HEALTHY | 80CB64 | GR0042 | N/A | 80CB64 Healthy Input | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054126 | 80XE64HEALTHY | 80CB64 | GR0042 | N/A | 80XE64 RLC Healthy | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054127 | 80XE64FLT | 80CB64 | GR0042 | N/A | 80XE64 RLC Fault | OFF | ON | ON |  |  |  |  | Reverse | 0
%Z054207 | 75PW62AALM | 75PW62A | GR0032 | N/A | Circuit Wtr Pp1 PreAlarm | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054208 | 75PW62AFUS | 75PW62A | GR0032 | N/A | Circuit Wtr Pp1FuseBlown | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054219 | FSL30727A | 75PW62A | n/a | N/A | Tails Pp A GlandFlowSwLo | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054306 | 75PW62BALM | 75PW62B | GR0032 | N/A | rcuit Wtr Pp2 Prealarm | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054307 | 75PW62BFUS | 75PW62B | GR0032 | N/A | rcuit Wtr Pp2 Fuse Blown | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054318 | FSL30727B | 75PW62B | n/a | N/A | Tail PpB Gland Flow SwLo | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054325 | ZSO30788 | KV30788 | GR0341 | N/A | Tails Gland PW66C Disch | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054326 | ZSC30788 | KV30788 | GR0341 | N/A | Tails Gland PW66C Disch | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054327 | ZSO30789 | KV30789 | GR0341 | N/A | Tails Gland Supply Inlet | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054328 | ZSC30789 | KV30789 | GR0341 | N/A | Tails Gland Supply Inlet | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054407 | FSL30727C | FV30731C | n/a | N/A | Tails PpC Gland FlowSwLo | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054415 | HS30691 | n/a | n/a | N/A | CIL3 HCNWarnLight Switch | OFF | ON | ON |  |  |  |  | Direct | 0
%Z054416 | HS30692 | n/a | n/a | N/A | CIL3CarbScn HCNWarnSwtch | OFF | ON | ON |  |  |  |  | Direct | 0

## 4. Digital Output
KCGM GROWTH PROJECT
DIGITAL OUTPUT
DIGITAL INSTRUMENTS OUTPUT
Tag Source | Tag Name | P&ID | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev
%Z023309 O | SV65333GO | 65-PI-10004 | Wtr Addn ToC Attitn Tank | OFF | ON | ON |  |  |  | Direct | 0
%Z023310 D | SV65334GO | 65-PI-10004 | Wtr Addn ToC AttrnTkCone | OFF | ON | ON |  |  |  | Direct | 0
%Z023312 | SV65336GO | 65-PI-10004 | Carbn Attritn To CIL 1 | OFF | ON | ON |  |  |  | Direct | 0
%Z023313 | SV65337GO | 65-PI-10004 | Carbn Attritn To CIL2 | OFF | ON | ON |  |  |  | Direct | 0
%Z023314 | SV65338GO | 65-PI-10004 | Carbn Attritn To CIL 3 | OFF | ON | ON |  |  |  | Direct | 0
%Z023323 | UA30391R | n/a | CIL2 HCNWarn Light Red | OFF | ON | ON |  |  |  | Direct | 0
%Z023324 | UA30391A | n/a | CIL2 HCNWarn Light Amber | OFF | ON | ON |  |  |  | Direct | 0
%Z023325 | UA30391G | n/a | CIL2 HCNWarn Light Green | OFF | ON | ON |  |  |  | Direct | 0
%Z023326 | 80XS01BLU3 | n/a | Blue Lgtn Alert CIL 2 | OFF | ON | ON |  |  |  | Direct | 0
%Z023327 | 80XS01AMB3 | n/a | Amber Lgtn Alert CIL 2 | OFF | ON | ON |  |  |  | Direct | 0
%Z023328 | 80XS01RED3 | n/a | Red Lgtn Alert CIL 2 | OFF | ON | ON |  |  |  | Direct | 0
%Z023329 | n/a | n/a | Res CynProbe (16/5/19) | OFF | ON | ON |  |  |  | Direct | 0
%Z023330 | n/a | n/a | Res CynProbe (16/5/19) | OFF | ON | ON |  |  |  | Direct | 0
%Z031328 | SV81309GO | n/a | Air ReceiverPurge Output | OFF | ON | ON |  |  |  | Direct | 0
%Z031330 | UA30385GO | n/a | SIREN Go Output | OFF | ON | ON |  |  |  | Direct | 0
%Z032301 | UA30373ACGO | n/a | HCN Beacon/ Sounder ELTN | OFF | ON | ON |  |  |  | Direct | 0
%Z032302 | UA30373DGO | n/a | HCN Beacon/ Sounder ELTN | OFF | ON | ON |  |  |  | Direct | 0
%Z032303 | UA30373BGO | n/a | HCN Beacon/ Sounder CIL2 | OFF | ON | ON |  |  |  | Direct | 0
%Z032304 | UA30373EFGGO | n/a | HCN Beacon/ Sounder CIL2 | OFF | ON | ON |  |  |  | Direct | 0
%Z032305 | n/a | n/a | RES 240321 Fixed HCN | OFF | ON | ON |  |  |  | Direct | 0
%Z032306 | n/a | n/a | RES 240321 Fixed HCN | OFF | ON | ON |  |  |  | Direct | 0
%Z032307 | n/a | n/a | RES 240321 Fixed HCN | OFF | ON | ON |  |  |  | Direct | 0
%Z055323 | UA30667 | n/a | 30SC62M StrtWarningSiren | OFF | ON | ON |  |  |  | Direct | 0
%Z055324 | UI30667 | n/a | 30SC62M StrtWarningLight | OFF | ON | ON |  |  |  | Direct | 0
%Z055332 | UA30668 | n/a | 30TK63 Overflow Siren | OFF | ON | ON |  |  |  | Direct | 0
%Z055405 | 30PS66GO | n/a | Silt Trap PpPermissive | OFF | ON | ON |  |  |  | Direct | 0
%Z055406 | 30PS67GO | n/a | Overflow Pp Permissive | OFF | ON | ON |  |  |  | Direct | 0
%Z055407 | UA30691R | n/a | CIL3 TK62A Cyanide Light | OFF | ON | ON |  |  |  | Direct | 0
%Z055408 | UA30691A | n/a | CIL3 TK62B Cyanide Light | OFF | ON | ON |  |  |  | Direct | 0
%Z055409 | UA30691G | n/a | CIL3 TK62E Cyanide Light | OFF | ON | ON |  |  |  | Direct | 0
%Z055410 | UA30692R | n/a | CIL3 TK62F Cyanide Light | OFF | ON | ON |  |  |  | Direct | 0
%Z055411 | UA30692A | n/a | CIL3CarbScrenCyanidLight | OFF | ON | ON |  |  |  | Direct | 0
%Z055412 | UA30692G | n/a | CIL3 Entry -Cyanid Light | OFF | ON | ON |  |  |  | Direct | 0
%Z055413 | UA30673ABGO | n/a | HCN Beacon/Sounder CSCrn | OFF | ON | ON |  |  |  | Direct | 0
%Z055414 | UA30673CDEGO | n/a | HCN Beacon/ Sounder CIL3 | OFF | ON | ON |  |  |  | Direct | 0
%Z055431 | 30SW62TST | n/a | 30-SW-62 MCCEmergCOTest | OFF | ON | ON |  |  |  | Direct | 0
%Z055432 | 30SW62RTN | n/a | 30-SW-62 MCCRetnToNormal | OFF | ON | ON |  |  |  | Direct | 0

## 5. Totalisers
KCGM GROWTH PROJECT
TOTALISERS
Reset Period
Tag Source | Tag Name | Type | P&ID | Description | Abbreviated Description (Faceplate) | Units | Shift | Day | Cont | Comments | Rev

## 6. OnOff Valves
KCGM GROWTH PROJECT
ONOFF VALVES
Permissives and Trips
Tag Name | Drawing | Graphic | P&ID | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) Tags | Open Condition (Auto Mode) Description | Close Condition (Auto Mode) Tags | Close Condition (Auto Mode) Description | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open | Close | Bypass | Reset Required | Comments | Rev
KV30388 | DR0008 | .GR0301 .GR0320 | 30-PI-313 | CIL2 Feed Valve Open | VLV08 | N/A | x | [17 empty] | 0
KV30389 | DR0008 | .GR0301 .GR0320 | 30-PI-313 | CIL2 Bypass Valve Open | VLV08 | N/A | x | [17 empty] | 0
KV65352 | DR0008 | .GR0655 | N/a | CIL2 CARBON INLET VALVE | VLV05 | CLOSE | x | x | Rising Edge Detection(%GS01306.PV.OFF) OR Rising Edge Detection((CR3MSTT.PV.ON AND CR3MTOCIL2.PV.ON) OR (CR2MSTT.PV.ON AND CR2MTOCIL3.PV.OFF) OR (%GS00511.PV.ON AND %GS00611.PV.ON)) OR Rising Edge Detection (%GS03006.PV.1) | Rising Edge Detection (Txfr Vssl Drain Vlv Opn) OR Rising Edge Detection (Sequence Start AND Carbon Regen 3 to CIL2 OR Sequence Start AND Carbon Regen 2 to CIL3 OR Carbon Regen 1 to CIL2 AND CR1M Start) OR Rising Edge Detection (SIO Open Command from the loaded carbon transfer step 2) | Rising Edge Detection (65SC31RUN.PV.OFF) OR Rising Edge Detection (%GS03006.PV.0) | Rising Edge Detection (Drive Running) OR Rising Edge Detection (SIO Close Command from the loaded carbon transfer step 1A and step 2) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
KV65354 | DR0008 | .GR0655 | 2000-F30-PID- PR-1005 | CIL2 CARBON DRAIN VALVE | VLV05 | CLOSE | x | x | Rising Edge Detection (%GS03106.PV.1) | Rising Edge Detection (SIO Open Command from loaded carbon transfer step 2) | Rising Edge Detection (%GS03106.PV.0) AND (KV65352.PV.0) | Rising Edge Detection (SIO Close Command from loaded carbon transfer step 1A and step2) AND (Inlet Valve Closed) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
KV65355 | DR0008 | .GR0655 | 2000-F30-PID- PR-1005 | CIL2 CARBON DISCH VALVE | VLV05 | CLOSE | x | x | %GS01206.PV.ON AND KV65355.MODE.AUT | Txfr Vssl Dschg Vlv Opn AND Txfr Vssl Dischrg Vlv in Auto | NOT(%GS01206.PV.ON AND KV65355.MODE.AUT) | NOT (Txfr Vssl Dschg Vlv Opn AND Txfr Vssl Dischrg Vlv in Auto) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
KV65356 | DR0008 | .GR0655 | 2000-F30-PID- PR-1005 | CIL2 CARBON WATER VALVE | VLV05 | CLOSE | x | x | %GS01406.PV.ON AND KV65356.MODE.AUT | Vssl Txfr Water Vlv Opn AND Vssl Txfr Water Vlv in Auto | NOT (%GS01406.PV.ON AND KV65356.MODE.AUT) | NOT (Vssl Txfr Water Vlv Opn AND Vssl Txfr Water Vlv in Auto) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV65350 | DR0008 | .GR0651 | 2000-F30-PID- PR-1005 | CIL2 LCarbn Wtr Vlv | VLV03 | CLOSE | x | x | 65SC31RUN.PV.ON | 65SC31 Drive Running | NOT 65SC31RUN.PV.ON | NOT 65SC31 Drive Running | [11 empty] | MAY BE OPERATED FROM FIELD | 0
KV65333 | DR0009 | .GR0649 | 65-PI-1004 | Carbon Attrit Wtr Additn | VLV05 | CLOSE | x | x | Rising Edge Detection ((CA1MPAU.PV.OFF AND CA1M.SV.1) AND CA1MRL.X01.LE) | See Appendix A - Item 11 | Rising Edge Detection ((CA1MPAU.PV.OFF AND CA1M.SV.1) AND 60s On Delay Timer(CA1MRL.X01.GE)) | See Appendix A - Item 11 | [12 empty] | 0
KV65334 | DR0009 | .GR0649 | 65-PI-1004 | Carbon Attrit Cone Wtr | VLV05 | CLOSE | x | x | Rising Edge Detection (CA1MPAU.PV.OFF AND CA1M.SV.5) | Rising Edge Detection (Module Not Paused AND Module In Step 5) | CA1MPAU.PV.ON OR 180S Timer To On (5S Timer To On (CA1MRL.X02.LE) OR CA1MDESTLVL.PV.OFF)) | Module Paused OR 180S Timer To On (5S Timer To On (Hopper Lo Level) OR Dest screen lvl not OK)) | [12 empty] | 0
KV65335 | DR0009 | .GR0649 | 65-PI-1004 | Carbon Attrit Tk Dischrg | VLV05 | CLOSE | x | x | Rising Edge Detection(5S On Delay Timer (CA1MPAU.PV.OFF AND CA1M.SV.5 AND 65PP70.PV.2)) | Rising Edge Detection(5S Timer To On(Module Not Paused AND Module In Step 5 AND Drive Running)) | CA1MPAU.PV.ON OR (5S Timer To On (CA1MRL.X02.LE) OR CA1MDESTLVL.PV.OFF)) | Module Pause OR (5S Timer To On (Hopper Lo Level) OR Dest screen lvl not OK)) | [12 empty] | 0
KV65336 | DR0009 | .GR0649 | 65-PI-1004 | CIL1 Carbon AttritToCIL1 | VLV05 | CLOSE | x | x | Rising Edge Detection (CA1MPAU.PV.OFF AND CA1M.SV.5 AND CA1MDEST.SV.1) | Rising Edge Detection(Module Not Paused AND Module In Step 5 AND CIL 1 Selected) | CA1MPAU.PV.ON OR 180s Timer To On (5S Timer To On(CA1MRL.X02.LE) OR CA1MDESTLVL.PV.OFF) | Module Paused OR 180s Timer To On (5S Timer To On(Hopper Lo Level) OR Dest screen lvl not OK)) | [12 empty] | 0
KV65337 | DR0009 | .GR0649 | 65-PI-1004 | CIL2 Carbon AttritToCIL2 | VLV05 | CLOSE | x | x | Rising Edge Detection (CA1MPAU.PV.OFF AND CA1M.SV.5 AND CA1MDEST.SV.2) | Rising Edge Detection (Module Not Paused AND Module In Step 5 AND CIL 2 Selected) | CA1MPAU.PV.ON OR 180S Timer To On(5S Timer To On(CA1MRL.X02.LE) OR CA1MDESTLVL.PV.OFF) | Module Paused OR 180S Timer To On(5S Timer To On(Hopper Lo Level) OR Dest screen lvl not OK) | [12 empty] | 0
KV65338 | DR0009 | .GR0649 | 65-PI-1004 | CIL3 Carbon AttritToCIL3 | VLV05 | CLOSE | x | x | Rising Edge Detection (CA1MPAU.PV.OFF AND CA1M.SV.5 AND CA1MDEST.SV.3) | Rising Edge Detection (Module Not Paused AND Module In Step 5 AND CIL 3 Selected) | CA1MPAU.PV.ON OR 180S Timer To On(5S Timer To On(CA1MRL.X02.LE) OR CA1MDESTLVL.PV.OFF) | Module Paused OR 180S Timer To On(5S Timer To On(Hopper Lo Level) OR Dest screen lvl not OK) | [12 empty] | 0
FV3065A | DR0026 | .GR0330 | 2000-F30-PID- PR-10008 | Loaded CarbnFeedingTK62B | N/A | N/A | x | [16 empty] | DUMMY VALVE, ONLY USED IN SOFTWARE | 0
FV3065B | DR0026 | .GR0330 | 2000-F30-PID- PR-10008 | Loaded CarbnFeeding SC65 | N/A | N/A | x | [17 empty] | 0
FV30690A | DR0028 | .GR0302 | 2000-F30-PID- PR-10001 | Thkr 3 U/F AGland Water | VLV01 | CLOSE | x | x | 30PP61A.PV.2 | 30PP61A Drive Running | NOT 30PP61A.PV.2 | NOT 30PP61A Drive Running | [12 empty] | 0
FV30690B | DR0028 | .GR0302 | 2000-F30-PID- PR-10001 | Thkr 3 U/F BGland Water | VLV01 | CLOSE | x | x | 30PP61B.PV.2 | 30PP61B Drive Running | NOT 30PP61B.PV.2 | NOT 30PP61B Drive Running | [12 empty] | 0
FV30731A | DR0029 | .GR0341 | 2000-F30-PID- PR-10015 | FTails Pmp AGland Water | VLV01 | CLOSE | x | x | 30PP62AGO.PV.L | 30PP62AGO Drive Start Output | NOT 30PP62AGO.PV.L | NOT 30PP62AGO Drive Start Output | [11 empty] | 30PP62AGO Drive Start Output Puts FV30731A Mode to Auto | 0
FV30731B | DR0029 | .GR0341 | 2000-F30-PID- PR-10015 | FTails Pmp BGland Water | VLV01 | CLOSE | x | x | 30PP62BGO.PV.L | 30PP62BGO Drive Start Output | NOT 30PP62BGO.PV.L | NOT 30PP62BGO Drive Start Output | [11 empty] | 30PP62BGO Drive Start Output Puts FV30731B Mode to Auto | 0
FV30731C | DR0029 | .GR0341 | 2000-F30-PID- PR-10015 | FTails Pmp CGland Water | VLV01 | CLOSE | x | x | 30PP62CGO.PV.L | 30PP62CGO Drive Start Output | NOT 30PP62CGO.PV.L | NOT 30PP62CGO Drive Start Output | [11 empty] | 30PP62CGO Drive Start Output Puts FV30731C Mode to Auto | 0
FV30631A | DR0030 | .GR0330 | 2000-F30-PID- PR-10008 | CIL3 Tk62A Feed Valve | VLV01 | OPEN | x |  |  |  | Rising Edge Detection (FV30631A.MODE.AUT) | Rising Edge Detection (Mode = Auto) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30631B | DR0030 | .GR0330 | 2000-F30-PID- PR-10008 | CIL3 Tk62B Feed Valve | VLV01 | CLOSE | x |  |  |  | Rising Edge Detection (FV30631B.MODE.AUT) | Rising Edge Detection (Mode = Auto) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30636 | DR0030 | .GR0330 | N/A | CIL3 BCarb Screen Water | VLV01 | N/A | x | [16 empty] | NO LOGIC TO DRIVE OUTPUT. APPEARS TO BE DUMMY LOGIC | 0
FV30675A | DR0030 | .GR0330 | N/A | CIL3 Tk62F ScreenBypass | VLV03 | CLOSE | x |  |  |  | 30SW62NAV.PV.OFF (With Rising Edge Detection) | 415V Supply Not Avail. | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30675B | DR0030 | .GR0330 | N/A | CIL3 Tk62F ScreenBypass | VLV03 | CLOSE | x |  |  |  | 30SW62NAV.PV.OFF (With Rising Edge Detection) | 415V Supply Not Avail. | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30680 | DR0030 | .GR0330 | N/A | CIL3 LCarb Screen Water | VLV01 | CLOSE | x | x | 65SC65RUN.PV.ON | Drive Running | NOT 65SC65RUN.PV.ON | NOT Drive Running | [12 empty] | 0
KV30688 | DR0030 | .GR0302 .GR0330 | N/A | CIL3 Feed Valve | VLV08 | N/A | x | [17 empty] | 0
KV30689 | DR0030 | .GR0302 .GR0330 | N/A | CIL3 Bypass Valve | VLV08 | N/A | x | [17 empty] | 0
SV30732 | DR0030 | .GR0341 | 2000-F30-PID- PR-10015 | Tails Pump B to Line B | VLV05 | CLOSE | x | [16 empty] | MAY BE OPERATED FROM FIELD | 0
SV30733 | DR0030 | .GR0341 | 2000-F30-PID- PR-10015 | Tails Pump D to Line B | VLV05 | CLOSE | x | [16 empty] | MAY BE OPERATED FROM FIELD | 0
FV30617 | DR0031 | .GR0209 .GR0302 | 2000-F30-PID- PR-10001 | Thickener 3 Feed to CIL3 | VLV05 | CLOSE | x | x | FV30617.MODE.AUT AND 30TH61ASLT.PV.ON | Mode = Auto AND Open Valve | NOT (FV30617.MODE.AUT AND 30TH61ASLT.PV.ON) AND ZSH30618.PV.ON | NOT (Mode = Auto AND Open Valve) AND Thk3 RecycleVlv Open LSW | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30618 | DR0031 | .GR0209 .GR0302 | 2000-F30-PID- PR-10001 | Thickener 3 Recycle Vlv | VLV05 | CLOSE | x | x | FV30618.MODE.AUT AND 30TH61BSLT.PV.ON | Mode = Auto AND Open Valve | NOT (FV30618.MODE.AUT AND 30TH61BSLT.PV.ON) AND ZSH30617.PV.ON | NOT (Mode = Auto AND Open Valve) AND CIL3 Feed Vlv Open LSW | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30634A | DR0031 | .GR0302 | 2000-F30-PID- PR-10001 | Thknr 3 U/F PpA DrainVlv | VLV01 | OPEN | x | x | 30PP61A.PV.2 | 30PP61A Drive Started | NOT 30PP61A.PV.2 | NOT 30PP61A Drive Started | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30634B | DR0031 | .GR0302 | 2000-F30-PID- PR-10001 | Thknr 3 U/F PpB DrainVlv | VLV01 | OPEN | x | x | 30PP61B.PV.2 | 30PP61B Drive Started | NOT 30PP61B.PV.2 | NOT 30PP61B Drive Started | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30608A | DR0031 | .GR0302 | 2000-F30-PID- PR-10001 | Thknr 3 U/F PpA SuctnVlv | VLV01 | CLOSE | x | x | Rising Edge Detection (NOT 30PP61SEL.SWCR[1].0 AND 30PP61ASLT.PV.ON) | Rising Edge Detection (NOT(COLOUR = BLACK) AND A Drive Selceted) | Rising Edge Detection (NOT FV30608A.MODE.AUT) OR Rising Edge Detection(NOT(NOT 30PP61SEL.SWCR[1].0 AND 30PP61ASLT.PV.ON)) | Rising Edge Detection (NOT FV30608A Mode = Auto) OR Rising Edge Detection(NOT(NOT(COLOUR = BLACK) AND A Drive Selceted)) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30608B | DR0031 | .GR0302 | 2000-F30-PID- PR-10001 | Thknr 3 U/F PpB SuctnVlv | VLV01 | CLOSE | x | x | Rising Edge Detection (NOT 30PP61SEL.SWCR[2].0 AND 30PP61BSLT.PV.ON) | Rising Edge Detection (NOT(COLOUR = BLACK) AND B Drive Selceted) | Rising Edge Detection (NOT FV30608B.MODE.AUT) OR Rising Edge Detection (NOT(NOT 30PP61SEL.SWCR[2].0 AND 30PP61BSLT.PV.ON)) | Rising Edge Detection (NOT FV30608B Mode = Auto) OR Rising Edge Detection(NOT(NOT(COLOUR = BLACK) AND B Drive Selceted)) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30649A | DR0031 | .GR0302 | 2000-F30-PID- PR-10001 | Thknr 3 U/F DiluteWaterA | VLV01 | CLOSE | x | x | Rising Edge Detection(30PP61A.PV.2) | Rising Edge Detection(Drive Running) | Rising Edge Detection (NOT FV30649A.MODE.AUT) OR Falling Edge Detection(30PP61A.PV.2) | Rising Edge Detection (NOT FV30649A Mode = Auto) OR Falling Edge Detection(Drive Running) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30649B | DR0031 | .GR0302 | 2000-F30-PID- PR-10001 | Thknr 3 U/F DiluteWaterB | VLV01 | CLOSE | x | x | Rising Edge Detection (30PP61B.PV.2) | Rising Edge Detection(Drive Running) | Rising Edge Detection (NOT FV30649B.MODE.AUT) OR Falling Edge Detection (30PP61B.PV.2) | Rising Edge Detection (NOT FV30649B Mode = Auto) OR Falling Edge Detection(Drive Running) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30700 | DR0032 | .GR0331 .GR0340 | 2000-F30-PID- PR-10010 | Safety Scrn Bypass Vlv | VLV01 | OPEN | x |  |  |  | Rising Edge Detection (NOT FV30700.MODE.AUT) | Rising Edge Detection (NOT FV30700 Mode = Auto) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30701A | DR0032 | .GR0331 .GR0340 | 2000-F30-PID- PR-10010 | Safety ScrnAFeed Valve | VLV01 | CLOSE | x | x | 30SL61A.MODE.AUT AND 30SL61ARUN.PV.ON | Safety Screen A AUTO AND Safety Screen A RUN | Rising Edge Detection (NOT FV30701A.MODE.AUT) OR NOT (30SL61A.MODE.AUT AND 30SL61ARUN.PV.ON) | Rising Edge Detection (NOT FV30701A Mode = Auto) OR NOT (Safety Screen A AUTO AND Safety Screen A RUN) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30701B | DR0032 | .GR0331 .GR0340 | 2000-F30-PID- PR-10010 | Safety ScrnBFeed Valve | VLV01 | CLOSE | x | x | 30SL61B.MODE.AUT AND 30SL61BRUN.PV.ON | Safety Screen B AUTO AND Safety Screen B RUN | Rising Edge Detection (NOT FV30701B.MODE.AUT) OR NOT (30SL61B.MODE.AUT AND 30SL61BRUN.PV.ON) | Rising Edge Detection (NOT FV30701B Mode = Auto) OR NOT (Safety Screen B AUTO AND Safety Screen B RUN) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30701C | DR0032 | .GR0331 .GR0340 | 2000-F30-PID- PR-10010 | Safety ScrnCFeed Valve | VLV01 | CLOSE | x | x | 30SL61C.MODE.AUT AND 30SL61CRUN.PV.ON | Safety Screen C AUTO AND Safety Screen C RUN | Rising Edge Detection (NOT FV30701C.MODE.AUT) OR NOT (30SL61C.MODE.AUT AND 30SL61CRUN.PV.ON) | Rising Edge Detection (NOT FV30701C Mode = Auto) OR NOT (Safety Screen C AUTO AND Safety Screen C RUN) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30701D | DR0032 | .GR0331 .GR0340 | 2000-F30-PID- PR-10010 | Safety ScrnDFeed Valve | VLV01 | CLOSE | x | x | 30SL61D.MODE.AUT AND 30SL61DRUN.PV.ON | Safety Screen D AUTO AND Safety Screen D RUN | Rising Edge Detection (NOT FV30701D.MODE.AUT) OR NOT (30SL61D.MODE.AUT AND 30SL61DRUN.PV.ON) | Rising Edge Detection (NOT FV30701D Mode = Auto) OR NOT (Safety Screen D AUTO AND Safety Screen D RUN) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30702A | DR0032 | .GR0331 .GR0340 | 2000-F30-PID- PR-10010 | Safety ScrnASpray Water | VLV01 | CLOSE | x | x | 30SL61A.PV.2 | 30SL61A Screen Started | Rising Edge Detection (NOT FV30702A.MODE.AUT AND 30SL61A.PV.2) | Rising Edge Detection (NOT( Mode = Auto AND Screen Started)) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30702B | DR0032 | .GR0331 .GR0340 | 2000-F30-PID- PR-10010 | Safety ScrnBSpray Water | VLV01 | CLOSE | x | x | 30SL61B.PV.2 | 30SL61B Screen Started | Rising Edge Detection (NOT FV30702B.MODE.AUT AND 30SL61B.PV.2) | Rising Edge Detection (NOT( Mode = Auto AND Screen Started)) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30702C | DR0032 | .GR0331 .GR0340 | 2000-F30-PID- PR-10010 | Safety ScrnCSpray Water | VLV01 | CLOSE | x | x | 30SL61C.PV.2 | 30SL61C Screen Started | Rising Edge Detection (NOT FV30702C.MODE.AUT AND 30SL61C.PV.2) | Rising Edge Detection (NOT( Mode = Auto AND Screen Started)) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30702D | DR0032 | .GR0331 .GR0340 | 2000-F30-PID- PR-10010 | Safety ScrnDSpray Water | VLV01 | CLOSE | x | x | 30SL61D.PV.2 | 30SL61D Screen Started | Rising Edge Detection (NOT FV30702D.MODE.AUT AND 30SL61D.PV.2) | Rising Edge Detection (NOT( Mode = Auto AND Screen Started)) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30719 | DR0032 | .GR0331 | N/A | FTails Tank Water Additn | VLV01 | CLOSE | x | x | FV30719.MODE.AUT AND FV30719SST.PV.ON | Mode = Auto AND FV30719 Sequence OPEN Command | NOT (FV30719.MODE.AUT AND FV30719SST.PV.ON) | NOT (Mode = Auto AND FV30719 Sequence OPEN Command) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30729A | DR0032 | .GR0331 .GR0340 | N/A | Tails DiluteWater ValveA | VLV01 | CLOSE | x |  |  |  | Rising Edge Detection (NOT FV30729A.MODE.AUT) | Rising Edge Detection (NOT Mode = Auto) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30729B | DR0032 | .GR0331 .GR0340 | N/A | Tails DiluteWater ValveB | VLV01 | CLOSE | x |  |  |  | Rising Edge Detection (NOT FV30729B.MODE.AUT) | Rising Edge Detection (NOT Mode = Auto) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV75603 | DR0032 | N/A | N/A | Elu CN WtrTkWater Valve | VLV01 | CLOSE | x | x | LIC75603.ALRM.LL AND FV75603.MODE.AUT OR Rising Edge Detection(5S On Delay Timer(LIC75603RL.X01.LT) AND FV75603.MODE.AUT) | Tank 75TK62 Level Low AND Mode = Auto Rising Edge Detection(5S On Delay Timer(Tank Level Low) AND Mode = Auto) | NOT (LIC75603.ALRM.LL AND FV75603.MODE.AUT) 5S On Delay Timer(LIC75603RL.X02.GE) OR 600S On Delay Timer(FV75603.MODE.AUT AND FV75603.PV.2) | NOT( Tank 75TK62 Level Low AND Mode = Auto) 5S On Delay Timer (Tank Level OK) OR 600S On Delay Timer (Mode = Auto AND Valve Open) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30721B | DR0033 | .GR0331 .GR0341 | 2000-F30-PID- PR-10015 | FTails Pump BScuttle Vlv | VLV01 | OPEN | x | x | 2s Off Delay Timer (Rising Edge Detection (30PP62B.PV.0)) | 2s Off Delay Timer (Rising Edge Detection (DRIVE FAILED)) | 2S Off Delay Timer (Rising Edge Detection (30PP62B1SST.PV.ON OR 30PP62B1SLT.PV.ON OR 30PP62B3SLT.PV.ON OR 30PP62B3SST.PV.ON OR 30PP62B2SLT.PV.ON)) | 2S Off Delay Timer (Rising Edge Detection (DRIVE B1 SELECTED TO RUN OR DRIVE B1 SELECTED TO RUN OR DRIVE B3 SELECTED TO RUN ORDRIVE B3 SELECTED TO RUN OR DRIVE B2 SELECTED TO RUN)) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30721C | DR0033 | .GR0331 .GR0341 | 2000-F30-PID- PR-10015 | FTails Pump CScuttle Vlv | VLV01 | OPEN | x | x | 2s Off Delay Timer (Rising Edge Detection(30PP62C.PV.0)) | 2s Off Delay Timer (Rising Edge Detection (DRIVE FAILED)) | 2s Off Delay Timer (Rising Edge Detection (30PP62CSST.PV.ON OR 30PP62CSLT.PV.ON)) | 2s Off Delay Timer (Rising Edge Detection (DRIVE C SELECTED TO RUN OR DRIVE START FLAG)) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30722A | DR0033 | .GR0331 .GR0341 | 2000-F30-PID- PR-10015 | FTails Pump AFlush Vlv | VLV01 | CLOSE | x | x | 2s Off Delay Timer(Rising Edge Detection( 30PP62ASLT.PV.OFF OR 30PP62A.PV.0) | 2s Off Delay Timer(Rising Edge Detection( DRIVE SELECTED TO STOP OR DRIVE FAILED) | 2s Off Delay Timer(Rising Edge Detection(30S On Delay Timer (30PP62B1SLT.PV.ON OR 30PP62A.PV.0) OR 1800S On Delay Timer(30PP62ASLT.PV.OFF)) | Off Delay Timer(Rising Edge Detection(30S On Delay Timer (DRIVE SELECTED TO STOP OR DRIVE FAILED) OR 1800S On Delay Timer(DRIVE SELECTED TO STOP)) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30722B | DR0033 | .GR0331 .GR0341 | 2000-F30-PID- PR-10015 | FTails Pump BFlush Vlv | VLV01 | CLOSE | x | x | 2s Off Delay Timer (Rising Edge Detection (30PP62B.PV.0 OR (30PP62B1SLT.PV.OFF AND 30PP62B2SLT.PV.OFF AND 30PP62B3SLT.PV.OFF))) | 2s Off Delay Timer (Rising Edge Detection (30PP62B DRIVE FAILED OR (30PP62B1 DRIVE SELECTED TO STOP AND 30PP62B2 DRIVE SELECTED TO STOP AND 30PP62B3 DRIVE SELECTED TO STOP))) | See Appendix A - Item 12 | See Appendix A - Item 12 | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30722C | DR0033 | .GR0331 .GR0341 | 2000-F30-PID- PR-10015 | FTails Pump CFlush Vlv | VLV01 | CLOSE | x | x | 2s Off Delay Timer (Rising Edge Detection(30PP62CSLT.PV.OFF OR 30PP62B3SLT.PV.ON OR 30PP62C.PV.0)) | 2s Off Delay Timer (Rising Edge Detection(30PP62C DRIVE SELECTED TO STOP OR 30PP6B DRIVE SELECTED TO RUN OR 30PP62C DRIVE FAILED)) | See Appendix A - Item 13 | See Appendix A - Item 13 | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30723 | DR0033 | .GR0343 .GR0331 .GR0341 | N/A | FTails Pump Bto NewLine2 | VLV01 | CLOSE | x | x | 2s Off Delay Timer(Rising Edge Detection( 30PP62B1SST.PV.ON OR 30PP62B1SLT.PV.ON) | 2s Off Delay Timer(Rising Edge Detection( DRIVE B1 SELECTED TO RUN OR DRIVE B1 SELECTED TO RUN) | Rising Edge Detection (NOT FV30723.MODE.AUT) (More Auto Close Conditions see Appendix A - Item 14) | Rising Edge Detection (NOT Mode = Auto) (More Auto Close Conditions see Appendix A - Item 14) | [11 empty] | See Appendix A - Item 14 MAY BE OPERATED FROM FIELD | 0
FV30724 | DR0033 | .GR0343 .GR0331 .GR0341 | N/A | FTails Pump Bto Old Line | VLV01 | CLOSE | x | x | 2s Off Delay Timer(Rising Edge Detection(30PP62B3SLT.PV.ON OR 30PP62B3SST.PV.ON) | 2s Off Delay Timer(Rising Edge Detection(DRIVE B3 SELECTED TO RUN OR DRIVE B3 SELECTED TO RUN) | Rising Edge Detection (NOT FV30724.MODE.AUT) (More Auto Close Conditions see Appendix A - Item 15) | Rising Edge Detection (NOT Mode = Auto) (More Auto Close Conditions see Appendix A - Item 15) | [11 empty] | See Appendix A - Item 15 MAY BE OPERATED FROM FIELD | 0
FV30725 | DR0033 |  | N/A | FTails Pump Bto NewLine3 |  |  | x | x | 2s Off Delay Timer(Rising Edge Detection(30PP62B2SLT.PV.ON) | 2s Off Delay Timer(Rising Edge Detection(DRIVE B2 SELECTED TO RUN) | Rising Edge Detection (NOT FV30725.MODE.AUT) (More Auto Close Conditions see Appendix A - Item 16) | Rising Edge Detection (NOT Mode = Auto) (More Auto Close Conditions see Appendix A - Item 16) | [11 empty] | See Appendix A - Item 16 MAY BE OPERATED FROM FIELD
FV30720A | DR0033 | .GR0331 .GR0341 | 2000-F30-PID- PR-10015 | FTails Pump AInlet Vlv | VLV01 | CLOSE | x | x | 2s Off Delay Timer(Rising Edge Detection((30PP62ASST.PV.ON OR 30PP62ASLT.PV.ON) AND FV30721A.PV.2)) | 2s Off Delay Timer(Rising Edge Detection((30PP62A DRIVE SELECTED TO RUN OR 30PP62A DRIVE SELECTED TO RUN) AND DUMP VALVE CLOSED)) | 2s Off Delay Timer(Rising Edge Detection(30PP62ASLT.PV.OFF OR 30PP62B1SLT.PV.ON OR 30PP62A.PV.0)) OR Rising Edge Detection(2S On Delay Timer(NOT(30PP62ARUN.PV.ON))) | 2s Off Delay Timer(Rising Edge Detection(30PP62A DRIVE SELECTED TO STOP OR 30PP62B1 DRIVE SELECTED TO START OR DRIVE FAILED)) OR Rising Edge Detection(2S On Delay Timer(NOT(30PP62A Pump Running))) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30720B | DR0033 | .GR0331 .GR0341 .GR0751 | 2000-F30-PID- PR-10015 | FTails Pump BInlet Vlv | VLV01 | CLOSE | x | x | 2s Off Delay Timer(Rising Edge Detection(FV30721B.PV.2 AND (30PP62B3SLT.PV.ON OR 30PP62B3SST.PV.ON OR 30PP62B2SLT.PV.ON OR 30PP62B1SST.PV.ON OR 30PP62B1SLT.PV.ON) | 2s Off Delay Timer(Rising Edge Detection(DUMP VALVE CLOSED AND (DRIVE B3 SELECTED TO RUN OR DRIVE B3 SELECTED TO RUN OR DRIVE B2 SELECTED TO RUN OR DRIVE B1 SELECTED TO RUN OR DRIVE B1 SELECTED TO RUN) | 2s Off Delay Timer(Rising Edge Detection(30PP62B1SLT.PV.OFF AND 30PP62B2SLT.PV.OFF AND 30PP62B3SLT.PV.OFF) OR 30PP62B.PV.0)) OR Riding Edge Detection(2S On Delay Timer(NOT(30PP62BRUN.PV.ON))) | 2s Off Delay Timer(Rising Edge Detection(DRIVE SELECTED TO STOP AND DRIVE SELECTED TO STOP AND DRIVE SELECTED TO STOP) OR DRIVE FAILED)) OR Riding Edge Detection(2S On Delay Timer(NOT(30PP62B Pump Running))) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30720C | DR0033 | .GR0331 .GR0341 | 2000-F30-PID- PR-10015 | FTails Pump CInlet Vlv | VLV01 | CLOSE | x | x | 2s Off Delay Timer( Rising Edge Detection((30PP62CSST.PV.ON OR 30PP62CSLT.PV.ON) AND FV30721C.PV.2)) | 2s Off Delay Timer( Rising Edge Detection((30PP62C DRIVE SELECTED TO RUN OR 30PP62C DRIVE SELECTED TO RUN) AND FV30721C DUMP VALVE CLOSED)) | 2s Off Delay Timer(Rising Edge Detection(30PP62CSLT.PV.OFF OR 30PP62B3SLT.PV.ON OR 30PP62C.PV.0) OR Rising Edge Detection(2S On Delay Timer(NOT(30PP62CRUN.PV.ON))) | 2s Off Delay Timer(Rising Edge Detection(30PP62C DRIVE SELECTED TO STOP OR 30PP62B DRIVE SELECTED TO RUN OR 30PP62C DRIVE FAILED) OR Rising Edge Detection(2S On Delay Timer(NOT(30PP62C Pump Running))) | [11 empty] | MAY BE OPERATED FROM FIELD | 0
FV30721A | DR0033 | .GR0331 .GR0341 | 2000-F30-PID- PR-10015 | FTails Pump AScuttle Vlv | VLV01 | OPEN | x | x | 2s Off Delay Timer(Rising Edge Detection(30PP62A.PV.0) | 2s Off Delay Timer(Rising Edge Detection(30PP62A DRIVE FAILED) | 2s Off Delay Timer(Rising Edge Detection(30PP62ASST.PV.ON OR 30PP62ASLT.PV.ON) | 2s Off Delay Timer(Rising Edge Detection(30PP62A OR 30PP62A DRIVE SELECTED TO RUN) | [12 empty] | 0
KV30721D | DR0033 | .GR0341 | 2000-F30-PID- PR-10015 | FTails Pump DScuttle Vlv | VLV01 | OPEN | x | [16 empty] | Assumption made regarding fail position since this is a drain valve. | 0
KV30722D | DR0033 | .GR0341 | 2000-F30-PID- PR-10015 | FTails Pump DFlush Vlv | VLV01 | CLOSE | x | [16 empty] | Assumption made regarding fail position | 0
KV30720D | DR0033 | .GR0341 .GR0751 | 2000-F30-PID- PR-10015 | FTails Pump DInlet Vlv | VLV01 | CLOSE | x |  |  |  | Rising Edge Detection(2S On Delay Timer(NOT 30PP62DRUN.PV.ON) | Rising Edge Detection(2S On Delay Timer(NOT 30PP62D Pump Running) | [12 empty] | 0
KV30783 | DR0033 | .GR0341 | 2000-F30-PID- PR-10015 | FTails GlandPW68A Disch | VLV05 | CLOSE | x | x | Rising Edge Detection(KV30783.MODE.AUT AND 75PW68ARUN.PV.ON) | Rising Edge Detection(KV30783 Mode = Auto AND 75PW68A Drive Running) | NOT 75PW68ARUN.PV.ON | NOT 75PW68A Drive Running | [12 empty] | 0
KV30784 | DR0033 | .GR0341 | 2000-F30-PID- PR-10015 | FTails GlandPW68B Disch | VLV05 | CLOSE | x | x | Rising Edge Detection(KV30784.MODE.AUT AND 75PW68BRUN.PV.ON) | Rising Edge Detection(KV30784 Mode = Auto AND 75PW68B Drive Running) | NOT 75PW68BRUN.PV.ON | NOT 75PW68B Drive Running | [12 empty] | 0
KV30788 | DR0033 | .GR0341 | 2000-F30-PID- PR-10015 | FTails GlandPW68C Disch | VLV05 | CLOSE | x | x | Rising Edge Detection(KV30788.MODE.AUT AND 75PW68CRUN.PV.ON) | Rising Edge Detection(KV30788 Mode = Auto AND 75PW68C Drive Running) | NOT 75PW68CRUN.PV.ON | NOT 75PW68C Drive Running | [12 empty] | 0
KV30789 | DR0033 | .GR0341 | 2000-F30-PID- PR-10015 | FTails GlandSystem Inlet | VLV05 | CLOSE | x | [16 empty] | Assumption made regarding fail position | 0
KV66719 | DR0039 | .GR0674 | N/A | AR Cyanide Inlet Vlv A | VLV05 | CLOSE | x | x | (GS05007-105.PV.ON OR GS05107-105.PV.ON) AND KV66719.MODE.AUT | (Open From Acacia Reagent Mixing Sequence OR Open From Sub35_2) AND Valve in Auto | NOT (GS05007-105.PV.ON OR GS05107-105.PV.ON) AND KV66719.MODE.AUT | NOT (Open From Acacia Reagent Mixing Sequence OR Open From Sub35_2) AND Valve in Auto | [11 empty] | %GS05107 not set anywhere | 0
KV30900 | DR0056 | .GR0731 .GR0733 | 75-PI-50301 | Tails Booster 77A Suct | VLV05 | CLOSE | x | x | KV30900.MODE.AUT AND %WB000207.PV.1 | PP77A Suct Mode = AUT AND PP77A Suct Output ON | KV30900.MODE.AUT AND NOT %WB000207.PV.1 | PP77A Suct Mode = AUT AND NOT PP77A Suct Output ON | [11 empty] | INTERFACES TO LOCAL PLC | 0
KV30906 | DR0056 | .GR0731 .GR0733 | 75-PI-50301 | Tails Booster 77A Dschrg | VLV05 | CLOSE | x | x | PP77A Suct Output ON AND %WB000209.PV.1 | PP77A Dschrg Mode = AUT AND PP77A Dschrg Output ON | PP77A Suct Output ON AND NOT %WB000209.PV.1 | PP77A Dschrg Mode = AUT AND NOT PP77A Dschrg Output ON | [11 empty] | INTERFACES TO LOCAL PLC | 0
KV30910 | DR0056 | .GR0731 .GR0733 | 75-PI-50301 | Tails Booster 77A Drain | VLV05 | CLOSE | x | x | KV30910.MODE.AUT AND %WB000211.PV.1 | PP77A Drain Mode = AUT AND PP77A Drain Output ON | KV30910.MODE.AUT AND NOT %WB000211.PV.1 | PP77A Drain Mode = AUT AND NOT PP77A Drain Output ON | [11 empty] | INTERFACES TO LOCAL PLC | 0
KV30901 | DR0056 | .GR0731 .GR0733 | 75-PI-50301 | Tails Booster 77B Suct | VLV05 | CLOSE | x | x | KV30901.MODE.AUT AND %WB000208.PV.1 | PP77B Suct Mode = AUT AND PP77B Suct Output ON | KV30901.MODE.AUT AND NOT %WB000208.PV.1 | PP77B Suct Mode = AUT AND NOT PP77B Suct Output ON | [11 empty] | INTERFACES TO LOCAL PLC | 0
KV30907 | DR0056 | .GR0731 .GR0733 | 75-PI-50301 | Tails Booster 77B Dschrg | VLV05 | CLOSE | x | x | KV30907.MODE.AUT AND %WB000210.PV.1 | PP77B Dschrg Mode = AUT AND PP77B Dschrg Output ON | KV30907.MODE.AUT AND NOT %WB000210.PV.1 | PP77B Dschrg Mode = AUT AND NOT PP77B Dschrg Output ON | [11 empty] | INTERFACES TO LOCAL PLC | 0
KV30911 | DR0056 | .GR0731 .GR0733 | 75-PI-50301 | Tails Booster 77B Drain | VLV05 | CLOSE | x | x | KV30911.MODE.AUT AND %WB000212.PV.1 | PP77B Drain Mode = AUT AND PP77B Drain Output ON | KV30911.MODE.AUT AND NOT %WB000212.PV.1 | PP77B Drain Mode = AUT AND NOT PP77B Drain Output ON | [11 empty] | INTERFACES TO LOCAL PLC | 0
KV30930 | DR0056 | .GR0731 | 75-PI-50301 | Tails Booster 77A Flush | VLV08 | N/A | x | [16 empty] | INTERFACES TO LOCAL PLC | 0
KV30931 | DR0056 | .GR0731 | 75-PI-50301 | Tails Booster 77B Flush | VLV08 | N/A | x | [16 empty] | INTERFACES TO LOCAL PLC | 0
KV30932 | DR0063 | .GR0741 .GR0743 | 75-PI-50302 | Tails Booster 78A Suct | VLV05 | CLOSE | x | x | KV30932.MODE.AUT AND %WB020207.PV.1 | PP78A Suct Mode = AUT AND PP78A Suct Output ON | KV30932.MODE.AUT AND NOT %WB020207.PV.1 | PP78A Suct Mode = AUT AND NOT PP78A Suct Output ON | [11 empty] | ".AOFS" Masked by Kal Tails PLC Link OK "KV30932.AOFS" INTERFACES TO LOCAL PLC | 0
KV30938 | DR0063 | .GR0741 .GR0743 | 75-PI-50302 | Tails Booster 78A Dschrg | VLV05 | CLOSE | x | x | KV30938.MODE.AUT AND %WB020209.PV.1 | PP78A Dschrg Mode = AUT AND PP78A Dschrg Output ON | KV30938.MODE.AUT AND NOT %WB020209.PV.1 | PP78A Dschrg Mode = AUT AND NOT PP78A Dschrg Output ON | [11 empty] | ".AOFS" Masked by Kal Tails PLC Link OK "KV30932.AOFS" INTERFACES TO LOCAL PLC | 0
KV30942 | DR0063 | .GR0741 .GR0743 | 75-PI-50302 | Tails Booster 78A Drain | VLV05 | CLOSE | x | x | KV30942.MODE.AUT AND %WB020211.PV.1 | PP78A Drain Mode = AUT AND PP78A Drain Output ON | KV30942.MODE.AUT AND NOT %WB020211.PV.1 | PP78A Drain Mode = AUT AND NOT PP78A Drain Output ON | [11 empty] | ".AOFS" Masked by Kal Tails PLC Link OK "KV30932.AOFS" INTERFACES TO LOCAL PLC | 0
KV30933 | DR0063 | .GR0741 .GR0743 | 75-PI-50302 | Tails Booster 78B Suct | VLV05 | CLOSE | x | x | KV30933.MODE.AUT AND %WB020208.PV.1 | PP78B Suct Mode = AUT AND PP78B Suct Output ON | KV30933.MODE.AUT AND NOT %WB020208.PV.1 | PP78B Suct Mode = AUT AND NOT PP78B Suct Output ON | [11 empty] | ".AOFS" Masked by Kal Tails PLC Link OK "KV30932.AOFS" INTERFACES TO LOCAL PLC | 0
KV30939 | DR0063 | .GR0741 .GR0743 | 75-PI-50302 | Tails Booster 78B Dschrg | VLV05 | CLOSE | x | x | KV30939.MODE.AUT AND %WB020210.PV.1 | PP78B Dschrg Mode = AUT AND PP78B Dschrg Output ON | KV30939.MODE.AUT AND NOT %WB020210.PV.1 | PP78B Dschrg Mode = AUT AND NOT PP78B Dschrg Output ON | [11 empty] | ".AOFS" Masked by Kal Tails PLC Link OK "KV30932.AOFS" INTERFACES TO LOCAL PLC | 0
KV30943 | DR0063 | .GR0741 .GR0743 | 75-PI-50302 | Tails Booster 78B Drain | VLV05 | CLOSE | x | x | KV30943.MODE.AUT AND %WB020212.PV.1 | PP78B Drain Mode = AUT AND PP78B Drain Output ON | KV30943.MODE.AUT AND NOT %WB020212.PV.1 | PP78B Drain Mode = AUT AND NOT PP78B Drain Output ON | [11 empty] | ".AOFS" Masked by Kal Tails PLC Link OK "KV30932.AOFS" INTERFACES TO LOCAL PLC | 0
KV30962 | DR0063 | .GR0741 | 75-PI-50302 | Tails Booster 78A Flush | VLV08 | N/A | x | [16 empty] | ".AOFS" Masked by Kal Tails PLC Link OK "KV30932.AOFS" INTERFACES TO LOCAL PLC | 0
KV30963 | DR0063 | .GR0741 | 75-PI-50302 | Tails Booster 78B Flush | VLV08 | N/A | x | [16 empty] | ".AOFS" Masked by Kal Tails PLC Link OK "KV30932.AOFS" INTERFACES TO LOCAL PLC | 0
KV301101 | DR0064 | .GR0751 | N/a | Fim1 Booster Suction Vlv | VLV05 | CLOSE | x | x | KV301101.MODE.AUT AND %WB061413.PV.1 | Valve Mode = AUT AND Valve Open Output On | KV301101.MODE.AUT AND %WB061414.PV.1 | Valve Mode = AUT AND Valve Close Output On | [11 empty] | ".AOFS" Masked by Fim1 PLC Link OK "FIM1LINKOK.PV" INTERFACES TO LOCAL PLC | 0
KV301102 | DR0064 | .GR0751 | N/a | Fim1 Booster Dschrg Vlv | VLV05 | CLOSE | x | x | KV301102.MODE.AUT AND %WB061415.PV.1 | Valve Mode = AUT AND Valve Open Output On | KV301102.MODE.AUT AND %WB061416.PV.1 | Valve Mode = AUT AND Valve Close Output On | [11 empty] | ".AOFS" Masked by Fim1 PLC Link OK "FIM1LINKOK.PV" INTERFACES TO LOCAL PLC | 0
KV301103 | DR0064 | .GR0751 | N/a | Fim1 Booster Bps Vlv 1 | VLV05 | CLOSE | x | x | KV301103.MODE.AUT AND %WB061501.PV.1 | Valve Mode = AUT AND Valve Open Output On | KV301103.MODE.AUT AND %WB061502.PV.1 | Valve Mode = AUT AND Valve Open Output On | [11 empty] | ".AOFS" Masked by Fim1 PLC Link OK "FIM1LINKOK.PV" INTERFACES TO LOCAL PLC | 0
KV301104 | DR0064 | .GR0751 | N/a | Fim1 Booster Bps Vlv 2 | VLV05 | CLOSE | x | x | KV301104.MODE.AUT AND %WB061503.PV.1 | Valve Mode = AUT AND Valve Open Output On | KV301104.MODE.AUT AND %WB061504.PV.1 | Valve Mode = AUT AND Valve Open Output On | [11 empty] | ".AOFS" Masked by Fim1 PLC Link OK "FIM1LINKOK.PV" INTERFACES TO LOCAL PLC | 0
KV65361 | DR0008 | .GR0651 |  |  | N/A | N/A |  | x | 65SC31RUN.PV.ON | 65SC31 Drive Running | NOT 65SC31RUN.PV.ON | NOT 65SC31 Drive Running | [11 empty] | Block exists but no I/O associated. Assumption is deleted equipment but logic not completely deleted. | 0

## 7. Control Valves
KCGM GROWTH PROJECT
CONTROL VALVES
Permissive and Trips
Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open | Close | Bypass | Reset Required | Comments | Rev

## 8. PID Cont
KCGM GROWTH PROJECT
PID CONT
|  |  |  | Modes | [5 empty] | Setpoint Limits |  |  | Process Value Limits |  |  | Alarms |  |  |  | Alarm Priority |  | Controlled/Manipulated Variable | [10 empty] | CASCADE INPUT
Tag Source | Tag Name | Drawing | Controller Description | Manual | Auto | Cascade | Process Value Tag | Security Level | Upper Equipment | Min | Max | Unit | Min | Max | Unit | A_LL |  |  | A_HH | Priority | Alarm Masking Conditions | Range Min | Range Max | Lower Limit | Upper Limit | Unit | Destination Description | Destination (Output) Tag | Direct / Reverse Acting | P | I | D | Tag | Description | Comment | Rev
| AC30321 | DR0004 | CIL2 Tk Lime pH Probe 2 | X | X |  | %Z021102 | 3 | 30TK32B | 8.8 | 9.2 | pH | 7.00 | 10.00 | pH | 7 | 7 | 10 | 10 | Medium |  | 0.0 | 100.0 | 10 | 85 | % | PID possibly decomissioned | None | REVERSE | 550 | 60 | 0 |  |  |  | 1 | NO
| FIC30378 | DR0004 | CIL2 CyanideAdditionFlow | X | X |  | %Z021103 | 3 | 30TK32A | 0 | 6 | L/MIN | 0.0 | 20.0 | L/MIN | 0 | 0 | 12.5 | 14 | Medium |  | 0.0 | 100.0 | 0 | 100 | % | FC30378 OUTPUTTO FY30378 (Through High Selector FIC30378AS.IN2) | %Z021104 | REVERSE | 130 | 10 | 0 |  |  |  | 1 | MIN
| MIC30378 | DR0004 | CIL2 CyanideAdditionKGT | X | X | X | FIC30378CALC.CPV1 | 3 | FIM_CIL_2 | 0 | 0.3 | KG/T | 0.00 | 0.40 | KG/T | 0 | 0 | 0.4 | 0.4 | Medium |  | 0.0 | 100.0 | 0 | 100 | % | FC30378 OUTPUTTO FY30378 (Through High Selector FIC30378AS.IN1) | %Z021104 | REVERSE | 400 | 10 | 0 | AIC30381FF |  |  | 1 | MIN
| FIC30622 | DR0019 | CIL3 CyanideAdditionFlow | X | X |  | %Z061101 | 3 | FIM_CIL_3 | 0 | 7 | L/MIN | 0.0 | 20.0 | L/MIN | 0 | 0 | 12.5 | 14 | Medium |  | 0.0 | 100.0 | 0 | 100 | % | AY30622 Cyanide Flow Vlv (Throught High Selector FIC30622AS.IN2) | %Z061102 | REVERSE | 150 | 30 | 0 |  |  |  | 1 | MIN
| MIC30622 | DR0019 | CIL3 CyanideAdditionKGT | X | X | X | FIC30622CALC.CPV1 | 3 | FIM_CIL_3 | 0 | 0.4 | KG/T | 0.00 | 0.30 | KG/T | 0 | 0 | 0.3 | 0.3 | Medium |  | 0.0 | 100.0 | 0 | 100 | % | AY30622 Cyanide Flow Vlv (Throught High Selector FIC30622AS.IN1) | %Z061102 | REVERSE | 400 | 10 | 0 | AIC30381 | CIL2 Cyanide Analyser |  | 1 | MIN
| PIC30607A | DR0020 | Thickener #3 Bed Pressur | X | X |  | PIC30607.PV | 3 | FIM-CIL | 0 | 100 | % | 0.0 | 100.0 | % | 0 | 0 | 80 | 80 | User (14) |  | 0.0 | 1000.0 | 150 | 900 | M3/H | Complex logic see Appendix | PY30608.SET | DIRECT | 50 | 2500 | 0 |  |  |  | 1 | NO
| NIC30601A | DR0020 | Thickener #3 Torque | X | X |  | NI30601.PV | 3 | FIM-CIL | 0 | 100 | % | 0.0 | 100.0 | % | 0 | 0 | 100 | 100 | User (14) |  | 0.0 | 1000.0 | 150 | 900 | M3/H | Complex logic see Appendix | PY30608.SET | DIRECT | 50 | 100 | 0 |  |  |  | 1 | NO
| DIC30613 | DR0020 | Thickener #3 U/F Density | X | X | X | %Z064110 | 3 | FIM-CIL | 0 | 100 | % | 0.0 | 80.0 | % | 10 | 30 | 75 | 80 | User (14) |  | 0.0 | 1000.0 | 150 | 900 | M3/H | Complex logic see Appendix | PY30608.SET | DIRECT | 200 | 1800 | 0 | DIC30613ADD | Via level controller LIC75601DV1 with setpoint addition |  | 1 | NO
| FIC30641 | DR0020 | Thick 3 Byp Flow Ctrl | X | X | X | FI30641.PV | 3 | FIM-CIL | 200 | 1000 | L/MIN | 0.0 | 1000.0 | L/MIN | 0 | 0 | 1000 | 1000 | Medium |  | 0.0 | 100.0 | 25 | 100 | % | Thickener #3U/F Pp A & B Spd (Through High Selector PY30607SEL and Out Splitter PY30607) | %Z063115 %Z063116 | REVERSE | 250 | 120 | 0 | SY30607SEL3 | Highest of: User setpoint FD30615 or NIC30601A or DIC30613 or PIC30607A |  | 1 | HOUR
| FIC30615 | DR0020 | Thick 3 U/F Flow Ctrl | X | X | X | FI30615.PV | 3 | FIM-CIL | 200 | 1000 | L/MIN | 0.0 | 1000.0 | L/MIN | 0 | 0 | 1000 | 1000 | Medium |  | 0.0 | 100.0 | 50 | 100 | % | Thickener #3U/F Pp A & B Spd (Through High Selector PY30607SEL and Out Splitter PY30607) | %Z063115 %Z063116 | REVERSE | 250 | 120 | 0 | SY30607SEL3 | Highest of: User setpoint FD30615 or NIC30601A or DIC30613 or PIC30607A |  | 1 | HOUR
| FIC30684 | DR0020 | CIL3 Lead Nitrate Flow | X | X |  | %Z064112 | 3 | FIM-CIL | 0 | 200 | L/MIN | 0.0 | 200.0 | L/MIN | 0 | 0 | 200 | 200 | Medium |  | 0.0 | 100.0 | 0 | 100 | % | FY30684 CIL3 PBNO3 Addn Output | %Z064113 | REVERSE | 300 | 50 | 0 |  |  |  | 1 | HOUR
| LIC75601DV1 | DR0020 | Thickener 3 Level Control | X | X |  | LI75601.PV | 4 | FIM-CIL | 0 | 100 | % | 0.00 | 100.00 | % | 0 | 0 | 100 | 100 | Logging |  | -30 | 30 | 0 | 3 | %SOL | Thickener #3 U/F Density | DIC30613ADD | REVERSE | 100 | 20 | 0 |  |  |  | 1 | NO
| AC30620 | DR0022 | CIL3 Leach Tank pH | X | X |  | AC30620AVEM.CPV | 3 | 30TK62B | 0 | 9.5 | pH | 8.00 | 10.00 | pH | 8.4 | 8.6 | 9.5 | 9.8 | Medium |  | 0.0 | 100.0 | 5 | 100 | % | PID possibly decomissioned | None | REVERSE | 50 | 200 | 0 |  |  |  | 1 | NO
| LC30719 | DR0023 | FTails Tank Level | X | X |  | LI30719SEL.PV | 3 | 30TK63 | 0 | 100 | % | 0.0 | 100.0 | % | 0 | 30 | 90 | 100 | Medium |  | 0.0 | 1600.0 | 500 | 1150 | M3/H | Through Splitter LY30719.SET | FIC30742.SET FIC30738.SET SY30743ADD.SET FIC30738X SET | DIRECT | 200 | 500 | 0 |  |  |  | 1 | NO
| FIC30738X | DR0023 | FTails Pump D Flow | X | X | X | FI30738.PV | 3 | FIM-CIL | 350 | 1500 | M3/H | 0.0 | 1600.0 | M3/H | 350 | 400 | 1600 | 1600 | Medium |  | 0.0 | 100.0 | 50 | 95 | % | 30PP62D FTails Pump D Selector (Lowest) | SY30745 | REVERSE | 600 | 30 | 0 | LC30719 | Ftails Tank Level (via FOUT LY30719) |  | 1 | NO
| PIC30739A | DR0023 | FTails Pump B Flow (OB: THIS MAY BE AN ERROR) | X | X |  | PI30739.PV | 4 | FIM-CIL | 0 | 1200 | KPA | 0.0 | 1200.0 | KPA | 0 | 0 | 1200 | 1200 | Medium |  | 0.0 | 100.0 | 0 | 100 | % | 30PP62D FTails Pump D Selector (Lowest) | SY30745 | REVERSE | 200 | 40 | 0 |  |  |  | 1 | NO
| IIC30744D | DR0023 | FTails Pump D Current | X | X |  | %Z065111 | 4 | FIM-CIL | 0 | 687 | AMPS | 0.0 | 687.0 | AMPS | 0 | 0 | 687 | 687 | Medium |  | 0.0 | 100.0 | 70 | 100 | % | 30PP62D FTails Pump D Selector (Lowest) | SY30745 | REVERSE | 250 | 5 | 0 |  |  |  | 1 | NO
| FIC30742 | DR0023 | FTails Pump A Flow | X | X | X | FI30742.PV | 3 | FIM-CIL | 460 | 1500 | M3/H | 0.0 | 1600.0 | M3/H | 350 | 400 | 1600 | 1600 | Medium |  | 0.0 | 100.0 | 50 | 95 | % | SY30746A Tails Pp A Speed Output (Through Low Selector SY30742.IN2) | %Z063105 | REVERSE | 600 | 30 | 0 | LC30719 | Ftails Tank Level (via FOUT LY30719) |  | 1 | NO
| FIC30743 | DR0023 | FTails Pump C Flow | X | X | X | FI30743.PV | 3 | FIM-CIL | 460 | 1500 | M3/H | 0.0 | 1600.0 | M3/H | 350 | 400 | 1600 | 1600 | Medium |  | 0.0 | 100.0 | 45 | 100 | % | SY30746C Tails Pp C Speed Output (Through Low Selector SY30743.IN2) | %Z063107 | REVERSE | 400 | 120 | 0 | LC30719 | Ftails Tank Level (via FOUT LY30719) |  | 1 | NO
| FIC30738 | DR0023 | FTails Pump B Flow | X | X | X | FIC30738A.PV | 3 | FIM-CIL | 460 | 1500 | M3/H | 0.0 | 1600.0 | M3/H | 350 | 400 | 1600 | 1600 | Medium |  | 0.0 | 100.0 | 50 | 100 | % | SY30746B Tails Pp B Speed Output (Through Low Selector SY30738.IN2) | %Z063106 | REVERSE | 600 | 120 | 0 | LC30719 | Ftails Tank Level (via FOUT LY30719) |  | 1 | NO
| LIC30719A | DR0023 | FTails Tank Level | X | X |  | LI30719SEL.PV | 3 | FIM-CIL | 0 | 100 | % | 0.0 | 100.0 | % | 0 | 0 | 100 | 100 | Logging |  | -100.0 | 100.0 | -100 | 50 | M3/H | PID possibly decomissioned | None | REVERSE | 1000 | 40 | 0 |  |  |  | 1 | NO
| LIC30719B | DR0023 | FTails Tank Level | X | X |  | LI30719SEL.PV | 3 | FIM-CIL | 0 | 100 | % | 0.0 | 100.0 | % | 0 | 0 | 100 | 100 | Medium |  | 0.0 | 100.0 | 0 | 100 | % | PID possibly decomissioned | None | DIRECT | 100 | 20 | 0 |  |  |  | 1 | NO
| LIC30719C | DR0023 | FTails Tank Level | X | X |  | LI30719SEL.PV | 3 | FIM-CIL | 0 | 100 | % | 0.0 | 100.0 | % | 0 | 0 | 100 | 100 | Medium |  | 0.0 | 100.0 | 0 | 100 | % | PID possibly decomissioned | None | DIRECT | 100 | 20 | 0 |  |  |  | 1 | NO
| PIC30740 | DR0023 | FTails Pump A Flow | X | X |  | PI30740.PV | 4 | FIM-CIL | 0 | 1200 | KPA | 0.0 | 1200.0 | KPA | 0 | 0 | 1200 | 1200 | Medium |  | 0.0 | 100.0 | 40 | 100 | % | SY30746A Tails Pp A Speed Output (Through Low Slector SY30742.IN1) | %Z063105 | REVERSE | 200 | 30 | 0 |  |  |  | 1 | NO
| IIC30744A | DR0023 | Tails Pp A Amps | X | X |  | %Z062107 | 4 | FIM-CIL | 0 | 687 | AMPS | 0.0 | 687.0 | AMPS | 0 | 0 | 687 | 687 | Medium |  | 0.0 | 100.0 | 70 | 100 | % | SY30746A Tails Pp A Speed Output (Through Low Slector SY30742.IN3) | %Z063105 | REVERSE | 250 | 5 | 0 |  |  |  | 1 | NO
| PIC30739 | DR0023 | FTails Pump B Flow | X | X |  | PIC30739CAL.CPV | 4 | FIM-CIL | 0 | 1200 | KPA | 0.0 | 1200.0 | KPA | 0 | 0 | 1200 | 1200 | Medium |  | 0.0 | 100.0 | 40 | 100 | % | SY30746B Tails Pp B Speed Output (Through Low Selector SY30738.IN1) | %Z063106 | REVERSE | 300 | 25 | 0 |  |  |  | 1 | NO
| IIC30744B | DR0023 | Tails Pp B Amps | X | X |  | %Z062108 | 4 | FIM-CIL | 0 | 687 | AMPS | 0.0 | 687.0 | AMPS | 0 | 0 | 687 | 687 | Medium |  | 0.0 | 100.0 | 70 | 100 | % | SY30746B Tails Pp B Speed Output (Through Low Selector SY30738.IN3) | %Z063106 | REVERSE | 250 | 5 | 0 |  |  |  | 1 | NO
| PIC30741 | DR0023 | FTails Pump C Flow | X | X |  | PI30741.PV | 4 | FIM-CIL | 0 | 1200 | KPA | 0.0 | 1200.0 | KPA | 0 | 0 | 1200 | 1200 | Medium |  | 0.0 | 100.0 | 55 | 100 | % | SY30746C Tails Pp C Speed Output (Through Low Selector SY30743.IN1) | %Z063107 | REVERSE | 200 | 30 | 0 |  |  |  | 1 | NO
| IIC30744C | DR0023 | Tails Pp C Amps | X | X |  | %Z062109 | 4 | FIM-CIL | 0 | 687 | AMPS | 0.0 | 687.0 | AMPS | 0 | 0 | 687 | 687 | Medium |  | 0.0 | 100.0 | 70 | 100 | % | SY30746C Tails Pp C Speed Output (Through Low Selector SY30743.IN3) | %Z063107 | REVERSE | 250 | 5 | 0 |  |  |  | 1 | NO
| LIC30719 | DR0045 | FTails Tk Water Additn | X | X |  | LI30719SEL.PV | 3 | FIM-CIL | 0 | 100 | % | 0.0 | 100.0 | % | 0 | 0 | 95 | 100 | Medium |  | 0.0 | 100.0 | 0 | 100 | % | FY30719 Tails HopperWtr Addition (Through High Selector LIC30719ASH.IN1) | %Z072107 | REVERSE | 30 | 500 | 0 |  |  |  | 1 | NO
| PIC30770 | DR0045 | FTails Gland Water Pres | X | X |  | %Z064102 | 4 | FIM-CIL | 0 | 2500 | KPA | 0.0 | 2500.0 | KPA | 1000 | 1400 | 2500 | 2500 | Medium |  | 0.0 | 100.0 | 25 | 100 | % | SY30779 FTails Gland Water Pump A Speed and SY30782 FTails Gland Water Pump B Speed (Via PIC30770FO.SET) | %Z072113 %Z072116 | REVERSE | 65 | 10 | 0 |  |  |  | 1 | NO
| PIC75502 | DR0045 | Cyan Water Pressure | X | X |  | PI75502.PV | 3 | FIM-CIL | 0 | 1000 | KPA | 0.0 | 1000.0 | KPA | 0 | 0 | 1000 | 1000 | Medium |  | 0.0 | 100.0 | 0 | 30 | % | FY30719 Tails HopperWtr Addition (Through High Selector LIC30719ASH.IN2) | %Z072107 | DIRECT | 650 | 25 | 0 |  |  |  | 1 | NO
| AC30320 | DR0004 | CIL2 Tk 32A Lime Add. pH | X | X |  | AI30393C.PV OR AI30393A.PV VIA Selector AC30320SEL | 3 | 30TK32A | 8.8 | 9.5 | pH | 0.0 | 10.0 | pH | 8.4 | 8.6 | 9.95 | 10 | Medium |  | 5.0 | 100.0 | 5 | 100 | % | CIL2 CyanideAdditionKGT | MIC30622 | REVERSE | 50 | 200 | na |  |  | PI Controller only. | 1 | NO
| AIC30381 | DR0004 | CIL2 Cyanide Analyser | X | X |  | %Z021113 (AIC30381AVG) | 3 | CIL2_CN | 0.0 | 500.0 | PPM | 0.0 | 500.0 | PPM | 25 | 50 | 325 | 375 | Medium |  | 0.0 | 0.4 | 0 | 0.3 | KG/T |  |  | REVERSE | 90 | 65 | na |  |  | PI Controller only. | 1 | NO
| AIC30637 | DR0019 | CIL3 Cyanide Analyser | X | X |  | %Z065109 (AIC30637AVG) | 3 | CIL3_CN | 0.0 | 500.0 | PPM | 0.0 | 500.0 | PPM | 25 | 50 | 325 | 375 | Medium |  | 0.0 | 0.4 | 0 | 0.3 | KG/T |  |  | REVERSE | 90 | 65 | na |  |  | PI Controller only. | 1 | NO
| PIC30607 | DR0020 | Thick. #3 Bed Pressure | X | X |  | %Z063114 (Bed pressure tx flot tails thickener 3) | 3 | FIM-CIL | 0.0 | 100.0 | % | 0.0 | 100.0 | % | 0 | 0 | 70 | 75 | User (14) |  | 0.0 | 100.0 | 55 | 97 | % | SY30607SEL | SY30607SEL | DIRECT | 40 | 600 | na |  |  | PI Controller only. | 1 | NO

## 9. Drives
KCGM GROWTH PROJECT
DRIVES
[16 empty] | Start Condition (Auto Mode) |  | Stop Condition (Auto Mode) |  |  | Interlocks
Tag Name | Graphic | P&ID | Name | Drive Type | Speed Min | Speed Max | Speed Units | SP Lower Limit | SP Upper Limit | Current Max | Manual | Auto | Alarm Level | Security Level | Upper Equipment | Tag | Description | Tag | Description | # | Tag | Description | Delay On | Delay Off | Start Permissive | Process | Critical | Hardwired to Drive | Bypass | Reset Required | Comments | Rev
75PW72A | .GR0032 | 75-PI-0462 | Gland Water Pump 72A | UNKNOWN | 0 | 100 | % |  |  |  | X | X | Medium | 1 | FIM-CIL | (75PW72ABSTBYRUN.PV.ON OR (75PW72ABDUTYRUN.PV.ON AND 75PW72ADUTY.PV.ON)) AND: 30SW31NBC.PV.ON AND 30SW31NBC.PV.ON AND 75PW72A.MODE.AUT | Standby pump auto start or (duty pump auto start and pump 75PW72A is duty) and Normal Supply Available and Normal Supply CB closed and Pump 75PW72A in Auto | 75PW72A.ALRM.ANS+ OR (75PW72A.PV.2 AND NOT (75PW72ABSTBYRUN.PV.ON OR (75PW72ABDUTYRUN.PV.ON AND 75PW72ADUTY.PV.ON))) | Pump 75PW72A Fail To Start or (Pump 75PW72A Running and not (Standby pump auto start or (duty pump auto start and Pump 75PW72A selected as duty))) | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW72AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW72ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 75PW72RL.X01.LT | Drive Amps < 30A | 300 |  |  |  | x |  |  |  |  | 0
75PW72B | .GR0032 | 75-PI-0462 | Gland Water Pump 72B | UNKNOWN | 0 | 100 | % |  |  |  | X | X | Medium | 1 | FIM-CIL | (75PW72ABSTBYRUN.PV.ON OR (75PW72ABDUTYRUN.PV.ON AND 75PW72BDUTY.PV.ON)) AND: 30SW31NBC.PV.ON AND 30SW31NBC.PV.ON AND 75PW72B.MODE.AUT | Standby pump auto start or (duty pump auto start and pump 75PW72B is duty) and Normal Supply Available and Normal Supply CB closed and Pump 75PW72B in Auto | 75PW72A.ALRM.ANS+ OR (75PW72B.PV.2 AND NOT (75PW72ABSTBYRUN.PV.ON OR (75PW72ABDUTYRUN.PV.ON AND 75PW72BDUTY.PV.ON))) | Pump 75PW72A Fail To Start or (Pump 75PW72A Running and not (Standby pump auto start or (duty pump auto start and Pump 75PW72A selected as duty))) | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW72BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW72BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
|  |  | (DUTY PUMP CONDITIONS) 75PW72A/B (STANDBY PUMP CONDITIONS) 75PW72A/B | [12 empty] | GS04607-105.PV.ON (5 second delay) GS04507-105.PV.ON (5 second delay) | LI75690 > 85% LI75690 > 75% | GS04807-105.PV.ON (5 second delay) GS04707-105.PV.ON (5 second delay) | LI75690 < 95% LI75690 < 90% | [11 empty] | Duty selected by operator via | 0
[31 empty] | Duty automatically swapped on single drive fault | 0
75PW19A | .GR0311 | 75-PI-0461 | Cyanide Water Pmp19A | DOL | [6 empty] | x |  | Medium | 3 | FIM-CIL | [16 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW19AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW19ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
75PW19A | .GR0311 | 75-PI-0461 | Cyanide Water Pmp19A | DOL | [6 empty] | x |  | Medium | 3 | FIM-CIL | [16 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW19BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW19BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
65AG70 | .GR0649 | 65-PI-1004 | Carbon Attrtion Agitator | DOL | [6 empty] | x |  | Medium | 1 | FIM-CIL | [16 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 65AG70FLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 65AG70STP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 65AG70RL.X01.GE | Lo Hopper Lvl Interlock |  |  |  |  | x |  |  |  |  | 0
65PP70 .GR0649 65-PI-1004 |  |  | Carbon Attrtion Tx Pump | DOL | [6 empty] | x |  | Medium | 1 | FIM-CIL | [16 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 65PP70FLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 65PP70STP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
25CM31C | .GR0051 |  | Flot Air Compressor C | DOL | [6 empty] | x |  | Medium | 3 | FIM-CIL | [16 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 25CM31CFLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[22 empty] | E-Stop | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
81CM33 | .GR0051 | 81-PI-0463 | Instro Air Compressor | DOL | [6 empty] | x |  | Medium | 3 | FIM-CIL | [16 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 81CM33FLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[22 empty] | E-Stop | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30SC62B | .GR0330 | 2000-F30-PID-PR-10008 | CIL3 Tk62B Inter Screen | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SW62NAV.PV.ON (15 secs delay) | Normal Power Available (sub 68) (15 second delay) | 30SC62B.ALRM.ANS+ | Drive Failed to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SC62BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC62BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 81CM33FLT | Compressor Trip Fault |  |  |  |  | x |  |  |  |  | 0
30SC62C | .GR0330 | 2000-F30-PID-PR-10008 | CIL3 Tk62C Inter Screen | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SW62NAV.PV.ON (20 secs delay) | Normal Power Available (sub 68) (20 second delay) | 30SC62C.ALRM.ANS+ | Drive Failed to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SC62CFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC62CSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30SC62D | .GR0330 | 2000-F30-PID-PR-10009 | CIL3 Tk62D Inter Screen | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SW62NAV.PV.ON (25 secs delay) | Normal Power Available (sub 68) (25 second delay) | 30SC62D.ALRM.ANS+ | Drive Failed to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SC62DFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC62DSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30SC62E | .GR0330 | 2000-F30-PID-PR-10009 | CIL3 Tk62E Inter Screen | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SW62NAV.PV.ON (30 secs delay) | Normal Power Available (sub 68) (30 second delay) | 30SC62E.ALRM.ANS+ | Drive Failed to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SC62EFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC62ESTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30SC62F | .GR0330 | 2000-F30-PID-PR-10009 | CIL3 Tk62F Inter Screen | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SW62NAV.PV.ON (35 secs delay) | Normal Power Available (sub 68) (35 second delay) | 30SC62F.ALRM.ANS+ | Drive Failed to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SC62FFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC62FSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30PP66 | .GR0652 | 2000-F30-PID-PR-10008 | CIL3 Loaded Carb Txfr Pp | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | [16 empty] | 1
[16 empty] | (((FV3065A.MV.2 AND FV3065B.MV.0) AND ((CR3MTOCIL2.PV.OFF AND 65SC65RUN.PV.ON) OR (65SC31RUN.PV.ON AND CR3MTOCIL2.PV.ON))) AND NOT(CR3MSTP.PV.ON)) OR (CR3MOVRST.PV.1 AND 30PP66OVR.PV.1) | See Appendix A - Item 1 | ((NOT ((CR3MTOCIL2.PV.OFF AND 65SC65RUN.PV.ON) OR (65SC31RUN.PV.ON AND CR3MTOCIL2.PV.ON)) OR CR3MSTP.PV.ON OR 30PP66.ALRM.ANS+) OR (CR3MTMR1.BSTS.CTUP AND CR3MTMR1.BSTS.CTUP) OR 30PP66TM.BSTS.CTUP OR (CR2MTOCIL3.PV.ON AND (CR2MSTT.PV.ON OR CR2M.BSTS.RUN)) | See Appendix A - Item 1 |  |  | Comunication Fault |  |  |  |  | x |  |  |  | - LC block set a timer for manual operation up to 4 hours then stop (check LC2) - CIL logic on DR0010 - Timers logic in block LSH65966LC on DR0026 | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP66FLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP66STP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
65SC65 | .GR0652 | 2000-F30-PID-PR-10008 | CIL3 Loaded Carbon Scrn | DOL | [6 empty] | x | x | Medium | 3 | 65SC65 | %GS01906.PV.ON AND ((CR3MSTT.PV.ON AND CR3MTOCIL2.PV.OFF) OR (CR2MSTT.PV.ON AND CR2MTOCIL3.PV.ON)) | Inlet Valve Open AND ((CR3M Module Start AND NOT CR3M To CIL2) OR (CR2M Mudule Start AND CR2M To CIL3)) | (30PP66RUN.PV.OFF AND 65SC65TM.BSTS.CTUP) OR 65SC65.ALRM.ANS+ | Drive Running And 13 Minute Off Delay Timer Completed OR Drive Fail To Start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | - CIL logic on DR0010 - Timers logic in block LSH65966LC on DR0026 - FV30680 Auto start and stop logic inside LC block | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 65SC65FLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 65SC65STP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30PP65A | .GR0330 | 2000-F30-PID-PR-10009 | CIL3 Tk62F Carbon Pump | DOL | [6 empty] | x | x | Medium | 3 | FIM_CIL_TRAINS | 30PP65ASST.PV.ON | Sequence Start, See CTR3MSFC | NOT (30PP65ASST.PV.ON AND NOT 30PP65A.ALRM.ANS+) | Drive not in Auto mode or fail to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP65AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP65ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30PP65B | .GR0330 | 2000-F30-PID-PR-10009 | CIL3 Tk62E Carbon Pump | DOL | [6 empty] | x | x | Medium | 3 | FIM_CIL_TRAINS | 30PP65BSST.PV.ON | Sequence Start, See CTR3MSFC | NOT (30PP65BSST.PV.ON AND NOT 30PP65B.ALRM.ANS+) | Drive not in Auto mode or fail to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP65BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP65BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30PP65C | .GR0330 | 2000-F30-PID-PR-10009 | CIL3 Tk62D Carbon Pump | DOL | [6 empty] | x | x | Medium | 3 | FIM_CIL_TRAINS | 30PP65CSST.PV.ON | Sequence Start, See CTR3MSFC | NOT (30PP65CSST.PV.ON AND NOT 30PP65C.ALRM.ANS+) | Drive not in Auto mode or fail to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Manual mode operation limited to 6 hours then the drive is stopped | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP65CFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP65CSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30PP65D | .GR0330 | 2000-F30-PID-PR-10008 | CIL3 Tk62C Carbon Pump | DOL | [6 empty] | x | x | Medium | 3 | FIM_CIL_TRAINS |  | See Appendix A - Item 2 |  | See Appendix A - Item 2 | [11 empty] | Manual mode operation limited to 6 hours then the drive is stopped | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP65DFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP65DSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | %GS01806.PV.ON OR NOT (FV3065B.MV.2 AND FV3065A.MV.0) | Level Switch High (remote source) OR NOT Ld Carbn PP65D to SC65 active AND Ld Carbn PP65D to PP66 inactive |  |  |  | x | [5 empty] | 0
30PS61A | .GR0330 | 2000-F30-PID-PR-10008 | CIL3 Area Sump Pump A | DOL | [6 empty] | x |  | Medium | 3 | FIM-CIL | [16 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PS61AFLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[22 empty] | E-Stop | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30PS61B | .GR0330 | 2000-F30-PID-PR-10008 | CIL3 Area Sump Pump B | DOL | [6 empty] | x |  | Medium | 3 | FIM-CIL | [16 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PS61BFLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[22 empty] | E-Stop | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30PS61C | .GR0330 | 2000-F30-PID-PR-10009 | CIL3 Area Sump Pump C | DOL | [6 empty] | x |  | Medium | 3 | FIM-CIL | [16 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PS61CFLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[22 empty] | E-Stop | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30AG62A | .GR0330 | 2000-F30-PID-PR-10008 | CIL3 Tk62A Agitator | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SW62NAV.PV.ON 60 Second delay %SW0869 (CIL3GRPSTT) 1 second delay | Normal power available on for 60 seconds CIL 3 Group Start 1 second delay | 30AG62A.ALRM.ANS+ | Drive fail to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30AG62AFLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30AG62ASTP | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30AG62B | .GR0330 | 2000-F30-PID-PR-10008 | CIL3 Tk62B Agitator | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SW62NAV.PV.ON 65 Second delay %SW0869 (CIL3GRPSTT) 3 second delay | Normal power available on for 65 seconds CIL 3 Group Start 3 second delay | 30AG62A.ALRM.ANS+ | Drive fail to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30AG62BFLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30AG62BSTP | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30AG62C | .GR0330 | 2000-F30-PID-PR-10008 | CIL3 Tk62C Agitator | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SW62NAV.PV.ON 70 Second delay %SW0869 (CIL3GRPSTT) 6 second delay | Normal power available on for 70 seconds CIL 3 Group Start 6 second delay | 30AG62C.ALRM.ANS+ | Drive fail to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30AG62CFLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30AG62CSTP | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30AG62D | .GR0330 | 2000-F30-PID-PR-10009 | CIL3 Tk62D Agitator | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SW62NAV.PV.ON 75 Second delay %SW0869 (CIL3GRPSTT) 10 second delay | Normal power available on for 75 seconds CIL 3 Group Start 10 second delay | 30AG62D.ALRM.ANS+ | Drive fail to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30AG62DFLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30AG62DSTP | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30AG62E | .GR0330 | 2000-F30-PID-PR-10009 | CIL3 Tk62E Agitator | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SW62NAV.PV.ON 80 Second delay %SW0869 (CIL3GRPSTT) 15 second delay | Normal power available on for 80 seconds CIL 3 Group Start 15 second delay | 30AG62E.ALRM.ANS+ | Drive fail to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30AG62EFLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30AG62ESTP | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30AG62F | .GR0330 | 2000-F30-PID-PR-10009 | CIL3 Tk62F Agitator | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SW62NAV.PV.ON 85 Second delay %SW0869 (CIL3GRPSTT) 21 second delay | Normal power available on for 85 seconds CIL 3 Group Start 21 second delay | 30AG62F.ALRM.ANS+ | Drive fail to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30AG62FFLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30AG62FSTP | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30TH61 | .GR0302 | 2000-F30-PID-PR-10001 | Thickener 3 Rake Drive | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | (30SW62EAV.PV.ON OR 30SW62NAV.PV.ON) AND NOT 30TH61.ALRM.ANS+ | (Emergency Power Available Or Normal Power Available) AND Drive not Fail To Start | see description | Auto stop condition is the invert of the auto start condition | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30TH61FLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30TH61STP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30PP61A | .GR0302 | 2000-F30-PID-PR-10001 | Thickener 3 U/F Pump A | VSD | 0 | 100 | % |  |  |  | x | x | Medium | 3 | FIM-CIL | 30PP61ASST.PV.ON | Sequence Start | 30PP61A.ALRM.ANS+ | Drive fail to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP61AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP61ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | FV30608A.PV.2 | Thickener 3 Underflow Pump A Suction Valve Open |  |  |  | x | [5 empty] | 0
[21 empty] | FV30649A.PV.2 | Thickener 3 Underflow Dilution Water Valve A Open |  |  |  | x | [5 empty] | 0
[21 empty] | (NOT FI30808.ALRM.LL) OR FI30808.AOFS.AOF OR 30PP61ARUN.PV.1 | Glandwater Low Flow Alarm (masked against drive running and alarm disable) |  |  |  |  | x |  |  |  |  | 0
30PP61B | .GR0302 | 2000-F30-PID-PR-10001 | Thickener 3 U/F Pump B | VSD | 0 | 100 | % |  |  |  | x | x | Medium | 3 | FIM-CIL | 30PP61BSST.PV.ON | Sequence Start | 30PP61B.ALRM.ANS+ | Drive fail to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP61BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP61BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | FV30608B.PV.2 | Thickener 3 Underflow Pump B Suction Valve Open |  |  |  | x | [5 empty] | 0
[21 empty] | FV30649B.PV.2 | Thickener 3 Underflow Dilution Water Valve B Open |  |  |  | x | [5 empty] | 0
[21 empty] | (NOT FI30808.ALRM.LL) OR FI30808.AOFS.AOF OR 30PP61BRUN.PV.1 | Glandwater Low Flow Alarm (masked against drive running and alarm disable) |  |  |  |  | x |  |  |  |  | 0
75PW62A | .GR0031 | 75-PI-0461 | CircuitWaterPump A | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 75PW62ACHG.PV.ON | Duty Changeover Pump A | 75PW62BCHG.PV.ON | Duty Changeover Pump B | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW62AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW62ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
75PW62B | .GR0031 | 75-PI-0461 | CircuitWaterPump B | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 75PW62BCHG.PV.ON | Duty Changeover Pump B | 75PW62ACHG.PV.ON | Duty Changeover Pump A | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
75PW17A | .GR0031 | 2000-F75-PID-PR-1003 | Bore Water Pump 17A | DOL | [6 empty] | x | x |  | 3 | FIM_BORE_WTR | [5 empty] | 75PW62BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW62BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[13 empty] | Medium | [18 empty] | 1
[16 empty] | 75PW17SEL.MV01.ON AND 75PW17DTYSTT.PV.ON 75PW17SEL.MV02.ON AND 75PW17SBYSTT.PV.ON | Pump A is Duty AND Duty Run Requested Pump A is Standby AND Standby Run Requested | 75PW17SEL.MV01.ON AND 75PW17DTYSTT.PV.OFF 75PW17SEL.MV02.ON AND 75PW17SBYSTT.PV.OFF | Pump A is Duty AND Duty Run is not requested Pump A is Standby AND Standby Run is not requested |  |  | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW17AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW17ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
75PW17B | .GR0031 | 2000-F75-PID-PR-1003 | Bore Water Pump 17B | DOL | [6 empty] | x | x | Medium | 3 | FIM_BORE_WTR | 75PW17SEL.MV02.ON AND 75PW17DTYSTT.PV.ON 75PW17SEL.MV01.ON AND 75PW17SBYSTT.PV.ON | Pump B is Duty AND Duty Run Requested Pump B is Standby AND Standby Run Requested | 75PW17SEL.MV02.ON AND 75PW17DTYSTT.PV.OFF 75PW17SEL.MV01.ON AND 75PW17SBYSTT.PV.OFF | Pump B is Duty AND Duty Run is not requested Pump B is Standby AND Standby Run is not requested | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW17BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW17BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
81CM61 | .GR0051 | N/A | Instrument Compressor | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 81CM61.MODE.AUT | Compressor in auto mode | NOT 81CM61.MODE.AUT | Compressor not in auto mode | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 81CM61FLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 81CM61STP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30SL61A | .GR0340 | 2000-F30-PID-PR-10010 | CarbonSafetyScreen A | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SL61ASST.PV.ON | Sequence Start | NOT 30SL61ASST.PV.ON | Not Sequence Start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SL61AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SL61ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | HA30704A.PV.OFF | Pull Wire |  |  |  |  | x |  |  |  |  | 0
[21 empty] | ZA30703A.PV.OFF | Belt Drift Switch (While Belt Drift Bypass inactive) |  |  |  |  | x |  |  |  | Belt Drift bypass only allowed for 120 seconds | 0
30SL61B | .GR0340 | 2000-F30-PID-PR-10010 | CarbonSafetyScreen B | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SL61BSST.PV.ON | Sequence Start | NOT 30SL61BSST.PV.ON | Not Sequence Start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SL61BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SL61BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | HS30706A.PV.OFF | Pull Wire |  |  |  |  | x |  |  |  |  | 0
[21 empty] | ZS30705A.PV.OFF | Belt Drift Switch (While Belt Drift Bypass inactive) |  |  |  |  | x |  |  |  | Belt Drift bypass only allowed for 120 seconds | 0
30SL61C | .GR0340 | 2000-F30-PID-PR-10010 | CarbonSafetyScreen C | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SL61CSST.PV.ON | Sequence Start | NOT 30SL61CSST.PV.ON | Not Sequence Start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SL61CFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SL61CSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | HS30708A.PV.OFF | Pull Wire |  |  |  |  | x |  |  |  |  | 0
[21 empty] | ZS30707A.PV.OFF | Belt Drift Switch (While Belt Drift Bypass inactive) |  |  |  |  | x |  |  |  | Belt Drift bypass only allowed for 120 seconds | 0
30SL61D | .GR0340 | 2000-F30-PID-PR-10010 | CarbonSafetyScreen D | DOL | [6 empty] | x | x | Medium | 3 | 30SL61D | 30SL61DSST.PV.ON | Sequence Start | NOT 30SL61DSST.PV.ON | Not Sequence Start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SL61DFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SL61DSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | HA30710A.PV.OFF | Pull Wire |  |  |  |  | x |  |  |  |  | 0
[21 empty] | ZA30709A.PV.OFF | Belt Drift Switch (While Belt Drift Bypass inactive) |  |  |  |  | x |  |  |  | Belt Drift bypass only allowed for 120 seconds | 0
30PP62A | .GR0341 | 2000-F30-PID-PR-10015 | FTails Pump A | VSD | 0 | 100 | % |  |  |  | x | x | Medium | 3 | 30PP62A | [15 empty] | When started this sets FV30731A.MODE.AUT, | 1
[16 empty] | (30PP62ASST.PV.ON OR 30PP62ASLT.PV.ON) AND FV30720A.PV.2 | Drive selected to run and suction valve open | 30PP62ASLT.PV.OFF (1800 Second Delay) (30PP62B1SLT.PV.ON OR 30PP62A.PV.0) 30 second delay 30SW31NAV.PV.OFF | Drive selected to stop (1800 second delay) Either the "B" drive is selected to run or Ftails Pump A is faulted (both with 30 second delay) POWER OUTAGE SUB38 |  |  | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP62AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP62ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | FAL30727A.PV.OFF OR FAL30727A.AOFS.AOF | Glandwater Flow (Masked against alarm disabled) |  | 1800 |  |  | x |  |  |  |  | 0
[21 empty] | TI30761A.ALRM.HH | Motor Temp Alarm |  | 2 |  |  | x |  |  |  | See Appendix A - Item 3 | 0
[21 empty] | TI30761B.ALRM.HH | Motor Temp Alarm |  | 2 |  |  | x |  |  |  |  | 0
[21 empty] | TI30761C.ALRM.HH | Motor Temp Alarm |  | 2 |  |  | x |  |  |  |  | 0
[21 empty] | PAHH30740.PV.OFF | Line A Press HH |  |  |  |  | x |  |  |  |  | 0
[21 empty] | FALL30742.PV.OFF OR (FV30722A.PV.2 AND FV30720A.PV.0) | Line A Flow LL OR (Tails Pump A Flush Water Valve Open AND Tails Pump A Feed Valve Closed) |  |  |  |  | x |  |  |  |  | 0
[21 empty] | FAHH30741.PV.OFF OR (FV30722A.PV.2 AND FV30720A.PV.0) | Line A Flow Diff HH OR (Tails Pump A Flush Water Valve Open AND Tails Pump A Feed Valve Closed) |  |  |  |  | x |  |  |  |  | 0
[21 empty] | PALL30740.PV.OFF OR (FV30722A.PV.2 AND FV30720A.PV.0) | Line A Possible Burst OR (Tails Pump A Flush Water Valve Open AND Tails Pump A Feed Valve Closed) |  |  |  |  | x |  |  |  |  | 0
[21 empty] | ((PP77B-BYPASS.PV.ON OR %WB001711.PV.1) AND TAILSLINEA- FIM.PV.ON) OR (TAILSLINEA-KAL.PV.ON AND (PP78A- BYPASS.PV.ON OR %WB021714.PV.1)) | Either: Booster 77B is bypassed or not ready while Line A to Fim 2 is active, or Booster 78A is bypassed or not ready while line A to Kal A is active |  |  |  |  | x |  |  |  |  | 0
30PP62B | .GR0341 | 2000-F30-PID-PR-10015 | FTails Pump B | VSD | 0 | 100 | % |  |  |  | x | x | Medium | 3 | FIM-CIL | ((30PP62B1SST.PV.ON OR 30PP62B1SLT.PV.ON) OR 30PP62B2SLT.PV.ON OR (30PP62B3SLT.PV.ON OR 30PP62B3SST.PV.ON)) AND FV30720B.PV.2 | (B1 Selected to run (SST or SLT) OR B2 Selected to run (SLT) OR B3 Selected to run (SST or SLT)) AND Suction Valve is open | See Appendix A - Item 4 | See Appendix A - Item 4 | [11 empty] | Starting this drive will set valve FV30731B to auto and open it | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP62BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP62BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | FAL30727B.PV.OFF OR FAL30727B.AOFS.AOF | Gland Water Flow Alarm OR Gland Wtr Flow Alrm AOF | 3600 |  |  |  | x |  |  |  |  | 0
[21 empty] | TI30763A.ALRM.HH OR TI30763B.ALRM.HH OR TI30763C.ALRM.HH | Any motor temperature alarm | 120 |  |  |  | x |  |  |  |  | 0
[21 empty] | (FV30722B.PV.2 AND FV30720B.PV.0) OR 30PP62BRUN.PV.ON | Tails Pump B Flush Water Valve Open and Tails Pump B Feed Valve Closed while drive running | 10 |  |  |  | x |  |  |  |  | 0
[21 empty] | PUMPBTOLINEB.PV.ON AND (FALL30738.PV.OFF AND FAHH30739.PV.OFF AND PALL30739.PV.OFF AND PAHH30739.PV.OFF) | Line B flow Low Low OR High High OR Burst OR Pressure High High while Tails Pump B is operating down Line B | 3 |  |  |  | x |  |  |  |  | 0
[21 empty] | PUMPBTOLINEA.PV.ON AND (FALL30742.PV.OFF AND FAHH30741.PV.OFF AND PALL30740.PV.OFF AND PAHH30740.PV.OFF) | Line A flow Low Low OR High High OR Burst OR Pressure High High while Tails Pump B is operating down Line A | 3 |  |  |  | x |  |  |  |  | 0
[21 empty] | PUMPBTOLINEC.PV.ON AND (FALL30743.PV.OFF AND FAHH30744.PV.OFF AND PALL30741.PV.OFF AND PAHH30741.PV.OFF) | Line C flow Low Low OR High High OR Burst OR Pressure High High while Tails Pump B is operating down Line C | 3 |  |  |  | x |  |  |  | See Appendix A - Item 5 | 0
[21 empty] | TAILSLINEC-FIM.PV.ON AND ( %WB001714.PV.1 OR PP77A- BYPASS.PV.ON ) AND ( ( (NOT(30PP62C.PV.2 AND FV30720C.PV.2) ) OR FV30720B.PV.0 ) AND 30PP62B-LINEC.PV.ON ) | Line B to FIM 2 B Operating AND ( Booster 77A Not Ready OR Bypassed ) AND ( Pump C Not Running Or its suction not open Or Pump B's suction is not closed while tails pump B down line C is active ) |  |  |  |  | x |  |  |  | See Appendix A - Item 6 | 0
[21 empty] | TAILSLINEC-KAL.PV.ON AND ( %WB021714.PV.1 OR PP78A- BYPASS.PV.ON ) AND ( ( (NOT(30PP62C.PV.2 AND FV30720C.PV.2) ) OR FV30720B.PV.0 ) AND 30PP62B-LINEC.PV.ON ) | Line B to KAL A Operating AND ( Booster 78A Not Ready OR Bypassed ) AND ( Pump C Not Running Or its suction not open Or Pump B's suction is not closed while tails pump B down line C is active ) |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TAILSLINEA-FIM.PV.ON AND ( %WB021711.PV.1 OR PP78B- BYPASS.PV.ON ) AND ( 30PP62B-LINEA.PV.ON AND (NOT 30PP62A.PV.2 AND FV30720A.PV.2) OR FV30720B.PV.0 ) | Line A to FIM 2 A Operating AND ( Booster 78B Not Ready OR Bypassed ) AND ( Tails Pump B Operating Down Line A While Pump A Is Running with its suction valve is open and not closed ) |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TAILSLINEC-KALB.PV.ON AND ( %WB021711.PV.1 OR PP78B- BYPASS.PV.ON ) AND ( ( (NOT(30PP62C.PV.2 AND FV30720C.PV.2) ) OR FV30720B.PV.0 ) AND 30PP62B-LINEC.PV.ON ) | Line B to KAL B AND ( Booster 78B Not Ready OR Bypassed ) AND ( Pump C Not Running Or its suction not open Or Pump B's suction is not closed while tails pump B down line C is active ) |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TAILSLINEB-OLD.PV.ON AND ( 30PP62B-LINEB.PV.ON AND (FV30720B.PV.0 OR NOT(30PP62D.PV.2 AND KV30720D.PV.2)) ) AND ( (KV301104.PV.2 AND KV301103.PV.2) OR (%WB060114.PV.1 AND 30PP79.ALRM.NR) OR (PI301110.ALRM.LL AND %WB060114.PV.0) ) | Line B to FIM 1 Operating AND ( Tails Pump B Down Line B AND Either Pump B Suction Clsd OR (Pump D Running With suction open) ) AND ( (Booster 79 Byp Vlv 1 and 2 Open) OR (Booster 79 Ready AND Not Tripped) OR (PP79 Low Suction Pres AND Booster 79 Is Ready) ) |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TAILSLINEB-NEW.PV.ON AND ( %WB021714.PV.1 OR PP78A- BYPASS.PV.ON ) AND ( 30PP62B-LINEB.PV.ON AND (FV30720B.PV.0 OR NOT(30PP62D.PV.2 AND KV30720D.PV.2)) ) | Line B to KAL A Operating AND ( Booster 78A Not Ready OR Bypassed ) AND ( Tails Pump B Down Line B AND Either Pump B Suction Clsd OR (Pump D Running With suction open) ) |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TAILSLINEA-KAL.PV.ON AND ( %WB021714.PV.1 OR PP78A- BYPASS.PV.ON ) AND ( 30PP62B-LINEA.PV.ON AND (NOT 30PP62A.PV.2 AND FV30720A.PV.2) OR FV30720B.PV.0 ) | Line A to KAL A Operating AND ( Booster 78A Not Ready OR Bypassed ) AND ( Tails Pump B Operating Down Line A While Pump A Is Running with its suction valve is open and not closed ) |  |  |  |  | x |  |  |  |  | 0
30PP62C | .GR0341 | 2000-F30-PID-PR-10015 | FTails Pump C | VSD | 0 | 100 | % |  |  |  | x | x | Medium | 3 | 30PP62C | (30PP62CSST.PV.ON OR 30PP62CSLT.PV.ON) AND FV30720C.PV.2 | Drive selected to run (either SST or SLT) and suction valve is open | 30PP62B3SLT.PV.ON OR 30PP62C.PV.0 (30 second timer) 30PP62CSLT.PV.OFF (1800 second timer) | Drive B selected to run or drive C failed (30 second delay timer) Drive selected to stop (1800 second delay timer) | [11 empty] | Starting this drive will set valve FV30731C to auto and open it | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP62CFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP62CSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP62CRDY.PV.OFF | Drive Ready |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP62CRUN.PV.OFF | Drive Not Running (Fail to start) | 3 |  |  | x |  |  |  |  | See Appendix A - Item 7 | 0
[21 empty] | FAL30727C.PV.OFF OR FAL30727C.AOFS.AOF | Gland Water Flow Alarm (While alarm enabled) | 600 |  |  |  | x |  |  |  | This has a comment marking the timer 1800 sec, but its currently configured as 600 sec | 0
[21 empty] | TI30765A.ALRM.HH OR TI30765B.ALRM.HH OR TI30765C.ALRM.HH | Any motor temperature high high alarm | 120 |  |  |  | x |  |  |  |  | 0
[21 empty] | PAHH30741.PV.OFF | Line C Press HH |  |  |  |  | x |  |  |  |  | 0
[21 empty] | (FV30722C.PV.2 AND FV30720C.PV.0) OR FALL30743.PV.OFF | Line C Flow LL While Tails Pump C Flush Water On and Tails Pump C Feed Valve Off |  |  |  |  | x |  |  |  |  | 0
[21 empty] | (FV30722C.PV.2 AND FV30720C.PV.0) OR FAHH30744.PV.OFF | Line C Flow Diff HH While Tails Pump C Flush Water On and Tails Pump C Feed Valve Off |  |  |  |  | x |  |  |  |  | 0
[21 empty] | (FV30722C.PV.2 AND FV30720C.PV.0) OR PALL30741.PV.OFF | Line C Possible Burst While Tails Pump C Flush Water On and Tails Pump C Feed Valve Off |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TAILSLINEC-FIM.PV.ON AND (PP77A-BYPASS.PV.ON OR %WB00171 | 4Line C to FIM 2 B Operating while Booster 77A Ready Or Bypassed |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TAILSLINEC-KAL.PV.ON AND (PP78A-BYPASS.PV.ON OR %WB02171 | Line C to KAL A Operating while Booster 78A Ready Or Bypassed |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TAILSLINEC-KALB.PV.ON AND (PP78B-BYPASS.PV.ON OR %WB0217 | Line C to KAL B Operating while Booster 78B Ready Or Bypassed |  |  |  |  | x |  |  |  |  | 0
30PP62D | .GR0311 | 2000-F30-PID-PR-10015 | FTails Pump D | VSD | 0 | 100 | % |  |  | 662.5 | x |  | Medium | 3 | 30PP62D | [15 empty] | Pump D Running will put SY30745, IIC30744D into auto. Drive stopped will put KV30720D into auto, close the valve and then set into manual all 2 seconds apart. | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP62DFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP62DSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP62DRDY.PV.OFF | Drive Ready |  |  |  |  | x |  |  |  |  | 0
[21 empty] | FI30727D.ALRM.LL OR FI30727D.AOFS.AOF | Gland Water Flow Alarm (While alarm enabled) | 600 |  |  |  | x |  |  |  | See Appendix A - Item 8 | 0
[21 empty] | TI30754A.ALRM.HH OR TI30754B.ALRM.HH OR TI30754C.ALRM.HH | Any motor temperature high high alarm | 120 |  |  |  | x |  |  |  |  | 0
[21 empty] | PAHH30739.PV.OFF | PAHH30739.PV.OFF |  |  |  |  | x |  |  |  |  | 0
[21 empty] | (KV30722D.PV.2 AND KV30720D.PV.0) OR FALL30738.PV.OFF | Line D Flow LL While Tails Pump B Flush Water On and Tails Pump B Feed Valve Off |  |  |  |  | x |  |  |  |  | 0
[21 empty] | (KV30722D.PV.2 AND KV30720D.PV.0) OR FAHH30739.PV.OFF | Line D Flow Diff HH While Tails Pump B Flush Water On and Tails Pump B Feed Valve Off |  |  |  |  | x |  |  |  |  | 0
[21 empty] | (KV30722D.PV.2 AND KV30720D.PV.0) OR PALL30739.PV.OFF | Line D Possible Burst While Tails Pump B Flush Water On and Tails Pump B Feed Valve Off |  |  |  |  | x |  |  |  |  | 0
[21 empty] | (TAILSLINEB-NEW.PV.ON AND (PP78A-BYPASS.PV.ON OR %WB021714.PV.1)) OR ( TAILSLINEB-OLD.PV.ON AND ( (KV301103.PV.2 AND KV301104.PV.2) OR ( %WB060114.PV.1 AND NOT 30PP79.ALRM.TRIP ) OR (PI301110.ALRM.LL OR %WB060114.PV.0 (5 second delay)))) | Line B to KAL A AND Booster 78A Bypassed Or Not Ready OR ( Line B to FIM 1 Operating AND ( (Booster 79 Bypass Valves 1 and 2 closed) OR (Booster 79 Ready And Not Tripped) OR ( PP79 Low Suction Pressure and Booster 79 Not Ready (5 second delay) ) ) ) |  |  |  |  | x |  |  |  |  | 0
30SC64A | .GR0340 | 2000-F30-PID-PR-10010 | Fine Carbon Dewater Scrn | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SL61A.PV.2 OR 30SL61B.PV.2 | Sequence Start A or B | NOT (30SL61A.PV.2 OR 30SL61B.PV.2) 30SC64A.ALRM.ANS+ | Neither Sequence Start A or B Drive failed to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SC64AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC64ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30SC64B | .GR0340 | 2000-F30-PID-PR-10010 | Fine Carbon Dewater Scrn | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | 30SL61C.PV.2 OR 30SL61D.PV.2 | Sequence Start C or D | NOT (30SL61C.PV.2 OR 30SL61D.PV.2) 30SC64B.ALRM.ANS+ | Neither Sequence Start Cor D Drive failed to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SC64BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC64BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30FN62A | .GR0341 | N/A | FTails Pmp ACooling Fan | DOL | [6 empty] | x | x | Medium | 1 | 30PP62A | 30PP62A.PV.2 | Sequence A start | NOT 30PP62A.PV.2 (300 Sec Delay) 30FN62A.ALRM.ANS+ | No sequence A start (300 second delay) Drive failed to start | [11 empty] | "30PP62A.PV.2" sequence A start will set drive into Auto mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30FN62AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[22 empty] | E-Stop | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 30PP62AILK | Pump 30PP62A (Ftails A) is interlocked |  |  |  |  | x |  |  |  |  | 0
[21 empty] | PUMPAILKSW | Pump 30PP62A (Ftails A) is interlocked |  |  |  |  | x |  |  |  |  | 0
30FN62B | .GR0341 | N/A | Ftails Pump B Cooling Fan | DOL | [6 empty] | x | x | Medium | 1 | FIM-CIL | 30PP62B.PV.2 | Sequence B start | NOT 30PP62B.PV.2 (300 Sec Delay) 30FN62B.ALRM.ANS+ | No sequence B start (300 second delay) Drive failed to start | [11 empty] | "30PP62B.PV.2" sequence B start will set drive into Auto mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30FN62BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[22 empty] | E-Stop | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 30PP62BILK | Pump 30PP62B (Ftails B) is interlocked |  |  |  |  | x |  |  |  |  | 0
[21 empty] | PUMPBILKSW | Pump 30PP62B (Ftails B) is interlocked |  |  |  |  | x |  |  |  |  | 0
30FN62C | .GR0341 | N/A | Ftails Pump C Cooling Fan | DOL | [6 empty] | x | x | Medium | 1 | 30PP62C | 30PP62C.PV.2 | Sequence C start | NOT 30PP62C.PV.2 (300 Sec Delay) 30FN62C.ALRM.ANS+ | No sequence C start (300 second delay) Drive failed to start | [11 empty] | "30PP62C.PV.2" sequence C start will set drive into Auto mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP62CFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP62CSSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP62CRDY | Drive Ready |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP62CILK | Pump 30PP62C (Ftails C) is interlocked |  |  |  |  | x |  |  |  |  | 0
[21 empty] | PUMPCILKSW | Pump 30PP62C (Ftails C) is interlocked |  |  |  |  | x |  |  |  |  | 0
30FN62D | .GR0341 | N/A | FTails Pmp DCooling Fan | DOL | [6 empty] | x | x | Medium | 1 | FIM-CIL | 30PP62D.PV.2 | Sequence D Start | NOT 30PP62D.PV.2 (300 Sec Delay) 30FN62D.ALRM.ANS+ | No sequence D start (300 second delay) Drive failed to start | [11 empty] | "30PP62D.PV.2" sequence D start will set drive into Auto mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30FN62DFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[22 empty] | E-Stop | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 30PP62DILK | Pump 30PP62D (Ftails D) is interlocked |  |  |  |  | x |  |  |  |  | 0
[21 empty] | PUMPDILKSW | Pump 30PP62D (Ftails D) is interlocked |  |  |  |  | x |  |  |  |  | 0
80CB64 | .GR0042 | N/A | South SwYardHarm. Filter | DOL | [6 empty] | x | x | Medium | 1 | FIM-CIL | %GS00101.PV.1 %GS00201.PV.1 GS02907-105.PV.1 GS07303-105.PV.1 | MTC SAG Running MTC BM Running FIM BM1 Running FIM BM2 Running | NOT (%GS00101.PV.1 OR %GS00201.PV.1 OR GS02907-105.PV.1 OR GS07303-105.PV.1) | None of the auto start equipment is running | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Fault | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | E-Stop | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 80CB64LINE.PV.1 | 80CB64 Healthy Input |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 80XE64HEALTHY.PV.0 | 80XE64 RLC Healthy Input |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 80XE64FLT.PV.1 | 80XE64 RLC Fault Input |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 80CB64LINE.PV.0 | 80CB64 Healthy Input |  |  |  | x | [5 empty] | 0
[21 empty] | 80XE64HEALTHY.PV.1 | 80XE64 RLC Healthy Input |  |  |  | x | [5 empty] | 0
[21 empty] | 80XE64FLT.PV.0 | 80XE64 RLC Fault Input |  |  |  | x | [5 empty] | 0
[21 empty] | 80CB64ZSO.PV.1 | Not Open Discharge Delay | 3 |  |  | x | [5 empty] | 0
30AG66 | GR0036 | N/A | Spillage Agitator | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | NOT LIC30520.ALRM.LO NOT 30AG66.ALRM.ANS+ | Tank Level Not Low Not Drive Fail To Start | LIC30520.ALRM.LO 30AG66.ALRM.ANS+ | Tank Level Low Drive Fail To Start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30AG66FLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30AG66STP.PV.ON | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | LIC30520.ALRM.LL | Tank Level Low Low |  |  |  | x | x |  |  |  |  | 0
[21 empty] | 30AG66FLT | Spillage Agi Fault |  |  |  | x | x |  |  |  |  | 0
30PP69 | .GR0036 | N/A | Spillage Txfr Pump | DOL | [6 empty] | x | x | Medium | 3 | 30TK64 | 30PP69SST.PV.ON AND NOT 30PP69.ALRM.ANS+ | Sequence Start and not drive failed to start | 30PP69SST.PV.OFF 30PP69.ALRM.ANS+ | Not Sequence start Drive Failed to start | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP69FLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP69STP.PV.ON | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | LIC30520.ALRM.LL | Tank Low Low Level |  |  |  |  | x |  |  |  |  | 0
[21 empty] | (30PP62ARUN.PV.ON OR 30PP62BRUN.PV.ON OR 30PP62CRUN.PV.ON OR 30PP62DRUN.PV.ON) AND LC30719.ALRM.HH | Any tails pump A to D running while tails hopper high high alarm |  |  |  |  | x |  |  |  |  | 0
30SC66 | GR0036 | N/A | Spillage Vib Screen | DOL | [6 empty] | x | x | Medium | 3 | 30TK64 | %GS03412.PV.ON AND NOT 30SC66.ALRM.ANS+ | "Drive" Starting (External reference) and not drive failed to start | %GS03412.PV.OFF (600 Sec Delay) | Remote reference pump not starting with 600 second delay | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SC66FLT | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC66STP.PV.ON | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | LIC30520.ALRM.HH | Tank Level High High |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC66FLT | Spillage Vib Scrn Flt |  |  |  |  | x |  |  |  |  | 0
75PW71A | .GR0032 | 75-PI-1500 | Knlsn Fluidisng Wtr Pmp A | DOL | [5 empty] | 100 | x | x | Medium | 1 | FIM-CIL | 75PW71ASLT.PV.ON AND 75PW71REQ.PV.ON 75PW71ASLT.PV.OFF AND 75PW71RL.X01.GT 75PW71ACHG.PV.ON | Pump Selected Duty AND Fld Wtr Reqd For GCT's Pump Selected Standby AND More than 3 Conc Running Changeover Pumps | 75PW71RL.X01.LE AND 75PW71BSLT.PV.ON AND 75PW71BRUN.PV.ON 75PW71REQ.PV.OFF 75PW71RL.X02.EQ | 3 or less Conc Running AND B Pump Selected AND Drive B Running FldWtr Not Reqd ForGCT's No Conc Running | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW71AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW71ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 75PW71AALM.PV.ON | Drive Thermistor Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TI75710A.ALRM.HH AND NOT TI75710A.AOFS.AOF | Motor Winding A Temp HH (and not masked) |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TI75710B.ALRM.HH AND NOT TI75710B.AOFS.AOF | Motor Winding B Temp HH (and not masked) |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TI75710C.ALRM.HH AND NOT TI75710C.AOFS.AOF | Motor Winding C Temp HH (and not masked) |  |  |  |  | x |  |  |  |  | 0
75PW71B | .GR0032 | 75-PI-1500 | Knlsn Fluidisng Wtr PmpB | DOL | [5 empty] | 100 | x | x | Medium | 1 | FIM-CIL | 75PW71BSLT.PV.ON AND 75PW71REQ.PV.ON 75PW71BSLT.PV.OFF AND 75PW71RL.X01.GT 75PW71BCHG.PV.ON | Pump Selected Duty AND Fld Wtr Reqd For GCT's Pump Selected Standby AND More than 3 Conc Running Changeover Pumps | 75PW71RL.X01.LE AND 75PW71ASLT.PV.ON AND 75PW71ARUN.PV.ON 75PW71REQ.PV.OFF 75PW71RL.X02.EQ | 3 or less Conc Running AND A Pump Selected AND Drive A Running FldWtr Not Reqd ForGCT's No Conc Running | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW71BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW71BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 75PW71BALM.PV.ON | Drive Thermistor Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TI75708A.ALRM.HH AND NOT TI75708A.AOFS.AOF | Motor Winding A Temp HH (and not masked) |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TI75708B.ALRM.HH AND NOT TI75708B.AOFS.AOF | Motor Winding B Temp HH (and not masked) |  |  |  |  | x |  |  |  |  | 0
[21 empty] | TI75708C.ALRM.HH AND NOT TI75708C.AOFS.AOF | Motor Winding C Temp HH (and not masked) |  |  |  |  | x |  |  |  |  | 0
75PW68A | .GR0341 | 2000-F30-PID-PR-10015 | FTails GlandWater Pump A | VSD | 0 | 100 | % |  |  |  | x | x | Medium | 3 | 30PP62A | 75PW68RL.X01.LE AND 75PW68BRUN.PV.ON | Low Glandwater Pressure and Pump B Running | [13 empty] | Valve KV30783 set to auto mode when this drive starts | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW68AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW68ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | (KV30783.PV.2 AND KV30783.MODE.AUT) OR NOT 75PW68ARUN.PV. | Valve KV30783 Not open in Auto mode while drive running | 2 |  |  |  | x |  |  |  |  | 0
75PW68B | .GR0341 | 2000-F30-PID-PR-10015 | FTails GlandWater Pump B | VSD | 0 | 100 | % |  |  |  | x | x | Medium | 3 | 75TK63 | 75PW68RL.X01.LE AND 75PW68ARUN.PV.ON | Low Glandwater Pressure and Pump A Running | [13 empty] | Valve KV30784 set to auto mode when this drive starts | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW68BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW68BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | (KV30784.PV.2 AND KV30784.MODE.AUT) OR NOT 75PW68BRUN.PV. | Valve KV30784 Not open in Auto mode while drive running | 2 |  |  |  | x |  |  |  |  | 0
75PW68C | .GR0341 | 2000-F30-PID-PR-10015 | FTails GlandWater Pump C | VSD | 0 | 100 | % |  |  |  | x |  | Medium | 3 | 30PP62C | [15 empty] | Valve KV30788 set to auto mode when this drive starts | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW68CFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW68CSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | (KV30788.PV.2 AND KV30788.MODE.AUT) OR NOT 75PW68CRUN.PV. | Valve KV30788 Not open in Auto mode while drive running | 1 |  |  |  | x |  |  |  |  | 0
75PW13A | .GR0160 | 2000-F75-PID-PR-1003 | Bore Water Pump 13A | DOL | [5 empty] | 100 | x | x | Medium | 1 | FIM-CIL | LI7506.PV | WshDwn Wtr Tk Lvl | NOT LI7506.PV | Not WshDwn Wtr Tk Lvl | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW13AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW13ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
75PW13B | .GR0160 | 2000-F75-PID-PR-1003 | Bore Water Pump 13B | DOL | [5 empty] | 100 | x | x | Medium | 1 | FIM-CIL | LI7506.PV | WshDwn Wtr Tk Lvl | NOT LI7506.PV | Not WshDwn Wtr Tk Lvl | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW13BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW13BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
75PW63A | .GR0160 | 2000-F75-PID-PR-10003 | CyanideWaterPump 63A | DOL | [5 empty] | 100 | x | x | Medium | 1 | FIM-CIL | 30SW31NAV.PV.ON (90 sec delay) | Normal Power Availiable (90 second delay) | [14 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW63AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW63ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
75PW63B | .GR0160 | 2000-F75-PID-PR-10003 | CyanideWaterPump 63B | DOL | [5 empty] | 100 | x | x | Medium | 1 | FIM-CIL | 30SW31NAV.PV.ON (90 sec delay) | Normal Power Availiable (90 second delay) | [14 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW63BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW63BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
75PW65 | .GR0160 | N/A | Thickener Fast Fill Pp | DOL | [5 empty] | 100 | x | x | Medium | 1 | FIM-CIL | 75PW65TK51-G.PV.1 AND %GS02001.PV.1 75PW65TK61-G.PV.1 AND L75PW65STT.PV.1 | TK51 FastFill Cntrl Strt (G75PW65STT from FCS1) TK61 FastFill Cntrl Strt | 75PW65TK51-G.PV.1 AND %GS02001.PV.0 75PW65TK61-G.PV.1 AND L75PW65STT.PV.0 75PW65NONE-G.PV.1 | NOT TK51 FastFill Cntrl Strt NOT TK61 FastFill Cntrl Strt NONE SELECTED | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 75PW65FLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 75PW65STP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30PP75 | .GR0160 | 30-PI-1000 | Carbon Recov Scrn Pump | DOL | [5 empty] | 100 | x |  | Medium | 1 | FIM-CIL | [16 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP75FLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP75STP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30AG32A | .GR0320 | 30-PI-0313 | CIL2 TK32A Agitator | DOL | [6 empty] | x | x | Medium | 3 | CIL-MTC | 30SW31NAV.PV.ON %SW0870.PV.ON (1 sec delay) | Normal Power Available CIL2 Group Start (1 second delay) | 30AG32A.ALRM.ANS+ | Drive fail to start | [11 empty] | CIL2 Group Start (%SW0870.PV.ON) Sets this drive to auto mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30AG32AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30AG32ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30AG32B | .GR0320 | 30-PI-0313 | CIL2 TK32B Agitator | DOL | [6 empty] | x | x | Medium | 3 | CIL-MTC | 30SW31NAV.PV.ON (5 sec delay) %SW0870.PV.ON (3 sec delay) | Normal Power Available (5 second delay) CIL2 Group Start (3 second delay) | 30AG32B.ALRM.ANS+ | Drive fail to start | [11 empty] | CIL2 Group Start (%SW0870.PV.ON) Sets this drive to auto mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30AG32BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30AG32BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30AG32C | .GR0320 | 30-PI-0313 | CIL2 TK32C Agitator | DOL | [6 empty] | x | x | Medium | 3 | CIL-MTC | 30SW31NAV.PV.ON (10 sec delay) %SW0870.PV.ON (6 sec delay) | Normal Power Available (10 second delay) CIL2 Group Start (6 second delay) | 30AG32C.ALRM.ANS+ | Drive fail to start | [11 empty] | CIL2 Group Start (%SW0870.PV.ON) Sets this drive to auto mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30AG32CFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30AG32CSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30AG32D | .GR0320 | 30-PI-0313 | CIL2 TK32D Agitator | DOL | [6 empty] | x | x | Medium | 3 | CIL-MTC | 30SW31NAV.PV.ON (15 sec delay) %SW0870.PV.ON (10 sec delay) | Normal Power Available (15 second delay) CIL2 Group Start (10 second delay) | 30AG32D.ALRM.ANS+ | Drive fail to start | [11 empty] | CIL2 Group Start (%SW0870.PV.ON) Sets this drive to auto mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30AG32DFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30AG32DSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30AG32E | .GR0320 | 30-PI-0313 | CIL2 TK32E Agitator | DOL | [6 empty] | x | x | Medium | 3 | CIL-MTC | 30SW31NAV.PV.ON (20 sec delay) %SW0870.PV.ON (15 sec delay) | Normal Power Available (20 second delay) CIL2 Group Start (15 second delay) | 30AG32E.ALRM.ANS+ | Drive fail to start | [11 empty] | CIL2 Group Start (%SW0870.PV.ON) Sets this drive to auto mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30AG32EFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30AG32ESTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30AG32F | .GR0320 | 30-PI-0313 | CIL2 TK32F Agitator | DOL | [6 empty] | x | x | Medium | 3 | CIL-MTC | 30SW31NAV.PV.ON (25 sec delay) %SW0870.PV.ON (21 sec delay) | Normal Power Available (25 second delay) CIL2 Group Start (21 second delay) | 30AG32F.ALRM.ANS+ | Drive fail to start | [11 empty] | CIL2 Group Start (%SW0870.PV.ON) Sets this drive to auto mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30AG32FFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30AG32FSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30SC34B | .GR0320 | 30-PI-0313 | CIL2 TK32B Inter Screen | DOL | [6 empty] | x | x | Medium | 3 | CIL-MTC | 30SC34B.MODE.AUT AND (30SW31NAV.PV.ON (18 second delay)) %SW0870.PV.ON (3 sec delay) | Normal Power Available for longer than 18 seconds CIL2 Group Start (3 second delay) | 30AG32A.ALRM.ANS+ | CIL2 TK32B Inter Screen Failed To Start | [11 empty] | CIL2 Group Start (%SW0870.PV.ON) Sets this drive to manual mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SC34BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC34BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30SC34C | .GR0320 | 30-PI-0313 | CIL2 TK32C Inter Screen | DOL | [6 empty] | x | x | Medium | 3 | CIL-MTC | 30SC34C.MODE.AUT AND (30SW31NAV.PV.ON (8 second delay)) %SW0870.PV.ON (6 sec delay) | Normal Power Available for longer than 8 seconds CIL2 Group Start (6 second delay) | 30SC34C.ALRM.ANS+ | CIL2 TK34C Inter Screen Failed To Start | [11 empty] | CIL2 Group Start (%SW0870.PV.ON) Sets this drive to manual mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SC34CFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC34CSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30SC34D | .GR0320 | 30-PI-0313 | CIL2 TK32D Inter Screen | DOL | [6 empty] | x | x | Medium | 3 | CIL-MTC | 30SC34D.MODE.AUT AND (30SW31NAV.PV.ON (8 second delay)) %SW0870.PV.ON (10 sec delay) | Normal Power Available for longer than 8 seconds CIL2 Group Start (10 second delay) | 30SC34D.ALRM.ANS+ | CIL2 TK34D Inter Screen Failed To Start | [11 empty] | CIL2 Group Start (%SW0870.PV.ON) Sets this drive to manual mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SC34DFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC34DSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30SC34E | .GR0320 | 30-PI-0313 | CIL2 TK32E Inter Screen | DOL | [6 empty] | x | x | Medium | 3 | CIL-MTC | 30SC34E.MODE.AUT AND (30SW31NAV.PV.ON (13 second delay)) %SW0870.PV.ON (15 sec delay) | Normal Power Available for longer than 13 seconds CIL2 Group Start (15 second delay) | 30SC34E.ALRM.ANS+ | CIL2 TK34E Inter Screen Failed To Start | [11 empty] | CIL2 Group Start (%SW0870.PV.ON) Sets this drive to manual mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SC34EFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC34ESTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
30SC34F 30PP32 | .GR0320 .GR0310 | 30-PI-0313 30-PI-0313 | CIL2 TK32F Inter Screen CIL2 Loaded Carb Xfer Pp | DOL DOL | [6 empty] | x x | x x | Medium Medium | 3 3 | CIL-MTC CIL-MTC | 30SC34F.MODE.AUT AND (30SW31NAV.PV.ON (13 second delay)) %SW0870.PV.ON (21 sec delay) | Normal Power Available for longer than 13 seconds CIL2 Group Start (21 second delay) | 30SC34F.ALRM.ANS+ | CIL2 TK34F Inter Screen Failed To Start | [11 empty] | CIL2 Group Start (%SW0870.PV.ON) Sets this drive to manual mode | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30SC34FFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30SC34FSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. Manual mode operation limited to 4 hours, drive will be stopped. | 0 1
[17 empty] | See Appendix A - Item 9 |  | See Appendix A - Item 9 |  |  | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP32FLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP32STP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 30PP32FLTX | Drive Aux Fault Input |  |  |  |  | x |  |  |  |  | 0
[21 empty] | LSH65359.PV.ON | Txfr Vssl Lvl Hi |  |  |  | x | [5 empty] | 0
[21 empty] | NOT (FV3035B.PV.OFF AND FV3035A.PV.ON) | NOT (Valve FV3035B Closed AND Valve FV3035A Open) |  |  |  | x | [5 empty] | 0
30PP35A | .GR0310 | 30-PI-0313 | CIL2 Tk32C Carbon Pump | DOL | [6 empty] | x | x | Medium | 3 | FIM_CIL_TRAINS |  | See Appendix A - Item 10 |  | See Appendix A - Item 10 | [11 empty] | Manual mode operation limited to 6 hours, drive will be stopped. | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP35AFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP35ASTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 30PP35AFLTX | Drive Aux Fault Input |  |  |  |  | x |  |  |  |  | 0
[21 empty] | LSH65359.PV.ON | Txfr Vssl Lvl Hi |  |  |  | x | [5 empty] | 0
[21 empty] | NOT (FV3035B.PV.OFF AND FV3035A.PV.ON) | NOT (Valve FV3035B Closed AND Valve FV3035A Open) |  |  |  | x | [5 empty] | 0
30PP35B | .GR0310 | 30-PI-0313 | CIL2 Tk32D Carbon Pump | DOL | [6 empty] | x | x | Medium | 3 | FIM_CIL_TRAINS | 30PP35BSST.PV.ON (Rising Trigger) | Sequence Control: See CTR2MSFC Sequences Description | 30PP35BSST.PV.ON (Falling Trigger) | Sequence Control: See CTR2MSFC Sequences Description | [11 empty] | Manual mode operation limited to 6 hours, drive will be stopped. | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP35BFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP35BSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 30PP35BFLTX | Drive Aux Fault Input |  |  |  |  | x |  |  |  |  | 0
30PP35C | .GR0310 | 30-PI-0313 | CIL2 Tk32E Carbon Pump | DOL | [6 empty] | x | x | Medium | 3 | FIM_CIL_TRAINS | 30PP35CSST.PV.ON (Rising Trigger) | Sequence Control: See CTR2MSFC Sequences Description | 30PP35CSST.PV.ON (Falling Trigger) | Sequence Control: See CTR2MSFC Sequences Description | [11 empty] | Manual mode operation limited to 6 hours, drive will be stopped. | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP35CFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP35CSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 30PP35CFLTX | Drive Aux Fault Input |  |  |  |  | x |  |  |  |  | 0
30PP35D | .GR0310 | 30-PI-0313 | CIL2 Tk32F Carbon Pump | DOL | [6 empty] | x | x | Medium | 3 | FIM_CIL_TRAINS | 30PP35CSST.PV.ON (Rising Trigger) | Sequence Control: See CTR2MSFC Sequences Description | 30PP35CSST.PV.ON (Falling Trigger) | Sequence Control: See CTR2MSFC Sequences Description | [11 empty] | Manual mode operation limited to 6 hours, drive will be stopped. | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 30PP35DFLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PP35DSTP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 30PP35DFLTX | Drive Aux Fault Input |  |  |  |  | x |  |  |  |  | 0
65SC31 | .GR0160 | 30-PI-0313 | CIL2 Loaded CarbonScreen | DOL | [5 empty] | 100 | x | x | Medium | 1 | CIL-MTC | KV65352OPN.PV.ON AND ((CR2MTOCIL3.PV.OFF AND CR2MSTT.PV.ON) OR (CR3MTOCIL2.PV.ON AND CR3MSTT.PV.ON) OR (%GS00511.PV.ON AND %GS00611.PV.ON)) | CIL2 Carbon Inlet Valve Open AND ((CR2M to CIL3 Not Active AND CR2MSTT Module Active) OR (CR3M to CIL2 Is Active AND CR3MSTT Module Active) OR (CR1M to CIL2 Active AND CR1M Started)) | LSH65359.PV.OFF (Latched triggering LSH65359TM2) | Txfr Vssl Lvl Hi for 10 minutes | [12 empty] | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | 65SC31FLT.PV.ON | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 65SC31STP.PV.OFF | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | 65SC31FLTX | Drive Aux Fault Input |  |  |  |  | x |  |  |  |  | 0
The following drives are connected via comms:
30PP77A | 0 | 75-PI-5301 | Tails Booster Pump PP77A | DOL | [6 empty] | x | x | Medium | 3 | 30PP77A | %WB015106.PV.1 | Drive is running (Via remote PLC) | NOT %WB015106.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015104.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB015101.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015103.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB000503.PV.1 | PLC Interlocks |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB000504.PV.1 | PLC Start Permissive |  |  | x | [6 empty] | 0
[21 empty] | %WB015105.PV.1 | Earth Fault |  |  |  |  | x |  |  |  |  | 0
30PW01A | 0 | 75-PI-5303 | Fim 2 Seal Water Pump A | DOL | [6 empty] | x | x | Medium | 3 | FIM2_BOOSTER_STN | %WB015208.PV.1 | Drive is running (Via remote PLC) | NOT %WB015208.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015206.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | 30PW01A.MV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | %WB000215.PV.1 | PLC Interlocks |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB015207.PV.1 | Earth Fault |  |  |  |  | x |  |  |  |  | 0
30PW01B | 0 | 75-PI-5303 | Fim 2 Seal Water Pump B | DOL | [6 empty] | x | x | Medium | 3 | FIM2_BOOSTER_STN | %WB015214.PV.1 | Drive is running (Via remote PLC) | NOT %WB015214.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015212.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB015210.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | %WB000216.PV.1 | PLC Interlocks |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB015213.PV.1 | Earth Fault |  |  |  |  | x |  |  |  |  | 0
30PP77B | 0 | 75-PI-5301 | Tails Booster Pump PP77B | DOL | [6 empty] | x | x | Medium | 3 | 30PP77B | %WB015113.PV.1 | Drive is running (Via remote PLC) | NOT %WB015113.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015111.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB015108.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015110.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB000706.PV.1 | PLC Interlocks |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB000507.PV.1 | PLC Start Permissive |  |  | x | [6 empty] | 0
[21 empty] | %WB015112.PV.1 | Earth Fault |  |  |  |  | x |  |  |  |  | 0
30PS71 | 0 | 75-PI-5301 | Fim 2 Tails Booster Sump | DOL | [6 empty] | x | x | Medium | 3 | FIM2_BOOSTER_STN | %WB015202.PV.1 | Drive is running (Via remote PLC) | NOT %WB015202.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015201.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB015115.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015203.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
30PW03 | 0 | n/a | Fim 2 Booster Seal Water | DOL | [6 empty] | x | x | Medium | 3 | FIM2_BOOSTER_STN | %WB015503.PV.1 | Drive is running (Via remote PLC) | NOT %WB015503.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015502.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB015216.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015504.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
30PO77A | 0 | N/A | PP77A Oil Pump | DOL | [6 empty] | x | x | Medium | 3 | 30PP77A | %WB015508.PV.1 | Drive is running (Via remote PLC) | NOT %WB015508.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015507.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB015505.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015509.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
30FN77A | 0 | N/A | PP77A Oil Cooling Fan | DOL | [6 empty] | x | x | Medium | 3 | 30PP77A | %WB015513.PV.1 | Drive is running (Via remote PLC) | NOT %WB015513.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015512.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB015510.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015514.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
30PO77B | 0 | N/A | PP77B Oil Pump | DOL | [6 empty] | x | x | Medium | 3 | 30PP77B | %WB015602.PV.1 | Drive is running (Via remote PLC) | NOT %WB015602.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015601.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB015515.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015603.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
30FN77B | 0 | N/A | PP77B Oil Cooling Fan | DOL | [6 empty] | x | x | Medium | 3 | 30PP77B | %WB015607.PV.1 | Drive is running (Via remote PLC) | NOT %WB015607.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015606.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB015604.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB015608.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
30PP78A | 0 | 75-PI-5302 | Tails Booster Pump PP78A | DOL | [6 empty] | x | x | Medium | 3 | 30PP78A | %WB035106.PV.1 | Drive is running (Via remote PLC) | NOT %WB035106.PV.1 %WB020503.PV.1 | Drive not running (Via remote PLC) PLC Interlocks | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035104.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB035101.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035103.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB020503.PV.1 | PLC Interlocks |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB020504.PV.1 | PLC Start Perms |  |  | x | [6 empty] | 0
[21 empty] | %WB035105.PV.1 | Earth Fault |  |  |  |  | x |  |  |  |  | 0
30PW02A | 0 | 75-PI-5304 | Katails Seal Wtr Pmp A | DOL | [6 empty] | x | x | Medium | 3 | KALT_BOOSTER_STN | %WB035208.PV.1 | Drive is running (Via remote PLC) | NOT %WB035208.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035206.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB035204.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | %WB020215.PV.1 | PLC Interlocks |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB035207.PV.1 | Earth Fault |  |  |  |  | x |  |  |  |  | 0
30PW02B | 0 | 75-PI-5304 | Kaltails Seal Wtr Pmp B | DOL | [6 empty] | x | x | Medium | 3 | KALT_BOOSTER_STN | %WB035214.PV.1 | Drive is running (Via remote PLC) | NOT %WB035214.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035212.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB035210.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Drive Ready | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[21 empty] | %WB020216.PV.1 | PLC Interlocks |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB035213.PV.1 | Earth Fault |  |  |  |  | x |  |  |  |  | 0
30PP78B | 0 | 75-PI-5302 | Tails Booster Pump PP78B | DOL | [6 empty] | x | x | Medium | 3 | 30PP78B | %WB035113.PV.1 | Drive is running (Via remote PLC) | NOT %WB035113.PV.1 %WB020706.PV.1 | Drive not running (Via remote PLC) PLC Interlocks | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035111.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB035108.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035110.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB020706.PV.1 | PLC Interlocks |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB020507.PV.1 | PLC Start Perms |  |  | x | [6 empty] | 0
[21 empty] | %WB035112.PV.1 | Earth Fault |  |  |  |  | x |  |  |  |  | 0
30PS72 | 0 | 75-PI-5302 | Kaltail Booster Sump Pmp | DOL | [6 empty] | x | x | Medium | 3 | KALT_BOOSTER_STN | %WB035202.PV.1 | Drive is running (Via remote PLC) | NOT %WB035202.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035201.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB035115.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035203.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
30PW04 | 0 | n/a | Kaltail Booster Seal Wtr | DOL | [6 empty] | x | x | Medium | 3 | KALT_BOOSTER_STN | %WB035503.PV.1 | Drive is running (Via remote PLC) | NOT %WB035503.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035502.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB021602.PV.1 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035504.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB021602.PV.1 | PLC Interlocks |  |  |  |  | x |  |  |  |  | 0
30PO78A | 0 | n/a | PP78A Oil Pump | DOL | [6 empty] | x | x | Medium | 3 | 30PP78A | %WB035508.PV.1 | Drive is running (Via remote PLC) | NOT %WB035508.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035507.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB035505.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035509.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
30FN78A | 0 | n/a | PP78A Oil Cooling Fan | DOL | [6 empty] | x | x | Medium | 3 | 30PP78A | %WB035513.PV.1 | Drive is running (Via remote PLC) | NOT %WB035513.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035512.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB035510.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035514.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
30PO78B | 0 | n/a | PP78B Oil Pump | DOL | [6 empty] | x | x | Medium | 3 | 30PP78B | %WB035602.PV.1 | Drive is running (Via remote PLC) | NOT %WB035602.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035601.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB035515.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035603.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
30FN78B | 0 | n/a | PP78B Oil Cooling Fan | DOL | [6 empty] | x | x | Medium | 3 | 30PP78B | %WB035607.PV.1 | Drive is running (Via remote PLC) | NOT %WB035607.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035606.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB035604.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB035608.PV.0 | Drive Ready | [9 empty] | 0
30PP79 | 0 | n/a | Fim 1 Tails Booster | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | %WB060111.PV.1 | Drive is running (Via remote PLC) | NOT %WB060111.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB060113.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB060116.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB060114.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB061410.PV.1 | PLC Interlocks |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB060115.PV.1 | Earth Fault |  |  |  |  | x |  |  |  |  | 0
30FN79 | 0 | n/a | Fim 1 Booster Cool Fan | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | %WB060601.PV.1 | Drive is running (Via remote PLC) | NOT %WB060601.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB060602.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB060604.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB060603.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB061412.PV.1 | PLC Interlocks |  |  |  |  | x |  |  |  |  | 0
30PW75 | 0 | n/a | Fim 1 Booster G/Wtr Pump | DOL | [6 empty] | x | x | Medium | 3 | FIM-CIL | %WB060201.PV.1 | Drive is running (Via remote PLC) | NOT %WB060201.PV.1 | Drive not running (Via remote PLC) | [11 empty] | via comms | 1
[22 empty] | Comunication Fault |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[22 empty] | Fail to Start/Stop |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB060203.PV.1 | Drive Fault |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB060205.PV.0 | E-Stop |  |  |  |  | x |  |  |  |  | 0
[22 empty] | MCC Healthy | [8 empty] | Interlock is not applicable but provided by client supplied template as standard. Dummy switch to be used. | 0
[22 empty] | Out Of Service |  |  |  |  | x |  |  |  | Client supplied templates shall have this interlock as standard. | 0
[21 empty] | %WB060204.PV.0 | Drive Ready |  |  |  |  | x |  |  |  |  | 0
[21 empty] | %WB061411.PV.1 | PLC Interlocks |  |  |  |  | x |  |  |  |  | 0

## 10. Sequence
KCGM GROWTH PROJECT
SEQUENCE
SEQUENCES
Seq No. | Seq Description | Step | Action | Tag / Item | Description | Next Step Delay (s) | Step Advance Condition | Comments | Rev | Equipment Permissives | Recovery Seq. No if Step Faults
PLEASE REFER TO SEQUENCE FLOWCHART DELIVERABLE DOCUMENTS

## 11. Calculation
KCGM GROWTH PROJECT
CALCULATION
|  |  | Unit | SH | SL | Alarm Level | Security Level | Upper Equipment | Inputs |  |  |  | Operator Input | Calc. Value | Manual Input
Tag Name | Drawin | Description (Software Tag Only) | [6 empty] | # | Tag | Unit | Description |  |  | Nom | Min | Max | Calculation | Comments | Rev
SW75PW13CAL | DR0003 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | 1 | LI7506 | % | RV (Washdown WtrTank Level) | [5 empty] | LI75061:CCST; SW75PW13A.SV = RV SW75PW13B.SV = RV + P01 |  | 1
75PW72ARUNTM | DR0003 |  | % | 9999999 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 75PW72A.ONTM alias reset 75PW72ARST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
75PW72BRUNTM | DR0003 |  | % | 9999999 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 75PW72B.ONTM alias reset 75PW72BRST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
MI30337 | DR0004 | THICKNER 2 U/F Massflow | T/HR | 2000 | 0 | Medium | 4 | FIM-CIL | 1 | DIC30313 | %SOL | RV (Thick 2 U/F Density) | [5 empty] | FC303161:CCST; * * CIL 2 MASS FLOW CALCULATION * * *I nputs *FLOW: Feed Flow *%SOL: Feed Density *WTR: Density of Water *FOR: Fimiston Ore Density |  | 1
[9 empty] | 2 | FI30315 | M3/H | RV1 (Flot Thknr#2Under Flow) | [5 empty] | * *C alculations *MASS: Calculated Dry Tonnes *SG: Slurry SG * program * alias WTR DYS010501WTR.PV alias FOR DYS010501FOR.PV alias FLOW MI30337.RV1 alias %SOL MI30337.RV alias MASS CPV alias FLOC MI30337.RV5 alias PUMPA MI30337.RV2 alias PUMPB MI30337.RV3 alias RECVLV MI30337.RV4 * float SG * SG = 100/((%SOL/FOR) + (100 - %SOL)/WTR) * if ( ((PUMPA == 1) or (PUMPB == 1)) and (RECVLV == 0) ) then MASS = FLOW*SG*%SOL/100 else MASS = 0 end if * P02 = FLOW P03 = %SOL P04 = WTR P05 = FOR P06 = SG * P08 = Flocculant usage ; Flocculant concentration = 2.5[g/l] if (FLOC < 0 or MASS <= 0) then FLOC = 0 end if * if (MASS == 0) then MASS = 0.01 end if * P08 = (FLOC*2.5)/MASS * end |  | 0
[9 empty] | 3 | 30PP31A | % | RV2 (Thickener 2 U/Flow PumpA) | [7 empty] | 0
[9 empty] | 4 | 30PP31B | % | RV3 (Thickener 2 U/Flow PumpB) | [7 empty] | 0
[9 empty] | 5 | FV30652 |  | RV4 (Thickener#2 Recycle Vlv) | [7 empty] | 0
[9 empty] | 6 | FC30316 | L/HR | RV5 (F/Tail Thick 2 Floc Flow) | [7 empty] | 0
AIC30381FF | DR0004 |  | % | 2 | 0 | Logging | 4 | FIM-CIL | 1 | FI30338 | M3/H | RV (CIL2 BARREN ELUATE FLOW) | [5 empty] | FV659821:CCST; !This computes the cyanide content on the barren eluate to compensate for the flow on the cyanide supply. ! P01 = CYANINDE PPM CONCENTRATION AVERAGE ~ 2960ppm |  | 1
[9 empty] | 2 | MICIL2LAG1 | T/HR | RV1 | [5 empty] | ! RV = BARREN ELUATE FLOW FI30338 ! RV1 = TOTAL FLOW INTO THE CIL MICIL2LAG1.CPV ! P02 = SPECIFIC GRAVITY (ASSUMPTION = 1) alias PUMP RV2 alias VALVE RV3 if (RV > 0 and RV1 > 0 and PUMP == 2 and VALVE == 2) then CPV1 = (P01 * RV * P02) / RV1 CPV = CPV1 / 1000 else CPV = 0 end if if (CIL1TAILSDST.PV01 == ON) THEN A IC30381.MH = 0.3 else A IC30381.MH = 0.4 end if |  | 0
[9 empty] | 3 | 66PP65 | % | RV2 (BarrenEluate Dist Pump) | [7 empty] | 0
[9 empty] | 4 | FV65982 |  | RV3 (BarrenEluateTransf.Valve) | [7 empty] | 0
MI19579CIL2 | DR0004 | MTC LchFdU/FCil2Massflow | T/HR | 2000 | 0 | Medium | 4 | FIM-CIL | 1 | DI19577 |  | RV | [5 empty] | FV195821:CCST; * * CIL 2 MASS FLOW CALCULATION * * *I nputs *FLOW: Feed Flow *%SOL: Feed Density *WTR: Density of Water *FOR: Fimiston Ore Density * |  | 1
[9 empty] | 2 | FI30384 | M3/H | RV1 (CIL2 Slurry Flow frm MTC) | [5 empty] | *C alculations *MASS: Calculated Dry Tonnes *SG: Slurry SG * program * alias MASS CPV alias WTR DYS010501WTR.PV alias FOR DYS010501FOR.PV alias %SOL RV alias FLOW RV1 alias PUMPA RV2 alias PUMPB RV3 alias RECVLV RV4 * float SG * SG = 100/((%SOL/FOR) + (100 - %SOL)/WTR) * if ( ((PUMPA == 1) or (PUMPB == 1)) and (RECVLV == 0) ) then MASS = FLOW*SG*%SOL/100 else MASS = 0 end if * P02 = FLOW P03 = %SOL P04 = WTR P05 = FOR P06 = SG end |  | 0
[9 empty] | 3 | 19PP52A | % | RV2 (MTC ThicknerU/F Pump A) | [7 empty] | 0
[9 empty] | 4 | 19PP52B | % | RV3 (MTC ThicknerU/F Pump B) | [7 empty] | 0
[9 empty] | 5 | FV19582 |  | RV4 (MTC Thicknr Recirc Vlv) | [7 empty] | 0
FIC30378CALC2 | DR0004 | CIL1 2D NaCNFlowAddition | L/MIN | 50 | 0 | Medium | 1 | FIM-CIL | [9 empty] | 1:CCST; ******************************************************************* * CYANIDE ADDITION KG/T SETPOINT CONVERSION * * This calc takes operator kg/t setpoint and convert it to a * l/min flow setpoint for cyanide. * * Inputs * RV : kg/t Cyanide Setpoint * RV1 : Total Mass flow * Locals * P01 : Cyanide Conversion Factor * This varies by season - Winter 28.5% => 0.3410 * Summer 30.5% => 0.3605 *P 08 : Kg/t Max Setpoint * * Outputs * CPV : FIC l/min setpoint * CPV1 : Back calculate AIC MV when controller tracking * ******************************************************************* alias MASSFL FIC30378CALC.RV1 alias CYNFCT FIC30378CALC.P01 * Backcalculate kg/t from l/min setpoint for tracking, set at 0 kg/t if no massflow if (MASSFL > 0) then P02 = (FIC30378.SV*(60*CYNFCT))/MASSFL else P02 = 0 end if * Clamp backcalculated kg/t if (P02 > 10) then CPV = 10 else CPV = P02 end if if (MASSFL < 10) then FIC30378AS.SW = 2 else FIC30378AS.SW = 1 if ({FIC30378.PV=CAL} <> 1) {FIC30378.MODE.CAS} = 1 end if if ({FIC30378AS.MODE.AUT} <> 1 AND {FIC30378AS.ALRM.OOP} <> 1) then {FIC30378AS.MODE.AUT} = 1 end if if (({MIC30378.MODE.AUT}==1) AND (MIC30378.SV > P08)) then MIC30378.SV = P08 end if FlowHI = FIC30378CALC.P03 * 1.2 FlowHH = FlowHI + 1.5 P07 = P06 + 1.5 FIC30378.PH = dmax(P06,FlowHI) FIC30378.HH = dmax(P07,FlowHH) |  | 1
FIC30378CALC3 | DR0004 | CIL1 2D NaCNFlowAddition | L/MIN | 50 | 0 | Medium | 1 | FIM-CIL | [9 empty] | 1:CCST; integer oneshot alias RST CIL2FLWTRPRST.PV if ({FIC30378AS.SEL.2} == 0 or {FIC30378.MODE.CAS} == 0) FIC30378.SV = FIC30378CALC.P03 P01 = dabs(FIC30378.DV) if (MICIL2LAG1.CPV < 10 and oneshot == 0) then P08 = FIC30378.SUM + P07 oneshot = 1 else if (MICIL2LAG1.CPV > 10) then P08 = 0 oneshot = 0 end if if (RST == 1) then P08 = FIC30378.SUM + P07 RST = 0 end if |  | 1
FIC30378CALC | DR0004 | CIL1 2D NaCNFlowAddition | L/MIN | 50 | 0 | Medium | 1 | FIM-CIL | 1 | AIC30381 | PPM | RV (CIL2 Cyanide Analyser) | [5 empty] | MICIL2LAG11:CCST; ******************************************************************* * CYANIDE ADDITION KG/T SETPOINT CONVERSION * * This calc takes operator kg/t setpoint and convert it to a * l/min flow setpoint for cyanide. * * Inputs * RV : kg/t Cyanide Setpoint * RV1 : Total Mass flow * Locals * P01 : Cyanide Conversion Factor * This varies by season - Winter 28.5% => 0.3410 * Summer 30.5% => 0.3605 * * Outputs * CPV : FIC l/min setpoint * CPV1 : Back calculate AIC MV when controller tracking * ******************************************************************* alias MASSFL RV1 alias CNSTR DYS010501CYN.SV * Calculate Cyanide Conversion Factor based on CN Strength * CN factor is a linear equation: 0.012926x -0.0338 P01 = 0.012926 * CNSTR -0.0338 if (CIL2KGTBYP.PV==1) then CPV = RV goto A1 end if * l/min setpoint calculation for FIC, limit to low of 2 l/min P03 = MASSFL*RV/(60*P01) CPV = dlimit(P03,0,P05) A1: * Set AIC tracking if (({FIC30378.MODE.CAS}<>1) AND (FIC30378AS.SW == 2)) then A IC30381TSW.PV=1 else A IC30381TSW.PV=0 end if |  | 1
[9 empty] | 2 | MICIL2LAG1 | T/HR | RV1 | [5 empty] | * Backcalculate kg/t from l/min setpoint for tracking, set at 0 kg/t if no massflow if (MASSFL > 0) then P02 = (FIC30378.PV*(60*P01))/MASSFL else P02 = 0 end if * Clamp backcalculated kg/t if (P02 > 10) then CPV1 = 10 else CPV1 = P02 end if |  | 0
AC30320CL | DR0004 | CIL2 Leach Tank pH Calc | % | 100.0 | 0.0 | Medium | 4.0 | FIM-CIL | [9 empty] | 1:CCST; program DOUBLE C * A = AC30320.MV B = AC30320TM.PH C = A * B / 100 CPV = INT(C) CPV1 = AC30320.SV + 0.2 * 6 Mar 08 * Adjust PL/LL alarms based on setpoint - cap at PL 8.6, LL 8.4 P01 = AC30320.SV - 0.3 P02 = AC30320.SV - 0.5 if (P01<8.6) then P01 = 8.6 end if AC30320.PL = P01 if (P02<8.4) then P02 = 8.4 end if AC30320.LL = P02 if (AC30320.SV < 8.6) AC30320.SV = 8.6!changed from 8.8 to 8.6 with |  | 1.0
permission from mets, 1/4/2020 P08 = AI30320.PV - AC30321.PV P08 = dabs(P08) end
AIC30381CALC | DR0004 |  | % | 100 | 0 | Logging | 4 | FIM-CIL | [9 empty] | 1:CCST; * * FLAT LINE AND SUDDEN LARGE CONCENTRATION CHANGE DETECTION * FLAT LINE DETECTION: GETS ABSOLUTE VALUE OF DIFFERENCE BETWEEN CURRENT * AND THE DELAYED CN READING. * CONCENTRATION JUMP DETECTION: CALCULATES DIFFERENCE BETWEEN CURRENT AND PREVIOUS CN VALUE. * CPV AND CPV1 USED IN AIC30381RL (AIC30381LC) TO ACTUALLY DETECT THE CONDITIONS. * program double diffFlatLine double diffCNJump double curCN double delaydCN double prevCN curCN = RV1 delaydCN = RV2 * FLAT LINE DETECTION diffFlatLine = curCN-delaydCN CPV = dabs(diffFlatLine) * CONCENTRATION JUMP DETECTION diffCNJump = curCN - prevCN CPV1 = dabs(diffCNJump) prevCN = curCN end |  | 0
CIL2LIME | DR0004 | CIL2 Lime Calc | KG/T | 100 | 0 | Logging | 4 | FIM-CIL | [9 empty] | 1:CCST; ******************************************************************* * LIME/CYANIDE ADDITION KG/T SETPOINT CONVERSION * * This calculates the actual kg/t of lime used on CIL 2 * * Inputs * P01 : Total Mass flow feed * P02 : Specific Gravity of Slurry * * Locals * P06 : Fraction Solids of Lime * P07 : Lime Slurry SG * * Outputs * P08: Lime Actual kg/t * ******************************************************************* alias MASSFL MI30337.CPV alias LIMEFLOW FI30333AVE.CPV P01 = MI30337.CPV * kg/t actual calculation from - also handle divide by zero if (MASSFL >= 0.1) then P08 = LIMEFLOW * (P06*P07*1000) / MASSFL else P08 = 0 end if CPV = P08 |  | 1
AI30381SD | DR0010 | CIL2 SD,AVGfor reports | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; ************************************************************************************ * The CALCU calculates a standard deviation and is used for reporting only * * The calculation is based on a formula below : * * _ _ _ _ _ _ * * (x1-x)*(x1-x)+(x2-x)*(x2-x)+...+(xn-x)*(xn-x) * * standard deviation = SQRT ( --------------------------------------------- ) * * n-1 * ************************************************************************************ program double x, avg, sum, sum1 * n - number of samples * x - sum to calculate the 'avg' average * sum - sum calculation * P01 - standard deviation alias GS00602 GS00602-105.PV if (GS00602==1) then n = n + 1 x = x + AIC30381.PV avg = x/n sum = sum + (AIC30381.PV-avg)*(AIC30381.PV-avg) * To make sure there is no division by 0 |  | 0
if (n >= 2) then sum1 = sum/(n-1) end if P01 = sqrt(sum1) P02 = avg end if end
CA1MDESTCAL | DR0015 |  | % | 100.0 | 0.0 | Medium | 4.0 | FIM-CIL | [9 empty] | 1:CCST; alias Count CA1MCOUNT.PV if (Count==1) and (CATOCIL1.PV==0) then Count = 2! Change to select CIL2 end if if (Count==2) and (CATOCIL2.PV==0) then Count = 3! Change to select CIL3 end if if (Count==3) and (CATOCIL3.PV==0) then Count = 4! Change to select no destination end if if (Count==4) and ((CATOCIL1.PV==1) OR (CATOCIL2.PV==1) OR (CATOCIL3.PV==1)) then Count = 1 ! Change to select CIL1 end if if (Count>=5) or (Count<=0) then Count = 4 end if {CA1MDEST.MODE.CAS} = 1 |  | 1
MI30637X | DR0019 | THICKNER 3 U/F Massflow | T/HR | 2000.0 | 0.0 | Medium | 4.0 | FIM-CIL | 1 | DIC30613 | % | RV (Thickener #3 U/F Density) | [5 empty] | FV306181:CCST; * * CIL 3 MASS FLOW CALCULATION * * *I nputs *FLOW: Feed Flow *%SOL: Feed Density *WTR: Density of Water *FOR: Fimiston Ore Density * *C alculations *MASS: Calculated Dry Tonnes *SG: Slurry SG * program * alias WTR DYS010501WTR.PV alias FOR DYS010501FOR.PV alias FLOW RV1 alias %SOL RV alias MASS CPV alias PUMPA RV2 alias PUMPB RV3 alias RECVLV RV4 * float SG * SG = 100/((%SOL/FOR) + (100 - %SOL)/WTR) * if ( ((PUMPA == 1) or (PUMPB == 1)) and (RECVLV == 0) ) then MASS = FLOW*SG*%SOL/100 else MASS = 0 end if * P02 = FLOW P03 = %SOL P04 = WTR P05 = FOR P06 = SG end |  | 1
[9 empty] | 2 | FI30615 | M3/H | RV1 (CIL3 Feed Flow) | [7 empty] | 0
[9 empty] | 3 | 30PP61A | % | RV2 (Thickener 3 U/F Pump A) | [7 empty] | 0
[9 empty] | 4 | 30PP61B | % | RV3 (Thickener 3 U/F Pump B) | [7 empty] | 0
[9 empty] | 5 | FV30618 |  | RV4 (Thickener 3 Recycle Vlv) | [7 empty] | 0
MI19579CIL3 | DR0019 | MTC LchFdU/FCil3Massflow | T/HR | 2000 | 0 | Medium | 4 | FIM-CIL | 1 | DI19577 |  | RV | [5 empty] | FIC195781:CCST; * * CIL 3 MASS FLOW CALCULATION * * *I nputs *FLOW: Feed Flow *%SOL: Feed Density *WTR: Density of Water *FOR: Fimiston Ore Density * *C alculations *MASS: Calculated Dry Tonnes *SG: Slurry SG * program * alias MASS CPV alias WTR DYS010501WTR.PV alias FOR DYS010501FOR.PV alias %SOL RV alias FLOWCIL2 RV1 alias PUMPA RV2 alias PUMPB RV3 alias RECVLV RV4 alias FLOW RV5 * float SG * SG = 100/((%SOL/FOR) + (100 - %SOL)/WTR) * if ( ((PUMPA == 1) or (PUMPB == 1)) and (RECVLV == 0) and (FLOW >= FLOWCIL2)) then MASS = (FLOW-FLOWCIL2)*SG*%SOL/100 else MASS = 0 end if * P02 = FLOW P03 = %SOL P04 = WTR P05 = FOR P06 = SG end |  | 1
[9 empty] | 2 | FI30384 | M3/H | RV1 (CIL2 Slurry Flow frm MTC) | [7 empty] | 0
[9 empty] | 3 | 19PP52A | % | RV2 (MTC ThicknerU/F Pump A) | [7 empty] | 0
[9 empty] | 4 | 19PP52B | % | RV3 (MTC ThicknerU/F Pump B) | [7 empty] | 0
[9 empty] | 5 | FV19582 |  | RV4 (MTC Thicknr Recirc Vlv) | [7 empty] | 0
[9 empty] | 6 | FIC19578 | M3/H | RV5 (MTC Thick U/F Flow Ctrl) | [7 empty] | 0
FIC30622CALC2 | DR0019 | CIL1 2D NaCNFlowAddition | L/MIN | 50 | 0 | Medium | 1 | FIM-CIL | 1 | MICIL3LAG1 | T/HR | RV1 | [5 empty] | 1:CCST; ******************************************************************* * CYANIDE ADDITION KG/T SETPOINT CONVERSION * * This calc takes operator kg/t setpoint and convert it to a * l/min flow setpoint for cyanide. * * Inputs * RV : kg/t Cyanide Setpoint * RV1 : Total Mass flow * Locals * P01 : Cyanide Conversion Factor * This varies by season - Winter 28.5% => 0.3410 * Summer 30.5% => 0.3605 *P 08 : Kg/t Max Setpoint * * Outputs * CPV : FIC l/min setpoint * CPV1 : Back calculate AIC MV when controller tracking * ******************************************************************* alias MASSFL FIC30622CALC.RV1 alias CYNFCT FIC30622CALC.P01 * Backcalculate kg/t from l/min setpoint for tracking, set at 0 kg/t if no massflow if (MASSFL > 10) then P02 = (FIC30622.SV*(60*CYNFCT))/MASSFL else P02 = 0 end if * Clamp backcalculated kg/t if (P02 > 10) then CPV = 10 else CPV = P02 end if if (MASSFL < 10) then FIC30622AS.SW = 2 else FIC30622AS.SW = 1 {FIC30622.MODE.CAS} = 1 end if if ({FIC30622AS.MODE.AUT} <> 1) then {FIC30622AS.MODE.AUT} = 1 end if if (({MIC30622.MODE.AUT}==1) AND (MIC30622.SV > P08)) then MIC30622.SV = P08 end if |  | 0
AIC30637FF |  |  | % | 2 | 0 | Logging | 4 | FIM-CIL | 1 | FI30638 | M3/H | RV (CIL3 BARREN ELUATE FLOW) | [5 empty] | FV659821:CCST; !This computes the cyanide content on the barren eluate to compensate for the flow on the cyanide supply. ! P01 = CYANINDE PPM CONCENTRATION AVERAGE ~ 2960ppm ! RV = BARREN ELUATE FLOW FI60338 |  | 1
| DR0019 | [7 empty] | 2 | MICIL3LAG1 | T/HR | RV1 | [5 empty] | ! RV1 = TOTAL FLOW INTO THE CIL CIL3FEEDX.CPV ! P02 = SPECIFIC GRAVITY (ASSUMPTION = 1) alias PUMP RV2 alias VALVE RV3 if (RV > 0 and RV1 > 0 and PUMP == 2 and VALVE == 2) then CPV1 = (P01 * RV * P02) / RV1 CPV = CPV1 / 1000 else CPV = 0 end if if (CIL1TAILSDST.PV02 == ON) then A IC30637.MH = 0.3 else A IC30637.MH = 0.4 end if |  | 0
[9 empty] | 3 | 66PP65 | % | RV2 (BarrenEluate Dist Pump) | [7 empty] | 0
[9 empty] | 4 | FV65982 |  | RV3 (BarrenEluateTransf.Valve) | [7 empty] | 0
AIC30637CALC | DR0019 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; * * FLAT LINE AND SUDDEN LARGE CONCENTRATION CHANGE DETECTION * FLAT LINE DETECTION: GETS ABSOLUTE VALUE OF DIFFERENCE BETWEEN CURRENT * AND THE DELAYED CN READING. * CONCENTRATION JUMP DETECTION: CALCULATES DIFFERENCE BETWEEN CURRENT AND PREVIOUS CN VALUE. * CPV AND CPV1 USED IN AIC30381RL (AIC30381LC) TO ACTUALLY DETECT THE CONDITIONS. * program double diffFlatLine double diffCNJump double curCN double delaydCN double prevCN curCN = RV1 delaydCN = RV2 * FLAT LINE DETECTION diffFlatLine = curCN-delaydCN CPV = dabs(diffFlatLine) * CONCENTRATION JUMP DETECTION diffCNJump = curCN - prevCN CPV1 = dabs(diffCNJump) prevCN = curCN end |  | 1
CIL2AND3MAXCN | DR0019 |  | % | 100.0 | 0.0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; * * Sets .MH of CN analysers and .SVH of Mass Flow CN controllers * based on CIL1 tails destination. Enforces max limits if manually changed * * P01: Max CN addition to CIL not receiving CIL1 tails. * P02: Max CN addition to CIL receiving CIL1 tails. * program alias CIL2 CIL1TOCIL2.PV alias CIL3 CIL1TOCIL3.PV if (CIL2 == 1) then A IC30381.MH = P02 A IC30637.MH = P01 MIC30378.SVH = P02 MIC30622.SVH = P01 else if (CIL3 == 1) then A IC30381.MH = P01 A IC30637.MH = P02 MIC30378.SVH = P01 MIC30622.SVH = P02 end if *Enforce max limits if ({AIC30381.MODE.MAN} and AIC30381.MV > AIC30381.MH) then AIC30381.MV = AIC30381.MH end if if ({AIC30637.MODE.MAN} and AIC30637.MV > AIC30637.MH) then A IC30637.MV = AIC30637.MH end if if ({MIC30378.MODE.AUT} and MIC30378.SV > MIC30378.SVH) then MIC30378.SV = MIC30378.SVH end if if ({MIC30622.MODE.AUT} and MIC30622.SV > MIC30622.SVH) then MIC30622.SV = MIC30622.SVH end if end |  | 1
FIC30622CALC3 | DR0019 | CIL1 2D NaCNFlowAddition | L/MIN | 50.000 | 0.000 | Medium | 1 | FIM-CIL | [9 empty] | 1:CCST; integer oneshot alias RST CIL3FLWTRPRST.PV if ({FIC30622AS.SEL.2} == 0 or {FIC30622.MODE.CAS} == 0) FIC30622.SV = FIC30622CALC.P03 P01 = dabs(FIC30622.DV) if (MICIL3LAG1.CPV < 10 and oneshot == 0) then P08 = FIC30622.SUM + P07 oneshot = 1 else if (MICIL3LAG1.CPV > 10) then P08 = 0 oneshot = 0 end if if (RST == 1) then P08 = FIC30622.SUM + P07 RST = 0 end if |  | 1
KGPERTONNE3 | DR0020 |  | L/HR | 700 | 0 | Medium | 1 | FIM-CIL | 1 | MI30637 | T/HR | RV (CIL3 Feedrate) | [5 empty] | 1:CCST; ******************************************************************* * LEAD NITRATE ADDITION KG/T SETPOINT CONVERSION * * This calc takes operator kg/t setpoints and converts them to * l/hr flow setpoints for lead nitrate * * Inputs * RV : Total Mass flow from thickener U/flow lines A and B * RV1: MTC Thickener Mass Underflow * * Locals * P01: Lead Nitrate kg/t setpoint for FIC30684 * P02: Lead Nitrate Concentration 0.4 kg/L * P03: MTC Thickener Bias ( 50% ) * P04: * P05: * P06: * P07: * * Outputs * CPV: FIC30684 l/h setpoint * CPV1: * CPV2: * CPV3: * * MJS 03/10/03 ******************************************************************* alias MASSFL RV alias MASSFL2 RV1 * m3/h setpoint calculation for FI30684 CPV = MASSFL*P01/P02 + MASSFL2*P01*P03/P02 |  | 1
[9 empty] | 2 | MI19579 | T/HR | RV1 (MTC Thickener U/F) | [7 empty] | 0
SYPP61CALC | DR0020 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; * THICKNER PUMP SPEED RECIRC CONTROL program if (SY30607A.MODE==MAN) then SY30607A.ML=75 SY30607B.ML=75 if (SY30607A.MV < 75) then SY30607A.MV=75 end if if (SY30607B.MV < 75) then SY30607B.MV=75 end if else SY30607A.ML=0 SY30607B.ML=0 end if if ((({SY30607SEL3.MODE.MAN}) OR (SY30607SEL3.SW <> 4)) OR (({SY30607SEL2.MODE.MAN}) OR (SY30607SEL2.SW <> 4))) then {SY30607SEL3.MODE.AUT} = 1 SY30607SEL3.SW = 4 {SY30607SEL2.MODE.AUT} = 1 SY30607SEL2.SW = 4 end if end |  | 1
AI30637BCAL | DR0021 |  | ppm | 200.00 | 0.00 | Medium | 4 | FIM-CIL | 1 | AI30637BAVG | ppm | RV | [5 empty] | AI30637BDSET31:CCST; ******************************************************************* * AI30637B CYANIDE ADDITION PPM SETPOINT * * This calc used the AI30637B one hour average to * calculate a new setpoint for Cyanide addition. * * Inputs * RV : AI30637B one hour average * RV1 : AI30637B Target * RV2 : Cyanide addition operator setpoint (minimum) * RV3 : Max Cyanide addition setpoint * * Locals * P01 : Cyanide Decay Factor per tank * P02 : Tanks online * P03 : Cyanide Decay Factor * * * Outputs * CPV : Cyanide addition setpoint based on AI30637B one hour average * ******************************************************************* program P03 = P01 * P02 /100 CPV = ( ( (RV1 - RV) ) * (P03 + 1) ) + RV2 IF (CPV > RV3 ) THEN CPV = RV3 END IF IF (CPV < RV2 ) THEN CPV = RV2 END IF END |  | 1
[9 empty] | 2 | AI30637BDSET1 | PPM | RV1 (AI30637B Target) | [7 empty] | 0
[9 empty] | 3 | AI30637BDSET2 | ppm | RV2 (Cyanide addition operato) | [7 empty] | 0
[9 empty] | 4 | AI30637BDSET3 |  | RV3 | [7 empty] | 0
AI30382CAL | DR0021 |  | PPM | 200.00 | 0.00 | Medium | 4 | FIM-CIL | 1 | AI30382AVG | PPM | RV | [5 empty] | AI30382DSET31:CCST; ******************************************************************* * AI30637B CYANIDE ADDITION PPM SETPOINT * * This calc used the AI30382 average to * calculate a new setpoint for Cyanide addition. * * Inputs * RV : AI30382 average * RV1 : TK32F Target * RV2 : TK32A Target (minimum Cyanide addition setpoint)* RV3 : Max Cyanide addition setpoint * * Locals * P01 : Cyanide Decay Factor per tank * P02 : Tanks online * P03 : Cyanide Decay Factor * * * Outputs * CPV : Cyanide addition setpoint based on AI30637B one hour average * ******************************************************************* program * Decay Factor Calculation P03 = P01 * P02 /100 * Output Calculation CPV = ( ( (RV1 - RV) ) * (P03 + 1) ) + RV2 * Maximum IF (CPV > RV3 ) THEN |  | 1
[9 empty] | 2 | AI30382DSET1 | PPM | RV1 (TK32F Target) | [7 empty] | 0
[9 empty] | 3 | AI30382DSET2 | PPM | RV2 (TK32A Traget) | [7 empty] | 0
[9 empty] | 4 | AI30382DSET3 |  | RV3 | [5 empty] | CPV = RV3 END IF * Minimum IF (CPV < RV2 ) THEN CPV = RV2 END IF END |  | 0
1:CCST; program DOUBLE C * A = AC30620.MV B = AIC30620B.PH C = A * B / 100 CPV = INT(C) CPV1 = AC30620.SV + 0.2 * 6 Mar 08 * Adjust PL/LL alarms based on setpoint - cap at PL 8.6, LL 8.4 P01 = AC30620.SV - 0.3 P02 = AC30620.SV - 0.5
AIC30620D | DR0022 | CIL3 Leach Tank pH Calc | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | if (P01<8.6) then P01 = 8.6 end if AC30620.PL = P01 if (P02<8.4) then P02 = 8.4 end if AC30620.LL = P02 if (AC30620.SV < 8.6) AC30620.SV = 8.6!changed from 8.8 to 8.6 with permission from mets, 1/4/2020 P08 = AI30693A.PV - AI30693C.PV P08 = dabs(P08) end |  | 0
AIC30631 | DR0022 |  | % | 100 | 0 | Logging | 4 | FIM-CIL | 1 | 19SW62RMN |  | RV1 | [5 empty] | 1:CCST; *********************************************************** * * RATE OF CHANGE PROGRAM * * PROGRAMMER: C BAADE * DATE: 29/10/97 * * This program calculates the rate of change of thickener * underflow over a ten minute period. * ************************************************************ * * VARIABLES * * n = number of samples * hr= time (hours) * min = time (min) * ROC = Rate of Change * * program double ROC n = n + 1 min = int(RV1) hr = int(RV2) ROC = (ROC + RV3)/n P01 = RV1 P02 = RV2 P03 = RV3 P04 = ROC P05 = n if (n > 60) then n = 0 end if end |  | 1
[9 empty] | 2 | 19SW62RH |  | RV2 | [7 empty] | 0
[9 empty] | 3 | FI30615 |  | RV3 | [7 empty] | 0
DI306131:CCST; * * CIL 3 MASS FLOW CALCULATION * * *I nputs *FLOW: Feed Flow *%SOL: Feed Density *WTR: Density of Water *FOR: Fimiston Ore Density * *C alculations *MASS: Calculated Dry Tonnes *SG: Slurry SG * program * alias WTR DYS010501WTR.PV alias FOR DYS010501FOR.PV alias FLOW FI30615.PV alias %SOL RV alias MASS CPV alias FLOC FI30616.PV alias CYNC FIC30378CALC.P01
MI30637 | DR0022 | CIL3 Feedrate | T/HR | 3000 | 0 | Medium | 4 | FIM-CIL | 1 | DI30613 |  | RV | [5 empty] | alias PUMPA 30PP61ARUN.PV alias PUMPB 30PP61BRUN.PV alias RECVLV FV30618.PV * float SG * SG = 100/((%SOL/FOR) + (100 - %SOL)/WTR) * if ( ((PUMPA == 1) or (PUMPB == 1)) and (RECVLV == 0) ) then MASS = FLOW*SG*%SOL/100 else MASS = 0 end if * P02 = FLOW P03 = %SOL P04 = WTR P05 = FOR P06 = SG * P08 = Floc usage ; Floc concentration = 2.5[g/l] if (MASS == 0) then MASS = 0.01 end if * P08 = (FLOC*2.5)/MASS * ******************************************************************* * Locals * P07 : Cyanide Conversion Factor * This varies by season - Winter 28.5% => 0.3410 * Summer 30.5% => 0.3605 * * Outputs * CPV1 : Back calculate AIC MV when controller tracking * ******************************************************************* * Backcalculate kg/t from l/min setpoint for tracking, set at 0 kg/t if no massflow if (MASS > 0) then CPV1 = (FIC30622.SV*(60*CYNC))/MASS else CPV1 = 0 end if |  | 1
CIL3LIME | DR0022 |  | % | 100 | 0 | Logging | 4 | FIM-CIL | [9 empty] | 1:CCST; ******************************************************************* * LIME/CYANIDE ADDITION KG/T SETPOINT CONVERSION * * This calculates the actual kg/t of lime used on CIL 3 * * Inputs * P01 : Total Mass flow feed * P02 : Specific Gravity of Slurry * * Locals * P06 : Fraction Solids of Lime * P07 : Lime Slurry SG * * Outputs * P08: Lime Actual kg/t * ******************************************************************* alias MASSFL MI30637.CPV alias LIMEFLOW FI30633AVE.CPV P01 = MI30637.CPV * kg/t actual calculation from - also handle divide by zero if (MASSFL >= 0.1) then P08 = LIMEFLOW * (P06*P07*1000) / MASSFL else P08 = 0 end if CPV = P08 |  | 1
PIC30739CAL | DR0023 | FTails Pump B Flow | KPA | 1200 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; program if (PUMPBTOLINEB.PV == 1) then CPV = RV2 PIC30739.SV = P02 else if (PUMPBTOLINEA.PV == 1) then CPV = RV1 PIC30739.SV = PIC30740.SV else if (PUMPBTOLINEC.PV == 1) then CPV = RV3 PIC30739.SV = PIC30741.SV else CPV = RV2 PIC30739.SV = P02 end if end if end if end |  | 1
SY30745CALC | DR0023 |  | % | 2000 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; ************************************************************* * 30PP62D SPEED CONTROL * * This ensures that all control blocks are in their * correct modes. * * Outputs: * ************************************************************* * Force control block states {SY30745.MODE.AUT}=1 SY30745.SW=4 {PIC30739A.MODE.AUT}=1 !{SY3033.MODE.CAS}=1 |  | 1
SY30743CALC | DR0023 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; *This Calc Block limits the Operator input to between 1.0-1.4. * ROH 27/06/08 if (SY30743ADD.GAIN < 0.8) then SY30743ADD.GAIN = 0.8 end if if (SY30743ADD.GAIN > 1.4) then SY30743ADD.GAIN = 1.4 end if if ({SY30743ADD.MODE.CAS} <> 1) {SY30743ADD.MODE.CAS} = 1 |  | 1
LC30719CALC | DR0023 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; ************************************************************* * Minimum Output Selection * * This ensures that the AS-H blocks for the various pumps * have the correct minimum values depending on PID mode. * When in CAS the level control should not request less than 480m³/h * When in PRD the level control should not request less than 70% * ************************************************************* *if ({FIC30742.MODE.CAS} == 1 OR {FIC30738.MODE.CAS} == 1 OR {FIC30743.MODE.CAS} == 1) then *LC30719.ML = P01 *else if ({FIC30738X.MODE.CAS} == 1) then *LC30719.ML = P03 *else *LC30719.ML = P02 *end if |  | 1
30PP61ARUNTM | DR0028 |  | % | 9999999 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP61A.ONTM alias reset 30PP61ARST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
30PP61BRUNTM | DR0028 |  | % | 9999999 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP61B.ONTM alias reset 30PP61BRST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
75PW17ARUNTM | DR0028 |  | % | 9999999 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 75PW17A.ONTM alias reset 75PW17ARST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
75PW17BRUNTM | DR0028 |  | % | 9999999 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 75PW17B.ONTM alias reset 75PW17BRST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
75PW62ARUNTM | DR0028 |  | % | 9999999 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 75PW62A.ONTM alias reset 75PW62ARST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
75PW62BRUNTM | DR0028 |  | % | 9999999 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 75PW62B.ONTM alias reset 75PW62BRST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
30PP62ARUNTM | DR0029 |  | % | 9999999 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP62A.ONTM alias reset 30PP62ARST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
30PP62BRUNTM | DR0029 |  | % | 9999999 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP62B.ONTM alias reset 30PP62BRST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
30PP62CRUNTM | DR0029 |  | % | 9999999 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP62C.ONTM alias reset 30PP62CRST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
30PP62DRUNTM | DR0029 |  | % | 9999999 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP62D.ONTM alias reset 30PP62DRST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
30PP62ARUNTM2 | DR0029 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP62A.ONTM *Endless Run Hours Calcu Block if(runtime == 0) then P04 = P03 +1 end if if (runtime > 0) then P03 = P04 end if P01 = P02 + (P04 * 27777) P02 = runtime / 3600 P05 = runtime |  | 1
30PP62BRUNTM2 | DR0029 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP62B.ONTM *Endless Run Hours Calcu Block if(runtime == 0) then P04 = P03 +1 end if if (runtime > 0) then P03 = P04 end if P01 = P02 + (P04 * 27777) P02 = runtime / 3600 P05 = runtime |  | 1
30PP62CRUNTM2 | DR0029 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP62C.ONTM *Endless Run Hours Calcu Block if(runtime == 0) then P04 = P03 +1 end if if (runtime > 0) then P03 = P04 end if P01 = P02 + (P04 * 27777) P02 = runtime / 3600 P05 = runtime |  | 1
30PP62DRUNTM2 | DR0030 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP62D.ONTM *Endless Run Hours Calcu Block if(runtime == 0) then P04 = P03 +1 end if if (runtime > 0) then P03 = P04 end if P01 = P02 + (P04 * 27777) P02 = runtime / 3600 P05 = runtime |  | 1
FI30738CALC | DR0036 |  | M3/H | 1200 | 0 | Logging | 4 | FIM-CIL | [9 empty] | 1:CCST; ! ! Calculate Line B Flow based on Pump Amps ! ! alias PUMPB 30PP62B.PV alias VLVB FV30724.PV alias PUMPD 30PP62D.PV alias AMPSB II30744B.PV alias AMPSD IIC30744D.PV if (PUMPD == 2) then CPV1 = P01 * AMPSD + P02 else if (PUMPB == 2 AND VLVB == 2) then CPV1 = P03 * AMPSB + P04 else CPV1 = 0 end if CPV2 = RV * 12 if (P08 == 1) then CPV = CPV1 else CPV = CPV2 end if |  | 1
TAILSLEAKCALC | DR0037 | TAILS LEAK DETECTION | % | 100 | 0 | Logging | 7 | FIM-CIL | [9 empty] | 1:CCST; * This program set the PV of tags FA30741HH to one if tag FI30741 goes high- high. * It also sets the PV of tags FA30744HH to one if tag FI30744 goes high-high. * It also sets the PV of tags FA30739HH to one if tag FI30739 goes high-high. * The sum block of these tags can then be used as counters. * This method was chosen instead of counters because it made calculations easier in PI and * the SUM value goes up to 99999999 instead of 10000 found on the counter. * * John Karageorgos - 29/4/98 program if ({FLOWDIFFRL.X03.GE}) then * FA30739HH.PV = 1 CPV2 = 1 else * FA30744HH.PV = 0 CPV2 = 0 end if if ({FLOWDIFFRL.X01.GE}) then * FA30741HH.PV = 1 CPV = 1 else * FA30741HH.PV = 0 CPV = 0 end if if ({FLOWDIFFRL.X05.GE}) then * FA30744HH.PV = 1 CPV1 = 1 else * FA30744HH.PV = 0 CPV1 = 0 end if end |  | 1
TAILSLEAKCALC2 | DR0037 | TAILS LEAK DETECTION | % | 100 | 0 | Logging | 4 | FIM-CIL | [9 empty] | 1:CCST; * This calculation block increments the value of tags FA30741CTP * and FA30744CTP when ever the respective tags FA30741HH and * FA30744HH register a 1, which is a HI-HI alarm of the tails difference * flowrate for tails lines A and C respectively. * This calcultion block has been set up as a one shot and is triggered * logic chart TAILSLEAK. * John Karageorgos - 30/4/98 * John Karageorgos - 26/8/99 program if ({FLOWDIFFRL.X03.GE}) then! TAILS B FLOW RATE DIFFERENCE HIHI FA30739CTP.PV = FA30739CTP.PV + 1 end if if ({FLOWDIFFRL.X01.GE}) then! TAILS A FLOW RATE DIFFERENCE HIHI FA30741CTP.PV = FA30741CTP.PV + 1 end if if ({FLOWDIFFRL.X05.GE}) then! TAILS C FLOW RATE DIFFERENCE HIHI FA30744CTP.PV = FA30744CTP.PV + 1 end if end |  | 1
TAILSLEAKCALD | DR0037 | TAILS LEAK DETECTION | % | 100 | 0 | Logging | 7 | FIM-CIL | [9 empty] | 1:CCST; * This program set the PV of tags FA30742DHH to one if tag FI30742D goes high-high. * It also sets the PV of tags FA30743HH to one if tag FI30743D goes high-high. * It also sets the PV of tags FA30738HH to one if tag FI30738D goes high-high. * The sum block of these tags can then be used as counters. * This method was chosen instead of counters because it made calculations easier in PI and * the SUM value goes up to 99999999 instead of 10000 found on the counter. * * John Karageorgos - 29/4/98 program if ({TAILSLEAKRL.X07.GE}) then * FA30742HH.PV = 1 CPV = 1 else * FA30742HH.PV = 0 CPV = 0 end if if ({TAILSLEAKRL.X11.GE}) then * FA30743HH.PV = 1 CPV1 = 1 else * FA30743HH.PV = 0 CPV1 = 0 end if if ({TAILSLEAKRL.X09.GE}) then * FA30738HH.PV = 1 CPV2 = 1 else * FA30738HH.PV = 0 CPV2 = 0 end if end |  | 1
TAILSLEAKCALE | DR0037 | TAILS LEAK DETECTION | % | 100 | 0 | Logging | 7 | FIM-CIL | [9 empty] | 1:CCST; * This program set the PV of tags PA30740HH to one if tag PI30740D goes high- high. * It also sets the PV of tags PA30741HH to one if tag PI30741D goes high-high. * It also sets the PV of tags PA30739HH to one if tag PI30739D goes high-high. * The sum block of these tags can then be used as counters. * This method was chosen instead of counters because it made calculations easier in PI and * the SUM value goes up to 99999999 instead of 10000 found on the counter. * * John Karageorgos - 17/9/99 program if ({TAILSLEAKRL.X08.LE}) then * PA30740HH.PV = 1 CPV = 1 else * PA30740HH.PV = 0 CPV = 0 end if if ({TAILSLEAKRL.X12.LE}) then * PA30741HH.PV = 1 CPV1 = 1 else * PA30741HH.PV = 0 CPV1 = 0 end if if ({TAILSLEAKRL.X10.LE}) then * PA30739HH.PV = 1 CPV2 = 1 else * PA30739HH.PV = 0 CPV2 = 0 end if end |  | 1
TAILSLEAKCALC3 | DR0037 | TAILS LEAK DETECTION | % | 100 | 0 | Logging | 7 | FIM-CIL | [9 empty] | 1:CCST; * This calculation block increments the value of tags FA30741CTP * and FA30744CTP when ever the respective tags FA30741HH and * FA30744HH register a 1, which is a HI-HI alarm of the tails difference * flowrate for tails lines A and C respectively. * This calcultion block has been set up as a one shot and is triggered * logic chart TAILSLEAK. * John Karageorgos - 17/9/99 program if ({TAILSLEAKRL.X07.GE} and {TAILSLEAKRL.X08.LE}) then IA = FPA30741CTP.PV FA30741CTP.PV = IA + 1 end if if ({TAILSLEAKRL.X09.GE} and {TAILSLEAKRL.X10.LE}) then IB = FPA30739CTP.PV FPA30739CTP.PV = IB + 1 end if if ({TAILSLEAKRL.X11.GE} and {TAILSLEAKRL.X12.LE}) then IC = FPA30744CTP.PV FPA30744CTP.PV = IC + 1 end if end |  | 1
TAILSLEAKCALC4 | DR0037 | TAILS LEAK DETECTION | % | 100 | 0 | Logging | 7 | FIM-CIL | [9 empty] | 1:CCST; * This calculation block increments the value of tags FA30741CTP * and FA30744CTP when ever the respective tags FA30741HH and * FA30744HH register a 1, which is a HI-HI alarm of the tails difference * flowrate for tails lines A and C respectively. * This calcultion block has been set up as a one shot and is triggered * logic chart TAILSLEAK. * John Karageorgos - 17/9/99 program if ({TAILSLEAKRL.X09.GE}) then FA30738CTP.PV = FA30738CTP.PV + 1 end if if ({TAILSLEAKRL.X07.GE}) then FA30742CTP.PV = FA30742CTP.PV + 1 end if if ({TAILSLEAKRL.X11.GE}) then FA30743CTP.PV = FA30743CTP.PV + 1 end if end |  | 1
TAILSLEAKCALC5 | DR0037 | TAILS LEAK DETECTION | % | 100 | 0 | Logging | 7 | FIM-CIL | [9 empty] | 1:CCST; * This calculation block increments the value of tags FA30741CTP * and FA30744CTP when ever the respective tags FA30741HH and * FA30744HH register a 1, which is a HI-HI alarm of the tails difference * flowrate for tails lines A and C respectively. * This calcultion block has been set up as a one shot and is triggered * logic chart TAILSLEAK. * John Karageorgos - 17/9/99 program if ({TAILSLEAKRL.X10.LE}) then PA30739CTP.PV = PA30739CTP.PV + 1 end if if ({TAILSLEAKRL.X08.LE}) then PA30740CTP.PV = PA30740CTP.PV + 1 end if if ({TAILSLEAKRL.X12.LE}) then PA30741CTP.PV = PA30741CTP.PV + 1 end if end |  | 1
TAILSLEAKCALF | DR0037 | TAILS LEAK DETECTION | % | 100 | 0 | Logging | 7 | FIM-CIL | [9 empty] | 1:CCST; * This program set the PV of tags FPA30741HH to one if tag PI30740D goes low- low and tag FI30742D goes high-high. * It also sets the PV of tags FPA30744HH to one if tag PI30741D goes low-low and tag FI30743D goes high-high. * It also sets the PV of tags FPA30739HH to one if tag PI30739D goes low-low and tag FI30738D goes high-high. * The sum block of these tags can then be used as counters. * This method was chosen instead of counters because it made calculations easier in PI and * the SUM value goes up to 99999999 instead of 10000 found on the counter. * * John Karageorgos - 17/9/99 program if ({TAILSLEAKRL.X07.GE} and {TAILSLEAKRL.X08.LE}) then * FPA30741HH.PV = 1 CPV = 1 else * FPA30741HH.PV = 0 CPV = 0 end if if ({TAILSLEAKRL.X11.GE} and {TAILSLEAKRL.X12.LE}) then * FPA30744HH.PV = 1 CPV1 = 1 else * FPA30744HH.PV = 0 CPV1 = 0 end if if ({TAILSLEAKRL.X09.GE} and {TAILSLEAKRL.X10.LE}) then * FPA30739HH.PV = 1 CPV2 = 1 else * FPA30739HH.PV = 0 CPV2 = 0 end if end |  | 1
TAILSLINEBCALC | DR0037 | TAILS LEAK DETECTION | % | 100 | 0 | Logging | 7 | FIM-CIL | [9 empty] | 1:CCST; program if ({TAILSLINEB-OLD.PV.1}) then TAILSLINEBVALS.DT01 = 25 TAILSLINEBVALS.DT02 = -25 TAILSLINEBVALS.DT03 = 75 TAILSLINEBVALS.DT04 = -150 FI75681SEL.SW = 1 end if if ({TAILSLINEB-NEW.PV.1}) then TAILSLINEBVALS.DT01 = 20 TAILSLINEBVALS.DT02 = -20 TAILSLINEBVALS.DT03 = 76 TAILSLINEBVALS.DT04 = -151 FI75681SEL.SW = 2 end if if ({TAILSLINEB-KAL.PV.1}) then TAILSLINEBVALS.DT01 = 20 TAILSLINEBVALS.DT02 = -20 TAILSLINEBVALS.DT03 = 76 TAILSLINEBVALS.DT04 = -151 FI75681SEL.SW = 3 end if |  | 1
TAILSLINEACALC | DR0037 | TAILS LEAK DETECTION | % | 100 | 0 | Logging | 7 | FIM-CIL | [9 empty] | 1:CCST; program if ({TAILSLINEA-FIM.PV.1}) then TAILSLINEAVALS.DT01 = 18 TAILSLINEAVALS.DT02 = -18 TAILSLINEAVALS.DT03 = 150 TAILSLINEAVALS.DT04 = -50 FI75680SEL.SW = 1 end if if ({TAILSLINEA-KAL.PV.1}) then TAILSLINEAVALS.DT01 = 20 TAILSLINEAVALS.DT02 = -20 TAILSLINEAVALS.DT03 = 76 TAILSLINEAVALS.DT04 = -151 FI75680SEL.SW = 3 end if |  | 1
TAILSLINECCALC | DR0037 | TAILS LEAK DETECTION | % | 100 | 0 | Logging | 7 | FIM-CIL | [9 empty] | 1:CCST; program if ({TAILSLINEC-FIM.PV.1}) then TAILSLINECVALS.DT01 = 30 TAILSLINECVALS.DT02 = -30 TAILSLINECVALS.DT03 = 150 TAILSLINECVALS.DT04 = -50 FI75682SEL.SW = 1 end if if ({TAILSLINEC-KAL.PV.1}) then TAILSLINECVALS.DT01 = 50 TAILSLINECVALS.DT02 = -50 TAILSLINECVALS.DT03 = 76 TAILSLINECVALS.DT04 = -151 FI75682SEL.SW = 2 end if if ({TAILSLINEC-KALB.PV.1}) then TAILSLINECVALS.DT01 = 20 TAILSLINECVALS.DT02 = -20 TAILSLINECVALS.DT03 = 76 TAILSLINECVALS.DT04 = -151 FI75682SEL.SW = 3 end if |  | 1
75PW71CALC | DR0038 | Num of Conc Running Calc | % | 5 | 0 | Medium | 3 | FIM-CIL | [9 empty] | 1:CCST; * * CALCULATION OF NUMBER OF CONC RUNNING * * For use in 75PW71RL/75PW71SELLC4 to determine if standby water pump reqd * * Calculation *CPV: Number of Gravity Circuit Concentrators Running * * program alias RUNA 20CO09ARUN-AX.PV alias RUNB 20CO09BRUN-AX.PV alias RUNC 20CO31ARUN-AX.PV alias RUND 20CO31BRUN-AX.PV alias RUNE 19CO54RUN-AX.PV CPV = RUNA+RUNB+RUNC+RUND+RUNE P01 = RUNA P02 = RUNB P03 = RUNC P04 = RUND P05 = RUNE end |  | 1
LIC30719CALC | DR0045 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | 1 | LCVM |  | RV | [5 empty] | 1:CCST; if ({LC30719.MODE.IMAN} <> 1) then LIC30719.SV = LC30719.SV - 10 oneshot = 0 else if (oneshot == 0) then LIC30719.SV = LC30719.SV oneshot = 1 |  | 1
[9 empty] | 2 | LC1M |  | RV1 | [5 empty] | end if if ((RV == 1 or RV1 == 1 or RV2 == 1) and {PIC75502.MODE.AUT}) then LIC30719ASH.SW = 2 else LIC30719ASH.SW = 1 end if if (LIC30719ASH.MH <> P01) LIC30719.MH = LIC30719ASH.MH if (LIC30719.MH <> P02) LIC30719ASH.MH = LIC30719.MH P01 = LIC30719ASH.MH P02 = LIC30719.MH |  | 0
[9 empty] | 3 | LC2M |  | RV2 | [7 empty] | 0
TAILSLNEASANDCL | DR0045 | Tails Line ASand.Thrshld | KPA | 1200 | 0 | Medium | 4 | FIM-CIL | 1 | TAILSLNEASANDLA G |  | RV | [5 empty] | TAILSLNEASANDLAG1:CCST; * Calcualtes the Presure Threshold at which sanding * in Tails Line A could be occuring. * * RV: FI30742.PV Tails Line A Flow * * Pressure Threshold = (0.55 KPA/M3/H * flow M3/H) + 400 KPA * program CPV = 0.55 * RV + 400 end |  | 1
TAILSCALC | DR0050 | GR0341 Display Data | HR | 40000 | 0 | Logging | 4 | FIM-CIL | 1 | S38FCLOCK |  | RV1 | [5 empty] | 1:CCST; * * RV1 = Hr; RV2 = Min; RV3 = Sec; * P01 - Number of times overflow * P02 - Number of times 30PP62A tripped * P03 - Number of times 30PP62B tripped * P04 - Number of times 30PP62C tripped * P05 - Number of times 30PP62D tripped * program * alias OVERFLOW LC30719.PV alias TRIPA 30PP62AFLT.PV alias TRIPB 30PP62BFLT.PV alias TRIPC 30PP62CFLT.PV alias TRIPD 30PP62DFLT.PV if (RV1 == 5 and RV2 == 59 and RV3 => 50) then P01 = 0!* Reset P02 = 0 P03 = 0 end if * if (OVERFLOW >=98 and DONE1 == 0) then P01 = P01 + 1 DONE1 = 1 end if if (OVERFLOW < 90 ) then DONE1 = 0 end if * if (TRIPA ==1 and DONE2 == 0) then P02 = P02 + 1 DONE2 = 1 end if if (TRIPA ==0 ) then DONE2 = 0 end if * if (TRIPB ==1 and DONE3 == 0) then P03 = P03 + 1 DONE3 = 1 end if if (TRIPB ==0 ) then DONE3 = 0 end if end |  | 1
[9 empty] | 2 | S38FCLOCK |  | RV2 | [7 empty] | 0
[9 empty] | 3 | S38FCLOCK |  | RV3 | [7 empty] | 0
TAILSCALC2 | DR0050 | GR0341 Display Data | HR | 40000 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; * * RV1 = Hr; RV2 = Min; RV3 = Sec; * P01 - Number of times overflow * P02 - Number of times 30PP62A tripped * P03 - Number of times 30PP62B tripped * P04 - Number of times 30PP62C tripped * P05 - Number of times 30PP62D tripped * program * alias OVERFLOW LC30719.PV alias TRIPA 30PP62AFLT.PV alias TRIPB 30PP62BFLT.PV alias TRIPC 30PP62CFLT.PV alias TRIPD 30PP62DFLT.PV if (RV1 == 5 and RV2 == 59 and RV3 => 50) then P01 = 0!* Reset P02 = 0 P03 = 0 P04 = 0 P05 = 0 end if * if (TRIPC ==1 and DONE4 == 0) then P04 = P04 + 1 DONE4 = 1 end if if (TRIPC ==0 ) then DONE4 = 0 end if * if (TRIPD ==1 and DONE5 == 0) then P05 = P05 + 1 DONE5 = 1 end if if (TRIPD ==0 ) then DONE5 = 0 end if end |  | 1
TAILSL1CAL | DR0050 | Tails Line 1 Flow Diff | M3/H | 40000 | 0 | Logging | 4 | FIM-CIL | [9 empty] | 1:CCST; * * 1/5/06 - Tails Line New Test Leak Detection * * FLOWP : Tails Flow Plant End * FLOWD : Tails Flow Dam End * * program * alias FLOWP FI30742DLAY.CPV alias FLOWD FI75680LAG.CPV * float LEAK float DIFF LEAK = ((FLOWP + FLOWD)/2)*P01 DIFF = FLOWP-FLOWD if (DIFF<0) then DIFF = -1*DIFF end if if (DIFF > LEAK) then FSL30741.PV=1 else FSL30741.PV=0 end if if (FLOWP<50) then FSL30741.PV=0 end if P02 = LEAK P03 = DIFF end |  | 1
TAILSL2CAL | DR0050 | Tails Line 2 Flow Diff | M3/H | 40000 | 0 | Logging | 4 | FIM-CIL | [9 empty] | 1:CCST; * * 1/5/06 - Tails Line New Test Leak Detection * * FLOWP : Tails Flow Plant End * FLOWD : Tails Flow Dam End * * program * alias FLOWP FI30738DLAY.CPV alias FLOWD FI75681SEL.PV * float LEAK float DIFF LEAK = ((FLOWP + FLOWD)/2)*P01 DIFF = FLOWP-FLOWD if (DIFF<0) then DIFF = -1*DIFF end if if (DIFF > LEAK) then FSL30739.PV=1 else FSL30739.PV=0 end if if (FLOWP<50) then FSL30739.PV=0 end if P02 = LEAK P03 = DIFF end |  | 1
TAILSL3CAL | DR0050 | Tails Line 3 Flow Diff | M3/H | 40000 | 0 | Logging | 4 | FIM-CIL | [9 empty] | 1:CCST; * * 1/5/06 - Tails Line New Test Leak Detection * * FLOWP : Tails Flow Plant End * FLOWD : Tails Flow Dam End * * program * alias FLOWP FI30743DLAY.CPV alias FLOWD FI75682LAG.CPV * float LEAK float DIFF LEAK = ((FLOWP + FLOWD)/2)*P01 DIFF = FLOWP-FLOWD if (DIFF<0) then DIFF = -1*DIFF end if if (DIFF > LEAK) then FSL30744.PV=1 else FSL30744.PV=0 end if if (FLOWP<50) then FSL30744.PV=0 end if P02 = LEAK P03 = DIFF end |  | 1
PI30920CALC | DR0055 |  | % | 100 | 0 | Logging | 4 | 30PP77A | [9 empty] | 1:CCST; PI30920.LL = PIC30920.SV - 75 PI30920.PL = PIC30920.SV - 50 PI30920.PH = PIC30920.SV + 150 PI30920.HH = PIC30920.SV + 200 |  | 1
PLC-COMMS-FM3 | DR0056 |  | % | 100 | 0 | Logging | 4 | FIM2_BOOSTER_STN | [9 empty] | 1:CCST; ************************************************* *COMMS COUNTER FOR RTO PLC LINK* ************************************************* alias PLCOK FIM2LINKOK.PV alias READ PLC-RD-FM3.PV integer count if (READ >= 10) then CPV = 0 else CPV = READ + 1 end if if (READ == P01 and count < P03) then count = count + 1 else if (READ == P01 and count >= P03) then PLCOK = 0 else count = 0 PLCOK = 1 end if P01 = READ P02 = count |  | 1
30PP77ARUNTM | DR0056 |  | % | 9999999 | 0 | Medium | 4 | 30PP77A | [9 empty] | 1:CCST; alias runtime 30PP77A.ONTM alias reset 30PP77ARST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
30PP77BRUNTM | DR0056 |  | % | 9999999 | 0 | Medium | 4 | 30PP77B | [9 empty] | 1:CCST; alias runtime 30PP77B.ONTM alias reset 30PP77BRST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
30PP77ARUNTM2 | DR0056 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP77A.ONTM *Endless Run Hours Calcu Block if(runtime == 0) then P04 = P03 +1 end if if (runtime > 0) then P03 = P04 end if P01 = P02 + (P04 * 27777) P02 = runtime / 3600 P05 = runtime |  | 1
30PP77BRUNTM2 | DR0056 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP77B.ONTM *Endless Run Hours Calcu Block if(runtime == 0) then P04 = P03 +1 end if if (runtime > 0) then P03 = P04 end if P01 = P02 + (P04 * 27777) P02 = runtime / 3600 P05 = runtime |  | 1
PIC3090X_SP | DR0059 |  | % | 100 | 0 | Medium | 4 | FIM2_BOOSTER_STN | [9 empty] | 1:CCST; if (PIC30902.SV < 200) PIC30902.SV = 200 if (PIC30903.SV < 200) PIC30903.SV = 200 |  | 1
PI30952CALC | DR0061 |  | % | 100 | 0 | Logging | 4 | KALT_BOOSTER_STN | [9 empty] | 1:CCST; PI30952.LL = PIC30952.SV - 75 PI30952.PL = PIC30952.SV - 50 PI30952.PH = PIC30952.SV + 150 PI30952.HH = PIC30952.SV + 200 |  | 1
PIC3093X_SP | DR0062 |  | % | 100 | 0 | Medium | 4 | KALT_BOOSTER_STN | [9 empty] | 1:CCST; if (PIC30934.SV < 200) PIC30934.SV = 200 if (PIC30935.SV < 200) PIC30935.SV = 200 |  | 1
KT-COMMS-FM3 | DR0063 |  | % | 100 | 0 | Logging | 4 | KALT_BOOSTER_STN | [9 empty] | 1:CCST; ************************************************* *COMMS COUNTER FOR RTO PLC LINK* ************************************************* alias PLCOK KTLINKOK.PV alias READ KT-RD-FM3.PV integer count if (READ >= 10) then CPV = 0 else CPV = READ + 1 end if if (READ == P01 and count < P03) then count = count + 1 else if (READ == P01 and count >= P03) then PLCOK = 0 else count = 0 PLCOK = 1 end if P01 = READ P02 = count |  | 1
30PP78ARUNTM | DR0063 |  | % | 9999999 | 0 | Medium | 4 | 30PP78A | [9 empty] | 1:CCST; alias runtime 30PP78A.ONTM alias reset 30PP78ARST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
30PP78BRUNTM | DR0063 |  | % | 9999999 | 0 | Medium | 4 | 30PP78B | [9 empty] | 1:CCST; alias runtime 30PP78B.ONTM alias reset 30PP78BRST.PV if(runtime == 0) then overflow = 99999999 - startval startval = 0 end if if (reset == 1) then startval = runtime overflow = 0 reset = 0 end if P01 = (runtime - startval + overflow)/3600 |  | 1
30PP78ARUNTM2 | DR0063 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP78A.ONTM *Endless Run Hours Calcu Block if(runtime == 0) then P04 = P03 +1 end if if (runtime > 0) then P03 = P04 end if P01 = P02 + (P04 * 27777) P02 = runtime / 3600 P05 = runtime |  | 1
30PP78BRUNTM2 | DR0063 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | [9 empty] | 1:CCST; alias runtime 30PP78B.ONTM *Endless Run Hours Calcu Block if(runtime == 0) then P04 = P03 +1 end if if (runtime > 0) then P03 = P04 end if P01 = P02 + (P04 * 27777) P02 = runtime / 3600 P05 = runtime |  | 1
SY30PP79CALC | DR0064 |  | % | 100 | 0 | Medium | 4 | FIM-CIL | 1 | SY30PP79SW |  | RV | [5 empty] | SY30PP79SW1:CCST; CPV = RV - 10 |  | 1
30PP79COMMS | DR0064 |  | % | 100 | 0 | Logging | 4 | FIM-CIL | 1 | %WW0647 |  | RV | [5 empty] | 1:CCST; alias PLCOK FIM1LINKOK.PV integer count, READ READ = int(RV) if (READ >= 10) then CPV = 0 else CPV = READ + 1 end if if (READ == P01 and count < P03) then count = count + 1 else if (READ == P01 and count >= P03) then PLCOK = 0 else count = 0 PLCOK = 1 end if P01 = READ P02 = count |  | 1

## 12. Misc
KCGM GROWTH PROJECT
MISC
MISC. INSTRUMENTS AND CONTROLLERS
Tag Name | P&ID | Description | Normal State | Alarm State | Hardwired (y/n) | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev
FIC30738A | DR0023 | Flow SelectrSwitch | [6 empty] | Medium selector switch (SS-M) feeding downstream PID controller FIC30738 | 0