## Revisions
PROCESS CONTROL TABLES - REAGENTS MIXING & STORAGE (STAGE 2)
REVISION HISTORY
KCGM GROWTH PROJECT
2000-F72-LST-PR-10101
NORTHERN STAR RESOURCES LIMITED
Revision
Date
1 - Reissued for Design
2 - Post FAT Updates
2026-09-01
- Strikethrough indicates removal from design
C - Issued for Client Review
0 - Issued for Design
- Vendor data TBC highlighted
- Revision 2 changes highlighted in orange
- Changes highlighted in orange
2025-09-01
2025-05-28
Document Changes
A - Issued for Internal Review
B - Issued for Tender
2024-08-05
2025-04-11
- Vendor data TBC highlighted or red text
- Vendor data TBC highlighted or red text
2024-08-22
- Vendor data TBC highlighted or red text

## 1. Analogue Input
KCGM GROWTH PROJECT
ANALOGUE INPUT
[5 empty] | Range |  |  | Process Switchpoints | [11 empty] | Alarms
Tag Source | Tag Name | P&ID | Abbreviated Description (Faceplate) | Trend (sec) | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Comments | Rev
TIT72480 | TI72480 | 2000-F72-PID-PR-10001 | F24PP406/7 Raw Water | 1 | -5 | 100 | °C | [12 empty] | 5 | 5 | 10 | 5 | [6 empty] | C
F72CALC10105 | FNI7240X | 2000-F72-PID-PR-10001 | F72MB411 Total Water | 1 | 0 | 200 | m3/h | [16 empty] | 96.5 | 5 | 105.4 | 5 |  | A A_ _H HH i = = A A lala rmrm | 1
LIT72401 | LI72401 | 2000-F72-PID-PR-10001 | F72SI411 Lime Silo 1 | 1 | 0 | 100 | % | [12 empty] | 5 | 5 | 10 | 5 | 89 | 5 | 98 | 5 |  |  | 1
PDT72404 | PDI72404 | 2000-F72-PID-PR-10001 | F72DC411 Filter DP | 1 | 0 | 500 | Pa | [14 empty] | 20 | 30 | 90 | 30 | 200 | 5 | If XV72419 AND XV72420 = Closed: OR XV72420 | A_HH = Close trip XV72419 and XV72420 | 1
PT72490 | PI72490 | 2000-F72-PID-PR-10001 | F72CY658 Cyclone | 1 | 0 | 200 | kPa | [12 empty] | 80 | 5 | 90 | 5 | 130 | 5 | 140 | 5 | 7 - S t |  | 1
SS-DUAL TIT72412 AND TIT72414 | TI72412 | 2000-F72-PID-PR-10001 | F72HP411 Temperature | 1 | 0 | 110 | °C | [21 empty] | SS-DUAL TIT72412 AND TIT72414 Hold PV on deviation and alarm Set deviation (DL) = 5°C (TBC during commissioning) | 1
F72CALC10106 | FNI7242X | 2000-F72-PID-PR-10002 | F72MB412 Total Water | 1 | 0 | 200 | m3/h | [16 empty] | 96.5 | 5 | 105.4 | 5 |  | A A_ _H HH i = = A A lala rmrm | 1
LIT72421 | LI72421 | 2000-F72-PID-PR-10002 | F72SI412 Lime Silo 2 | 1 | 0 | 100 | % | [12 empty] | 5 | 5 | 10 | 5 | 89 | 5 | 98 | 5 |  |  | 1
PDT72424 | PDI72424 | 2000-F72-PID-PR-10002 | F72DC412 Filter DP | 1 | 0 | 500 | Pa | [14 empty] | 20 | 30 | 90 | 30 | 200 | 5 | If XV72433 AND XV72434 = Closed: OR XV72434 | A_HH = Close trip XV72433 and XV72434 | 1
PT72491 | PI72491 | 2000-F72-PID-PR-10002 | F72CY659 Cyclone | 1 | 0 | 200 | kPa | [12 empty] | 80 | 5 | 90 | 5 | 130 | 5 | 140 | 5 | 7 - S t |  | 1
SS-DUAL TIT72432 AND TIT72416 | TI72432 | 2000-F72-PID-PR-10001 | F72HP412 Temperature | 1 | 0 | 110 | °C | [21 empty] | SS-DUAL TIT72432 AND TIT72416 Hold PV on deviation and alarm Set deviation (DL) = 5°C (TBC during commissioning) | 1
PT72451 | PI72451 | 2000-F72-PID-PR-10003 | F72PP656/7 MOL Rturn | 1 | 0 | 200 | kPa | [14 empty] | 30 | 5 | 120 | 5 |  |  | u g | TBC Ringmain design | 1
PIT72450 | PI72450 | 2000-F72-PID-PR-10003 | F72PP656/7 MOL Discharge | 1 | 0 | 1000 | kPa | [12 empty] | 250 | 5 | 300 | 5 | 680 | 5 | 700 | 5 | 7 - o 7 t | TBC Ringmain design | 0
LIT72461 | LI72461 | 2000-F72-PID-PR-10003 | F72PS419 Sump Level | 1 | 0 | 100 | % | 10 | 5 |  | 40 | 5 | [11 empty] | 70 | 5 |  |  |  |  | C
LIT72462 | LI72462 | 2000-F72-PID-PR-10003 | F72PS466 Sump Level | 1 | 0 | 100 | % | 10 | 5 |  | 40 | 5 | [11 empty] | 70 | 5 |  |  |  |  | C
LIT72463 | LI72463 | 2000-F72-PID-PR-10003 | F72PS467 Sump Level | 1 | 0 | 100 | % | 10 | 5 |  | 40 | 5 | [11 empty] | 70 | 5 |  |  |  |  | C
SS-DUAL LIT72531A AND LIT72531B | LI72531 | 2000-F72-PID-PR-10005 | F72TK437 Cyanide Level | 1 | 0 | 100 | % | [6 empty] | 90 | 5 |  |  |  |  | 10 | 5 | 25 | 5 | 90 | 5 | 95 | 5 |  | Dual redundancy level transmitters, LIT72531A & B Use lowest PV on deviation and alarm Set deviation (DL) = 5% (TBC during commissioning) | 2
SS-DUAL LIT72535A AND LIT72535B | LI72535 | 2000-F72-PID-PR-10005 | F72TK439 Cyanide Level | 1 | 0 | 100 | % | [6 empty] | 90 | 5 |  |  |  |  | 10 | 5 | 25 | 5 | 90 | 5 | 95 | 5 |  | Dual redundancy level transmitters, LIT72535A & B Use lowest on deviation and alarm Set deviation (DL) = 5% (TBC during commissioning) | 2
F72CALC10112 | LDI7253X | 2000-F72-PID-PR-10005 | F72TK437/9 Level Diff | 1 | 0 | 100 | % | [16 empty] | 3 | 5 | 6 | 5 |  | A A_ _H HH i = = A A lala rmrm HAZOP Action | C
PT72552 | PI72552 | 2000-F72-PID-PR-10005 | F72PP675/6 R/main Disch | 1 | 0 | 1000 | kPa | [14 empty] | 500 | 5 | 730 | 5 | 790 | 5 |  | Alarms & range estimated from Pipeflow calc. 100% recirc = 662kPag Nom supply = 626kPag | 1
PT72563 | PI72563 | 2000-F72-PID-PR-10005 | F72PP675/6 R/main Return | 1 | 0 | 600 | kPa | [14 empty] | 260 | 5 | 440 | 5 |  |  | u g a | Alarms & range estimated from Pipeflow calc. 100% recirc = 401kPag Nom supply = 308kPag | 1
LIT72581 | LI72581 | 2000-F72-PID-PR-10005 | F72PS423 Sump Level | 1 | 0 | 100 | % | 10 | 5 | [14 empty] | 90 | 5 |  |  |  | AP_ _L HL == AS lato rmp F72-PS-423 i | C
AIT72547 | AI72547 | 2000-F72-PID-PR-10005 | F72PP675/6 HCN Monitor | 1 | 0 | 30 | ppm | [21 empty] | Alarm via ASHH72547 | 0
AIT72548 | AI72548 | 2000-F72-PID-PR-10005 | F72TK437 HCN Monitor | 1 | 0 | 30 | ppm | [21 empty] | Alarm via ASHH72548 | 0
AIT72549 | AI72549 | 2000-F72-PID-PR-10005 | F72TK439 HCN Monitor | 1 | 0 | 30 | ppm | [21 empty] | Alarm via ASHH72549 | 0
TIT72592 | TI72592 | 2000-F72-PID-PR-10006 | F72TK434 Caustic Temp | 1 | -5 | 100 | °C |  |  |  | 25 | 5 |  | 35 | 5 |  |  |  |  | 16 | 5 | 20 | 5 | 44 | 5 | 47 | 5 |  | Low temperature alarms based on solubility of 50%w/w NaOH High temperature alarms based on Caustic Soda Service Graph at 50%w/w NaOH | 1
LIT72591 | LI72591 | 2000-F72-PID-PR-10006 | F72TK434 Caustic Level | 1 | 0 | 100 | % | [6 empty] | 70 | 5 |  |  |  |  | 10 | 5 | 25 | 5 | 90 | 5 | 95 | 5 |  | A _ L Lo = = A T la F 7 P 3 4 , 7 9 | 1
PIT72595 | PI72595 | 2000-F72-PID-PR-10006 | F72PP673/4 R/main Disch | 1 | 0 | 1000 | kPa | [14 empty] | 370 | 5 | 600 | 5 | 650 | 5 | u g 7 - o 4 t | Alarms & range estimated from Pipeflow calc. 100% recirc = 541kPag Nom supply = 465kPag | C
PT72597 | PI72597 | 2000-F72-PID-PR-10006 | F72PP673/4 R/main Return | 1 | 0 | 500 | kPa | [14 empty] | 180 | 5 | 280 | 5 |  |  | u g | Alarms & range estimated from Pipeflow calc. 100% recirc = 259kPag Nom supply = 215kPag | 1
TIT72598 | TI72598 | 2000-F72-PID-PR-10006 | F72PP673/4 R/main Return | 1 | -5 | 100 | °C | [12 empty] | 16 | 5 | 20 | 5 | 45 | 5 | 48 | 5 |  | Low temperature alarms based on solubility of 50%w/w NaOH High temperature alarms based on Caustic Soda Service Graph at 50%w/w NaOH | C
LIT72599 | LI72599 | 2000-F72-PID-PR-10006 | F72PS424 Sump Level | 1 | 0 | 100 | % | 10 | 5 | [14 empty] | 90 | 5 |  |  |  | A P__LH Li = A Sla torm = p F72-PS-424 | C
LIT72602 | LI72602 | 2000-F72-PID-PR-10007 | F72TK435 Acid Storage | 1 | 0 | 100 | % | [6 empty] | 60 | 5 |  |  |  |  | 10 | 5 | 25 | 5 | 90 | 5 | 95 | 5 |  |  | 2
LIT72612 | LI72612 | 2000-F72-PID-PR-10007 | F72TK424 Acid Dilution | 1 | 0 | 100 | % |  |  |  | Set as per F72CALC 10104 | 0 |  | 80 | 0 |  |  |  |  | 10 | 5 | 15 | 5 | 85 | 5 | 90 | 5 |  | Ensure 100% level = at bottom of overflow (3250mm RL) Ensure 0% level = at suction (150mm RL) | 1
FIT72610 | FI72610 | 2000-F72-PID-PR-10007 | F72PP683/4 Acid Dosing | 1 | 0 | 40 | m3/h | [12 empty] | 12 | 5 | 16 | 5 |  |  |  |  | g 7 - 6 | Alarms based on nominal of 23m3/h | C
PT72611 | PI72611 | 2000-F72-PID-PR-10007 | F72PP683/4 Acid Dosing | 1 | 0 | 500 | kPa | [14 empty] | 280 | 5 | 400 | 5 | 410 | 5 | g 7 - 6 | 2000-ME060B-F09-10006 | 1
PT72638 | PI72638 | 2000-F72-PID-PR-10007 | F72PP424 Discharge | 1 | 0 | 500 | kPa | [14 empty] | 200 | 5 | 400 | 5 | 460 | 5 |  | Pump Curve: 2000-ME060B-F09-10012 | 1
FIT72616 | FI72616 | 2000-F72-PID-PR-10007 | F72PP424 Acid Dilution | 1 | 0 | 150 | m3/h | [6 empty] | 0.1 | 5 | [13 empty] | f is c A 6 | 1
LIT72615 | LI72615 | 2000-F72-PID-PR-10007 | F72PS428 Sump Level | 1 | 0 | 100 | % | 10 | 5 | [14 empty] | 90 | 5 |  |  |  | A P__LH Li = A Sla torm = p F72-PS-428 | C
LIT72701 | LI72701 | 2000-F72-PID-PR-10015 | F72TK438 Nitrate Tank | 1 | 0 | 100 | % | [6 empty] | 75 | 5 |  |  |  |  | 10 | 5 | 25 | 5 | 90 | 5 | 95 | 5 |  |  | 1
LIT72741 | LI72741 | 2000-F72-PID-PR-10015 | F72PS426 Sump Level | 1 | 0 | 100 | % | 10 | 5 | [14 empty] | 90 | 5 |  |  |  | A P__LH Li = A Sla torm = p F72-PS-426 | C
PIT72731 | PI72731 | 2000-F72-PID-PR-10015 | F72PP681/682 Disch Press | 1 | 0 | 700 | kPa | [16 empty] | 550 | 5 | 580 | 5 |  | A_HH set below 600kPa PSV | C
LIT72689 | LI72689 | 2000-F72-PID-PR-10012 | F72PK406 IBC Skid 1 | 1 | 0 | 100 | % | [12 empty] | 10 | 5 | 25 | 5 | 90 | 5 |  |  |  |  | C
LIT72690 | LI72690 | 2000-F72-PID-PR-10012 | F72PK407 IBC Skid 2 | 1 | 0 | 100 | % | [12 empty] | 10 | 5 | 25 | 5 | 90 | 5 |  |  |  |  | C
LIT72691 | LI72691 | 2000-F72-PID-PR-10012 | F72PK408 IBC Skid 3 | 1 | 0 | 100 | % | [12 empty] | 10 | 5 | 25 | 5 | 90 | 5 |  |  |  |  | C
LIT72692 | LI72692 | 2000-F72-PID-PR-10012 | F72PK409 IBC Skid 4 | 1 | 0 | 100 | % | [12 empty] | 10 | 5 | 25 | 5 | 90 | 5 |  |  |  |  | C
UT72035 | TI72035 | - | F72SR001 Temperature | 1 | -5 | 100 | °C | [16 empty] | 30 | 60 |  |  |  |  | 0
UT72036 | XI72036 | - | F72SR001 Humidity | 1 | 0 | 100 | %RH | [22 empty] | C
ZT72407 | ZI72407 | 2000-F72-PID-PR-10001 | FCV72407 Position | 1 | 0 | 100 | % | [21 empty] | Refer to FCV72407 (Control Valves tab) | 1
ZT72408 | ZI72408 | 2000-F72-PID-PR-10001 | FCV72408 Position | 1 | 0 | 100 | % | [21 empty] | Refer to FCV72408 (Control Valves tab) | 1
ZT72427 | ZI72427 | 2000-F72-PID-PR-10002 | FCV72427 Position | 1 | 0 | 100 | % | [21 empty] | Refer to FCV72427 (Control Valves tab) | 1
ZT72428 | ZI72428 | 2000-F72-PID-PR-10002 | FCV72428 Position | 1 | 0 | 100 | % | [21 empty] | Refer to FCV72428 (Control Valves tab) | 1
TIT72633 | TI72633 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Feed | 1 | -5 | 100 | °C | [14 empty] | 5 | 5 | 55 | 5 |  |  |  |  | 1
PIT72634 | PI72634 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Feed | 1 | 0 | 1200 | kPa | [14 empty] | 160 | 5 | 360 | 5 | 990 | 5 |  |  | 1
TIT72635 | TI72635 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Rturn | 1 | -5 | 100 | °C | [14 empty] | 5 | 5 | 55 | 5 |  |  |  |  | 1
PIT72636 | PI72636 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Rturn | 1 | 0 | 1200 | kPa | [14 empty] | 100 | 5 | 275 | 5 | 990 | 5 |  |  | 1
FI72619S | FI72619 | 2000-F72-PID-PR-10011 | F72PK405 VPSA Flow | 1 | 0 | 3200 | m3/h | [21 empty] | SoftTag from F72-PK-405 | 1
PI72620S | PI72620 | 2000-F72-PID-PR-10011 | F72PK405 VPSA Pressure | 1 | 0 | 1000 | kPa | [21 empty] | SoftTag from F72-PK-405 | 1
TI72621S | TI72621 | 2000-F72-PID-PR-10011 | F72PK405 VPSA Temp | 1 | -200 | 300 | °C | [21 empty] | SoftTag from F72-PK-405 | 1
AI72622S | AI72622 | 2000-F72-PID-PR-10011 | F72PK405 Purity | 1 | 0 | 100 | % | [21 empty] | SoftTag from F72-PK-405 | 1
PI72623S | PI72623 | 2000-F72-PID-PR-10011 | F72PK405 Delivery | 1 | 0 | 1400 | kPa | [21 empty] | SoftTag from F72-PK-405 | 1
TI72624S | TI72624 | 2000-F72-PID-PR-10011 | F72PK405 DRIOX Temp | 1 | -200 | 300 | °C | [21 empty] | SoftTag from F72-PK-405 | 1
JI72625S | JI72625 | 2000-F72-PID-PR-10011 | F72PK405 VPSA Power | 1 | 0 | 3000 | kW | [21 empty] | SoftTag from F72-PK-405 | 1
LI72626S | LI72626 | 2000-F72-PID-PR-10011 | F72PK405 Tank TC1640 | 1 | 0 | 100 | % | [21 empty] | SoftTag from F72-PK-405 | 1
LI72627S | LI72627 | 2000-F72-PID-PR-10011 | F72PK405 Tank TC2640 | 1 | 0 | 100 | % | [21 empty] | SoftTag from F72-PK-405 | 1
FI72628S | FI72628 | 2000-F72-PID-PR-10011 | F72PK405 LOX Flow | 1 | 0 | 3200 | m3/h | [21 empty] | SoftTag from F72-PK-405 | 1
F72CALC10115 | WI72401 | 2000-F72-PID-PR-10001 | F72SI411 Lime Weight | 1 | 0 | 1500 | t | [22 empty] | 2
F72CALC10116 | WI72421 | 2000-F72-PID-PR-10002 | F72SI412 Lime Weight | 1 | 0 | 1500 | t | [22 empty] | 2
F72CALC10117 | WI72602 | 2000-F72-PID-PR-10007 | F72TK435 HCl Weight | 1 | 0 | 300 | t | [22 empty] | 2
F72CALC10118 | WI72591 | 2000-F72-PID-PR-10006 | F72TK435 NaOH Weight | 1 | 0 | 500 | t | [22 empty] | 2
F72CALC10119 | WI72701 | 2000-F72-PID-PR-10015 | F72TK438 Nitrate Weight | 1 | 0 | 500 | t | [22 empty] | 2
F72CALC10120 | WI72531 | 2000-F72-PID-PR-10005 | F72TK437 Cyanide Weight | 1 | 0 | 2000 | t | [22 empty] | 2
F72CALC10121 | WI72535 | 2000-F72-PID-PR-10005 | F72TK439 Cyanide Weight | 1 | 0 | 2000 | t | [22 empty] | 2

## 2. Analogue Output
KCGM GROWTH PROJECT
ANALOGUE OUTPUT
Range
Tag Source | Tag Name | P&ID | Abbreviated Description (Faceplate) | Trend (sec) | Min | Max | Unit | Comments | Rev
LY72401 | LI72401REM | 2000-F72-PID-PR-10001 | F72SI411 Lime Silo 1 | 1 | 0 | 100 | % | Write from LI27401 value. Force remote display to show 100% to indicate abnormal situation. | 2
LY72421 | LI72421REM | 2000-F72-PID-PR-10002 | F72SI412 Lime Silo 2 | 1 | 0 | 100 | % | Write from LI27421 value. Force remote display to show 100% to indicate abnormal situation. | 2
LY72531 | LI72531REM | 2000-F72-PID-PR-10005 | F72TK437 Cyanide Level | 1 | 0 | 100 | % | Write from LI72531 value. Force remote display to show 100% to indicate abnormal situation. | 2
LY72535 | LI72535REM | 2000-F72-PID-PR-10005 | F72TK439 Cyanide Level | 1 | 0 | 100 | % | Write from LI72535 value. Force remote display to show 100% to indicate abnormal situation. | 2
LY72591 | LI72591REM | 2000-F72-PID-PR-10006 | F72TK434 Caustic Level | 1 | 0 | 100 | % | Write from LI72591 value. Force remote display to show 100% to indicate abnormal situation. | 2
LY72602 | LI72602REM | 2000-F72-PID-PR-10007 | F72TK435 Acid Level | 1 | 0 | 100 | % | Write from LI72602 value. Force remote display to show 100% to indicate abnormal situation. | 2
LY72701 | LI72701REM | 2000-F72-PID-PR-10015 | F72TK438 Nitrate Level | 1 | 0 | 100 | % | Write from LI72701 value. Force remote display to show 100% to indicate abnormal situation. | 2
FY72693 | FC72693 | 2000-F72-PID-PR-10012 | F72PP698 Flowrate | 1 | 0 | 450 | L/min | Hardwired flowrate input for F72-PP-698 4.1mA = 0L/min 19.8mA = 450L/min Ref SMART Digital S - DDA IOM (Model DDA 7.5-16) | C
FY72694 | FC72694 | 2000-F72-PID-PR-10012 | F72PP699 Flowrate | 1 | 0 | 450 | L/min | Hardwired flowrate input for F72-PP-699 4.1mA = 0L/min 19.8mA = 450L/min Ref SMART Digital S - DDA IOM (Model DDA 7.5-16) | C
FY72695 | FC72695 | 2000-F72-PID-PR-10012 | F72PP700 Flowrate | 1 | 0 | 450 | L/min | Hardwired flowrate input for F72-PP-700 4.1mA = 0L/min 19.8mA = 450L/min Ref SMART Digital S - DDA IOM (Model DDA 7.5-16) | C
FY72696 | FC72696 | 2000-F72-PID-PR-10012 | F72PP701 Flowrate | 1 | 0 | 450 | L/min | Hardwired flowrate input for F72-PP-701 4.1mA = 0L/min 19.8mA = 450L/min Ref SMART Digital S - DDA IOM (Model DDA 7.5-16) | C
FY72697 | FC72697 | 2000-F72-PID-PR-10012 | F72PP702 Flowrate | 1 | 0 | 450 | L/min | Hardwired flowrate input for F72-PP-702 4.1mA = 0L/min 19.8mA = 450L/min Ref SMART Digital S - DDA IOM (Model DDA 7.5-16) | C
FY72698 | FC72698 | 2000-F72-PID-PR-10012 | F72PP703 Flowrate | 1 | 0 | 450 | L/min | Hardwired flowrate input for F72-PP-703 4.1mA = 0L/min 19.8mA = 450L/min Ref SMART Digital S - DDA IOM (Model DDA 7.5-16) | C
FY72699 | FC72699 | 2000-F72-PID-PR-10012 | F72PP704 Flowrate | 1 | 0 | 450 | L/min | Hardwired flowrate input for F72-PP-704 4.1mA = 0L/min 19.8mA = 450L/min Ref SMART Digital S - DDA IOM (Model DDA 7.5-16) | C
FY72700 | FC72700 | 2000-F72-PID-PR-10012 | F72PP705 Flowrate | 1 | 0 | 450 | L/min | Hardwired flowrate input for F72-PP-705 4.1mA = 0L/min 19.8mA = 450L/min Ref SMART Digital S - DDA IOM (Model DDA 7.5-16) | C

## 3. Digital Input
KCGM GROWTH PROJECT
DIGITAL INPUT
DIGITAL INPUTS
Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Source | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev
LSL72437 | LAL72437 | 2000-F72-PID-PR-10001 | F72-SI-411 Lime Silo 1 Switch Level Low | F72SI411 Lime Silo 1 | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
LSH72505 | LAH72505 | 2000-F72-PID-PR-10001 | F72-SI-411 Lime Silo 1 Switch Level High | F72SI411 Lime Silo 1 | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
SSL72438 | SAL72438 | 2000-F72-PID-PR-10001 | F72-VR-411 Lime Silo 1 Rotary Valve Speed Switch Low | F72VR411 Underspeed | Inactive | Active | Alarm (see comment) | Hardwired to DCS | 0 | 1. F72-VR-411 Not running 2. Mask for 30 seconds on F72-VR- 411 start | Speed monitoring from DCS (signal active per rotation). Calculate RPM 10 seconds rolling Logic: If calculated RPM <= F72VR411 US then activate _ alarm. See F72CALC10113 for F72VR411 US. _ Alarm masking duration to be confirmed during commissioning. | 1
SSL72403 | SAL72403 | 2000-F72-PID-PR-10001 | F72-FS-411 Lime Silo 1 Screw Feeder Speed Switch Low | F72FS411 Underspeed | Inactive | Active | Alarm (see comment) | Hardwired to DCS | 0 | 1. F72-FS-411 Not running 2. Mask for 30 seconds on F72-FS- 411 start | Speed monitoring from DCS (signal active per rotation). Calculate RPM 10 seconds rolling Logic: If calculated RPM <= 21.10 RPM then activate alarm. Alarm masking duration to be confirmed during commissioning. | 1
LSH72405 | LAH72405 | 2000-F72-PID-PR-10001 | F72-XM-658 Lime Slaker Vortex Prewetter Level Switch | F72XM658 Prewetter | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
LSL72456 | LAL72456 | 2000-F72-PID-PR-10001 | F72-MB-411 Lime Slaking Mill 1 Grease Unit Level Switch Low | F72MB411 Grease Lo | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
ZS72455 | ZA72455 | 2000-F72-PID-PR-10001 | F72-MB-411 Lime Slaking Mill 1 Grease Unit Pump Switch | F72MB411 Grease Pulse | Inactive | Active |  | Hardwired to DCS |  |  |  | 1
ZS72454A | ZA72454A | 2000-F72-PID-PR-10001 | F72-MB-411 Lime Slaking Mill 1 Vertical Position Switch 1 | F72MB411 Vertical Posn A | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 0
ZS72454B | ZA72454B | 2000-F72-PID-PR-10001 | F72-MB-411 Lime Slaking Mill 1 Vertical Position Switch 2 | F72MB411 Vertical Posn B | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 0
ZS72507A | ZA72507A | 2000-F72-PID-PR-10001 | F72-MB-411 Lime Slaking Mill 1 Horizontal Position Switch 1 | F72MB411 Horizntal Pos A | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 0
ZS72507B | ZA72507B | 2000-F72-PID-PR-10001 | F72-MB-411 Lime Slaking Mill 1 Horizontal Position Switch 2 | F72MB411 Horizntal Pos B | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 0
HS72498A | HS72498AOP | 2000-F72-PID-PR-10001 | F72-SI-411 Lime Silo 1 Fill Valve 1 LCP Open Pushbutton | F72SI411 Fill Vlv 1 Open | Inactive | Open |  | Hardwired to DCS |  |  | If HS72498AOP = Open: Set XV72419 to AUT Open XV72419 | C
HS72498B | HS72498BCL | 2000-F72-PID-PR-10001 | F72-SI-411 Lime Silo 1 Fill Valve 1 LCP Close Pushbutton | F72SI411 Fill Vlv 1 Clse | Inactive | Close |  | Hardwired to DCS |  |  | If HS72498ACL = Close: Set XV72419 to AUT Close XV72419 | C
HS72501A | HS72501AOP | 2000-F72-PID-PR-10001 | F72-SI-411 Lime Silo 1 Fill Valve 2 LCP Open Pushbutton | F72SI411 Fill Vlv 2 Open | Inactive | Open |  | Hardwired to DCS |  |  | If HS72501AOP = Open: Set XV72420 to AUT Open XV72420 | C
HS72501B | HS72501BCL | 2000-F72-PID-PR-10001 | F72-SI-411 Lime Silo 1 Fill Valve 2 LCP Close Pushbutton | F72SI411 Fill Vlv 2 Clse | Inactive | Close |  | Hardwired to DCS |  |  | If HS72501ACL = Close: Set XV72420 to AUT Close XV72420 | C
FSL72504 | FAL72504 | 2000-F72-PID-PR-10001 | F72-MB-411 Lime Slaking Mill 1 Trommel Spray Flow Switch | F72MB411 Trommel Spray | Normal | Alarm | Alarm | Hardwired to DCS | 3 | FCV72408 < 3% Open |  | C
FSL72506 | FAL72506 | 2000-F72-PID-PR-10001 | F72-WS-411 Slaked Lime Wet Scrubber 1 Feed Water | F72WS411 Feed Water | Normal | Alarm | Alarm | Hardwired to DCS | 3 | XV72457 = Closed |  | C
LSL72435 | LAL72435 | 2000-F72-PID-PR-10002 | F72-SI-412 Lime Silo 2 Switch Level Low | F72SI412 Lime Silo 2 | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
LSH72517 | LAH72517 | 2000-F72-PID-PR-10002 | F72-SI-412 Lime Silo 2 Switch Level High | F72SI412 Lime Silo 2 | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
SSL72436 | SAL72436 | 2000-F72-PID-PR-10002 | F72-VR-412 Lime Silo 2 Rotary Valve Speed Switch Low | F72VR412 Underspeed | Inactive | Active | Alarm (see comment) | Hardwired to DCS | 0 | 1. F72-VR-412 Not running 2. Mask for 30 seconds on F72-VR- 412 start | Speed monitoring from DCS (signal active per rotation). Calculate RPM 10 seconds rolling Logic: If calculated RPM <= F72VR412 US then activate _ alarm. See F72CALC10114 for F72VR412 US. _ Alarm masking duration to be confirmed during commissioning. | 1
SSL72423 | SAL72423 | 2000-F72-PID-PR-10002 | F72-FS-412 Lime Silo 2 Screw Feeder Speed Switch Low | F72FS412 Underspeed | Inactive | Active | Alarm (see comment) | Hardwired to DCS | 0 | 1. F72-FS-412 Not running 2. Mask for 30 seconds on F72-FS- 412 start | Speed monitoring from DCS (signal active per rotation). Calculate RPM 10 seconds rolling Logic: If calculated RPM <= 21.10 RPM then activate alarm. Alarm masking duration to be confirmed during commissioning. | 1
LSH72425 | LAH72425 | 2000-F72-PID-PR-10002 | F72-XM-659 Lime Slaker Vortex Prewetter 2 Level Switch | F72XM659 Prewetter | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
LSL72479 | LAL72479 | 2000-F72-PID-PR-10002 | Lime Slaking Mill 2 Grease Unit Level Switch Low | F72MB412 Grease Lo | Active | Normal | Active | Hardwired to DCS | 3 |  |  | C
ZS72477 | ZA72477 | 2000-F72-PID-PR-10002 | F72-MB-412 Lime Slaking Mill 2 Grease Unit Pump Switch | F72MB412 Grease Pulse | Inactive | Active |  | Hardwired to DCS |  |  |  | 1
ZS72478A | ZA72478A | 2000-F72-PID-PR-10002 | F72-MB-412 Lime Slaking Mill 1 Vertical Position Switch 1 | F72MB412 Vertical Posn A | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 0
ZS72478B | ZA72478B | 2000-F72-PID-PR-10002 | F72-MB-412 Lime Slaking Mill 1 Vertical Position Switch 2 | F72MB412 Vertical Posn B | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 0
ZS72519A | ZA72519A | 2000-F72-PID-PR-10002 | F72-MB-412 Lime Slaking Mill 1 Horizontal Position Switch 1 | F72MB412 Horizntal Pos A | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 0
ZS72519B | ZA72519B | 2000-F72-PID-PR-10002 | F72-MB-412 Lime Slaking Mill 1 Horizontal Position Switch 2 | F72MB412 Horizntal Pos B | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 0
HS72513A | HS72513AOP | 2000-F72-PID-PR-10002 | F72-SI-412 Lime Silo 2 Fill Valve 1 LCP Open Pushbutton | F72SI412 Fill Vlv 1 Open | Inactive | Open |  | Hardwired to DCS |  |  | If HS72513AOP = Open: Set XV72433 to AUT Open XV72433 | C
HS72513B | HS72513BCL | 2000-F72-PID-PR-10002 | F72-SI-412 Lime Silo 2 Fill Valve 1 LCP Close Pushbutton | F72SI412 Fill Vlv 1 Clse | Inactive | Close |  | Hardwired to DCS |  |  | If HS72513ACL = Close: Set XV72433 to AUT Close XV72433 | C
HS72510A | HS72510AOP | 2000-F72-PID-PR-10002 | F72-SI-412 Lime Silo 2 Fill Valve 2 LCP Open Pushbutton | F72SI412 Fill Vlv 2 Open | Inactive | Open |  | Hardwired to DCS |  |  | If HS72510AOP = Open: Set XV72434 to AUT Open XV72434 | C
HS72510B | HS72510BCL | 2000-F72-PID-PR-10002 | F72-SI-412 Lime Silo 2 Fill Valve 2 LCP Close Pushbutton | F72SI412 Fill Vlv 2 Clse | Inactive | Close |  | Hardwired to DCS |  |  | If HS72510ACL = Close: Set XV72434 to AUT Close XV72434 | C
FSL72516 | FAL72516 | 2000-F72-PID-PR-10002 | F72-MB-412 Lime Slaking Mill 2 Trommel Spray Flow Switch | F72MB412 Trommel Spray | Normal | Alarm | Alarm | Hardwired to DCS | 3 | FCV72428 < 3% Open |  | C
FSL72518 | FAL72518 | 2000-F72-PID-PR-10002 | F72-WS-412 Slaked Lime Wet Scrubber 2 Feed Water | F72WS412 Feed Water | Normal | Alarm | Alarm | Hardwired to DCS | 3 | XV72473 = Closed |  | C
ZSO72409 | ZIO72409 | 2000-F72-PID-PR-10001 | F72-XM-660 Lime Slaking Mill Ball Kibble Loading Hopper Transfer Valve 1 Open Position Switch | F72XM660 Transfer 1 Open | N Open _ | Open |  | Hardwired to DCS |  |  | See XV72409 | 0
ZSC72409 | ZIC72409 | 2000-F72-PID-PR-10001 | F72-XM-660 Lime Slaking Mill Ball Kibble Loading Hopper Transfer Valve 1 Close Position Switch | F72XM660 Trnsfer 1 Close | N Closed _ | Closed |  | Hardwired to DCS |  |  | See XV72409 | 0
ZSO72410 | ZIO72410 | 2000-F72-PID-PR-10001 | F72-XM-660 Lime Slaking Mill Ball Kibble Loading Hopper Transfer Valve 2 Open Position Switch | F72XM660 Transfer 2 Open | N Open _ | Open |  | Hardwired to DCS |  |  | See XV72410 | 0
ZSC72410 | ZIC72410 | 2000-F72-PID-PR-10001 | F72-XM-660 Lime Slaking Mill Ball Kibble Loading Hopper Transfer Valve 2 Close Position Switch | F72XM660 Trnsfer 2 Close | N Closed _ | Closed |  | Hardwired to DCS |  |  | See XV72410 | 0
ASHH72547 | AAHH72547 | 2000-F72-PID-PR-10005 | F72-PP-675/676 Cyanide Ringmain Pump 1/2 Hydrogen Cyanide Gas Detection Monitor | F72PP675/6 HCN Monitor | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Logic: Include 10 minute off delay on AAH72547 | C
ASHH72548 | AAHH72548 | 2000-F72-PID-PR-10005 | F72-TK-437 Cyanide Storage Tank 1 Unloading Platform Hydrogen Cyanide Gas Detection Monitor | F72TK437 HCN Monitor | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Logic: Include 10 minute off delay on AAH72548 | C
ASHH72549 | AAHH72549 | 2000-F72-PID-PR-10005 | F72-TK-439 Cyanide Storage Tank 2 Unloading Platform Hydrogen Cyanide Gas Detection Monitor | F72TK439 HCN Monitor | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Logic: Include 10 minute off delay on AAH72549 | C
HS72618A | HS72618ASTT | 2000-F72-PID-PR-10007 | F72-PS-428 Hydrochloric Acid Area Sump Pump LCS Start Push Button | F72PS428 Start | Inactive | Start |  | Hardwired to DCS |  |  | If HS72168A = Active (rising edge): Open SV72617 Local push button | C
HS72618B | HS72618BSTP | 2000-F72-PID-PR-10007 | F72-PS-428 Hydrochloric Acid Area Sump Pump LCS Stop Push Button | F72PS428 Stop | Inactive | Stop |  | Hardwired to DCS |  |  | If HS72168B = Active (rising edge): Close SV72617 Local push button | C
TSH72733 | TAH72733 | 2000-F72-PID-PR-10015 | F72-PP-681 Lead Nitrate Dosing Pump 1 Stator Temperature Switch | F72PP681 Stator Temp | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | C
TSH72734 | TAH72734 | 2000-F72-PID-PR-10015 | F72-PP-682 Lead Nitrate Dosing Pump 2 Stator Temperature Switch | F72PP682 Stator Temp | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | C
HS72713A | HS72713ASTT | 2000-F72-PID-PR-10015 | F72-PS-426 Lead Nitrate Area Sump Pump LCS Start Push Button | F72PS426 Start | Inactive | Start |  | Hardwired to DCS |  |  | If HS72713A = Active (rising edge): Open SV72712 Local push button | C
HS72713B | HS72713BSTP | 2000-F72-PID-PR-10015 | F72-PS-426 Lead Nitrate Area Sump Pump LCS Stop Push Button | F72PS426 Stop | Inactive | Stop |  | Hardwired to DCS |  |  | If HS72713B = Active (rising edge): Close SV72712 Local push button | C
FSL72681 | FAL72681 | 2000-72-PID-PR-10012 | F72-PP-698 Antiscalant Dosing Pump Flow Switch Low | F72PP698 Flow Lo | Normal | Alarm | Alarm | Hardwired to DCS | 3 | 1. F72-PP-698 Not Running 2. Mask for 10 seconds on F72-PP- 698 start up |  | C
XS72693A | XA72693 | 2000-F72-PID-PR-10012 | F72-PP-698 Antiscalant Dosing Pump 2 Alarm | F72PP698 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
XS72693B | XI72693 | 2000-F72-PID-PR-10012 | F72-PP-698 Antiscalant Dosing Pump 2 Running Status | F72PP698 Running | Inactive | Running |  | Hardwired to DCS |  |  |  | 0
FSL72682 | FAL72682 | 2000-72-PID-PR-10012 | F72-PP-699 Antiscalant Dosing Pump Flow Switch Low | F72PP699 Flow Lo | Normal | Alarm | Alarm | Hardwired to DCS | 3 | 1. F72-PP-699 Not Running 2. Mask for 10 seconds on F72-PP- 699 start up |  | C
XS72694A | XA72694 | 2000-F72-PID-PR-10012 | F72-PP-699 Antiscalant Dosing Pump 3 Alarm | F72PP699 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
XS72694B | XI72694 | 2000-F72-PID-PR-10012 | F72-PP-699 Antiscalant Dosing Pump 3 Running Status | F72PP699 Running | Inactive | Running |  | Hardwired to DCS |  |  |  | 0
FSL72683 | FAL72683 | 2000-72-PID-PR-10012 | F72-PP-700 Antiscalant Dosing Pump Flow Switch Low | F72PP700 Flow Lo | Normal | Alarm | Alarm | Hardwired to DCS | 3 | 1. F72-PP-700 Not Running 2. Mask for 10 seconds on F72-PP- 700 start up |  | C
XS72695A | XA72695 | 2000-F72-PID-PR-10012 | F72-PP-700 Antiscalant Dosing Pump 4 Alarm | F72PP700 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
XS72695B | XI72695 | 2000-F72-PID-PR-10012 | F72-PP-700 Antiscalant Dosing Pump 4 Running Status | F72PP700 Running | Inactive | Running |  | Hardwired to DCS |  |  |  | 0
FSL72684 | FAL72684 | 2000-72-PID-PR-10012 | F72-PP-701 Antiscalant Dosing Pump Flow Switch Low | F72PP701 Flow Lo | Normal | Alarm | Alarm | Hardwired to DCS | 3 | 1. F72-PP-701 Not Running 2. Mask for 10 seconds on F72-PP- 701 start up |  | C
XS72696A | XA72696 | 2000-F72-PID-PR-10012 | F72-PP-701 Antiscalant Dosing Pump 5 Alarm | F72PP701 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
XS72696B | XI72696 | 2000-F72-PID-PR-10012 | F72-PP-701 Antiscalant Dosing Pump 5 Running Status | F72PP701 Running | Inactive | Running |  | Hardwired to DCS |  |  |  | 0
FSL72685 | FAL72685 | 2000-72-PID-PR-10012 | F72-PP-702 Antiscalant Dosing Pump Flow Switch Low | F72PP702 Flow Lo | Normal | Alarm | Alarm | Hardwired to DCS | 3 | 1. F72-PP-702 Not Running 2. Mask for 10 seconds on F72-PP- 702 start up |  | C
XS72697A | XA72697 | 2000-F72-PID-PR-10012 | F72-PP-702 Antiscalant Dosing Pump 6 Alarm | F72PP702 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
XS72697B | XI72697 | 2000-F72-PID-PR-10012 | F72-PP-702 Antiscalant Dosing Pump 6 Running Status | F72PP702 Running | Inactive | Running |  | Hardwired to DCS |  |  |  | 0
FSL72686 | FAL72686 | 2000-72-PID-PR-10012 | F72-PP-703 Antiscalant Dosing Pump Flow Switch Low | F72PP703 Flow Lo | Normal | Alarm | Alarm | Hardwired to DCS | 3 | 1. F72-PP-703 Not Running 2. Mask for 10 seconds on F72-PP- 703 start up |  | C
XS72698A | XA72698 | 2000-F72-PID-PR-10012 | F72-PP-703 Antiscalant Dosing Pump 7 Alarm | F72PP703 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
XS72698B | XI72698 | 2000-F72-PID-PR-10012 | F72-PP-703 Antiscalant Dosing Pump 7 Running Status | F72PP703 Running | Inactive | Running |  | Hardwired to DCS |  |  |  | 0
FSL72687 | FAL72687 | 2000-72-PID-PR-10012 | F72-PP-704 Antiscalant Dosing Pump Flow Switch Low | F72PP704 Flow Lo | Normal | Alarm | Alarm | Hardwired to DCS | 3 | 1. F72-PP-704 Not Running 2. Mask for 10 seconds on F72-PP- 704 start up |  | C
XS72699A | XA72699 | 2000-F72-PID-PR-10012 | F72-PP-704 Antiscalant Dosing Pump 7 Alarm | F72PP704 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
XS72699B | XI72699 | 2000-F72-PID-PR-10012 | F72-PP-704 Antiscalant Dosing Pump 7 Running Status | F72PP704 Running | Inactive | Running |  | Hardwired to DCS |  |  |  | 0
FSL72688 | FAL72688 | 2000-72-PID-PR-10012 | F72-PP-705 Antiscalant Dosing Pump Flow Switch Low | F72PP705 Flow Lo | Normal | Alarm | Alarm | Hardwired to DCS | 3 | 1. F72-PP-705 Not Running 2. Mask for 10 seconds on F72-PP- 705 start up |  | C
XS72700A | XA72700 | 2000-F72-PID-PR-10012 | F72-PP-705 Antiscalant Dosing Pump 8 Alarm | F72PP705 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
XS72700B | XI72700 | 2000-F72-PID-PR-10012 | F72-PP-705 Antiscalant Dosing Pump 8 Running Status | F72PP705 Running | Inactive | Running |  | Hardwired to DCS |  |  |  | 0
TSH72484 | TAH72484 | 2000-F72-PID-PR-10016 | F72-PP-693 Concentrate Pre-Leach Thickener Flocculant Dosing Pump Stator Temperature | F72PP693 Stator Temp | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
TSH72485 | TAH72485 | 2000-F72-PID-PR-10016 | F72-PP-696 Thickeners Standby Flocculant Dosing Pump Stator Temperature | F72PP696 Stator Temp | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
TSH72486 | TAH72486 | 2000-F72-PID-PR-10016 | F72-PP-694 Concentrate Thickener Flocculant Dosing Pump Stator Temperature | F72PP694 Stator Temp | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | C
FSL72493 | FAL72493 | 2000-F72-PID-PR-10001 | F72-PP-658 Slaked Lime Transfer Pump Gland Water Flow Switch Low | F72PP658 Gland Water | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F72-PP-658 Not Running 2. Mask for 10 seconds on F72-PP- 658 start up |  | C
FSL72496 | FAL72496 | 2000-F72-PID-PR-10002 | F72-PP-659 Slaked Lime Transfer Pump Gland Water Flow Switch Low | F72PP659 Gland Water | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F72-PP-659 Not Running 2. Mask for 10 seconds on F72-PP- 659 start up |  | C
FSL72471 | FAL72471 | 2000-F72-PID-PR-10003 | F72-PP-656 Lime Ringmain Pump 1 Gland Water Flow Switch Low | F72PP656 Gland Water | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F72-PP-656 Not Running 2. Mask for 10 seconds on F72-PP- 656 start up |  | C
FSL72475 | FAL72475 | 2000-F72-PID-PR-10003 | F72-PP-657 Lime Ringmain Pump 2 Gland Water Flow Switch Low | F72PP657 Gland Water | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F72-PP-657 Not Running 2. Mask for 10 seconds on F72-PP- 657 start up |  | C
F72DCS413PS1 | F72DCS413 PS1 _ | - | F72-DCS-413 PS1 24VDC Healthy | F72DCS413 PS1 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72DCS413PS2 | F72DCS413 PS2 _ | - | F72-DCS-413 PS2 24VDC Healthy | F72DCS413 PS2 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72SW072PS | F72SW072 PS _ | - | F72-SW-072 ACB Shunt Trip 24VDC OK | F72SW072 ACBShunt 24V OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2
F72SW072AF | F72SW072 AF _ | - | F72-SW-072 Arc Flash Detection System Fault | F72SW072 Arc Flash Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72SW072OP | F72SW072 OP _ | - | F72-SW-072 Circuit Breaker Opened | F72SW072 CB Open | Inactive | Active |  | Hardwired to DCS |  |  |  | C
F72SW072CL | F72SW072 CL _ | - | F72-SW-072 Circuit Breaker Closed | F72SW072 CB Closed | Inactive | Active |  | Hardwired to DCS |  |  |  | C
F72SW072TRP | F72SW072 TRP _ | - | F72-SW-072 Circuit Breaker Tripped | F72SW072 CB Tripped | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72SW072SD | F72SW072 SD _ | - | F72-SW-072 Incomer Surge Diverter Ok | F72SW072 IncSurge Div OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72SR001ESTP | F72SR001 ESTP _ | - | F72-SR-001 Switchroom Emergency Shutdown Dcs Input | F72SR001 E Stop | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72SW072PS1 | F72SW072 PS1 _ | - | F72-SW-072 PS1 24VDC Healthy | F72SW072 PS1 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72SW072PS2 | F72SW072 PS2 _ | - | F72-SW-072 PS2 24VDC Healthy | F72SW072 PS2 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72FIP001ALM | F72FIP001 ALM _ | - | F72-FIP-001 Alarm | F72FIP001 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72FIP001ISL | F72FIP001 ISL _ | - | F72-FIP-001 Isolated | F72FIP001 Isolated | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72FIP001FLT | F72FIP001 FLT _ | - | F72-FIP-001 Fault | F72FIP001 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72SW172Q1CL | F72SW172Q1 CL _ | - | F72-SW-172 Mains Supply Circuit Breaker Closed | F72SW172 Main CB Closed | Inactive | Active |  | Hardwired to DCS |  |  |  | C
F72SW172Q1OP | F72SW172Q1 OP _ | - | F72-SW-172 Mains Supply Circuit Breaker Opened | F72SW172 Main CB Opened | Inactive | Active |  | Hardwired to DCS |  |  |  | 1
F72SW172Q2CL | F72SW172Q2 CL _ | - | F72-SW-172 Generator Supply Circuit Breaker Closed | F72SW172 Main CB Closed | Inactive | Active |  | Hardwired to DCS |  |  |  | C
F72SW172Q2OP | F72SW172Q2 OP _ | - | F72-SW-172 Generator Supply Circuit Breaker Opened | F72SW172 Main CB Opened | Inactive | Active |  | Hardwired to DCS |  |  |  | 1
ZSC72034 | ZAC72034 | - | F72-TR-072 REAGENTS 415V MCC Transformer Enclosure Door Position Switch Closed | F72TR072 415V MCC Door | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1
F72SW172SD | F72SW172 SD _ | - | F72-SW-172 Incomer Surge Diverter OK | F72SW172 IncSurge Div OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
LSH72033 | LAH72033 | - | F72-GE-172 Reagents Emergency 415V Generator Level Switch High | F72GE172 415V Gen Lvl Hi | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
LSL72033 | LAL72033 | - | F72-GE-172 Reagents Emergency 415V Generator Level Switch Low | F72GE172 415V Gen Lvl Lo | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72RIO003PS1 | F72RIO003 PS1 _ | - | F72-RIO-003 PS1 24VDC Healthy | F72RIO003 PS1 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72RIO003PS2 | F72RIO003 PS2 _ | - | F72-RIO-003 PS2 24VDC Healthy | F72RIO003 PS2 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | C
F72RIO004PS1 | F72RIO004 PS1 _ | - | F72-RIO-004 PS1 24VDC HEALTHY | F72RIO004 PS1 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1
F72RIO004PS2 | F72RIO004 PS2 _ | - | F72-RIO-004 PS2 24VDC HEALTHY | F72RIO004 PS2 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1
F72LU411PS | F72LU411 PS _ | - | F72-LU-411 LIME SLAKING MILL 1 AUTOLUBE GREASE SYSTEM 24VDC POWER SUPPLY HEALTHY | F72LU411 PS 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1
F72LU412PS | F72LU412 PS _ | - | F72-LU-412 LIME SLAKING MILL 2 AUTOLUBE GREASE SYSTEM 24VDC POWER SUPPLY HEALTHY | F72LU412 PS 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1
FQ72610 | FS72610 | 2000-F72-PID-PR-10007 | F72-PP-683/4 Acid Dosing Pumps Flow Indicating Transmitter | F72PP683/4 Total Pulse | Inactive | Active |  | Hardwired to DCS |  |  |  | 1
FQ72616 | FS72616 | 2000-F72-PID-PR-10007 | F72-PP-683/4 Acid Dosing Pumps to F72-TK-424 CIL 4 Acid Dilution Tank | F72TK424 Totaliser Pulse | Inactive | Active |  | Hardwired to DCS |  |  |  | 1
FSH72168 | FAH72168 | 2000-F24-PID-PR-10028 | F72-SE-424 LIME AREA SAFETY SHOWER 1 | F72SE424 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
FSH72169 | FAH72169 | 2000-F24-PID-PR-10028 | F72-SE-425 LIME AREA SAFETY SHOWER 2 | F72SE425 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
FSH72170 | FAH72170 | 2000-F24-PID-PR-10028 | F72-SE-426 LIME AREA SAFETY SHOWER 3 | F72SE426 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
FSH72177 | FAH72177 | 2000-F24-PID-PR-10028 | F72-SE-454 CAUSTIC TANKS AREA SAFETY SHOWER | F72SE454 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
FSH72178 | FAH72178 | 2000-F24-PID-PR-10028 | F72-SE-455 HCL AREA SAFETY SHOWER 1 | F72SE455 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
FSH72179 | FAH72179 | 2000-F24-PID-PR-10028 | F72-SE-456 LEAD NITRATE AREA SAFETY SHOWER | F72SE456 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
FSH72180 | FAH72180 | 2000-F24-PID-PR-10028 | F72-SE-457 SODIUM CYANIDE AREA SAFETY SHOWER 1 | F72SE457 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
FSH72181 | FAH72181 | 2000-F24-PID-PR-10028 | F72-SE-458 SODIUM CYANIDE AREA SAFETY SHOWER 2 | F72SE458 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
FSH72182 | FAH72182 | 2000-F24-PID-PR-10028 | F72-SE-459 SODIUM CYANIDE AREA SAFETY SHOWER 3 | F72SE459 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
FSH72183 | FAH72183 | 2000-F24-PID-PR-10028 | F72-SE-460 SODIUM CYANIDE AREA SAFETY SHOWER 4 | F72SE460 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
FSH72184 | FAH72184 | 2000-F24-PID-PR-10028 | F72-SE-461 SODIUM CYANIDE AREA SAFETY SHOWER 5 | F72SE461 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
FSH72185 | FAH72185 | 2000-F24-PID-PR-10028 | F72-SE-462 SODIUM CYANIDE AREA SAFETY SHOWER 6 | F72SE462 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
FSH72186 | FAH72186 | 2000-F24-PID-PR-10028 | F72-SE-504 SODIUM CYANIDE AREA SAFETY SHOWER 7 | F72SE504 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
FSH72187 | FAH72187 | 2000-F24-PID-PR-10028 | F72-SE-466 HCL AREA SAFETY SHOWER 2 | F72SE466 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 1
XI72629S | XI72629 | 2000-F72-PID-PR-10011 | F72-PK-405 Oxygen Plant Controller VPSA Running Feedback | F72PK405 Running | Inactive | Active |  | SoftTag |  |  |  | 1
XA72630S | XA72630 | 2000-F72-PID-PR-10011 | F72-PK-405 Oxygen Plant Controller VPSA Fault Feedback | F72PK405 Fault | Normal | Alarm | Alarm | SoftTag | 3 |  |  | 1
XA72631S | XA72631 | 2000-F72-PID-PR-10011 | F72-PK-405 Oxygen Plant Controller VPSA Fire Alarm Feedback | F72PK405 Fire | Normal | Alarm | Alarm | SoftTag | 0 |  |  | 1
F72TR072WTH | F72TR072 WTH _ | - | F72-TR-072 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F72TR072 Temp Hi | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | 1
F72GE172CBTRP | 72GE172CBTRP |  | F72-GE-172 REAGENTS EMERGENCY 415V GENERATOR CB TRIPPED | F72-GE-172 GEN CB TRP | Alarm | Normal | Alarm | Hardwired to DCS | 0

## 4. Digital Output
KCGM GROWTH PROJECT
DIGITAL OUTPUT
DIGITAL OUTPUTS
Tag Source | Tag Name | P&ID | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev
XY72499 | XI72499 | 2000-F72-PID-PR-10001 | F72SI411 Fill Vlv 1 Open | Inactive | Open |  |  |  | If XV72419 = Open: Activate XI72499 Note, no indicators active between limits | C
XY72500 | XI72500 | 2000-F72-PID-PR-10001 | F72SI411 Fill Vlv 1 Clse | Inactive | Close |  |  |  | If XV72419 = Closed: Activate XI72500 Note, no indicators active between limits | C
XY72502 | XI72502 | 2000-F72-PID-PR-10001 | F72SI411 Fill Vlv 2 Open | Inactive | Open |  |  |  | If XV72420 = Open: Activate XI72502 Note, no indicators active between limits | C
XY72503 | XI72503 | 2000-F72-PID-PR-10001 | F72SI411 Fill Vlv 2 Clse | Inactive | Close |  |  |  | If XV72420 = Closed: Activate XI72503 Note, no indicators active between limits | C
XY72511 | XI72511 | 2000-F72-PID-PR-10002 | F72SI412 Fill Vlv 1 Open | Inactive | Open |  |  |  | If XV72433 = Open: Activate XI72511 Note, no indicators active between limits | C
XY72512 | XI72512 | 2000-F72-PID-PR-10002 | F72SI412 Fill Vlv 1 Clse | Inactive | Close |  |  |  | If XV72433 = Closed: Activate XI72512 Note, no indicators active between limits | C
XY72514 | XI72514 | 2000-F72-PID-PR-10002 | F72SI412 Fill Vlv 2 Open | Inactive | Open |  |  |  | If XV72434 = Open: Activate XI72514 Note, no indicators active between limits | C
XY72515 | XI72515 | 2000-F72-PID-PR-10002 | F72SI412 Fill Vlv 2 Clse | Inactive | Close |  |  |  | If XV72434 = Closed: Activate XI72515 Note, no indicators active between limits | C
YY72540 | YA72540 | 2000-F72-PID-PR-10005 | F72TK437 Level HH | Off | On |  |  |  | Siren and Beacon If LI72531 ≥ A HH: _ Activate YA72540 | C
YY72546 | YA72546 | 2000-F72-PID-PR-10005 | F72TK439 Level HH | Off | On |  |  |  | Siren and Beacon If LI72535 ≥ A HH: _ Activate YA72546 | C
YY72593 | YA72593 | 2000-F72-PID-PR-10006 | F72TK434 Level HH | Off | On |  |  |  | Siren and Beacon If LI72591 ≥ A HH: _ Activate YA72593 | C
YY72547 | YA72547 | 2000-F72-PID-PR-10005 | F72PP675/6 HCN Siren | Off | On |  |  |  | Siren and Beacon If ASHH72547 = Inactive for 3 seconds: Activate YA72547 If ASHH72547 = Active for 10 minutes: Deactivate YA72547 | C
YY72548 | YA72548 | 2000-F72-PID-PR-10005 | F72TK437 HCN Siren | Off | On |  |  |  | Siren and Beacon If ASHH72548 = Inactive for 3 seconds: Activate YA72548 If ASHH72548 = Active for 10 minutes: Deactivate YA72548 | C
YY72549 | YA72549 | 2000-F72-PID-PR-10005 | F72TK439 HCN Siren | Off | On |  |  |  | Siren and Beacon If ASHH72549 = Inactive for 3 seconds: Activate YA72549 If ASHH72549 = Active for 10 minutes: Deactivate YA72549 | C
YY72605 | YA72605 | 2000-F72-PID-PR-10007 | F72TK435 Level HH | Off | On |  |  |  | Siren and Beacon If LI72602 ≥ A HH = Active: _ Activate YA72605 | C
YY72706 | YA72706 | 2000-F72-PID-PR-10015 | F72TK438 Level HH | Off | On |  |  |  | Siren and Beacon If LI72701 ≥ A HH = Active: _ Activate YA72701 | C
HS72693 | HS72693STT | 2000-F72-PID-PR-10012 | F72PP698 Start/Stop | Stop | Start |  |  |  | Required Dosing Pump settings (set from pump's local HMI, see IOM): • Set 'External stop' to normally closed (Setup > Inputs/Outputs > External stop), • Set to 'Running' operating state. "To start and stop the pump via bus, it needs to be in operating state "Running". When the pump is remotely stopped from bus, the "External stop" symbol is displayed and the pump switches to operating state "Standby" | 1
HS72694 | HS72694STT | 2000-F72-PID-PR-10012 | F72PP699 Start/Stop | Stop | Start |  |  |  | Required Dosing Pump settings (set from pump's local HMI, see IOM): • Set 'External stop' to normally closed (Setup > Inputs/Outputs > External stop), • Set to 'Running' operating state. "To start and stop the pump via bus, it needs to be in operating state "Running". When the pump is remotely stopped from bus, the "External stop" symbol is displayed and the pump switches to operating state "Standby" | 1
HS72695 | HS72695STT | 2000-F72-PID-PR-10012 | F72PP700 Start/Stop | Stop | Start |  |  |  | Required Dosing Pump settings (set from pump's local HMI, see IOM): • Set 'External stop' to normally closed (Setup > Inputs/Outputs > External stop), • Set to 'Running' operating state. "To start and stop the pump via bus, it needs to be in operating state "Running". When the pump is remotely stopped from bus, the "External stop" symbol is displayed and the pump switches to operating state "Standby" | 1
HS72696 | HS72696STT | 2000-F72-PID-PR-10012 | F72PP701 Start/Stop | Stop | Start |  |  |  | Required Dosing Pump settings (set from pump's local HMI, see IOM): • Set 'External stop' to normally closed (Setup > Inputs/Outputs > External stop), • Set to 'Running' operating state. "To start and stop the pump via bus, it needs to be in operating state "Running". When the pump is remotely stopped from bus, the "External stop" symbol is displayed and the pump switches to operating state "Standby" | 1
HS72697 | HS72697STT | 2000-F72-PID-PR-10012 | F72PP702 Start/Stop | Stop | Start |  |  |  | Required Dosing Pump settings (set from pump's local HMI, see IOM): • Set 'External stop' to normally closed (Setup > Inputs/Outputs > External stop), • Set to 'Running' operating state. "To start and stop the pump via bus, it needs to be in operating state "Running". When the pump is remotely stopped from bus, the "External stop" symbol is displayed and the pump switches to operating state "Standby" | 1
HS72698 | HS72698STT | 2000-F72-PID-PR-10012 | F72PP703 Start/Stop | Stop | Start |  |  |  | Required Dosing Pump settings (set from pump's local HMI, see IOM): • Set 'External stop' to normally closed (Setup > Inputs/Outputs > External stop), • Set to 'Running' operating state. "To start and stop the pump via bus, it needs to be in operating state "Running". When the pump is remotely stopped from bus, the "External stop" symbol is displayed and the pump switches to operating state "Standby" | 1
HS72699 | HS72699STT | 2000-F72-PID-PR-10012 | F72PP704 Start/Stop | Stop | Start |  |  |  | Required Dosing Pump settings (set from pump's local HMI, see IOM): • Set 'External stop' to normally closed (Setup > Inputs/Outputs > External stop), • Set to 'Running' operating state. "To start and stop the pump via bus, it needs to be in operating state "Running". When the pump is remotely stopped from bus, the "External stop" symbol is displayed and the pump switches to operating state "Standby" | 1
HS72700 | HS72700STT | 2000-F72-PID-PR-10012 | F72PP705 Start/Stop | Stop | Start |  |  |  | Required Dosing Pump settings (set from pump's local HMI, see IOM): • Set 'External stop' to normally closed (Setup > Inputs/Outputs > External stop), • Set to 'Running' operating state. "To start and stop the pump via bus, it needs to be in operating state "Running". When the pump is remotely stopped from bus, the "External stop" symbol is displayed and the pump switches to operating state "Standby" | 1
HS72508 | HS72508STT | 2000-F72-PID-PR-10001 | F72LU411 Start/Stop | Stop | Start |  |  |  | Starts / stops F72-LU-411 | 1
HS72509 | HS72509STT | 2000-F72-PID-PR-10002 | F72LU412 Start/Stop | Stop | Start |  |  |  | Starts / stops F72-LU-412 | 1
YY72520 | YA72520 | 2000-F72-PID-PR-10001 | F72MB411 Start Siren | Off | On |  |  |  | Siren is turned on for 10 seconds before F72-MB-411 Mill is allowed to start | 2
YY72521 | YY72521 | 2000-F72-PID-PR-10002 | F72MB412 Start Siren | Off | On |  |  |  | Siren is turned on for 10 seconds before F72-MB-412 Mill is allowed to start | 2

## 6. OnOff Valves
KCGM GROWTH PROJECT
ONOFF VALVES
Permissives and Trips
Tag Name | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position (Loss of Power) | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open | Close | Bypass | Reset Required | Comments | Rev
XV72419 | F72SI411 Lime Silo 1 Filling Line Isolation Valve 1 | F72SI411 Fill Valve 1 | DETAIL 4 | FC | X |  |  |  | CT1 CT2 CT3 OP1 | LI72401 >= A_HH LSH72505 Active PDI72404 >= A_HH | Lime Silo 1 Level HH Lime Silo 1 Switch Hi PDI72404 >= A_HH F72SI411 Delivery Capacity | 3 3 3 3 |  | X |  |  | X X X | X X X X |  | Intent is to have valve local open and close only (via push button), see HS72498OP/CL in Digitial Input tab. Valve can only be actuated from DCS graphics with Supervisor login | 2
[20 empty] | 2000-F72-TQY-ME-10322 | C 1 C
XV72420 | F72SI411 Lime Silo 1 Filling Line Isolation Valve 2 | F72SI411 Fill Valve 2 | DETAIL 4 | FC | X |  |  |  | CT1 CT2 CT3 OP1 | LI72401 >= A_HH LSH72505 Active PDI72404 >= A_HH | Lime Silo 1 Level HH Lime Silo 1 Switch Hi PDI72404 >= A_HH F72SI411 Delivery Capacity | 3 3 3 3 |  | X |  |  | X X X | X X X X |  | Intent is to have valve local open and close only (via push button), see HS72501OP/CL in Digitial Input tab. Valve can only be actuated from DCS graphics with Supervisor login | 2
[20 empty] | 2000-F72-TQY-ME-10322 | C 1 C
XV72413 | F72HP411 Slaked Lime Discharge Hopper 1 Drain Valve | F72HP411 Drain Valve | DETAIL 4 | FO | X | [15 empty] | 1
XV72458 | F72CY658 Slaked Lime Hydro-Cyclone 1 Actuated Feed Valve | F72CY658 Feed Valve 1 | DETAIL 3 | FL | X | [15 empty] | 2
XV72459 | F72CY658 Slaked Lime Hydro-Cyclone 1 Actuated Feed Valve | F72CY658 Feed Valve 2 | DETAIL 3 | FL | X | [15 empty] | 2
XV72460 | F72CY658 Slaked Lime Hydro-Cyclone 1 Actuated Feed Valve | F72CY658 Feed Valve 3 | DETAIL 3 | FL | X | [15 empty] | 2
XV72457 | F72WS411 Slaked Lime Wet Scrubber 1 Actuated Feed Valve | F72WS411 Scrubber Water | DETAIL 7 | FO | X | X | F72-SEQ-0106 | F72-SEQ-0108 | [12 empty] | 1
XV72433 | F72SI412 Lime Silo 2 Filling Line Isolation Valve 1 | F72SI412 Fill Valve 1 | DETAIL 4 | FC | X |  |  |  | CT1 CT2 CT3 OP1 | LI72421 >= A_HH LSH72517 Active PDI72424 >= A_HH | Lime Silo 2 Level HH Lime Silo 1 Switch Hi PDI72424 >= A_HH F72SI412 Delivery Capacity | 3 3 3 3 |  | X |  |  | X X X | X X X X |  | Intent is to have valve local open and close only (via push button), see HS72510OP/CL in Digitial Input tab. Valve can only be actuated from DCS graphics with Supervisor login | 2
[20 empty] | 2000-F72-TQY-ME-10322 | C 1 1
XV72434 | F72SI412 Lime Silo 2 Filling Line Isolation Valve 2 | F72SI412 Fill Valve 2 | DETAIL 4 | FC | X |  |  |  | CT1 CT2 CT3 OP1 | LI72421 >= A_HH LSH72517 Active PDI72424 >= A_HH | Lime Silo 2 Level HH Lime Silo 1 Switch Hi PDI72424 >= A_HH F72SI412 Delivery Capacity | 3 3 3 3 |  | X |  |  | X X X | X X X X |  | Intent is to have valve local open and close only (via push button), see HS72513OP/CL in Digitial Input tab. Valve can only be actuated from DCS graphics with Supervisor login | 2
[20 empty] | 2000-F72-TQY-ME-10322 | C 1 1
XV72415 | F72HP412 Slaked Lime Discharge Hopper 2 Drain Valve | F72HP412 Drain Valve | DETAIL 4 | FO | X | [15 empty] | 1
XV72467 | F72CY659 Slaked Lime Hydro-Cyclone 2 Actuated Feed Valve | F72CY659 Feed Valve 1 | DETAIL 3 | FL | X | [15 empty] | 2
XV72468 | F72CY659 Slaked Lime Hydro-Cyclone 2 Actuated Feed Valve | F72CY659 Feed Valve 2 | DETAIL 3 | FL | X | [15 empty] | 2
XV72469 | F72CY659 Slaked Lime Hydro-Cyclone 2 Actuated Feed Valve | F72CY659 Feed Valve 3 | DETAIL 3 | FL | X | [15 empty] | 2
XV72473 | F72WS412 Slaked Lime Wet Scrubber 2 Actuated Feed Valve | F72WS412 Scrubber Water | DETAIL 7 | FO | X | X | F72-SEQ-0107 | F72-SEQ-0109 | [12 empty] | 1
XV72409 | F72XM660 Lime Slaking Mill Ball Kibble Loading Hopper Gate 1 | F72XM660 Transfer 1 | DETAIL 12 | FL | [15 empty] | Detail 12. No control over DCS; feedback only. See ZSO72409 and ZSC72409 in Digital Inputs | C
XV72410 | F72XM660 Lime Slaking Mill Ball Kibble Loading Hopper Gate 1 | F72XM660 Transfer 2 | DETAIL 12 | FL | [15 empty] | Detail 12. No control over DCS; feedback only. See ZSO72410 and ZSC72410 in Digital Inputs | C
XV72464 | F72PS419 Milk of Lime Area Sump Pump 1 Flushing Valve | F72PS419 Water | DETAIL 7 | FC | X | X | F72-PS-419 = Running | [12 empty] | setpoints TBC during commissioning). HAZOP 350 | 1
XV72465 | F72PS466 Milk of Lime Area Sump Pump 2 Flushing Valve | F72PS466 Water | DETAIL 7 | FC | X | X | F72-PS-466 = Running | [12 empty] | setpoints TBC during commissioning). HAZOP 350 | 1
XV72466 | F72PS467 Milk of Lime Area Sump Pump 3 Flushing Valve | F72PS467 Water | DETAIL 7 | FC | X | X | F72-PS-467 = Running | [12 empty] | setpoints TBC during commissioning). HAZOP 350 | 1
XV72441 | F72PP656 Lime Ringmain Pump 1 Suction Valve | F72PP656 Suction | DETAIL 3 | FL | X | X | F72-SEQ-0101 | F72-SEQ-0102 | [12 empty] | C
XV72442 | F72PP656 Lime Ringmain Pump 1 Suction Flushing Valve | F72PP656 Suction Flush | DETAIL 3 | FL | X | X | F72-SEQ-0102 | F72-SEQ-0101 & F72-SEQ-0102 | [12 empty] | C
XV72443 | F72PP656 Lime Ringmain Pump 1 Suction Drain Valve | F72PP656 Suction Drain | DETAIL 3 | FL | X | X | F72-SEQ-0102 | F72-SEQ-0101 | OP1 | F72-PP-656 Not Running | F72-PP-656 Not Running | 3 |  | X |  |  |  | X |  |  | C
XV72452 | F72PP656 Lime Ringmain Pump 1 Discharge Drain Valve | F72PP656 Discharge Drain | DETAIL 3 | FL | X | X | F72-SEQ-0102 | F72-SEQ-0101 | [12 empty] | C
XV72444 | F72PP656 Lime Ringmain Pump 1 Discharge Valve | F72PP656 Discharge | DETAIL 3 | FL | X | X | F72-SEQ-0101 | F72-SEQ-0102 | OP1 | F72-PP-657 Not Running | F72-PP-657 Not Running | 3 |  | X |  |  |  | X |  |  | C
XV72445 | F72PP657 Lime Ringmain Pump 2 Suction Valve | F72PP657 Suction | DETAIL 3 | FL | X | X | F72-SEQ-0101 | F72-SEQ-0102 | [12 empty] | C
XV72446 | F72PP657 Lime Ringmain Pump 2 Suction Flushing Valve | F72PP657 Suction Flush | DETAIL 3 | FL | X | X | F72-SEQ-0102 | F72-SEQ-0101 & F72-SEQ-0102 | [12 empty] | C
XV72447 | F72PP657 Lime Ringmain Pump 2 Suction Drain Valve | F72PP657 Suction Drain | DETAIL 3 | FL | X | X | F72-SEQ-0102 | F72-SEQ-0101 | OP1 | F72-PP-657 Not Running | F72-PP-657 Not Running | 3 |  | X |  |  |  | X |  |  | C
XV72453 | F72PP657 Lime Ringmain Pump 2 Discharge Drain Valve | F72PP657 Discharge Drain | DETAIL 3 | FL | X | X | F72-SEQ-0102 | F72-SEQ-0101 | [12 empty] | C
XV72448 | F72PP657 Lime Ringmain Pump 2 Discharge Valve | F72PP657 Discharge | DETAIL 3 | FL | X | X | F72-SEQ-0101 | F72-SEQ-0102 | OP1 | F72-PP-656 Not Running | F72-PP-656 Not Running | 3 |  | X |  |  |  | X |  |  | C
XV72541 | F72TK437 Cyanide Delivery to Cyanide Storage Tank 1 Inlet Valve | F72TK437 Transfer Valve | DETAIL 8 | FC | X |  |  |  | CT1 OP1 | LI72531 ≥ A_HH | F72TK437 Level A HH F72TK437 Delivery Capacity | 3 3 |  | X |  |  | X | X X |  | 2000-F72-TQY-ME-10322 | C C
XV72542 | F72TK439 Cyanide Delivery to Cyanide Storage Tank 2 Inlet Valve | F72TK439 Transfer Valve | DETAIL 8 | FC | X |  |  |  | CT1 OP1 | LI72535 ≥ A_HH | F72TK439 Level A HH F72TK439 Delivery Capacity | 3 3 |  | X |  |  | X | X X |  | 2000-F72-TQY-ME-10322 | C C
XV72538 | F72TK437 Cyanide Storage Tank 1 Inlet Valve | F72TK437 Return Valve | DETAIL 9 | FL | X |  |  |  | CP1 | (F72-PP-675 AND F72-PP-676 Running AND (XV72539 Open) OR (F72-PP-675 AND F72-PP-676 Stopped) | F72TK439 Recirc Valve Open OR Pumps Stopped | 3 |  |  | X |  |  | X |  | Closing the recirc should be for maintenance purposes only | 2
XV72539 XV72536 | F72TK439 Cyanide Storage Tank 2 Inlet Valve F72PP675 Cyanide Storage Tank 1 Discharge Valve | F72TK439 Return Valve F72TK437 Discharge | DETAIL 9 DETAIL 9 | FL FL | X X |  |  |  | CP1 CP1 | (F72-PP-675 AND F72-PP-676 Running AND (XV72538 Open) OR (F72-PP-675 AND F72-PP-676 Stopped) F72-PP-675 Stopped | F72TK437 Recirc Valve Open OR Pumps Stopped F72-PP-675 Stopped | 3 3 |  |  | X X |  |  | X X |  | Closing the recirc should be for maintenance purposes only | 2 2
XV72537 XV72594 | F72PP676 Cyanide Storage Tank 2 Discharge Valve F72TK434 Caustic Delivery to Caustic Storage Tank Inlet Valve | F72TK439 Discharge F72TK434 Transfer Valve | DETAIL 9 DETAIL 7 | FL FC | X X |  |  |  | CP1 CT1 OP1 | F72-PP-676 Stopped LI72591 ≥ A_HH | F72-PP-676 Stopped F72TK434 Level HH F72TK434 Delivery Capacity | 3 3 3 |  | X | X |  | X | X X X |  | 2000-F72-TQY-ME-10322 | 2 C C
XV72596 | F72TK434 Caustic Storage Tank Discharge Valve | F72TK434 Outlet | DETAIL 7 | FC | X |  |  |  | CP1 | F72-PP-673 AND F72-PP-674 Stopped | F72-PP-673 AND F72-PP-674 Stopped | 3 |  |  | X |  |  | X |  |  | C
XV72603 | F72TK435 Hydrochloric Acid Storage Tank Outlet Valve | F72TK435 Outlet | DETAIL 7 | FC | X | X | F72-SEQ-0103 |  | CP1 | F72-PP-683 AND F72-PP-684 Stopped | F72-PP-683 AND F72-PP-684 Stopped | 3 |  |  | X |  |  | X |  |  | 0
XV72601 | F72TK435 Hydrochloric Acid Delivery to Acid Storage Tank Inlet Valve | F72TK435 Transfer Valve | DETAIL 8 | FC | X |  |  |  | CT1 OP1 | LI72602 ≥ A_HH | F72TK435 Level HH F72TK435 Delivery Capacity | 3 3 |  | X |  |  | X | X X |  | 2000-F72-TQY-ME-10322 | 1 C
XV72637 | F72TK424 CIL 4 Acid Dilution Tank Acid Recirculation Valve | F72TK424 Recirculation | DETAIL 7 | FO | X | X | F72-SEQ-0103 | F72-SEQ-0103 | [12 empty] | 1
XV72639 | F72TK424 CIL 4 Acid Dilution Tank Acid Discharge Valve | F72TK424 Forward | DETAIL 9 | FL | X | X | F72-SEQ-0103 | F72-SEQ-0103 | [12 empty] | 1
XV72614 | F72TK424 CIL 4 Acid Dilution Tank Scheme Water Inlet Valve | F72TK424 Water Valve | DETAIL 8 | FC | X | X | F72-SEQ-0103 | F72-SEQ-0103 | CT1 | LI72612 ≥ A_HH | F72TK424 Level HH | 3 |  |  |  |  | X | X |  | Supervisor level required for mode change and actuation | 2
SV72617 | F72PS428 Hydrochloric Acid Area Sump Pump Solenoid Air Valve | F72PS428 Air Supply | DETAIL 11 | FC |  | X | Refer to F72-PS-428 Drive tab | Refer to F72-PS-428 Drive tab | [12 empty] | 0
SV72712 | F72PS426 Led Nitrate Area Sump Pump Solenoid Air Valve | F72PS426 Air Supply | DETAIL 11 | FC |  | X | Refer to F72-PS-426 Drive tab | Refer to F72-PS-426 Drive tab | [12 empty] | 0
XV72705 | F72TK438 Lead Nitrate Delivery to Lead Nitrate Storage Tank Valve | F72TK438 Transfer Valve | DETAIL 8 | FC | X |  |  |  | CT1 OP1 | LI72701 ≥ A_HH | F72TK438 Level HH F72TK438 Delivery Capacity | 3 3 |  | X |  |  | X | X X |  | 2000-F72-TQY-ME-10322 | 1 C
SV72492 | F72PP658 Slaked Lime Transfer Pump Gland Water Solenoid Valve | F72PP658 Gland Supply | DETAIL 11 | FO | X | X | F72-PP-658 Start | [13 empty] | 2
SV72495 | F72PP659 Slaked Lime Transfer Pump Gland Water Solenoid Valve | F72PP659 Gland Supply | DETAIL 11 | FO | X | X | F72-PP-659 Start | [13 empty] | 2
SV72470 | F72PP656 Lime Ringmain Pump 1 Gland Water Solenoid Valve | F72PP656 Gland Supply | DETAIL 11 | FO | X | X | F72-SEQ-0101 OR F72-PP-656 Start | [13 empty] | 2
SV72474 | F72PP657 Lime Ringmain Pump 1 Gland Water Solenoid Valve | F72PP657 Gland Supply | DETAIL 11 | FO | X | X | F72-SEQ-0101 OR F72-PP-657 Start | [13 empty] | 2

## 5. Totalisers
KCGM GROWTH PROJECT
TOTALISERS
Reset Period
Tag Source | Tag Name | Type | P&ID | Abbreviated Description (Faceplate) | Units | Shift | Day | Cont | Comments | Rev
FQ72610 | FQI72610 | FQI | 2000-F72-PID-PR-10007 | F72PP683/4 Acid Dosing | m3 | x | x | x |  | 1
FQ72616 | FQI72616 | FQI | 2000-F72-PID-PR-10007 | F72TK424 Acid Dosing | m3 |  |  | x | Totaliser utilised as part of F72-SEQ-0103. | 1

## 8. PID Cont
KCGM GROWTH PROJECT
PID CONT
[5 empty] | Modes |  |  |  | Setpoint |  |  | Range |  |  | Process Switchpoints | [5 empty] | Alarms | [8 empty] | Controlled/Manipulated Variable | [10 empty] | Comment | Rev
Tag Source | Tag Name | P&ID | Abbreviated Description (Faceplate) | Normal Operating Mode | Manual | Auto | Cascade | Process Value Tag | Min | Max | Unit | Min | Max | Unit | P_LL |  |  |  |  | P_HH | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Range Min | Range Max | Lower Limit | Upper Limit | Unit | Destination Description | Destination (Output) Tag | Direct / Reverse Acting | P | I | D
TI72412 | TIC72412 | 2000-F72-PID-PR-10001 | F72HP411 Temperature | AUT | X | X |  | TI72412 | 50 | 70 | °C | 0 | 110 | °C | [8 empty] | 30 | 5 | 85 | 5 | 90 | 5 | If F72-FV-411 = Not Running: | 0 | 100 | 40 | 100 | % Speed VSD | F72-VR-411 Lime Silo 1 Rotary Valve VSD | F72-VR-411 VSD | Reverse |  |  |  | PV from SS DUAL block, refer TI72412 Analogue Input tab | 1
FIT72407 | FIC72407 | 2000-F72-PID-PR-10001 | F72XM658 Prewetter Water | CAS | X | X | X | FIT72407 | 50 | 80 | m3/h | 0 | 120 | m3/hr | [6 empty] | 51.5 | 5 | 58 | 5 | 70.8 | 5 | 77.3 | 5 | 7 A N 2 V 1 | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV72407) position | FCV72407 | Reverse |  |  |  | Include DV alarm. +/- 10% of range Cascade set value from F72CALC10108 | 2
FIT72408 | FIC72408 | 2000-F72-PID-PR-10001 | F72HP411 Feed Water | CAS | X | X | X | FIT72408 | 15 | 30 | m3/h | 0 | 60 | m3/hr | [8 empty] | 21 | 5 | 25.7 | 5 | 28.1 | 5 | 1 D - 5 | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV72408) position | FCV72408 | Reverse |  |  |  | Include DV alarm. +/- 10% of range Cascade set value from F72CALC10108 | 2
LIT72411 | LIC72411 | 2000-F72-PID-PR-10001 | F72HP411 Hopper Level | AUT | X | X |  | LIT72411 | 70 | 90 | % | 0 | 100 | % | [6 empty] | 10 | 5 | 30 | 5 | 92 | 5 | 95 | 5 |  | 0 | 100 | 40 | 100 | % Speed VSD | F72-PP-658 Slaked Lime Transfer Pump 1 VSD | F72-PP-658 VSD | Direct |  |  |  |  | 1
TI72432 | TIC72432 | 2000-F72-PID-PR-10002 | F72HP412 Temperature | AUT | X | X |  | TI72432 | 50 | 70 | °C | 0 | 110 | °C | [8 empty] | 30 | 5 | 85 | 5 | 90 | 5 | If F72-FV-412 = Not Running: | 0 | 100 | 40 | 100 | % Speed VSD | F72-VR-412 Lime Silo 2 Rotary Valve VSD | F72-VR-412 VSD | Reverse |  |  |  | PV from SS DUAL block, refer TI72432 Analogue Input tab | 1
FIT72427 | FIC72427 | 2000-F72-PID-PR-10002 | F72XM659 Prewetter Water | CAS | X | X | X | FIT72427 | 50 | 80 | m3/h | 0 | 120 | m3/hr | [6 empty] | 51.5 | 5 | 58 | 5 | 70.8 | 5 | 77.3 | 5 | 7 A N 2 V 1 | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV72427) position | FCV72427 | Reverse |  |  |  | Include DV alarm. +/- 10% of range Cascade set value from F72CALC10109 | 2
FIT72428 | FIC72428 | 2000-F72-PID-PR-10002 | F72HP412 Feed Water | CAS | X | X | X | FIT72428 | 15 | 30 | m3/h | 0 | 60 | m3/hr | [8 empty] | 21 | 5 | 25.7 | 5 | 28.1 | 5 | 1 D - 5 | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV72428) position | FCV72428 | Reverse |  |  |  | Include DV alarm. +/- 10% of range Cascade set value from F72CALC10109 | 2
LIT72431 | LIC72431 | 2000-F72-PID-PR-10002 | F72HP412 Hopper Level | AUT | X | X |  | LIT72431 | 70 | 90 | % | 0 | 100 | % | [6 empty] | 10 | 5 | 30 | 5 | 92 | 5 | 95 | 5 |  | 0 | 100 | 40 | 100 | % Speed VSD | F72-PP-659 Slaked Lime Transfer Pump 2 VSD | F72-PP-659 VSD | Direct |  |  |  |  | 1
LT72439 | LIC72439 | 2000-F72-PID-PR-10003 | F72TK467 MOL Level | AUT | X | X |  | LT72439 | 0 | 100 | % | 0 | 100 | % |  | 50 | 5 | 70 | 5 |  | 20 | 5 | 30 | 5 | 80 | 5 | 90 | 5 |  | 0 | 200 | 0 | 120 | m3/hr | FIC72407 and FIC72408 via F72CALC10108 and/or FIC72427 and FIC72428 via F72CALC10109 | F72-CALC-10008 and/or F72CALC10109 | Reverse |  |  |  | Refer to F72CALC10108 & F72CALC10109 | C
FIT72732 | FIC72732 | 2000-F72-PID-PR-10015 | F72PP681/2 Nitrate Flow | CAS | X | X | X | FIT72732 | 0 | 5 | m3/h | 0 | 7.5 | m3/hr | [6 empty] | 0.5 | 5 | 1 | 5 | [5 empty] | 0 | 100 | 40 | 100 | % Speed VSD |  | F72-PP-681 OR F72-PP- 682 VSD via HS72732 | Reverse |  |  |  | Cascade set value from F72CALC10101 Refer to Misc tab for HS72732 | C
FIT72632 | FIC72632 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Feed | AUT | X | X |  | FIT72632 | 0 | 50 | m3/h | 0 | 100 | m3/hr | [14 empty] | Mask deviation alarm if F72-PK-405 Not Running (XI72629 inactive) for > 1 minute | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV72632) position | FCV72632 | Reverse |  |  |  | Include DV alarm. +/- 10% of range | 1

## 7. Control Valves
KCGM GROWTH PROJECT
CONTROL VALVES
Permissive and Trips
Tag Name | P&ID | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open | Close | Bypass | Reset Required | Comments | Rev
FCV72407 | 2000-F72-PID-PR-10001 | F72XM658 Prewetter FCV | DETAIL 2 | FO | X | X |  |  | CT1 | LSH72405 Active | LSH72405 Active | 3 |  |  |  |  | X | X |  |  | C
[9 empty] | CT2 | LIC72411 ≥ A HH _ | LIC72411 ≥ A HH _ | 3 |  |  |  |  | X | X |  |  | C
FCV72408 | 2000-F72-PID-PR-10001 | F72HP411 Feed Water FCV | DETAIL 2 | FO | X | X |  |  | CT1 | LIC72411 ≥ A HH _ | LIC72411 ≥ A HH _ | 3 |  |  |  |  | X | X |  |  | C
FCV72427 | 2000-F72-PID-PR-10002 | F72XM659 Prewetter FCV | DETAIL 2 | FO | X | X |  |  | CT1 | LSH72425 Active | LSH72425 Active | 3 |  |  |  |  | X | X |  |  | C
[9 empty] | CT2 | LIC72431 ≥ A HH _ | LIC72431 ≥ A HH _ | 3 |  |  |  |  | X | X |  |  | 2
FCV72428 | 2000-F72-PID-PR-10002 | F72HP412 Feed Water FCV | DETAIL 2 | FO | X | X |  |  | CT1 | LIC72431 ≥ A HH _ | LIC72431 ≥ A HH _ | 3 |  |  |  |  | X | X |  |  | 2
FCV72616 | 2000-F72-PID-PR-10007 | F72TK424 Acid FCV | DETAIL 1 | FC | X | X |  |  | CT1 | LI72612 ≥ A HH _ | F72TK424 Level HH | 3 |  |  |  |  | X | X |  | Supervisor level required for mode change and actuation | 2
FCV72632 | 2000-F72-PID-PR-10011 | F72PK405 Cooling Water | DETAIL 1 | FO | X | X | [14 empty] | 2

## 9. Drives
KCGM GROWTH PROJECT
DRIVES
Interlocks
Tag Name | P&ID | Name | Drive Type | Speed Min | Speed Max | Speed Units | SP Lower Limit | SP Upper Limit | Current Max | Manual | Auto | Start Condition (Auto Mode) | Stop Condition (Auto Mode) | # | Description (Unhealthy Interlocks) | Delay On | Delay Off | Start Permissive | Process | Critical | Hardwired to Drive | Bypass | Reset Required | Comments | Rev
F72-BW-412 | 2000-F72-PID-PR-10001 | LIME DELIVERY BLOWER | VSD | 0 | 100 | % | 40 | 100 | 119 | X | [14 empty] | 2
[14 empty] | 1 | F72-BW-412 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F72-BW-412 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-BW-412 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-BW-412 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-BW-412 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F72-BW-412 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F72-BW-412 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F72-AT-411 | 2000-F72-PID-PR-10001 | LIME SILO 1 ACTIVATOR | DOL | [5 empty] | 4.2 | X | X | 72AT411 T1 Running _ 72AT411 T2 Elapses _ | 72AT411 T1 Elapses _ | [11 empty] | 2
[14 empty] | 1 | F72-AT-411 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-AT-411 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-AT-411 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-AT-411 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-AT-411 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-AT-411 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-AT-411 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | LI72401 ≤ A LL _ | 5 |  |  | X |  |  | X |  | Lime Silo level transmitter | C
[14 empty] | 9 | LSL72437 Active | 3 |  |  | X |  |  | X |  | Lime Silo level switch | C
[14 empty] | 10 | F72-VR-411 Not Running | 5 |  |  | X |  |  | X |  | Rotary valve | C
F72-VR-411 | 2000-F72-PID-PR-10001 | LIME SILO 1 ROTARY VALVE | VSD | 0 | 100 | % | 40 | 100 | 1.66 | X | X | F72-SEQ-0104 | F72-SEQ-0105 | [11 empty] | C
[14 empty] | 1 | F72-VR-411 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-VR-411 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-VR-411 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-VR-411 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-VR-411 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-VR-411 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-VR-411 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | SAL72438 Active AND F72-VR-411 Running | 3 |  |  | X |  |  | X |  | Rotary valve underspeed | C
[14 empty] | 9 | F72-FS-411 Not Running | 5 |  |  | X |  |  | X |  | Screw feeder | C
[14 empty] | 10 | F72-FN-411 Not Running | 5 |  |  | X |  |  | X |  | Wet scrubber fan | C
F72-FS-411 | 2000-F72-PID-PR-10001 | LIME SILO 1 SCREW FEEDER | DOL | [5 empty] | 9.83 | X | X | F72-SEQ-0104 | F72-SEQ-0105 | [11 empty] | C
[14 empty] | 1 | F72-FS-411 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-FS-411 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-FS-411 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-FS-411 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-FS-411 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-FS-411 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-FS-411 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | SAL72403 Active AND F72-FS-411 Running | 3 |  |  | X |  |  | X |  | Screw feeder underspeed | C
[14 empty] | 9 | F72-FV-411 Not Running | 5 |  |  | X |  |  | X |  | Vibrating conveyor | C
F72-FV-411 | 2000-F72-PID-PR-10001 | LIME SILO 1 VIBRATING CONVEYOR | DOL | [5 empty] | 8.54 | X | X | F72-SEQ-0104 | F72-SEQ-0105 | [11 empty] | C
[14 empty] | 1 | F72-FV-411 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-FV-411 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-FV-411 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-FV-411 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-FV-411 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-FV-411 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-FV-411 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | LSH72405 Active | 3 |  |  | X |  |  | X |  |  | C
[14 empty] | 9 | TIC72412 ≥ A HH _ | 5 |  |  | X |  |  | X |  | Slaked lime discharge hopper 1 temperature | 1
[14 empty] | 12 | F72-MB-411 Not Running | 5 |  |  | X |  |  | X |  | Slaking mill | C
[14 empty] | 13 | (LIC72411 ≤ A LL OR F72-AG-658 Not Running) AND _ F72-SEQ-0106 = Not Running | 35 |  |  | X |  |  | X |  | Lime slaking hopper level or hopper agitator stopped Sequence held and failed to conduct a controlled stop due to a low low hopper level or agitator not running. See F72-SEQ-0106 for initiating conditions. | 2
[14 empty] | 14 | LIC72411 ≥ A HH AND F72-SEQ-0106 = Not Running _ | 35 |  |  | X |  |  | X |  | Lime slaking hopper level Sequence held and failed to conduct a controlled stop due to a high high hopper level. See F72-SEQ-0106 for initiating conditions. | 2
[14 empty] | 15 | TIC72412 ≤ A Lo AND F72-SEQ-0106 = Hold/Paused _ | 10 |  |  | X |  |  | X |  | Sequence held and failed to conduct a controlled stop due to a low low hopper temperature. See F72-SEQ-0106 for initiating conditions. | 1
[14 empty] | 16 | FIC72407 ≤ A LL _ | 30 |  |  | X |  |  | X |  | Prewetter water low low flowrate | 1
F72-MB-411 | 2000-F72-PID-PR-10001 | LIME SLAKING MILL 1 | VSD | 0 | 100 | % | 95 | 100 | 411 | X | X | F72-SEQ-0104 | F72-SEQ-0105 | [11 empty] | C
[14 empty] | 1 | F72-MB-411 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-MB-411 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-MB-411 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-MB-411 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-MB-411 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-MB-411 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-MB-411 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | Vertical Position Fault | 3 |  |  | X |  |  | X |  | Logic: ZS72454A OR ZS72454B Active | 0
[14 empty] | 9 | Horizontal Position Fault | 3 |  |  | X |  |  | X |  | Logic: ZS72507A OR ZS72507B Active | 0
[14 empty] | 10 | F72LU411 T3A Alarm _ | 172800 |  |  | X |  |  | X |  | Grease fail alarm active for >= 48 hours | 1
[14 empty] | 11 | LSL72456 Active | 172800 |  |  | X |  |  | X |  | Grease level low for >= 48 hours | 1
F72-AG-658 | 2000-F72-PID-PR-10001 | SLAKED LIME DISCHARGE HOPPER 1 AGITATOR | DOL | [5 empty] | 1.66 | X | X | F72-SEQ-0104 | F72-SEQ-0105 | [11 empty] | C
[14 empty] | 1 | F72-AG-658 Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F72-AG-658 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F72-AG-658 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F72-AG-658 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F72-AG-658 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F72-AG-658 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F72-AG-658 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LIC72411 ≤ A Lo _ | 5 |  |  | X |  |  | X |  | Lime slaking hopper level | C
[14 empty] | 9 | XV72413 Not Closed | 5 |  |  | X |  |  | X |  | Lime slaking hopper drain valve | 1
F72-PP-658 | 2000-F72-PID-PR-10001 | SLAKED LIME TRANSFER PUMP 1 | VSD | 0 | 100 | % | 40 | 100 | 51.4 | X | X | F72-SEQ-0104 | F72-SEQ-0105 | [11 empty] | C
[14 empty] | 1 | F72-PP-658 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-658 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-658 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-658 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-658 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-658 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-658 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | SV72492 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland Water Valve in auto or open | C
[14 empty] | 9 | FSL72493 Inactive And F72-PP-658 Running | 10 |  |  | X |  |  |  |  | Gland Water flow switch | C
[14 empty] | 10 | LIC72411 ≤ A LL _ | 5 |  |  | X |  |  | X |  | Lime slaking hopper level | C
[14 empty] | 11 | XV72413 Not Closed | 5 |  |  | X |  |  | X |  | Lime slaking hopper drain valve | 1
[14 empty] | 12 | PI72490 ≥ A HH AND F72-SEQ-0106 = Not Running _ | 35 |  |  | X |  |  | X |  | Cyclone pressure Sequence held and failed to conduct a controlled stop due to a high high cyclone discharge pump pressure. See F72-SEQ-0106 for initiating conditions. | 2
[14 empty] | 13 | LIC72439 ≥ A HH AND F72-SEQ-0106 = Not Running _ | 35 |  |  | X |  |  | X |  | MOL Tank Sequence held and failed to conduct a controlled stop due to a high high MOL tank level. See F72-SEQ-0106 for initiating conditions. | 2
[14 empty] | 14 | Discharge Valves Closed | 5 |  |  | X |  |  | X |  | Logic: XV72458, XV72459 AND XV72460 = Closed | C
F72-FN-411 | 2000-F72-PID-PR-10001 | SLAKED LIME WET SCRUBBER 1 FAN | DOL | [5 empty] | 7.54 | X | X | F72-SEQ-0104 | F72-SEQ-0105 | [11 empty] | C
[14 empty] | 1 | F72-FN-411 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F72-FN-411 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-FN-411 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-FN-411 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-FN-411 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F72-FN-411 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F72-FN-411 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | FSL72506 Active | 3 |  |  | X |  |  | X |  | Slaked lime wet scrubber feed water flow | C
F72-LU-411 | 2000-F72-PID-PR-10001 | LIME SLAKING MILL 1 GREASE PUMP | DOL | [6 empty] | X | X | F72LU411 T1 Elapsed OR _ | ZS72455 Rising Edge OR | [10 empty] | Start/stop via HS72508STT (see Digital Output tab) | C
[12 empty] | F72LU411 T2 Elapsed _ | F72LU411 T3 Elapsed _ | 1 | F72-LU-411 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-LU-411 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-LU-411 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-LU-411 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-LU-411 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-LU-411 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-LU-411 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F72MB411S1.PV > 0.9*72MB411SC.MV | 0 |  | X |  |  |  | X |  | Mill speed feedback greater than 90% of setpoint speed | 1
F72-AT-412 | 2000-F72-PID-PR-10002 | LIME SILO 2 ACTIVATOR | DOL | [5 empty] | 4.2 | X | X | 72AT412 T1 Running _ 72AT412 T2 Elapses _ | 72AT412 T1 Elapses _ | [11 empty] | 2
[14 empty] | 1 | F72-AT-412 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-AT-412 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-AT-412 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-AT-412 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-AT-412 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-AT-412 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-AT-412 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | LI72421 ≤ A LL _ | 5 |  |  | X |  |  | X |  | Lime Silo level transmitter | C
[14 empty] | 9 | LSL72435 Active | 3 |  |  | X |  |  | X |  | Lime Silo level switch | C
[14 empty] | 10 | F72-VR-412 Not Running | 5 |  |  | X |  |  | X |  | Rotary valve | C
F72-VR-412 | 2000-F72-PID-PR-10002 | LIME SILO 2 ROTARY VALVE | VSD | 0 | 100 | % | 40 | 100 | 1.66 | X | X | F72-SEQ-0107 | F72-SEQ-0108 | [11 empty] | C
[14 empty] | 1 | F72-VR-412 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-VR-412 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-VR-412 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-VR-412 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-VR-412 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-VR-412 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-VR-412 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | SAL72436 Active AND F72-VR-412 Running | 3 |  |  | X |  |  | X |  | Rotary valve underspeed | C
[14 empty] | 9 | F72-FS-412 Not Running | 5 |  |  | X |  |  | X |  | Screw feeder | C
[14 empty] | 10 | F72-FN-412 Not Running | 5 |  |  | X |  |  | X |  | Wet scrubber fan | C
F72-FS-412 | 2000-F72-PID-PR-10002 | LIME SILO 2 SCREW FEEDER | DOL | [5 empty] | 9.83 | X | X | F72-SEQ-0107 | F72-SEQ-0108 | [11 empty] | C
[14 empty] | 1 | F72-FS-412 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-FS-412 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-FS-412 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-FS-412 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-FS-412 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-FS-412 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-FS-412 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | SAL72423 Active AND F72-FS-412 Running | 3 |  |  | X |  |  | X |  | Screw feeder underspeed | C
[14 empty] | 9 | F72-FV-412 Not Running | 5 |  |  | X |  |  | X |  | Vibrating conveyor | C
F72-FV-412 | 2000-F72-PID-PR-10002 | LIME SILO 2 VIBRATING CONVEYOR | DOL | [5 empty] | 8.54 | X | X | F72-SEQ-0107 | F72-SEQ-0108 | [11 empty] | A
[14 empty] | 1 | F72-FV-412 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-FV-412 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-FV-412 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-FV-412 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-FV-412 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-FV-412 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-FV-412 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | LSH72425 Active | 3 |  |  | X |  |  | X |  |  | C
[14 empty] | 9 | TIC72432 ≥ A HH _ | 5 |  |  | X |  |  | X |  | Slaked lime discharge hopper 2 temperature | 1
[14 empty] | 10 | F72-MB-412 Not Running | 5 |  |  | X |  |  | X |  | Slaking mill | C
[14 empty] | 11 | (LIC72431 ≤ A LL OR F72-AG-659 Not Running) AND _ F72-SEQ-0109 = Not Running | 35 |  |  | X |  |  | X |  | Lime slaking hopper level or hopper agitator stopped Sequence held and failed to conduct a controlled stop due to a low low hopper level or agitator not running. See F72-SEQ-0109 for initiating conditions. | 2
[14 empty] | 12 | LIC72431 ≥ A HH AND F72-SEQ-0109 = Not Running _ | 35 |  |  | X |  |  | X |  | Lime slaking hopper level Sequence held and failed to conduct a controlled stop due to a high high hopper level. See F72-SEQ-0109 for initiating conditions. | 2
[14 empty] | 13 | TIC72432 ≤ A Lo AND F72-SEQ-0109 = Hold/Paused _ | 10 |  |  | X |  |  | X |  | Sequence held and failed to conduct a controlled stop due to a low low hopper temperature. See F72-SEQ-0109 for initiating conditions. | 1
[14 empty] | 14 | FIC72427 ≤ A LL _ | 30 |  |  | X |  |  | X |  | Prewetter water low low flowrate | 1
[14 empty] | 15 | YY72520 Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to 72-MB-411 start | 2
F72-MB-412 | 2000-F72-PID-PR-10002 | LIME SLAKING MILL 2 | VSD | 0 | 100 | % | 95 | 100 | 411 | X | X | F72-SEQ-0107 | F72-SEQ-0108 | [11 empty] | C
[14 empty] | 1 | F72-MB-412 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-MB-412 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-MB-412 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-MB-412 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-MB-412 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-MB-412 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-MB-412 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | Vertical Position Fault | 3 |  |  | X |  |  | X |  | Logic: ZS72478A OR ZS72478B Active | 0
[14 empty] | 9 | Horizontal Position Fault | 3 |  |  | X |  |  | X |  | Logic: ZS72519A OR ZS72519B Active | 0
[14 empty] | 10 | F72-LU-412 Healthy | 0 |  | X |  |  |  | X |  | Healthy if: • F72LU412 T3A Alarm for <= 48 hours OR not in alarm AND _ • LSL72479 Active for <= 48 hours OR LSL72479 inactive | 1
[14 empty] | 10 | F72LU412 T3A Alarm _ | 172800 |  |  | X |  |  | X |  | Grease fail alarm active for >= 48 hours | 2
[14 empty] | 11 | LSL72479 Active | 172800 |  |  | X |  |  | X |  | Grease level low for >= 48 hours | 2
[14 empty] | 12 | YY72521 Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to 72-MB-412 start | 2
F72-AG-659 | 2000-F72-PID-PR-10002 | SLAKED LIME DISCHARGE HOPPER 2 AGITATOR | DOL | [5 empty] | 1.66 | X | X | F72-SEQ-0107 | F72-SEQ-0108 | [11 empty] | C
[14 empty] | 1 | F72-AG-659 Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F72-AG-659 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F72-AG-659 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F72-AG-659 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F72-AG-659 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F72-AG-659 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F72-AG-659 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LIC72431 ≤ A Lo _ | 5 |  |  | X |  |  | X |  | Lime slaking hopper level | C
[14 empty] | 9 | XV72415 Not Closed | 5 |  |  | X |  |  | X |  | Lime slaking hopper drain valve | 1
F72-PP-659 | 2000-F72-PID-PR-10002 | SLAKED LIME TRANSFER PUMP 2 | VSD | 0 | 100 | % | 40 | 100 | 51.4 | X | X | F72-SEQ-0107 | F72-SEQ-0108 | [11 empty] | A
[14 empty] | 1 | F72-PP-659 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-659 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-659 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-659 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-659 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-659 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-659 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | SV72495 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland Water Valve in auto or open | C
[14 empty] | 9 | FSL72496 Inactive And F72-PP-659 Running | 10 |  |  | X |  |  |  |  | Gland Water flow switch | C
[14 empty] | 10 | LIC72431 ≤ A LL _ | 5 |  |  | X |  |  | X |  | Lime slaking hopper level | C
[14 empty] | 11 | XV72415 Not Closed | 5 |  |  | X |  |  | X |  | Lime slaking hopper drain valve | 1
[14 empty] | 12 | PI72491 ≥ A HH AND F72-SEQ-0109 = Not Running _ | 35 |  |  | X |  |  | X |  | Cyclone pressure Sequence held and failed to conduct a controlled stop due to a high high cyclone discharge pump pressure. See F72-SEQ-0109 for initiating conditions. | 2
[14 empty] | 13 | LIC72439 ≥ A HH AND F72-SEQ-0109 = Not Running _ | 35 |  |  | X |  |  | X |  | MOL Tank Sequence held and failed to conduct a controlled stop due to a high high MOL tank level. See F72-SEQ-0109 for initiating conditions. | 2
[14 empty] | 14 | Discharge Valves Closed | 5 |  |  | X |  |  | X |  | Logic: XV72467, XV72468 AND XV72469 = Closed | C
F72-FN-412 | 2000-F72-PID-PR-10002 | SLAKED LIME WET SCRUBBER 2 FAN | DOL | [5 empty] | 7.54 | X | X | F72-SEQ-0107 | F72-SEQ-0108
[14 empty] | 1 | F72-FN-412 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F72-FN-412 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-FN-412 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-FN-412 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-FN-412 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F72-FN-412 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F72-FN-412 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | FSL72518 Active | 3 |  |  | X |  |  | X |  | Slaked lime wet scrubber feed water flow | C
F72-LU-412 | 2000-F72-PID-PR-10002 | LIME SLAKING MILL 2 GREASE PUMP | DOL | [6 empty] | X | X | F72LU412 T1 Elapsed OR _ | ZS72477 Rising Edge OR | [10 empty] | Start/stop via HS72509STT (see Digital Output tab) | C
[12 empty] | F72LU412 T2 Elapsed _ | F72LU412 T3 Elapsed _ | 1 | F72-LU-412 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-LU-412 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-LU-412 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-LU-412 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-LU-412 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-LU-412 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-LU-412 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F72MB412S1.PV > 0.9*72MB412SC.MV | 0 |  | X |  |  |  | X |  | Mill speed feedback greater than 90% of setpoint speed | 1
F72-PS-419 | 2000-F72-PID-PR-10003 | MILK OF LIME AREA SUMP PUMP 1 | DOL SP | [5 empty] | 51.4 | X | X | LI72461 ≥ A Hi _ | LI72461 ≤ P LL _ | [10 empty] | HAZOP 350 | 1
[14 empty] | 1 | F72-PS-419 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PS-419 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PS-419 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PS-419 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PS-419 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PS-419 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PS-419 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F72-PS-466 | 2000-F72-PID-PR-10003 | MILK OF LIME AREA SUMP PUMP 2 | DOL SP | [5 empty] | 51.4 | X | X | LI72462 ≥ A Hi _ | LI72462 ≤ P LL _ | [10 empty] | HAZOP 350 | 1
[14 empty] | 1 | F72-PS-466 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PS-466 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PS-466 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PS-466 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PS-466 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PS-466 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PS-466 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F72-PS-467 | 2000-F72-PID-PR-10003 | MILK OF LIME AREA SUMP PUMP 3 | DOL SP | [5 empty] | 51.4 | X | X | LI72463 ≥ A Hi _ | LI72463 ≤ P LL _ | [10 empty] | HAZOP 350 | 1
[14 empty] | 1 | F72-PS-467 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PS-467 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PS-467 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PS-467 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PS-467 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PS-467 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PS-467 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F72-PP-656 | 2000-F72-PID-PR-10003 | LIME RINGMAIN PUMP 1 | DOL | [5 empty] | 181 | X | X | F72-SEQ-0101 | F72-SEQ-0102 | [11 empty] | C
[14 empty] | 1 | F72-PP-656 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-656 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-656 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-656 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-656 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-656 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-656 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | SV72470 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland Water Valve in auto or open | C
[14 empty] | 9 | FSL72471 Inactive AND F72-PP-656 Running | 30 |  |  | X |  |  | X |  | Gland Water flow switch | C
[14 empty] | 10 | XV72441 Closed AND XV72442 Closed | 3 |  |  | X |  |  | X |  | Suction valve and flush valve closed | 1
[14 empty] | 11 | XV72443 Open | 3 |  |  | X |  |  | X |  | Suction drain valve | C
[14 empty] | 12 | XV72452 Open | 3 |  |  | X |  |  | X |  | Discharge drain valve | C
[14 empty] | 13 | XV72444 Closed | 3 |  |  | X |  |  | X |  | Discharge valve | C
[14 empty] | 14 | XV72448 Open | 3 |  |  | X |  |  | X |  | Lime Ringmain Pump 2 discharge valve | C
[14 empty] | 15 | LIC72439 < A LL _ | 30 |  |  | X |  |  | X |  | Milk of Lime Tank level | C
[14 empty] | 16 | F72-PP-657 Running | 3 |  |  | X |  |  | X |  | One Lime Ringmain Pump running | C
F72-PP-657 | 2000-F72-PID-PR-10003 | LIME RINGMAIN PUMP 2 | DOL | [5 empty] | 181 | X | X | F72-SEQ-0101 | F72-SEQ-0102 | [11 empty] | C
[14 empty] | 1 | F72-PP-657 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-657 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-657 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-657 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-657 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-657 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-657 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | SV72474 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland Water Valve in auto or open | C
[14 empty] | 9 | FSL72475 Inactive And F72-PP-657 Running | 30 |  |  | X |  |  | X |  | Gland Water flow switch | C
[14 empty] | 10 | XV72445 Closed AND XV72446 Closed | 3 |  |  | X |  |  | X |  | Suction valve and flush valve closed | 1
[14 empty] | 11 | XV72447 Open | 3 |  |  | X |  |  | X |  | Suction drain valve | C
[14 empty] | 12 | XV72453 Open | 3 |  |  | X |  |  | X |  | Discharge drain valve | C
[14 empty] | 13 | XV72448 Closed | 3 |  |  | X |  |  | X |  | Discharge valve. Bypass if recirc via 72-2520-LS-RL1-200 is required. | C
[14 empty] | 14 | XV72444 Open | 3 |  |  | X |  |  | X |  | Lime Ringmain Pump 1 discharge valve | C
[14 empty] | 15 | LIC72439 < A LL _ | 30 |  |  | X |  |  | X |  | Milk of Lime Tank level | C
[14 empty] | 16 | F72-PP-656 Running | 3 |  |  | X |  |  | X |  | One Lime Ringmain Pump running. Bypass if recirc via 72-2520-LS-RL1-200 is required. | C
F72-AG-467 | 2000-F72-PID-PR-10003 | MILK OF LIME TANK AGITATOR | DOL | [5 empty] | 51.4 | X | X | F72-SEQ-0101 | [12 empty] | 1
[14 empty] | 1 | F72-AG-467 Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F72-AG-467 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F72-AG-467 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F72-AG-467 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F72-AG-467 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F72-AG-467 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F72-AG-467 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LIC72439 < A Lo _ | 30 |  |  | X |  |  | X |  | Milk of Lime Tank level | C
F72-PP-675 | 2000-F72-PID-PR-10005 | CYANIDE RINGMAIN PUMP 1 | DOL | [5 empty] | 39 | X | [14 empty] | C
[14 empty] | 1 | F72-PP-675 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-675 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-675 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-675 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-675 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-675 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-675 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | XV72536 AND XV72537 Closed | 3 |  |  | X |  |  | X |  | Suction valves closed | C
[14 empty] | 9 | XV72538 AND XV72539 Closed | 3 |  |  | X |  |  | X |  | Discharge (recirc) valves closed | C
[14 empty] | 10 | PI72552 > A HH _ | 30 |  |  | X |  |  | X |  | Discharge pressure | C
[14 empty] | 11 | LI72531 < A LL AND XV72536 Opened _ | 3 |  |  | X |  |  | X |  | Cyanide Storage Tank 1 level | C
[14 empty] | 12 | LI72535 < A LL AND XV72537 Opened _ | 3 |  |  | X |  |  | X |  | Cyanide Storage Tank 2 level | C
[14 empty] | 13 | F72-PP-676 Running | 3 |  |  | X |  |  | X |  | One Cyanide Ringmain Pump running | C
F72-PP-676 | 2000-F72-PID-PR-10005 | CYANIDE RINGMAIN PUMP 2 | DOL | [5 empty] | 39 | X | [14 empty] | C
[14 empty] | 1 | F72-PP-676 Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F72-PP-676 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F72-PP-676 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F72-PP-676 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F72-PP-676 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F72-PP-676 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F72-PP-676 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | XV72536 AND XV72537 Closed | 3 |  |  | X |  |  | X |  | Suction valves closed | C
[14 empty] | 9 | XV72538 AND XV72539 Closed | 3 |  |  | X |  |  | X |  | Discharge (recirc) valves closed | C
[14 empty] | 10 | PI72552 > A HH _ | 30 |  |  | X |  |  | X |  | Discharge pressure | C
[14 empty] | 11 | LI72531 < A LL AND XV72536 Opened _ | 3 |  |  | X |  |  | X |  | Cyanide Storage Tank 1 level | C
[14 empty] | 12 | LI72535 < A LL AND XV72537 Opened _ | 3 |  |  | X |  |  | X |  | Cyanide Storage Tank 2 level | C
[14 empty] | 13 | F72-PP-675 Running | 3 |  |  | X |  |  | X |  | One Cyanide Ringmain Pump running | C
F72-PS-423 | 2000-F72-PID-PR-10005 | CYANIDE AREA SUMP PUMP | DOL SP | [5 empty] | 54 | [14 empty] | Local only | 0
[14 empty] | 1 | F72-PS-423 Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F72-PS-423 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F72-PS-423 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F72-PS-423 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F72-PS-423 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F72-PS-423 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F72-PS-423 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI72581 ≤ P LL _ | 5 |  |  |  | X |  |  |  | Critical to enforce an auto stop in local mode. Alarm not required. | 0
F72-PP-673 | 2000-F72-PID-PR-10006 | CAUSTIC RINGMAIN PUMP 1 | DOL | [5 empty] | 26.1 | X | [14 empty] | C
[14 empty] | 1 | F72-PP-673 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-673 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-673 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-673 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-673 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-673 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-673 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | XV72596 Closed | 3 |  |  | X |  |  | X |  | Common suction valve | C
[14 empty] | 9 | PI72595 > A HH _ | 30 |  |  | X |  |  | X |  | Discharge pressure | C
[14 empty] | 10 | LI72591 ≤ A LL _ | 5 |  |  | X |  |  | X |  | Caustic Storage Tank level | C
[14 empty] | 11 | F72-PP-674 Running | 3 |  |  | X |  |  | X |  | One Caustic Ringmain Pump running | C
F72-PP-674 | 2000-F72-PID-PR-10006 | CAUSTIC RINGMAIN PUMP 2 | DOL | [5 empty] | 26.1 | X | [14 empty] | C
[14 empty] | 1 | F72-PP-674 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-674 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-674 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-674 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-674 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-674 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-674 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | XV72596 Closed | 3 |  |  | X |  |  | X |  | Common suction valve | C
[14 empty] | 9 | PI72595 > A HH _ | 30 |  |  | X |  |  | X |  | Discharge pressure | C
[14 empty] | 10 | LI72591 ≤ A LL _ | 5 |  |  | X |  |  | X |  | Caustic Storage Tank level | C
[14 empty] | 11 | F72-PP-673 Running | 3 |  |  | X |  |  | X |  | One Caustic Ringmain Pump running | C
F72-PS-424 | 2000-F72-PID-PR-10006 | CAUSTIC AREA SUMP PUMP | DOL SP | [5 empty] | 51.4 | [14 empty] | Local only | 0
[14 empty] | 1 | F72-PS-424 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PS-424 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PS-424 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PS-424 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PS-424 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PS-424 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PS-424 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | LI72599 ≤ P LL _ | 5 |  |  |  | X |  |  |  | Critical to enforce an auto stop in local mode. Alarm not required. | 0
F72-HT-491 | 2000-F72-PID-PR-10006 | CAUSTIC STORAGE TANK IMMERSION HEATER | FE | [5 empty] | 181 | X | X | TI72592 < P Lo _ | TI72592 > P Hi _ | [11 empty] | C
[14 empty] | 1 | F72-HT-491 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F72-HT-491 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-HT-491 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-HT-491 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-HT-491 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F72-HT-491 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F72-HT-491 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | LI72591 < A LL _ | 5 |  |  | X |  |  | X |  | Caustic Storage Tank level | C
[14 empty] | 9 | TI72592 > A HH _ | 5 |  |  | X |  |  | X |  | Caustic Storage Tank temperature | 0
[14 empty] | 10 | F72-PP-673 AND F72-PP-674 Not Running | 5 |  |  | X |  |  | X |  | Ringmain pumps not running | 1
F72-PP-683 | 2000-F72-PID-PR-10007 | ACID DOSING PUMP 1 | DOL | [5 empty] | 13.4 | X | X | F72-SEQ-0103 | F72-SEQ-0103 | [10 empty] | Pump to start/stop as per existing logic. Refer to SP2 BF tie in list | 1
[14 empty] | 1 | F72-PP-683 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-683 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-683 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-683 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-683 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-683 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-683 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | PI72611 > A HH _ | 3 |  |  | X |  |  | X |  | Discharge pressure | C
[14 empty] | 9 | FI72610 < A LL AND F72-PP-683 Running _ | 10 |  |  | X |  |  | X |  | Discharge flow | 1
[14 empty] | 10 | Discharge Valves Closed | 10 |  |  | X |  |  | X |  | Logic: KV65705, KV65805 AND FCV72616 (<5%) = Closed | 2
[14 empty] | 11 | LI72602 < A LL _ | 3 |  |  | X |  |  | X |  | Acid Storage Tank | C
[14 empty] | 12 | F72-PP-684 Running | 3 |  |  | X |  |  | X |  | One Acid Dosing Pump running | C
[14 empty] | 13 | XV72603 Closed | 5 |  |  | X |  |  | X |  | Acid Tank Outlet / Pump suction valve closed | 0
F72-PP-684 | 2000-F72-PID-PR-10007 | ACID DOSING PUMP 2 | DOL | [5 empty] | 13.4 | X | X | F72-SEQ-0103 | F72-SEQ-0103 | [10 empty] | Pump to start/stop as per existing logic. Refer to SP2 BF tie in list | 1
[14 empty] | 1 | F72-PP-684 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-684 Fail to Start / Stop | 0 |  |  |  | X |  |  |  | Turn off Acid Dosing Pumps in auto if all discharge valves are not in fully open position. | C
[14 empty] | 3 | F72-PP-684 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-684 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-684 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-684 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-684 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | PI72611 > A HH _ | 3 |  |  | X |  |  | X |  | Discharge pressure | C
[14 empty] | 9 | FI72610 < A LL AND F72-PP-684 Running _ | 10 |  |  | X |  |  | X |  | Discharge flow | 1
[14 empty] | 10 | Discharge Valves Closed | 10 |  |  | X |  |  | X |  | Logic: KV65705, KV65805 AND FCV72616 (<5%) = Closed | 2
[14 empty] | 11 | LI72602 < A LL _ | 3 |  |  | X |  |  | X |  | Acid Storage Tank | C
[14 empty] | 12 | F72-PP-683 Running | 3 |  |  | X |  |  | X |  | One Acid Dosing Pump running | C
[14 empty] | 13 | XV72603 Closed | 5 |  |  | X |  |  | X |  | Acid Tank Outlet / Pump suction valve closed | 0
F72-PP-424 | 2000-F72-PID-PR-10007 | CIL4 DILUTED ACID DOSING PUMP | DOL | [5 empty] | 26.1 | X | X | F22-SEQ-0002 OR | F22-SEQ-0002 OR | [11 empty] | C
[12 empty] | F72-SEQ-0103 | F72-SEQ-0103 | 1 | F72-PP-424 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-424 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-424 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-424 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-424 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-424 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-424 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | Discharge Valves Closed | 10 |  |  | X |  |  | X |  | Logic: (XV22024 Closed OR XV72639 Closed) AND XV72637 Closed | 1
[14 empty] | 9 | LI72612 < A LL _ | 5 |  |  | X |  |  | X |  | CIL4 Acid Dilution Tank | C
[14 empty] | 10 | PI72638 > A HH _ | 10 |  |  | X |  |  | X |  | Discharge pressure | 1
F72-PS-428 | 2000-F72-PID-PR-10007 | HYDROCHLORIC ACID AREA SUMP PUMP | See Comment | [20 empty] | Configure SV72617 to drive output Local only, utilising HS push buttons to start/stop pneumatic pump by opening/closing air supply solenoid valve. Logic: If HS72618A Active (rising-edge), start F72-PS-428 If HS72618B Active (rising-edge), stop F72-PS-428 Drive start = open SV72617 Drive stop = close SV72617 | 0
[14 empty] | 1 | LI72615 ≤ P LL _ | 5 |  |  |  | X |  |  |  | Critical to enforce an auto stop in local mode. Alarm not required. | 0
F72-PS-426 | 2000-F72-PID-PR-10015 | LEAD NITRATE AREA SUMP PUMP | See Comment | [20 empty] | Configure SV72712 to drive output Local only, utilising HS push buttons to start/stop pneumatic pump by opening/closing air supply solenoid valve. Logic: If HS72713A Active (rising-edge), start F72-PS-428 If HS72713B Active (rising-edge), stop F72-PS-428 Drive start = open SV72712 Drive stop = close SV72712 | 0
[14 empty] | 1 | LI72741 ≤ P LL _ | 5 |  |  |  | X |  |  |  | Critical to enforce an auto stop in local mode. Alarm not required. | 0
F72-PP-698 | 2000-F72-PID-PR-10012 | ANTISCALANT DOSING PUMP 2 | FE | [6 empty] | X | X | F75-PW-481 OR F75-PW-482 OR F75-PW-483 Running | F75-PW-481 AND F75-PW-482 AND F75-PW-483 Stopped | [11 empty] | C
[14 empty] | 1 | LI72689 < A LL _ | 5 |  |  | X |  |  | X |  | IBC 2 | C
[14 empty] | 2 | FSL72681 Active And F72-PP-698 Running | 10 |  |  | X |  |  | X |  | F72-PP-698 Discharge low flow switch | 2
[14 empty] | 3 | Scheme Water Pumps Not Running | 30 |  |  | X |  |  | X |  | Logic: F75-PW-481 AND F72-PW-482 AND F72-PW-483 = Not Running | C
F72-PP-699 | 2000-F72-PID-PR-10012 | ANTISCALANT DOSING PUMP 3 | FE | [6 empty] | X | X | F22-PW-403 Running AND XV22021 Opened | F22-PW-403 Stopped AND XV22021 Closed | [11 empty] | C
[14 empty] | 1 | LI72689 < A LL _ | 5 |  |  | X |  |  | X |  | IBC 2 | C
[14 empty] | 2 | FSL72682 Active And F72-PP-699 Running | 10 |  |  | X |  |  | X |  | F72-PP-699 Discharge low flow switch | 2
[14 empty] | 3 | F22-PW-403 Not Running | 30 |  |  | X |  |  | X |  | CIL4 Carbon Eductor Pump | C
F72-PP-700 | 2000-F72-PID-PR-10012 | ANTISCALANT DOSING PUMP 4 | FE | [6 empty] | X | X | F22-PW-441 OR F22-PW-444 Running | F22-PW-441 AND F22-PW-444 Stopped | [11 empty] | C
[14 empty] | 1 | LI72689 < A LL _ | 5 |  |  | X |  |  | X |  | IBC 2 | C
[14 empty] | 2 | FSL72683 Active And F72-PP-700 Running | 10 |  |  | X |  |  | X |  | F72-PP-700 Discharge low flow switch | 2
[14 empty] | 3 | F22-PW-441/444 Not Running | 30 |  |  | X |  |  | X |  | CIL4 Elution Pump 1 & 2 | C
F72-PP-701 | 2000-F72-PID-PR-10012 | ANTISCALANT DOSING PUMP 5 | FE | [6 empty] | X | X | 65-PW-61 Running AND (KV65804 OR KV65704 Open) | 65-PW-61 Stopped OR (KV65804 AND KV65704 Closed) | [10 empty] | Carbon Transfer Water Pump (65-PW-61), KV65804 and KV65704 are brownfields pumps/valves. | C
[14 empty] | 1 | LI72690 < A LL _ | 5 |  |  | X |  |  | X |  | IBC 6 | C
[14 empty] | 2 | FSL72684 Active And F72-PP-701 Running | 10 |  |  | X |  |  | X |  | F72-PP-701 Discharge low flow switch | 2
[14 empty] | 3 | 65-PW-61 Not Running | 30 |  |  | X |  |  | X |  | Carbon Transfer Water Pump (65-PW-61) is a brownfields pump | C
F72-PP-702 | 2000-F72-PID-PR-10012 | ANTISCALANT DOSING PUMP 6 | FE | [6 empty] | X | X | 65-PW-61 Running AND (KV65816 OR KV65716 Open) | 65-PW-61 Stopped OR (KV65816 OR KV65716 Open) | [10 empty] | Carbon Transfer Water Pump (65-PW-61), KV65816 and KV65716 are brownfields pumps/valves. | C
[14 empty] | 1 | LI72690 < A LL _ | 5 |  |  | X |  |  | X |  | IBC 6 | C
[14 empty] | 2 | FSL72685 Active And F72-PP-702 Running | 10 |  |  | X |  |  | X |  | F72-PP-702 Discharge low flow switch | 2
[14 empty] | 3 | 65-PW-61 Not Running | 30 |  |  | X |  |  | X |  | Carbon Transfer Water Pump (65-PW-61) is a brownfields pump | C
F72-PP-703 | 2000-F72-PID-PR-10012 | ANTISCALANT DOSING PUMP 7 | FE | [6 empty] | X | X | 65-PP-61 Running | 65-PP-61 Stopped | [10 empty] | Elution Circuit No 1 Water Pump (65-PP-61) is a brownfields pump | C
[14 empty] | 1 | LI72691 < A LL _ | 5 |  |  | X |  |  | X |  | IBC 8 | C
[14 empty] | 2 | FSL72686 Active And F72-PP-703 Running | 10 |  |  | X |  |  | X |  | F72-PP-703 Discharge low flow switch | 2
[14 empty] | 3 | F65-PP-61 Not Running | 30 |  |  | X |  |  | X |  | Elution Circuit No 1 Water Pump (65-PP-61) is a brownfields pump | C
F72-PP-704 | 2000-F72-PID-PR-10012 | ANTISCALANT DOSING PUMP 8 | FE | [6 empty] | X | X | 65-PP-62 Running | 65-PP-62 Stopped | [10 empty] | Elution Circuit No 2 Water Pump (65-PP-62) is a brownfields pump | C
[14 empty] | 1 | LI72691 < A LL _ | 5 |  |  | X |  |  | X |  | IBC 8 | C
[14 empty] | 2 | FSL72687 Active And F72-PP-704 Running | 10 |  |  | X |  |  | X |  | F72-PP-704 Discharge low flow switch | 2
[14 empty] | 3 | 65-PP-62 Not Running | 30 |  |  | X |  |  | X |  | Elution Circuit No 2 Water Pump (65-PP-62) is a brownfields pump | C
F72-PP-705 | 2000-F72-PID-PR-10012 | ANTISCALANT DOSING PUMP 9 | FE | [6 empty] | X | X | 75-PW-83A OR B Running | 75-PW-83A AND B Stopped | [10 empty] | Circuit Water Pumps (75-PW-62A/B) are brownfields pumps | 2
[14 empty] | 1 | LI72692 < A LL _ | 5 |  |  | X |  |  | X |  | IBC 9 | C
[14 empty] | 2 | FSL72688 Active And F72-PP-705 Running | 10 |  |  | X |  |  | X |  | F72-PP-705 Discharge low flow switch | 2
[14 empty] | 3 | F75-PW-83A/B Not Running | 30 |  |  | X |  |  | X |  | F75-PW-83A/B are brownfields pumps | 2
F72-PP-681 | 2000-F72-PID-PR-10015 | LEAD NITRATE DOSING PUMP 1 | VSD | 0 | 100 | % | 40 | 100 | 3.16 | X
[14 empty] | 1 | F72-PP-681 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-681 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-681 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-681 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-681 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-681 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-681 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | PI72731 ≥ A HH _ | 5 |  |  | X |  |  | X |  | Common discharge pressure | C
[14 empty] | 9 | LI72701 ≤ A LL _ | 5 |  |  | X |  |  | X |  | Lead Nitrate Storage Tank | C
[14 empty] | 10 | TSH72733 Active | 3 |  |  | X |  |  | X |  | Stator temperature | C
[14 empty] | 11 | F72-PP-682 Running | 3 |  |  | X |  |  | X |  | One Lead Nitrate Pump running | C
F72-PP-682 | 2000-F72-PID-PR-10015 | LEAD NITRATE DOSING PUMP 2 | VSD | 0 | 100 | % | 40 | 100 | 3.16 | X
[14 empty] | 1 | F72-PP-682 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-682 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-682 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-682 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-682 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-682 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-682 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | PI72731 ≥ A HH _ | 5 |  |  | X |  |  | X |  | Common discharge pressure | C
[14 empty] | 9 | LI72701 ≤ A LL _ | 5 |  |  | X |  |  | X |  | Lead Nitrate Storage Tank | C
[14 empty] | 10 | TSH72734 Active | 3 |  |  | X |  |  | X |  | Stator temperature | C
[14 empty] | 11 | F72-PP-681 Running | 3 |  |  | X |  |  | X |  | One Lead Nitrate Pump running | C
F72-PP-693 | 2000-F72-PID-PR-10016 | CONCENTRATE PRE-LEACH THICKENER FLOCCULANT DOSING PUMP | VSD | 0 | 100 | % | 40 | 100 | 3.16 | X
[14 empty] | 1 | F72-PP-693 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-693 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-693 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-693 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-693 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-693 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-693 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | LI72032 ≤ A LL _ | 5 |  |  | X |  |  | X |  | Flocculant Storage Tank | C
[14 empty] | 9 | NI30301 > A HH _ | 5 |  |  | X |  |  | X |  | Concentrate Pre-Leach Thickener Torque is brownfields | 1
[14 empty] | 10 | TSH72484 Active | 3 |  |  | X |  |  | X |  | Stator temperature | C
[14 empty] | 11 | Duty Flocc Pump Running | 3 |  |  | X |  |  | X |  | Logic: F72-PP-696 Running and F72PP693 selected on HS30616 One Flocc Pump running per discharge line | 1
F72-PP-696 | 2000-F72-PID-PR-10016 | THICKENERS STANDBY FLOCCULANT DOSING PUMP | VSD | 0 | 100 | % | 40 | 100 | 3.16 | X
[14 empty] | 1 | F72-PP-696 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-696 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-696 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-696 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-696 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-696 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-696 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | LI72032 ≤ A LL _ | 5 |  |  | X |  |  | X |  | Flocculant Storage Tank | C
[14 empty] | 9 | Thickener Torque Hi | 5 |  |  | X |  |  | X |  | Logic: (NI30301 > A HH and F72PP693 selected on HS30616) OR _ (NI30601 > A HH and F72PP694 selected on HS30616) _ | 1
[14 empty] | 10 | TSH72485 Active | 3 |  |  | X |  |  | X |  | Stator temperature | C
[14 empty] | 11 | Standby Flocc Pump Running | 3 |  |  | X |  |  | X |  | Logic: (F72-PP-693 Running AND F72-PP-693 selected on HS30616) OR (F72-PP-694 Running AND F72-PP-694 selected on HS30616) One Flocc Pump running per discharge line | 1
F72-PP-694 | 2000-F72-PID-PR-10016 | CONCENTRATE THICKENER FLOCCULANT DOSING PUMP | VSD | 0 | 100 | % | 40 | 100 | 3.16 | X
[14 empty] | 1 | F72-PP-694 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F72-PP-694 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 3 | F72-PP-694 Drive Fault | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 4 | F72-PP-694 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F72-PP-694 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F72-PP-694 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F72-PP-694 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | LI72032 ≤ A LL _ | 5 |  |  | X |  |  | X |  |  | C
[14 empty] | 9 | NI30601 > A HH _ | 5 |  |  | X |  |  | X |  | Concentrate Thickener Torque is brownfields | 1
[14 empty] | 10 | TSH72486 Active | 3 |  |  | X |  |  | X |  | Stator temperature | C
[14 empty] | 11 | Duty Flocc Pump Running | 3 |  |  | X |  |  | X |  | Logic: F72-PP-696 Running and F72PP694 selected on HS30616 One Flocc Pump running per discharge line | 1

## 11. Calculation
KCGM GROWTH PROJECT
CALCULATION
|  |  | Unit | Inputs |  |  |  | Operator Input | Calc. Value | Manual Input
Tag Name | P&ID | Description (Software Tag Only) |  | # | Tag | Unit | Description |  |  | Nom | Min | Max | Calculation | Comments | Rev
F72CALC10101 | 2000-F72-PID-PR-10015 | F72PP681/682 Flowrate SP |  | 1 | FIC72732.SV | m3/h | Pump Flowrate Setpoint |  | X | [5 empty] | 0
|  |  |  | 2 | WI30411.PV | t/h (dry) | Concentrate Pre-Leach Mass Rate | [7 empty] | A
|  |  |  | 3 4 |  | g/t % w/v | Nominal Lead Nitrate Dosage g/t Concentrate Pre-Leach Thickener Underflow Supplied Lead Nitrate Solution Strength | X X |  | 10000 40 | 0 0 | 15000 100 |  | Engineer level required to change setpoint | A C
F72CALC10104 | 2000-F72-PID-PR-10007 | F72TK424 Acid Fill |  | 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 | LI72612.PV LI172612_INIT F72TK424_TOP F72TK424_BOT F72TK424_RAD F72TK424_HI_VOL F72TK424_INIT_VOL RESIDUAL_ACID_CON TARGET_ACID_CON ACID_STORAGE_CON ACID_STORAGE_SG CONC_ACID_REQ WATER_FILL_TARGET ACID_TRNSFR_REQ | % % % m m m m3 m3 %w/v %w/v %w/w t/m3 m3 % m3 % | F72TK424 Acid Dilution F72TK424 Acid Dilution Initial F72TK424 100% Level F72TK424 0% Level F72TK424 Radius F72TK424 Init Volume F72TK424 Residual Acid Conc. F72TK424 Acid Conc. Target F72TK435 Acid Storage Conc. F72TK435 Acid Storage SG F72TK424 Acid Required F72TK424 Water Fill Target F22PR411 Acid Required | [5 empty] | F72TK424_HI_VOL = PI()*(F72TK424_RAD^2)*((((F72TK424_TOP- Calculate Dilution Tank volume at LI172612_INIT (initial level): F72TK424_INIT_VOL = PI()*(F72TK424_RAD^2)*((((F72TK424_TOP- F72TK424_BOT)/100)*LI172612_INIT)+F72TK424_BOT) Calculate the volume of concentrated acid required to achieve the target acid concentration: CONC_ACID_REQ =((F72TK424_HI_VOL*TARGET_ACID_CON)- (F72TK424_INIT_VOL*RESIDUAL_ACID_CON))/(ACID_STORAGE_CON*ACID_STORAGE_SG) Calculate the Water Fill target for use in the sequence: (PI()*F72TK424_RAD^2*F72TK424_BOT))/(F72TK424_HI_VOL- (PI()*F72TK424_RAD^2*F72TK424_BOT))) (PI()*F72TK424_RAD^2*F72TK424_BOT))/(F72TK424_HI_VOL- (PI()*F72TK424_RAD^2*F72TK424_BOT))) | Show F72CALC10104 inputs/outputs on graphic close to F72-SEQ- 0103 area LI172612_INIT is written during F72-SEQ-0103 calculation Distance from F72TK424 0 RL to 100% level Distance from F72TK424 0 RL to 0% level F72TK424 Radius RESIDUAL_ACID_CON is set to equal TARGET_ACID_CON during F72-SEQ-0103 CONC_ACID_REQ used in F72-SEQ-0103 WATER_FILL_TARGET used in F72-SEQ-0103 | C C C C C C C C C C C C C C C C
[8 empty] | X X X X X X X X | X X X X X | 3.25 0.15 1.75 | 0 0 0 | 3.5 3.5 3
[10 empty] | 3 3 32 1.16 | 0 0 0 0.8 | 6 6 100 1.4
[10 empty] | 18.00 | 0 | 30
F72CALC10105 | 2000-F72-PID-PR-10001 | F72PK402 Total Water Flow 1 |  | 1 2 3 | FIC72407.PV FIC72408.PV FNI7240X | m3/h m3/h m3/h | F72XM658 Prewetter Water F72HP411 Feed Water F72MB411 Total Water | [5 empty] | FIC72407.PV + FIC72408.PV = FNI7240X.PV |  | C C C
X
F72CALC10106 | 2000-F72-PID-PR-10002 | F72PK402 Total Water Flow 2 |  | 1 2 3 | FIC72427.PV FIC72428.PV FNI7242X | m3/h m3/h m3/h | F72XM659 Prewetter Water F72HP412 Feed Water F72MB412 Total Water | [5 empty] | FIC724027.PV + FIC72428.PV = FNI7242X.PV |  | C C C
X
F72CALC10008 | 2000-F72-PID-PR-10001 | F72MB411 Water Split |  | 1 2 3 4 5 6 7 8 9 10 11 | HS72407 F72MB411_RATIO F72MB411_TON F72MB411_DEN F72MB411_SOL_SG F72MB411_WATER_CO F72MB411_WATER_TH F72MB411_WATER_MH FIC72407.SV FIC72408.SV LIC72439.MV | - - t/h %w/w t/m3 - t/h m3/h m3/h m3/h m3/h | F72MB411 Water Controller F72MB411 Water Ratio Split F72MB411 Tonnage F72MB411 Overflow Density F72MB411 Raw Water SG F72MB411 Water Correction Factor F72MB411 Water Req F72MB411 Water Req F72XM658 Prewetter Water SV F72HP411 Feed Water SV F72TK467 MOL Level MV | [5 empty] | If 'MOL Level Control' is selected on HS72407: LIC72439.MV * F72MB411_RATIO = FIC72407.SV LIC72439.MV - FIC72407.SV = FIC72408.SV If 'Fixed Rate Control' is selected on HS72407: F72MB411_TON * (1 - 'F72MB411_DEN / 100) / ('F72MB411_DEN / 100) = F72MB411_WATER_TH (F72MB411_WATER_TH / F72MB411_SOL_SG) * F72MB411_WATER_CO = F72MB411_WATER_MH F72MB411_WATER_MH * F72MB411_RATIO = FIC72407.SV F72MB411_WATER_MH - FIC72407.SV = FIC72408.SV | Refer to HS72407 in Misc tab Prewetter & Hopper Water Split If 'MOL Level Control', function splits the LIC72439.MV between 2 controllers, FIC72407 and FIC72408, based on an operator input (F72MB411_RATIO) Correction factor to be adjusted during commissioning to achieve the slaked lime density target. Note, will vary with raw water temperature. If 'Fixed Rate Control', function splits the F72MB411_WATER_MH between 2 controllers, FIC72407 and FIC72408, based on an operator input (F72MB411_RATIO) Inputs and outputs of this calc need to be viewable by the CRO from a graphic | C C C C C C C C C C C
[8 empty] | X X X X X | X X X X | 0.73 16.6 20 1.07 1.42 | 0 13 0 0.8 0 | 1 20 100 1.2 10
F72CALC10009 | 2000-F72-PID-PR-10002 | F72MB412 Water Split |  | 1 2 3 | HS72427 F72MB412_RATIO F72MB412_TON | - - t/h | F72MB412 Water Controller F72MB412 Water Ratio Split F72MB412 Tonnage | [6 empty] | Refer to HS72427 in Misc tab Prewetter & Hopper Water Split | C C C
[8 empty] | X X |  | 0.73 16.6 | 0 13 | 1 20
|  |  |  | 4 5 6 7 8 9 10 11 | F72MB412_DEN F72MB412_SOL_SG F72MB412_WATER_CO F72MB412_WATER_TH F72MB412_WATER_MH FIC72427.SV FIC72428.SV LIC72439.MV | %w/w t/m3 - t/h m3/h m3/h m3/h m3/h | F72MB412 Overflow Density F72MB412 Raw Water SG F72MB412 Water Correction Factor F72MB412 Water Req F72MB412 Water Req F72XM659 Prewetter Water SV F72HP412 Feed Water SV F72TK467 MOL Level MV | X X X | X X X X | 20 1.07 1.42 | 0 0.8 0 | 100 1.2 10 | If 'MOL Level Control' is selected on HS72427: LIC72439.MV * F72MB412_RATIO = FIC72427.SV LIC72439.MV - FIC72427.SV = FIC72428.SV If 'Fixed Rate Control' is selected on HS72427: F72MB412_TON * (1 - 'F72MB412_DEN / 100) / ('F72MB412_DEN / 100) = F72MB412_WATER_TH (F72MB412_WATER_TH / F72MB412_SOL_SG) * F72MB412_WATER_CO = F72MB412_WATER_MH F72MB412_WATER_MH * F72MB412_RATIO = FIC72427.SV F72MB412_WATER_MH - FIC72427.SV = FIC72428.SV | If 'MOL Level Control', function splits the LIC72439.MV between 2 controllers, FIC72427 and FIC72428, based on an operator input (F72MB412_RATIO) Correction factor to be adjusted during commissioning to achieve the slaked lime density target. Note, will vary with raw water temperature. If 'Fixed Rate Control', function splits the F72MB412_WATER_MH between 2 controllers, FIC72427 and FIC72428, based on an operator input (F72MB412_RATIO) Inputs and outputs of this calc need to be viewable by the CRO from a graphic | C C C C C C C C
F72CALC10112 | 2000-F72-PID-PR-10005 | F72TK437/9 Level Differential |  | 1 2 3 | LI72531.PV LI72535.PV LDI7253X.PV | % % % | F72TK437 Cyanide Level F72TK439 Cyanide Level F72TK437/9 Cyanide Tank Level Differential | [5 empty] | abs(LI72531 - LI72535) = LDI1753X.PV | Level differential to monitor tank level balance HAZOP action | C C C
X
F72CALC10113 | 2000-F72-PID-PR-10001 | F72VR411 Underspeed Alarm |  | 1 2 3 4 | F72VR411_USR 72VR411_MAXRPM F72VR411_US F72VR411SC.SV | % RPM RPM % | F72VR411 Underspeed Percent F72VR411 50Hz RPM F72VR411 Underspeed SV F72VR411 Speed Setpoint | X X | X | 80 14 | 0 0 | 100 30 | 72VR411_MAXRPM / 100 * F72VR411.SV * (F72VR411_USR / 100) = F72VR411_US | Engineer level access Engineer level access | 1 1 1 1
F72CALC10114 | 2000-F72-PID-PR-10002 | F72VR412 Underspeed Alarm |  | 1 2 3 4 | F72VR412_USR 72VR412_MAXRPM F72VR412_US F72VR412SC.SV | % RPM RPM % | F72VR412 Underspeed Percent F72VR412 50Hz RPM F72VR412 Underspeed SV F72VR412 Speed Setpoint | X X | X | 80 14 | 0 0 | 100 30 | 72VR412_MAXRPM / 100 * F72VR412.SV * (F72VR412_USR / 100) = F72VR412_US | Engineer level access Engineer level access | 1 1 1 1
F72CALC10115 | 2000-F72-PID-PR-10001 | F72SI411 Lime Weight |  | 1 2 3 4 5 7 | LI72401_RNG_LO LI72401_RNG_HI F72SI411_CON_HT F72SI411_CON_B F72SI411_CON_T F72SI411_LIME_SG | m m m m m - | LI72401 0% Level LI72401 100% Level F72SI411 Cone Height F72SI411 Cone Bot Radius F72SI411 Cone Top Radius F72SI411 Lime Bulk SG | X X X X X X |  | 1.87 19.74 5.23 1.89 4.98 0.95 | 0 15 0 0 0 0 | 5 25 10 5 10 1.2 | LI72401_METRES = LI72401_RNG_LO + ( (LI72401_RNG_HI - LI72401_RNG_LO) / 100) * LI72401.PV F72SI411_COND = (100 / (LI72401_RNG_HI - LI72401_RNG_LO)) * (F72SI411_CON_HT - LI72401_RNG_LO) WI72401 = IF LI72401.PV<=F72SI411_COND: (PI()*(F72SI411_CON_B^2*LI72401_METRES+F72SI411_CON_B*(F72SI411_CON_T- F72SI411_CON_B)/F72SI411_CON_HT*LI72401_METRES^2+(F72SI411_CON_T- F72SI411CONB)^2/(3*F72SI411CONHT^2)*LI72401METRES^3))*F72SI411LIMESG | This is the total tank height minus the transmitter span range Estimated as the tank height Height of the conical portion only Bottom radius of the conical portion Top radius of the conical portion and cylindrical portion | 2 2 2 2 2 2
|  |  |  | 8 | LI72401.PV | % | F72SI411 Lime Silo 1 | [5 empty] | _ _ _ _ _ _ _ IF LI72401.PV>F72SI411_COND: (PI()*(F72SI411_CON_B^2*F72SI411_CON_HT+F72SI411_CON_B*(F72SI411_CON_T- F72SI411CONB)/F72SI411CONHT*F72SI411CONHT^2+(F72SI411CONT- |  | 2
|  |  |  | 9 10 11 | LI72401_METRES F72SI411_COND WI72401 | m m t | F72SI411 Lime Silo 1 F72SI411 Calc Condition F72SI411 Lime Weight |  | X X X |  |  |  | _ _ _ _ _ _ _ _ F72SI411_CON_B)^2/(3*F72SI411_CON_HT^2)*F72SI411_CON_HT^3) + PI()*F72SI411_CON_T^2*(LI72401_METRES-F72SI411_CON_HT)))*F72SI411_LIME_SG | % to metres calculation If statement condition (top of conical base) | 2 2 2
F72CALC10116 | 2000-F72-PID-PR-10002 | F72SI412 Lime Weight |  | 1 2 3 4 5 7 | LI72421_RNG_LO LI72421_RNG_HI F72SI412_CON_HT F72SI412_CON_B F72SI412_CON_T F72SI412_LIME_SG | m m m m m - | LI72421 0% Level LI72421 100% Level F72SI412 Cone Height F72SI412 Cone Bot Radius F72SI412 Cone Top Radius F72SI412 Lime Bulk SG | X X X X X X |  | 1.87 19.74 5.23 1.89 4.98 0.95 | 0 15 0 0 0 0 | 5 25 10 5 10 1.2 | LI72421_METRES = LI72421_RNG_LO + ( (LI72421_RNG_HI - LI72421_RNG_LO) / 100) * LI72421.PV F72SI412_COND = (100 / (LI72421_RNG_HI - LI72421_RNG_LO)) * (F72SI412_CON_HT - LI72421_RNG_LO) WI72421 = IF LI72421.PV<=F72SI412_COND: (PI()*(F72SI412_CON_B^2*LI72421_METRES+F72SI412_CON_B*(F72SI412_CON_T- F72SI412_CON_B)/F72SI412_CON_HT*LI72421_METRES^2+(F72SI412_CON_T- F72SI412CONB)^2/(3*F72SI412CONHT^2)*LI72421METRES^3))*F72SI412LIMESG | This is the total tank height minus the transmitter span range Estimated as the tank height Height of the conical portion only Bottom radius of the conical portion Top radius of the conical portion and cylindrical portion | 2 2 2 2 2 2
|  |  |  | 8 | LI72421.PV | % | F72SI412 Lime Silo 1 | [5 empty] | _ _ _ _ _ _ _ IF LI72421.PV>F72SI412_COND: (PI()*(F72SI412_CON_B^2*F72SI412_CON_HT+F72SI412_CON_B*(F72SI412_CON_T- F72SI412CONB)/F72SI412CONHT*F72SI412CONHT^2+(F72SI412CONT- |  | 2
|  |  |  | 9 10 11 | LI72421_METRES F72SI412_COND WI72421 | m m t | F72SI412 Lime Silo 1 F72SI412 Calc Condition F72SI412 Lime Weight |  | X X X |  |  |  | _ _ _ _ _ _ _ _ F72SI412_CON_B)^2/(3*F72SI412_CON_HT^2)*F72SI412_CON_HT^3) + PI()*F72SI412_CON_T^2*(LI72421_METRES-F72SI412_CON_HT)))*F72SI412_LIME_SG | % to metres calculation If statement condition (top of conical base) | 2 2 2
F72CALC10117 | 2000-F72-PID-PR-10007 | F72TK435 HCl Weight |  | 1 | WI72602 | t | F72TK435 HCl Weight |  | X | [5 empty] | 2
|  |  |  | 2 3 4 | F72TK435_DIA LI72602_RNG HCL_SG | m m | F72TK435 Diameter LI72602 Range HCl SG | X X X |  | 5.1 9.7 1.16 | 0 0 0.5 | 10 20 2 | WI72602 = pi * ((F72TK435_DIA / 2)^2) * (LI72602/100 * F72TK435_RNG) * HCL_SG |  | 2 2 2
|  |  |  | 5 | LI72602.PV | % | F72TK435 Acid Storage | [7 empty] | 2
F72CALC10118 | 2000-F72-PID-PR-10006 | F72TK435 NaOH Weight |  | 1 | WI72591 | t | F72TK435 NaOH Weight |  | X | [5 empty] | 2
|  |  |  | 2 3 4 | F72TK434_DIA LI72591_RNG NAOH_SG | m m | F72TK434 Diameter LI72591 Range NaOH SG | X X X |  | 6.68 7.485 1.5 | 0 0 0.5 | 10 20 2 | WI72591 = pi * ((F72TK434_DIA / 2)^2) * (LI72591/100 * F72TK434_RNG) * NAOH_SG |  | 2 2 2
|  |  |  | 5 | LI72591.PV | % | F72TK434 Caustic Level | [7 empty] | 2
F72CALC10119 | 2000-F72-PID-PR-10015 | F72TK438 Nitrate Weight |  | 1 | WI72701 | t | F72TK438 Nitrate Weight |  | X | [5 empty] | 2
|  |  |  | 2 3 4 | F72TK438_DIA LI72701_RNG LN_SG | m m | F72TK438 Diameter LI72701 Range Lead Nitrate SG | X X X |  | 6.68 8.425 1.17 | 0 0 0.5 | 10 20 2 | WI72701 = pi * ((F72TK438_DIA / 2)^2) * (LI72701/100 * F72TK438_RNG) * LN_SG |  | 2 2 2
|  |  |  | 5 | LI72701.PV | % | F72TK438 Nitrate Tank | [7 empty] | 2
F72CALC10120 | 2000-F72-PID-PR-10005 | F72TK437 Cyanide Weight |  | 1 | WI72531 | t | F72TK437 Cyanide Weight |  | X | [5 empty] | 2
|  |  |  | 2 3 4 | F72TK437_DIA LI72531_RNG CN_SG | m m | F72TK437 Diameter LI72531 Range Cyanide SG | X X X |  | 11.46 12.51 1.24 | 0 0 0.5 | 20 20 2 | WI72531 = pi * ((F72TK437_DIA / 2)^2) * (LI72531/100 * F72TK437_RNG) * CN_SG |  | 2 2 2
|  |  |  | 5 | LI72531.PV | % | F72TK437 Cyanide Level | [7 empty] | 2
F72CALC10121 | 2000-F72-PID-PR-10005 | F72TK439 Cyanide Weight |  | 1 | WI72535 | t | F72TK439 Cyanide Weight |  | X | [5 empty] | 2
|  |  |  | 2 3 4 | F72TK439_DIA LI72535_RNG CN_SG | m m | F72TK439 Diameter LI72535 Range Cyanide SG | X X X |  | 11.46 12.51 1.24 | 0 0 0.5 | 20 20 2 | WI72535 = pi * ((F72TK439_DIA / 2)^2) * (LI72535/100 * F72TK439_RNG) * CN_SG |  | 2 2 2
|  |  |  | 5 | LI72535.PV | % | F72TK439 Cyanide Level | [7 empty] | 2

## 12. Misc
KCGM GROWTH PROJECT
MISC
MISC. INSTRUMENTS AND CONTROLLERS
Tag Name | P&ID | Description | Normal State | Alarm State | Hardwired (y/n) | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev
F72 FCV 1 _ _ | 2000-F72-PID-PR-10001 | TIC72412 HH Logic | Logic |  | N |  |  | If TIC72412 ≥ A HH: _ Open FCV72407 to 100% (configurable by Engineer). Open FCV72408 to 100% (configurable by Engineer). Resume control from respective FIC when TIC72412.PV <= TIC72412.SV for 10 seconds | 1
F72LU411 T1 _ | 2000-F72-PID-PR-10001 | F72MB411 Initial Grease | Timer PT = 60 seconds |  | N |  |  | Initial greasing cycle 1 minute after mill start up Start: F72-MB-411 = Running (rising edge) Stop: F72LU411 T1 Elapsed or F72-MB-411 = Not Running _ F72LU411 T1 elapsing starts F72-LU-411 _ | 1
F72LU411 T2 _ | 2000-F72-PID-PR-10001 | F72MB411 Grease Timer | Timer PT = 1800 seconds |  | N |  |  | Recurring greasing cycle every 30 minutes after the initial greasing cycle Start/Continue: F72-MB-411 = Running AND F72-LU-411 = Not Running AND F72LU411 T1 _ Not Running Pause: F72-MB-411 = Not Running Stop: F72LU411 T2 Elapsed _ F72LU411 T2 elapsing starts F72-LU-411 _ | 1
F72LU411 T3 _ | 2000-F72-PID-PR-10001 | F72MB411 Grease Fail | Timer PT = 120 seconds | Timer Elapsed | N | 0 |  | Grease failed alarm Start: F72LU411 T1 Elapsed or F72LU411 T2 Elapsed or F72-LU-411 = Running _ _ Stop: ZS72455 rising edge OR F72LU411 T3 Elapsed _ F72LU411 T3A to alarm if timer elapsed. Alarm can only clear if ZS72455 rising edge _ | 1
LIME1 AUT STT _ _ | 2000-F72-PID-PR-10001 | F72PK402 Lime 1 Auto Stt | Button (Enable / Disable) |  |  |  |  | LIME1 AUT STT Is used for auto starting and stopping F72-SEQ-0104 and F72-SEQ-0105 _ _ based on LIC72439 switchpoints (P Lo, P Hi). _ _ The CRO must enable LIME1 AUT STT to enable the above functionality. Include as button _ _ on DCS. | C
LIME1 FTS ALM _ _ | 2000-F72-PID-PR-10001 | F72PK402 Lime 1 Seq FTS | Normal | Alarm | N | 5 |  | If F72-SEQ-0104 fails to start on LIME AUTO 1 = ACTIVE AND LIC72439 <= P Lo, then _ _ _ alarm If F72-SEQ-0105 fails to start on LIME AUTO 1 = ACTIVE AND LIC72439 >= P Hi, then _ _ _ alarm | C
'F72 FCV 2 _ _ | 2000-F72-PID-PR-10002 | TIC72432 HH Logic | Logic |  |  |  |  | If TIC72432 ≥ A HH: _ Open FCV72427 to 100% (configurable by Engineer). Open FCV72428 to 100% (configurable by Engineer). Resume control from respective FIC when TIC72432.PV <= TIC72432.SV for 10 seconds | 1
F72LU412 T1 _ | 2000-F72-PID-PR-10002 | F72MB412 Initial Grease | Timer PT = 60 seconds |  | N |  |  | Initial greasing cycle 1 minute after mill start up Start: F72-MB-412 = Running (rising edge) Stop: F72LU412 T1 Elapsed or F72-MB-412 = Not Running _ F72LU412 T1 elapsing starts F72-LU-412 _ | 1
F72LU412 T2 _ | 2000-F72-PID-PR-10002 | F72MB412 Grease Timer | Timer PT = 1800 seconds |  | N |  |  | Recurring greasing cycle every 30 minutes after the initial greasing cycle Start/Continue: F72-MB-412 = Running AND F72-LU-412 = Not Running AND F72LU412 T1 _ Not Running Pause: F72-MB-412 = Not Running Stop: F72LU412 T2 Elapsed _ F72LU412 T2 elapsing starts F72-LU-412 _ | 1
F72LU412 T3 _ | 2000-F72-PID-PR-10002 | F72MB412 Grease Fail | Timer PT = 120 seconds | Timer Elapsed | N | 0 |  | Grease failed alarm Start: F72LU412 T1 Elapsed or F72LU412 T2 Elapsed or F72-LU-412 = Running _ _ Stop: ZS72477 rising edge OR F72LU412 T3 Elapsed _ F72LU412 T3A to alarm if timer elapsed. Alarm can only clear if ZS72477 rising edge _ | 1
LIME2 AUT STT _ _ | 2000-F72-PID-PR-10002 | F72PK402 Lime 2 Auto Stt | Button (Enable / Disable) |  |  |  |  | LIME2 AUT STT Is used for auto starting and stopping F72-SEQ-0107 and F72-SEQ-0108 _ _ based on LIC72439 switchpoints (P Lo, P Hi). _ _ The CRO must enable LIME2 AUT STT to enable the above functionality. Include as button _ _ on DCS. | 1
LIME2 FTS ALM _ _ | 2000-F72-PID-PR-10002 | F72PK402 Lime 2 Seq FTS | Normal | Alarm | N | 5 |  | If F72-SEQ-0107 fails to start on LIME2 AUTO = ACTIVE AND LIC72439 <= P Lo, then _ _ _ alarm If F72-SEQ-0108 fails to start on LIME2 AUTO ST = ACTIVE AND LIC72439 >= P Hi, then _ _ _ alarm | 1
HS72407 | 2000-F72-PID-PR-10001 | F72MB411 Water Controller | Operator Selection |  |  |  |  | Selector (1 selection only): MOL Level Control Fixed Rate Control One shot FIC72407 and FIC72408 to CAS when any selection is made Refer to F72CALC10008 for use of HS72407 | C
HS72427 | 2000-F72-PID-PR-10001 | F72MB412 Water Controller | Operator Selection |  |  |  |  | Selector (1 selection only): MOL Level Control Fixed Rate Control One shot FIC72427 and FIC72428 to CAS when any selection is made Refer to F72CALC10009 for use of HS72427 | C
F72AG467 OFF _ | 2000-F72-PID-PR-10003 | F72AG467 Off Alarm | Normal | Alarm | N | 5 | LIC72439.PV ≤ A Lo _ | If F72-AG-467 = Not Running: Activate F72AG467 OFF alarm _ | 1
LIME RM DUTY _ _ | 2000-F72-PID-PR-10003 | F72-PP-656/657 Duty | Operator Selection |  |  |  |  | Lime Ringmain Pumps duty selection Duty pump selector: F72-PP-656 OR F72-PP-657 | C
NACN RM DUTY _ _ | 2000-F72-PID-PR-10005 | F72-PP-675/676 Duty | Operator Selection |  |  |  |  | Cyanide Ringmain Pumps duty selection Duty pump selector: F72-PP-675 OR F72-PP-676 | C
NAOH RM DUTY _ _ | 2000-F72-PID-PR-10006 | F72-PP-673/674 Duty | Operator Selection |  |  |  |  | Caustic Ringmain Pumps duty selection Duty pump selector: F72-PP-673 OR F72-PP-674 | C
LIME RM OFF _ _ | 2000-F72-PID-PR-10003 | F72-PP-656 & 657 Stopped | Normal | Alarm | N | 60 |  | Lime Ringmain Pumps stopped F72-PP-656 AND F72-PP-657 = Stopped | 0
NACN RM OFF _ _ | 2000-F72-PID-PR-10005 | F72-PP-675 & 676 Stopped | Normal | Alarm | N | 60 |  | Cyanide Ringmain Pumps stopped F72-PP-675 AND F72-PP-676 = Stopped | 0
NAOH RM OFF _ _ | 2000-F72-PID-PR-10006 | F72-PP-673 & 674 Stopped | Normal | Alarm | N | 60 |  | Caustic Ringmain Pumps stopped F72-PP-673 AND F72-PP-674 = Stopped | 0
HS72609 | 2000-F72-PID-PR-10007 | F72PP683/684 Duty | Operator Selection |  |  |  |  | Acid Dosing Pumps duty selection Duty pump selector: F72-PP-683 OR F72-PP-684 | C
HS72732 | 2000-F72-PID-PR-10015 | F72PP681/682 Duty | Operator Selection |  |  |  |  | Lead Nitrate Dosing Pumps duty selection Duty pump selector: F72-PP-681 OR F72-PP-682 | A
HS30616B | 2000-F72-PID-PR-10016 | F72PP696 Discharge Path | Operator Selection |  |  |  |  | Operator to select F72PP696 discharge location 2 options (1 selection only): - F72PP693 - F72PP694 Notes: If F72PP693 selected, enable FIC30497 output to F72PP696 If F72PP694 selected, enable FIC30616 FIC30598 output to F72PP696 (FIC are brownfields, captured in Stage 2 BF tie in list. Copy Stage 1 F72 PAX/Frother standby pump logic) | 1
72AT411 T1 _ | 2000-F72-PID-PR-10001 | F72AT411 On Timer | Timer PT = 3 seconds |  |  |  |  | Start 72AT411 T1 if F72AT411 = Running 72AT411 T2 elapses _ _ Stop 72AT411 T1 when timer elapses. This will stop F72-AT-411 after PT seconds. See _ Drive tab DEFAULT SETTING: 3 SECONDS. ENGINEER CONFIGURABLE RANGE: 0 - 10 SECONDS | 2
72AT411 T2 _ | 2000-F72-PID-PR-10001 | F72AT411 Frequency Timer | Timer PT = 60 seconds |  |  |  |  | Loop timer if F72-VR-411 = RUNNING. Stop timer if F72-VR-411 = STOPPED. Start F72-AT-411 when 72AT411 T2 completes. See Drive tab _ DEFAULT SETTING: 60 SECONDS. ENGINEER CONFIGURABLE RANGE: 0 - 240 SECONDS | 2
72AT412 T1 _ | 2000-F72-PID-PR-10001 | F72AT412 On Timer | Timer PT = 3 seconds |  |  |  |  | Start 72AT412 T1 if F72AT412 = Running 72AT412 T2 elapses _ _ Stop 72AT412 T1 when timer elapses. This will stop F72-AT-412 after PT seconds. See _ Drive tab DEFAULT SETTING: 3 SECONDS. ENGINEER CONFIGURABLE RANGE: 0 - 10 SECONDS | 2
72AT412 T2 _ | 2000-F72-PID-PR-10001 | F72AT412 Frequency Timer | Timer PT = 60 seconds |  |  |  |  | Loop timer if F72-VR-412 = RUNNING. Stop timer if F72-VR-412 = STOPPED. Start F72-AT-412 when 72AT412 T2 completes. See Drive tab _ DEFAULT SETTING: 60 SECONDS. ENGINEER CONFIGURABLE RANGE: 0 - 240 SECONDS | 2
F72PS419 NA _ | 2000-F72-PID-PR-10003 | F72PS419 Not Auto | Inactive | Alarm | N | 30 |  | Alarm if: F72PS419 or XV72464 not in AUT HAZOP 350 | 1
F72PS466 NA _ | 2000-F72-PID-PR-10003 | F72PS466 Not Auto | Inactive | Alarm | N | 30 |  | Alarm if: F72PS466 or XV72465 not in AUT HAZOP 350 | 1
F72PS467 NA _ | 2000-F72-PID-PR-10003 | F72PS467 Not Auto | Inactive | Alarm | N | 30 |  | Alarm if: F72PS467 or XV72466 not in AUT HAZOP 350 | 1
FAH72616 | 2000-F72-PID-PR-10007 | FCV72616 Valve Passing | Inactive | Alarm | N | 30 | Mask if FCV72616 = Open (>=1%) AND Mask for 10 seconds on FCV72616 = Closed (<1%) | Activate if FI72616 >= P Hi _ HAZOP action | 1

## 13. Alarm Database
KCGM GROWTH PROJECT
ALARM DATABASE
ALARM DATABASE
Tag Name | P&ID | Abbreviated Description (Faceplate) | Type | Alarm State | Alarm Value | Alarm Units | On Delay (sec) | Alarm Masking Condition | Impact | Urgency | Priority | Operator Response | Rev
TI72480 | 2000-F72-PID-PR-10001 | F24PP406/7 Raw Water | Analogue Input | A_LL | 5 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Low raw water temperatures. Adjust lime slaking feed water flowrates to suit. | C
TI72480 | 2000-F72-PID-PR-10001 | F24PP406/7 Raw Water | Analogue Input | A_Lo | 10 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low raw water temperatures. Adjust lime slaking feed water flowrates to suit. | C
LI72401 | 2000-F72-PID-PR-10001 | F72SI411 Lime Silo 1 | Analogue Input | A_LL | 5 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Activator tripped. Advise supervisor of low silo levels. | C
LI72401 | 2000-F72-PID-PR-10001 | F72SI411 Lime Silo 1 | Analogue Input | A_Lo | 10 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | CRO to notify the supervisor that lime powder level is low and requires resupply | A
LI72401 | 2000-F72-PID-PR-10001 | F72SI411 Lime Silo 1 | Analogue Input | A_Hi | 89 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Ensure a lime transfer is not being conducted and that transfer valves are shut | C
LI72401 | 2000-F72-PID-PR-10001 | F72SI411 Lime Silo 1 | Analogue Input | A_HH | 98 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Ensure a lime transfer is not being conducted and that transfer valves are shut | C
PDI72404 | 2000-F72-PID-PR-10001 | F72DC411 Filter DP | Analogue Input | A_Hi | 90 | Pa | 30 | If XV72419 AND XV72420 = Closed: Mask A Lo _ Mask for 60 seconds post opening XV72419 OR XV72420 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise field operator to investigate potential issues with pulsing solenoids. | C
PDI72404 | 2000-F72-PID-PR-10001 | F72DC411 Filter DP | Analogue Input | A_HH | 200 | Pa | 5 | If XV72419 AND XV72420 = Closed: Mask A Lo _ Mask for 60 seconds post opening XV72419 OR XV72420 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise field operator to investigate potential issues with pulsing solenoids. | C
PI72490 | 2000-F72-PID-PR-10001 | F72CY658 Cyclone | Analogue Input | A_LL | 80 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-658 = Not Running _ _ 2. Mask A Lo and A LL for 30 seconds on F72-PP-658 _ _ Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check feed to lime slaking mill is correctly set and that adequate number of feed valves are open/closed | C
PI72490 | 2000-F72-PID-PR-10001 | F72CY658 Cyclone | Analogue Input | A_Lo | 90 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-658 = Not Running _ _ 2. Mask A Lo and A LL for 30 seconds on F72-PP-658 _ _ Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check feed to lime slaking mill is correctly set and that adequate number of feed valves are open/closed | C
PI72490 | 2000-F72-PID-PR-10001 | F72CY658 Cyclone | Analogue Input | A_Hi | 130 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-658 = Not Running _ _ 2. Mask A Lo and A LL for 30 seconds on F72-PP-658 _ _ Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check feed to lime slaking mill is correctly set and that adequate number of feed valves are open/closed | C
PI72490 | 2000-F72-PID-PR-10001 | F72CY658 Cyclone | Analogue Input | A_HH | 140 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-658 = Not Running _ _ 2. Mask A Lo and A LL for 30 seconds on F72-PP-658 _ _ Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Transfer pump tripped. Check that adequate number of cyclone feed valves are open. | C
LI72421 | 2000-F72-PID-PR-10002 | F72SI412 Lime Silo 2 | Analogue Input | A_LL | 5 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Activator tripped. Advise supervisor of low silo levels. | C
LI72421 | 2000-F72-PID-PR-10002 | F72SI412 Lime Silo 2 | Analogue Input | A_Lo | 10 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | CRO to notify the supervisor that lime powder level is low and requires resupply | A
LI72421 | 2000-F72-PID-PR-10002 | F72SI412 Lime Silo 2 | Analogue Input | A_Hi | 89 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Ensure a lime transfer is not being conducted and that transfer valves are shut | C
LI72421 | 2000-F72-PID-PR-10002 | F72SI412 Lime Silo 2 | Analogue Input | A_HH | 98 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Ensure a lime transfer is not being conducted and that transfer valves are shut | C
PDI72424 | 2000-F72-PID-PR-10002 | F72DC412 Filter DP | Analogue Input | A_Hi | 90 | Pa | 30 | If XV72433 AND XV72434 = Closed: Mask A Lo _ Mask for 60 seconds post opening XV72433 OR XV72434 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise field operator to investigate potential issues with pulsing solenoids. | C
PDI72424 | 2000-F72-PID-PR-10002 | F72DC412 Filter DP | Analogue Input | A_HH | 200 | Pa | 5 | If XV72433 AND XV72434 = Closed: Mask A Lo _ Mask for 60 seconds post opening XV72433 OR XV72434 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise field operator to investigate potential issues with pulsing solenoids. | C
PI72491 | 2000-F72-PID-PR-10002 | F72CY659 Cyclone | Analogue Input | A_LL | 80 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-659 = Not Running _ _ 2. Mask A Lo and A LL for 30 seconds on F72-PP-659 _ _ Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check feed to lime slaking mill is correctly set and that adequate number of feed valves are open/closed | C
PI72491 | 2000-F72-PID-PR-10002 | F72CY659 Cyclone | Analogue Input | A_Lo | 90 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-659 = Not Running _ _ 2. Mask A Lo and A LL for 30 seconds on F72-PP-659 _ _ Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check feed to lime slaking mill is correctly set and that adequate number of feed valves are open/closed | C
PI72491 | 2000-F72-PID-PR-10002 | F72CY659 Cyclone | Analogue Input | A_Hi | 130 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-659 = Not Running _ _ 2. Mask A Lo and A LL for 30 seconds on F72-PP-659 _ _ Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check feed to lime slaking mill is correctly set and that adequate number of feed valves are open/closed | C
PI72491 | 2000-F72-PID-PR-10002 | F72CY659 Cyclone | Analogue Input | A_HH | 140 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-659 = Not Running _ _ 2. Mask A Lo and A LL for 30 seconds on F72-PP-659 _ _ Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Transfer pump tripped. Check that adequate number of cyclone feed valves are open. | C
PI72451 | 2000-F72-PID-PR-10003 | F72PP656/7 MOL Rturn | Analogue Input | A_Lo | 30 | kPa | 5 | 1. Mask A Lo if F72-PP-656 and 657 is Not Running _ 2. Mask A Lo for 10 seconds on F72-PP-656 or 657 _ pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise field operator to investigate valve line up and potential loss of containment in the field. | C
PI72451 | 2000-F72-PID-PR-10003 | F72PP656/7 MOL Rturn | Analogue Input | A_Hi | 120 | kPa | 5 | 1. Mask A Lo if F72-PP-656 and 657 is Not Running _ 2. Mask A Lo for 10 seconds on F72-PP-656 or 657 _ pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise field operator to investigate valve line up and potential restrictions in the field. | A
PI72450 | 2000-F72-PID-PR-10003 | F72PP656/7 MOL Discharge | Analogue Input | A_LL | 250 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-656 and 657 is Not _ _ Running 2. Mask A Lo and A LL for 10 seconds on F72-PP-656 _ _ or 657 pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Advise field operator to investigate valve line up and potential loss of containment in the field. | C
PI72450 | 2000-F72-PID-PR-10003 | F72PP656/7 MOL Discharge | Analogue Input | A_Lo | 300 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-656 and 657 is Not _ _ Running 2. Mask A Lo and A LL for 10 seconds on F72-PP-656 _ _ or 657 pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise field operator to investigate valve line up and potential loss of containment in the field. | C
PI72450 | 2000-F72-PID-PR-10003 | F72PP656/7 MOL Discharge | Analogue Input | A_Hi | 680 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-656 and 657 is Not _ _ Running 2. Mask A Lo and A LL for 10 seconds on F72-PP-656 _ _ or 657 pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise field operator to investigate valve line up and potential restrictions in the field. | A
PI72450 | 2000-F72-PID-PR-10003 | F72PP656/7 MOL Discharge | Analogue Input | A_HH | 700 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-656 and 657 is Not _ _ Running 2. Mask A Lo and A LL for 10 seconds on F72-PP-656 _ _ or 657 pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Advise field operator to investigate valve line up and potential restrictions in the field. | C
LI72461 | 2000-F72-PID-PR-10003 | F72PS419 Sump Level | Analogue Input | A_Hi | 70 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Check line up and spillage in the field, then start Sump Pump if safe to do so. | C
LI72462 | 2000-F72-PID-PR-10003 | F72PS466 Sump Level | Analogue Input | A_Hi | 70 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Check line up and spillage in the field, then start Sump Pump if safe to do so. | C
LI72463 | 2000-F72-PID-PR-10003 | F72PS467 Sump Level | Analogue Input | A_Hi | 70 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Check line up and spillage in the field, then start Sump Pump if safe to do so. | C
LI72531 | 2000-F72-PID-PR-10005 | F72TK437 Cyanide Level | Analogue Input | A_LL | 10 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Cyanide ringmain pump tripped. CRO to investigate and confirm in the field if tank level is accurate. Escalate to supervisor for immediate re-supply | C
LI72531 | 2000-F72-PID-PR-10005 | F72TK437 Cyanide Level | Analogue Input | A_Lo | 25 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Investigate reagent consumption rate and potential leaks. Advise supervisor of low level and organise resupply. | A
LI72531 | 2000-F72-PID-PR-10005 | F72TK437 Cyanide Level | Analogue Input | A_Hi | 90 | % | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Immediate (<5 minutes) | High | Monitor high level event. Check transfer valves are closed. Advise supervisor if loading is occurring / imminent | C
LI72531 | 2000-F72-PID-PR-10005 | F72TK437 Cyanide Level | Analogue Input | A_HH | 95 | % | 5 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Evacuate area until levels stabilise and return to safe operating range. Monitor HCN gas monitors. | C
LI72535 | 2000-F72-PID-PR-10005 | F72TK439 Cyanide Level | Analogue Input | A_LL | 10 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Cyanide ringmain pump tripped. CRO to investigate and confirm in the field if tank level is accurate. Escalate to supervisor for immediate re-supply | 1
LI72535 | 2000-F72-PID-PR-10005 | F72TK439 Cyanide Level | Analogue Input | A_Lo | 25 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Investigate reagent consumption rate and potential leaks. Advise supervisor of low level and organise resupply. | 1
LI72535 | 2000-F72-PID-PR-10005 | F72TK439 Cyanide Level | Analogue Input | A_Hi | 90 | % | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Immediate (<5 minutes) | High | Monitor high level event. Check transfer valves are closed. Advise supervisor if loading is occurring / imminent | 1
LI72535 | 2000-F72-PID-PR-10005 | F72TK439 Cyanide Level | Analogue Input | A_HH | 95 | % | 5 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Evacuate area until levels stabilise and return to safe operating range. Monitor HCN gas monitors. | 1
PI72552 | 2000-F72-PID-PR-10005 | F72PP675/6 R/main Disch | Analogue Input | A_Lo | 500 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-675 and 676 is Not _ _ Running 2. Mask A Lo and A LL on F72-PP-675 or 676 pump _ _ start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise field operator to investigate valve line up and potential loss of containment in the field. | C
PI72552 | 2000-F72-PID-PR-10005 | F72PP675/6 R/main Disch | Analogue Input | A_Hi | 730 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-675 and 676 is Not _ _ Running 2. Mask A Lo and A LL on F72-PP-675 or 676 pump _ _ start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise field operator to investigate valve line up and potential restrictions in the field. | A
PI72552 | 2000-F72-PID-PR-10005 | F72PP675/6 R/main Disch | Analogue Input | A_HH | 790 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-675 and 676 is Not _ _ Running 2. Mask A Lo and A LL on F72-PP-675 or 676 pump _ _ start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Caustic ringmain pumps tripped. Investigate for potential blockages/restrictions. Check discharge valve positions. | C
PI72563 | 2000-F72-PID-PR-10005 | F72PP675/6 R/main Return | Analogue Input | A_Lo | 260 | kPa | 5 | 1. Mask A Lo if F72-PP-675 and 676 is Not Running _ 2. Mask A Lo on F72-PP-675 or 676 pump start-up _ | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise field operator to investigate valve line up and potential loss of containment in the field. | C
PI72563 | 2000-F72-PID-PR-10005 | F72PP675/6 R/main Return | Analogue Input | A_Hi | 440 | kPa | 5 | 1. Mask A Lo if F72-PP-675 and 676 is Not Running _ 2. Mask A Lo on F72-PP-675 or 676 pump start-up _ | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise field operator to investigate valve line up and potential restrictions in the field. | A
LI72581 | 2000-F72-PID-PR-10005 | F72PS423 Sump Level | Analogue Input | A_Hi | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Check line up and spillage in the field, then start Sump Pump if safe to do so. | C
TI72592 | 2000-F72-PID-PR-10006 | F72TK434 Caustic Temp | Analogue Input | A_LL | 16 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Low caustic temperature. Check in tank heater is operating as required. Advise supervisor immediately. | C
TI72592 | 2000-F72-PID-PR-10006 | F72TK434 Caustic Temp | Analogue Input | A_Lo | 20 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Low caustic temperature. Check in tank heater is operating as required. Advise supervisor immediately. | C
TI72592 | 2000-F72-PID-PR-10006 | F72TK434 Caustic Temp | Analogue Input | A_Hi | 44 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | High caustic temperature. Check in tank heater is operating as required. Advise supervisor immediately. | C
TI72592 | 2000-F72-PID-PR-10006 | F72TK434 Caustic Temp | Analogue Input | A_HH | 47 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | High caustic temperature. Check in tank heater is operating as required. Advise supervisor immediately. | C
LI72591 | 2000-F72-PID-PR-10006 | F72TK434 Caustic Level | Analogue Input | A_LL | 10 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Caustic dosing pumps tripped. CRO to investigate and confirm in the field if tank level is accurate. Escalate to supervisor for immediate re-supply | C
LI72591 | 2000-F72-PID-PR-10006 | F72TK434 Caustic Level | Analogue Input | A_Lo | 25 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Investigate reagent consumption rate and potential leaks. Advise supervisor of low level and organise resupply. | A
LI72591 | 2000-F72-PID-PR-10006 | F72TK434 Caustic Level | Analogue Input | A_Hi | 90 | % | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Prompt (>15 to <30 minutes) | Low | Monitor high level event. Check transfer valves are closed. Advise supervisor if loading is occurring / imminent | C
LI72591 | 2000-F72-PID-PR-10006 | F72TK434 Caustic Level | Analogue Input | A_HH | 95 | % | 5 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Evacuate area until levels stabilise and return to safe operating range. | C
PI72595 | 2000-F72-PID-PR-10006 | F72PP673/4 R/main Disch | Analogue Input | A_Lo | 370 | kPa | 5 | 1. Mask A Lo if F72-PP-673/674 is Not Running _ 2. Mask A Lo and A LL for 10 seconds on F72-PP-673 _ _ or 674 pump start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise field operator to investigate valve line up and potential loss of containment in the field. | C
PI72595 | 2000-F72-PID-PR-10006 | F72PP673/4 R/main Disch | Analogue Input | A_Hi | 600 | kPa | 5 | 1. Mask A Lo if F72-PP-673/674 is Not Running _ 2. Mask A Lo and A LL for 10 seconds on F72-PP-673 _ _ or 674 pump start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise field operator to investigate valve line up and potential restrictions in the field. | A
PI72595 | 2000-F72-PID-PR-10006 | F72PP673/4 R/main Disch | Analogue Input | A_HH | 650 | kPa | 5 | 1. Mask A Lo if F72-PP-673/674 is Not Running _ 2. Mask A Lo and A LL for 10 seconds on F72-PP-673 _ _ or 674 pump start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Acid dosing pumps tripped. Investigate for potential blockages/restrictions. Check discharge valve positions. | C
PI72597 | 2000-F72-PID-PR-10006 | F72PP673/4 R/main Return | Analogue Input | A_Lo | 180 | kPa | 5 | 1. Mask A Lo if F72-PP-673/674 is Not Running _ 2. Mask A Lo for 10 seconds on F72-PP-673 or 674 _ pump start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise field operator to investigate valve line up and potential loss of containment in the field. | C
PI72597 | 2000-F72-PID-PR-10006 | F72PP673/4 R/main Return | Analogue Input | A_Hi | 280 | kPa | 5 | 1. Mask A Lo if F72-PP-673/674 is Not Running _ 2. Mask A Lo for 10 seconds on F72-PP-673 or 674 _ pump start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise field operator to investigate valve line up and potential restrictions in the field. | A
TI72598 | 2000-F72-PID-PR-10006 | F72PP673/4 R/main Return | Analogue Input | A_LL | 16 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Low caustic temperature. Check in tank heater is operating as required. Advise supervisor immediately. | C
TI72598 | 2000-F72-PID-PR-10006 | F72PP673/4 R/main Return | Analogue Input | A_Lo | 20 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Low caustic temperature. Check in tank heater is operating as required. Advise supervisor immediately. | C
TI72598 | 2000-F72-PID-PR-10006 | F72PP673/4 R/main Return | Analogue Input | A_Hi | 45 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | High caustic temperature. Check in tank heater is operating as required. Advise supervisor immediately. | C
TI72598 | 2000-F72-PID-PR-10006 | F72PP673/4 R/main Return | Analogue Input | A_HH | 48 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | High caustic temperature. Check in tank heater is operating as required. Advise supervisor immediately. | C
LI72599 | 2000-F72-PID-PR-10006 | F72PS424 Sump Level | Analogue Input | A_Hi | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Check line up and spillage in the field, then start Sump Pump if safe to do so. | C
LI72602 | 2000-F72-PID-PR-10007 | F72TK435 Acid Storage | Analogue Input | A_LL | 10 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Acid dosing pumps tripped. CRO to investigate and confirm in the field if tank level is accurate. Escalate to supervisor for immediate re-supply | C
LI72602 | 2000-F72-PID-PR-10007 | F72TK435 Acid Storage | Analogue Input | A_Lo | 25 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Investigate reagent consumption rate and potential leaks. Advise supervisor of low level and organise resupply. | A
LI72602 | 2000-F72-PID-PR-10007 | F72TK435 Acid Storage | Analogue Input | A_Hi | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Monitor high level event. Check transfer valves are closed. Advise supervisor if loading is occurring / imminent | A
LI72602 | 2000-F72-PID-PR-10007 | F72TK435 Acid Storage | Analogue Input | A_HH | 95 | % | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Immediate (<5 minutes) | High | Evacuate area until levels stabilise and return to safe operating range. | C
LI72612 | 2000-F72-PID-PR-10007 | F72TK424 Acid Dilution | Analogue Input | A_LL | 10 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Discharge pump tripped. Check sequence is operating as intended else investigate in field. | C
LI72612 | 2000-F72-PID-PR-10007 | F72TK424 Acid Dilution | Analogue Input | A_Lo | 15 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check the CIL4 acid dilution batch mix and CIL4 acid wash sequence is operating correctly and setpoints are appropriately set. | A
LI72612 | 2000-F72-PID-PR-10007 | F72TK424 Acid Dilution | Analogue Input | A_Hi | 85 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Monitor high level event. Check acid and water feed valves to the tanks have closed. | A
LI72612 | 2000-F72-PID-PR-10007 | F72TK424 Acid Dilution | Analogue Input | A_HH | 90 | % | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Immediate (<5 minutes) | High | Evacuate area until levels stabilise and return to safe operating range. | C
FI72610 | 2000-F72-PID-PR-10007 | F72PP683/4 Acid Dosing | Analogue Input | A_LL | 12 | m3/h | 5 | 1. Mask A Lo and A LL if F72-PP-683/684 is Not _ _ Running 2. Mask A Lo and A LL for 10 seconds on F72-PP- _ _ 683/684 | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Advise maintenance/field operator to inspect equipment in the field. Pump running off curve. | A
FI72610 | 2000-F72-PID-PR-10007 | F72PP683/4 Acid Dosing | Analogue Input | A_Lo | 16 | m3/h | 5 | 1. Mask A Lo and A LL if F72-PP-683/684 is Not _ _ Running 2. Mask A Lo and A LL for 10 seconds on F72-PP- _ _ 683/684 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise maintenance/field operator to inspect equipment in the field. Pump running off curve. | A
PI72611 | 2000-F72-PID-PR-10007 | F72PP683/4 Acid Dosing | Analogue Input | A_Lo | 280 | kPa | 13629 | 1. Mask A Lo and A LL if F72-PP-683/684 is Not _ _ Running 2. Mask A Lo and A LL for 10 seconds on F72-PP- _ _ 683/684 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise field operator to investigate valve line up and potential loss of containment in the field. | C
PI72611 | 2000-F72-PID-PR-10007 | F72PP683/4 Acid Dosing | Analogue Input | A_Hi | 400 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-683/684 is Not _ _ Running 2. Mask A Lo and A LL for 10 seconds on F72-PP- _ _ 683/684 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise field operator to investigate valve line up and potential restrictions in the field. | A
PI72611 | 2000-F72-PID-PR-10007 | F72PP683/4 Acid Dosing | Analogue Input | A_HH | 410 | kPa | 5 | 1. Mask A Lo and A LL if F72-PP-683/684 is Not _ _ Running 2. Mask A Lo and A LL for 10 seconds on F72-PP- _ _ 683/684 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Acid dosing pump tripped. Advise maintenance/operations to investigate potential restrictions. | C
FAH72616 | 2000-F72-PID-PR-10007 | FCV72616 Valve Passing | Misc | Alarm |  |  | 30 | Mask if FCV72616 = Open (>=1%) AND Mask for 10 seconds on FCV72616 = Closed (<1%) | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Advise maintenance/field operator to inspect equipment in the field. Valve potentially passing. | 1
LI72615 | 2000-F72-PID-PR-10007 | F72PS428 Sump Level | Analogue Input | A_Hi | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Check line up and spillage in the field, then start Sump Pump if safe to do so. | C
LI72701 | 2000-F72-PID-PR-10015 | F72TK438 Nitrate Tank | Analogue Input | A_LL | 10 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Lead nitrate dosing pumps tripped. Escalate to supervisor for immediate re-supply | C
LI72701 | 2000-F72-PID-PR-10015 | F72TK438 Nitrate Tank | Analogue Input | A_Lo | 25 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Investigate reagent consumption rate and potential leaks. Advise supervisor of low level and organise resupply. | A
LI72701 | 2000-F72-PID-PR-10015 | F72TK438 Nitrate Tank | Analogue Input | A_Hi | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Monitor high level event. Check transfer valves are closed. Advise supervisor if loading is occurring / imminent | A
LI72701 | 2000-F72-PID-PR-10015 | F72TK438 Nitrate Tank | Analogue Input | A_HH | 95 | % | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Immediate (<5 minutes) | High | Evacuate area until levels stabilise and return to safe operating range. | C
LI72741 | 2000-F72-PID-PR-10015 | F72PS426 Sump Level | Analogue Input | A_Hi | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Check line up and spillage in the field, then start Sump Pump if safe to do so. | C
PI72731 | 2000-F72-PID-PR-10015 | F72PP681/682 Disch Press | Analogue Input | A_Hi | 550 | kPa | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise field operator to investigate valve line up and potential restrictions in the field. | A
PI72731 | 2000-F72-PID-PR-10015 | F72PP681/682 Disch Press | Analogue Input | A_HH | 580 | kPa | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Lead nitrate dosing pump tripped. Advise maintenance/operations to investigate potential blockages. | C
LI72689 | 2000-F72-PID-PR-10012 | F72PK406 IBC Skid 1 | Analogue Input | A_LL | 10 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Antiscalant dosing pump tripped. Check in field. Replace IBC immediately. | C
LI72689 | 2000-F72-PID-PR-10012 | F72PK406 IBC Skid 1 | Analogue Input | A_Lo | 25 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Investigate reagent consumption rate and potential leaks. Advise supervisor of low level and organise resupply. | A
LI72689 | 2000-F72-PID-PR-10012 | F72PK406 IBC Skid 1 | Analogue Input | A_Hi | 90 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check IBC in the field. | A
LI72690 | 2000-F72-PID-PR-10012 | F72PK407 IBC Skid 2 | Analogue Input | A_LL | 10 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Antiscalant dosing pump tripped. Check in field. Replace IBC immediately. | C
LI72690 | 2000-F72-PID-PR-10012 | F72PK407 IBC Skid 2 | Analogue Input | A_Lo | 25 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Investigate reagent consumption rate and potential leaks. Advise supervisor of low level and organise resupply. | A
LI72690 | 2000-F72-PID-PR-10012 | F72PK407 IBC Skid 2 | Analogue Input | A_Hi | 90 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check IBC in the field. | A
LI72691 | 2000-F72-PID-PR-10012 | F72PK408 IBC Skid 3 | Analogue Input | A_LL | 10 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Antiscalant dosing pump tripped. Check in field. Replace IBC immediately. | C
LI72691 | 2000-F72-PID-PR-10012 | F72PK408 IBC Skid 3 | Analogue Input | A_Lo | 25 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Investigate reagent consumption rate and potential leaks. Advise supervisor of low level and organise resupply. | A
LI72691 | 2000-F72-PID-PR-10012 | F72PK408 IBC Skid 3 | Analogue Input | A_Hi | 90 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check IBC in the field. | A
LI72692 | 2000-F72-PID-PR-10012 | F72PK409 IBC Skid 4 | Analogue Input | A_LL | 10 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Antiscalant dosing pump tripped. Check in field. Replace IBC immediately. | C
LI72692 | 2000-F72-PID-PR-10012 | F72PK409 IBC Skid 4 | Analogue Input | A_Lo | 25 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Investigate reagent consumption rate and potential leaks. Advise supervisor of low level and organise resupply. | A
LI72692 | 2000-F72-PID-PR-10012 | F72PK409 IBC Skid 4 | Analogue Input | A_Hi | 90 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check IBC in the field. | A
TIC72412 | 2000-F72-PID-PR-10001 | F72HP411 Temperature | Analogue PID | A_Lo | 30 | °C | 5 | If F72-FV-411 = Not Running: Mask A Lo alarm _ | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check feed and lime feed rate controls are working as intended. | 1
TIC72412 | 2000-F72-PID-PR-10001 | F72HP411 Temperature | Analogue PID | A_Hi | 85 | °C | 5 | If F72-FV-411 = Not Running: Mask A Lo alarm _ | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check feed and lime feed rate controls are working as intended. | 1
TIC72412 | 2000-F72-PID-PR-10001 | F72HP411 Temperature | Analogue PID | A_HH | 90 | °C | 5 | If F72-FV-411 = Not Running: Mask A Lo alarm _ | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Feeder tripped. Check temperature controller in auto and raw water flow is healthy | 1
LDI7253X | 2000-F72-PID-PR-10005 | F72TK437/9 Level Diff | Analogue Input | A_Hi | 3 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Cyanide Tank level differential. Check balance line valves are in the correct position | C
LDI7253X | 2000-F72-PID-PR-10005 | F72TK437/9 Level Diff | Analogue Input | A_HH | 6 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Cyanide Tank level differential. Check balance line valves are in the correct position | C
FNI7240X | 2000-F72-PID-PR-10001 | F72MB411 Total Water | Analogue Input | A_Hi | 96.5 | m3/h | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check lime feed water flow controllers are correctly set and healthy. | C
FNI7240X | 2000-F72-PID-PR-10001 | F72MB411 Total Water | Analogue Input | A_HH | 105.4 | m3/h | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check lime feed water flow controllers are correctly set and healthy. | C
PDI72404 | 2000-F72-PID-PR-10001 | F72DC411 Filter DP | Analogue Input | A_Lo | 20 | Pa | 30 | If XV72419 AND XV72420 = Closed: Mask A Lo _ Mask for 60 seconds post opening XV72419 OR XV72420 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise field operator to investigate potential issues with filter installation | C
FNI7242X | 2000-F72-PID-PR-10002 | F72MB412 Total Water | Analogue Input | A_Hi | 96.5 | m3/h | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check lime feed water flow controllers are correctly set and healthy. | C
FNI7242X | 2000-F72-PID-PR-10002 | F72MB412 Total Water | Analogue Input | A_HH | 105.4 | m3/h | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check lime feed water flow controllers are correctly set and healthy. | C
PDI72424 | 2000-F72-PID-PR-10002 | F72DC412 Filter DP | Analogue Input | A_Lo | 20 | Pa | 30 | If XV72433 AND XV72434 = Closed: Mask A Lo _ Mask for 60 seconds post opening XV72433 OR XV72434 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise field operator to investigate potential issues with filter installation | C
TI72035 | - | F72SR001 Temperature | Analogue Input | A_Hi | 30 | °C | 60 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrician to investigate. | C
LAL72437 | 2000-F72-PID-PR-10001 | F72SI411 Lime Silo 1 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Activator tripped. Advise supervisor of low silo levels. | C
LAH72505 | 2000-F72-PID-PR-10001 | F72SI411 Lime Silo 1 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Ensure a lime transfer is not being conducted and that transfer valves are shut | C
SAL72438 | 2000-F72-PID-PR-10001 | F72VR411 Underspeed | Digital Input | Alarm (see comment) |  |  | 0 | 1. F72-VR-411 Not running 2. Mask for 30 seconds on F72-VR-411 start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Rotary valve tripped. Advise field operator / maintenance to investigate underspeed. | C
SAL72403 | 2000-F72-PID-PR-10001 | F72FS411 Underspeed | Digital Input | Alarm (see comment) |  |  | 0 | 1. F72-FS-411 Not running 2. Mask for 30 seconds on F72-FS-411 start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Screw feeder tripped. Advise field operator / maintenance to investigate underspeed. | C
LAH72405 | 2000-F72-PID-PR-10001 | F72XM658 Prewetter | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Vibrating conveyor tripped. Advise field operator to investigate for restrictions in the field. | C
LAL72456 | 2000-F72-PID-PR-10001 | F72MB411 Grease Lo | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low grease level. Advise field operator / maintenance to refill. | C
LAL72435 | 2000-F72-PID-PR-10002 | F72SI412 Lime Silo 2 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Activator tripped. Advise supervisor of low silo levels. | C
LAH72517 | 2000-F72-PID-PR-10002 | F72SI412 Lime Silo 2 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Ensure a lime transfer is not being conducted and that transfer valves are shut | C
SAL72436 | 2000-F72-PID-PR-10002 | F72VR412 Underspeed | Digital Input | Alarm (see comment) |  |  | 0 | 1. F72-VR-412 Not running 2. Mask for 30 seconds on F72-VR-412 start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Rotary valve tripped. Advise field operator / maintenance to investigate underspeed. | C
SAL72423 | 2000-F72-PID-PR-10002 | F72FS412 Underspeed | Digital Input | Alarm (see comment) |  |  | 0 | 1. F72-FS-412 Not running 2. Mask for 30 seconds on F72-FS-412 start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Screw feeder tripped. Advise field operator / maintenance to investigate underspeed. | C
LAH72425 | 2000-F72-PID-PR-10002 | F72XM659 Prewetter | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Vibrating conveyor tripped. Advise field operator to investigate for restrictions in the field. | C
LAL72479 | 2000-F72-PID-PR-10002 | F72MB412 Grease Lo | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low grease level. Advise field operator / maintenance to refill. | C
AAHH72547 | 2000-F72-PID-PR-10005 | F72PP675/6 HCN Monitor | Digital Input | Alarm |  |  | 3 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Evacuate area as per site procedure | C
AAHH72548 | 2000-F72-PID-PR-10005 | F72TK437 HCN Monitor | Digital Input | Alarm |  |  | 3 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Evacuate area as per site procedure | C
AAHH72549 | 2000-F72-PID-PR-10005 | F72TK439 HCN Monitor | Digital Input | Alarm |  |  | 3 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Evacuate area as per site procedure | C
TAH72733 | 2000-F72-PID-PR-10015 | F72PP681 Stator Temp | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Pump tripped. Advise field operator / maintenance to investigate valve line up and equipment | C
TAH72734 | 2000-F72-PID-PR-10015 | F72PP682 Stator Temp | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Pump tripped. Advise field operator / maintenance to investigate valve line up and equipment | C
FAL72681 | 2000-72-PID-PR-10012 | F72PP698 Flow Lo | Digital Input | Alarm |  |  | 3 | 1. F72-PP-698 Not Running 2. Mask for 10 seconds on F72-PP-698 start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Dosing pump tripped. Advise field operator to investigate valve line up and potential restrictions in the field. | C
XA72693 | 2000-F72-PID-PR-10012 | F72PP698 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check dosing pump unit HMI to determine reason for alarm | C
FAL72682 | 2000-72-PID-PR-10012 | F72PP699 Flow Lo | Digital Input | Alarm |  |  | 3 | 1. F72-PP-699 Not Running 2. Mask for 10 seconds on F72-PP-699 start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Dosing pump tripped. Advise field operator to investigate valve line up and potential restrictions in the field. | C
XA72694 | 2000-F72-PID-PR-10012 | F72PP699 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check dosing pump unit HMI to determine reason for alarm | C
FAL72683 | 2000-72-PID-PR-10012 | F72PP700 Flow Lo | Digital Input | Alarm |  |  | 3 | 1. F72-PP-700 Not Running 2. Mask for 10 seconds on F72-PP-700 start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Dosing pump tripped. Advise field operator to investigate valve line up and potential restrictions in the field. | C
XA72695 | 2000-F72-PID-PR-10012 | F72PP700 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check dosing pump unit HMI to determine reason for alarm | C
FAL72684 | 2000-72-PID-PR-10012 | F72PP701 Flow Lo | Digital Input | Alarm |  |  | 3 | 1. F72-PP-701 Not Running 2. Mask for 10 seconds on F72-PP-701 start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Dosing pump tripped. Advise field operator to investigate valve line up and potential restrictions in the field. | C
XA72696 | 2000-F72-PID-PR-10012 | F72PP701 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check dosing pump unit HMI to determine reason for alarm | C
FAL72685 | 2000-72-PID-PR-10012 | F72PP702 Flow Lo | Digital Input | Alarm |  |  | 3 | 1. F72-PP-702 Not Running 2. Mask for 10 seconds on F72-PP-702 start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Dosing pump tripped. Advise field operator to investigate valve line up and potential restrictions in the field. | C
XA72697 | 2000-F72-PID-PR-10012 | F72PP702 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check dosing pump unit HMI to determine reason for alarm | C
FAL72686 | 2000-72-PID-PR-10012 | F72PP703 Flow Lo | Digital Input | Alarm |  |  | 3 | 1. F72-PP-703 Not Running 2. Mask for 10 seconds on F72-PP-703 start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Dosing pump tripped. Advise field operator to investigate valve line up and potential restrictions in the field. | C
XA72698 | 2000-F72-PID-PR-10012 | F72PP703 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check dosing pump unit HMI to determine reason for alarm | C
FAL72687 | 2000-72-PID-PR-10012 | F72PP704 Flow Lo | Digital Input | Alarm |  |  | 3 | 1. F72-PP-704 Not Running 2. Mask for 10 seconds on F72-PP-704 start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Dosing pump tripped. Advise field operator to investigate valve line up and potential restrictions in the field. | C
XA72699 | 2000-F72-PID-PR-10012 | F72PP704 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check dosing pump unit HMI to determine reason for alarm | C
FAL72688 | 2000-72-PID-PR-10012 | F72PP705 Flow Lo | Digital Input | Alarm |  |  | 3 | 1. F72-PP-705 Not Running 2. Mask for 10 seconds on F72-PP-705 start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Dosing pump tripped. Advise field operator to investigate valve line up and potential restrictions in the field. | C
XA72700 | 2000-F72-PID-PR-10012 | F72PP705 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check dosing pump unit HMI to determine reason for alarm | C
TAH72484 | 2000-F72-PID-PR-10016 | F72PP693 Stator Temp | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Pump tripped. Advise field operator / maintenance to investigate valve line up and equipment | C
TAH72485 | 2000-F72-PID-PR-10016 | F72PP696 Stator Temp | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Pump tripped. Advise field operator / maintenance to investigate valve line up and equipment | C
TAH72486 | 2000-F72-PID-PR-10016 | F72PP694 Stator Temp | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Pump tripped. Advise field operator / maintenance to investigate valve line up and equipment | C
FAL72493 | 2000-F72-PID-PR-10001 | F72PP658 Gland Water | Digital Input | Alarm |  |  | 3 | 1. F72-PP-658 Not Running 2. Mask for 10 seconds on F72-PP-658 start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Pump tripped. Advise field operator to investigate low gland water flow. | C
FAL72496 | 2000-F72-PID-PR-10002 | F72PP659 Gland Water | Digital Input | Alarm |  |  | 3 | 1. F72-PP-659 Not Running 2. Mask for 10 seconds on F72-PP-659 start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Pump tripped. Advise field operator to investigate low gland water flow. | C
FAL72471 | 2000-F72-PID-PR-10003 | F72PP656 Gland Water | Digital Input | Alarm |  |  | 3 | 1. F72-PP-656 Not Running 2. Mask for 10 seconds on F72-PP-656 start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Pump tripped. Advise field operator to investigate low gland water flow. | C
FAL72475 | 2000-F72-PID-PR-10003 | F72PP657 Gland Water | Digital Input | Alarm |  |  | 3 | 1. F72-PP-657 Not Running 2. Mask for 10 seconds on F72-PP-657 start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Pump tripped. Advise field operator to investigate low gland water flow. | C
F72DCS413 PS1 _ | - | F72DCS413 PS1 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | C
F72DCS413 PS2 _ | - | F72DCS413 PS2 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | C
F72SW072 PS _ | - | F72SW072 ACBShunt 24V OK | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | 2
F72SW072 AF _ | - | F72SW072 Arc Flash Fault | Digital Input | Alarm |  |  | 0 |  | Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness. | Prompt (>15 to <30 minutes) | High | Electrician to investigate | C
F72SW072 TRP _ | - | F72SW072 CB Tripped | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Switchroom tripped. Electrician to investigate | C
F72SW072 SD _ | - | F72SW072 IncSurge Div OK | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | C
F72SR001 ESTP _ | - | F72SR001 E Stop | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Switchroom tripped. Electrician to investigate | C
F72SW072 PS1 _ | - | F72SW072 PS1 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | C
F72SW072 PS2 _ | - | F72SW072 PS2 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | C
F72FIP001 ALM _ | - | F72FIP001 Alarm | Digital Input | Alarm |  |  | 0 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm Milling & Classification Area Switchroom. Follow site specific Fire Emergency Plan. | C
F72FIP001 ISL _ | - | F72FIP001 Isolated | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | C
F72FIP001 FLT _ | - | F72FIP001 Fault | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | C
ZAC72034 | - | F72TR072 415V MCC Door | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Restricted work area potential safety breach/issue | 1
F72SW172 SD _ | - | F72SW172 IncSurge Div OK | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | C
LAH72033 | - | F72GE172 415V Gen Lvl Hi | Digital Input | Alarm |  |  | 0 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | High fuel level in generator fuel reservoir. Operator to radio local field operator to cease re-fuelling. | C
LAL72033 | - | F72GE172 415V Gen Lvl Lo | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operational risk for backup power. Operator to organise re- fuelling. | C
F72RIO003 PS1 _ | - | F72RIO003 PS1 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | C
F72RIO003 PS2 _ | - | F72RIO003 PS2 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | C
ZA72454A | 2000-F72-PID-PR-10001 | F72MB411 Vertical Posn A | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise maintenance to investigate the mill's vertical position | 0
ZA72454B | 2000-F72-PID-PR-10001 | F72MB411 Vertical Posn B | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise maintenance to investigate the mill's vertical position | 0
ZA72507A | 2000-F72-PID-PR-10001 | F72MB411 Horizntal Pos A | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise maintenance to investigate the mill's horizontal position | 0
ZA72507B | 2000-F72-PID-PR-10001 | F72MB411 Horizntal Pos B | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise maintenance to investigate the mill's horizontal position | 0
FAL72504 | 2000-F72-PID-PR-10001 | F72MB411 Trommel Spray | Digital Input | Alarm |  |  | 3 | FCV72408 < 3% Open | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Advise field operator to investigate | C
FAL72506 | 2000-F72-PID-PR-10001 | F72WS411 Feed Water | Digital Input | Alarm |  |  | 3 | XV72457 = Closed | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Plant Tripped | Logging | Scrubber fan tripped. Check water valve is open, else investigate in field. | C
ZA72478A | 2000-F72-PID-PR-10002 | F72MB412 Vertical Posn A | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise maintenance to investigate the mill's vertical position | 0
ZA72478B | 2000-F72-PID-PR-10002 | F72MB412 Vertical Posn B | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise maintenance to investigate the mill's vertical position | 0
ZA72519A | 2000-F72-PID-PR-10002 | F72MB412 Horizntal Pos A | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise maintenance to investigate the mill's horizontal position | 0
ZA72519B | 2000-F72-PID-PR-10002 | F72MB412 Horizntal Pos B | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise maintenance to investigate the mill's horizontal position | 0
FAL72516 | 2000-F72-PID-PR-10002 | F72MB412 Trommel Spray | Digital Input | Alarm |  |  | 3 | FCV72428 < 3% Open | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Advise field operator to investigate | C
FAL72518 | 2000-F72-PID-PR-10002 | F72WS412 Feed Water | Digital Input | Alarm |  |  | 3 | XV72473 = Closed | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Plant Tripped | Logging | Scrubber fan tripped. Check water valve is open, else investigate in field. | C
LIC72411 | 2000-F72-PID-PR-10001 | F72HP411 Hopper Level | Analogue PID | A_LL | 10 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Transfer pump tripped. Check level controller in auto and feed to hopper is healthy | C
LIC72411 | 2000-F72-PID-PR-10001 | F72HP411 Hopper Level | Analogue PID | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Agitator tripped. Check level controller in auto and feed to hopper is healthy | C
LIC72411 | 2000-F72-PID-PR-10001 | F72HP411 Hopper Level | Analogue PID | A_Hi | 92 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Check level controller is operating as required, that adequate cyclone feed valves are open. Reduce feed rate if required. | C
LIC72411 | 2000-F72-PID-PR-10001 | F72HP411 Hopper Level | Analogue PID | A_HH | 95 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Check level controller is operating as required and that adequate cyclone feed valves are open. Reduce feed rate if required. | C
TIC72432 | 2000-F72-PID-PR-10002 | F72HP412 Temperature | Analogue PID | A_Lo | 30 | °C | 5 | If F72-FV-412 = Not Running: Mask A Lo alarm _ | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check feed and lime feed rate controls are working as intended. | 1
TIC72432 | 2000-F72-PID-PR-10002 | F72HP412 Temperature | Analogue PID | A_Hi | 85 | °C | 5 | If F72-FV-412 = Not Running: Mask A Lo alarm _ | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check feed and lime feed rate controls are working as intended. | 1
TIC72432 | 2000-F72-PID-PR-10002 | F72HP412 Temperature | Analogue PID | A_HH | 90 | °C | 5 | If F72-FV-412 = Not Running: Mask A Lo alarm _ | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Feeder tripped. Check temperature controller in auto and raw water flow is healthy | 1
LIC72431 | 2000-F72-PID-PR-10002 | F72HP412 Hopper Level | Analogue PID | A_LL | 10 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Transfer pump tripped. Check level controller in auto and feed to hopper is healthy | C
LIC72431 | 2000-F72-PID-PR-10002 | F72HP412 Hopper Level | Analogue PID | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Agitator tripped. Check level controller in auto and feed to hopper is healthy | C
LIC72431 | 2000-F72-PID-PR-10002 | F72HP412 Hopper Level | Analogue PID | A_Hi | 92 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Check level controller is operating as required, that adequate cyclone feed valves are open. Reduce feed rate if required. | C
LIC72431 | 2000-F72-PID-PR-10002 | F72HP412 Hopper Level | Analogue PID | A_HH | 95 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Check level controller is operating as required and that adequate cyclone feed valves are open. Reduce feed rate if required. | C
LIC72439 | 2000-F72-PID-PR-10003 | F72TK467 MOL Level | Analogue PID | A_LL | 20 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Agitator and discharge pumps tripped. Check level controllers and lime feed are operating as intended. | C
LIC72439 | 2000-F72-PID-PR-10003 | F72TK467 MOL Level | Analogue PID | A_Lo | 30 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check level controllers and lime feed rate. | C
LIC72439 | 2000-F72-PID-PR-10003 | F72TK467 MOL Level | Analogue PID | A_Hi | 80 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check level controllers and lime feed rate. | C
LIC72439 | 2000-F72-PID-PR-10003 | F72TK467 MOL Level | Analogue PID | A_HH | 90 | % | 5 |  | Environmental2: Minor on-site environmental impact, reportable to regulators. | Plant Tripped | Logging | Lime slaking transfer pumps tripped. Evacuate area until levels stabilise and return to safe operating range. | C
FIC72732 | 2000-F72-PID-PR-10015 | F72PP681/2 Nitrate Flow | Analogue PID | A_LL | 0.5 | m3/hr | 5 | 1. Mask A Lo & A LL F72-PP-681 AND 682 = Not _ _ Running 2. Mask A Lo & A LL for 10 seconds on F72-PP-681 OR _ _ 682 start | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Low nitrate flow rate. Advise field operator to check valve line up and for potential loss of containment. | C
FIC72732 | 2000-F72-PID-PR-10015 | F72PP681/2 Nitrate Flow | Analogue PID | A_Lo | 1 | m3/hr | 5 | 1. Mask A Lo & A LL F72-PP-681 AND 682 = Not _ _ Running 2. Mask A Lo & A LL for 10 seconds on F72-PP-681 OR _ _ 682 start | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Rapid (>5 to <15 minutes) | High | Low nitrate flow rate. Advise field operator to check valve line up and for potential loss of containment. | C
FIC72407 | 2000-F72-PID-PR-10001 | F72XM658 Prewetter Water | Analogue PID | A_LL | 51.5 | m3/hr | 5 | 1. Mask A Lo & A LL if F72-MB-411 AND F72-FV-411 = _ _ Not Running 2. Mask A Lo & A LL for 60 seconds on F72-MB-411 _ _ AND F72-FV-411 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
FIC72407 | 2000-F72-PID-PR-10001 | F72XM658 Prewetter Water | Analogue PID | A_Lo | 58 | m3/hr | 5 | 1. Mask A Lo & A LL if F72-MB-411 AND F72-FV-411 = _ _ Not Running 2. Mask A Lo & A LL for 60 seconds on F72-MB-411 _ _ AND F72-FV-411 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
FIC72407 | 2000-F72-PID-PR-10001 | F72XM658 Prewetter Water | Analogue PID | A_Hi | 70.8 | m3/hr | 5 | 1. Mask A Lo & A LL if F72-MB-411 AND F72-FV-411 = _ _ Not Running 2. Mask A Lo & A LL for 60 seconds on F72-MB-411 _ _ AND F72-FV-411 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
FIC72407 | 2000-F72-PID-PR-10001 | F72XM658 Prewetter Water | Analogue PID | A_HH | 77.3 | m3/hr | 5 | 1. Mask A Lo & A LL if F72-MB-411 AND F72-FV-411 = _ _ Not Running 2. Mask A Lo & A LL for 60 seconds on F72-MB-411 _ _ AND F72-FV-411 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
FIC72408 | 2000-F72-PID-PR-10001 | F72HP411 Feed Water | Analogue PID | A_Lo | 21 | m3/hr | 5 | 1. Mask A Lo if F72-MB-411 AND F72-PP-658 = Not _ Running 2. Mask A Lo for 60 seconds on F72-MB-411 AND F72- _ PP-658 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
FIC72408 | 2000-F72-PID-PR-10001 | F72HP411 Feed Water | Analogue PID | A_Hi | 25.7 | m3/hr | 5 | 1. Mask A Lo if F72-MB-411 AND F72-PP-658 = Not _ Running 2. Mask A Lo for 60 seconds on F72-MB-411 AND F72- _ PP-658 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
FIC72408 | 2000-F72-PID-PR-10001 | F72HP411 Feed Water | Analogue PID | A_HH | 28.1 | m3/hr | 5 | 1. Mask A Lo if F72-MB-411 AND F72-PP-658 = Not _ Running 2. Mask A Lo for 60 seconds on F72-MB-411 AND F72- _ PP-658 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
FIC72427 | 2000-F72-PID-PR-10002 | F72XM659 Prewetter Water | Analogue PID | A_LL | 51.5 | m3/hr | 5 | 1. Mask A Lo & A LL if F72-MB-412 AND F72-FV-412 = _ _ Not Running 2. Mask A Lo & A LL for 60 seconds on F72-MB-412 _ _ AND F72-FV-412 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
FIC72427 | 2000-F72-PID-PR-10002 | F72XM659 Prewetter Water | Analogue PID | A_Lo | 58 | m3/hr | 5 | 1. Mask A Lo & A LL if F72-MB-412 AND F72-FV-412 = _ _ Not Running 2. Mask A Lo & A LL for 60 seconds on F72-MB-412 _ _ AND F72-FV-412 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
FIC72427 | 2000-F72-PID-PR-10002 | F72XM659 Prewetter Water | Analogue PID | A_Hi | 70.8 | m3/hr | 5 | 1. Mask A Lo & A LL if F72-MB-412 AND F72-FV-412 = _ _ Not Running 2. Mask A Lo & A LL for 60 seconds on F72-MB-412 _ _ AND F72-FV-412 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
FIC72427 | 2000-F72-PID-PR-10002 | F72XM659 Prewetter Water | Analogue PID | A_HH | 77.3 | m3/hr | 5 | 1. Mask A Lo & A LL if F72-MB-412 AND F72-FV-412 = _ _ Not Running 2. Mask A Lo & A LL for 60 seconds on F72-MB-412 _ _ AND F72-FV-412 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
FIC72428 | 2000-F72-PID-PR-10002 | F72HP412 Feed Water | Analogue PID | A_Lo | 21 | m3/hr | 5 | 1. Mask A Lo if F72-MB-412 AND F72-PP-659 = Not _ Running 2. Mask A Lo for 60 seconds on F72-MB-412 AND F72- _ PP-659 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
FIC72428 | 2000-F72-PID-PR-10002 | F72HP412 Feed Water | Analogue PID | A_Hi | 25.7 | m3/hr | 5 | 1. Mask A Lo if F72-MB-412 AND F72-PP-659 = Not _ Running 2. Mask A Lo for 60 seconds on F72-MB-412 AND F72- _ PP-659 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
FIC72428 | 2000-F72-PID-PR-10002 | F72HP412 Feed Water | Analogue PID | A_HH | 28.1 | m3/hr | 5 | 1. Mask A Lo if F72-MB-412 AND F72-PP-659 = Not _ Running 2. Mask A Lo for 60 seconds on F72-MB-412 AND F72- _ PP-659 Start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate controller and control valve are operating in cascade and/or automatic mode. | 0
LIME RM OFF _ _ | 2000-F72-PID-PR-10003 | F72-PP-656 & 657 Stopped | Misc | Alarm |  |  | 60 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Lime ringmain pumps are stopped. Restart ringmain pump. | 0
NACN RM OFF _ _ | 2000-F72-PID-PR-10005 | F72-PP-675 & 676 Stopped | Misc | Alarm |  |  | 60 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Cyanide ringmain pumps are stopped. Restart ringmain pump. | 0
NAOH RM OFF _ _ | 2000-F72-PID-PR-10006 | F72-PP-673 & 674 Stopped | Misc | Alarm |  |  | 60 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Sodium hydroxide ringmain pumps are stopped. Restart ringmain pump. | 0
F72AG467 OFF _ | 2000-F72-PID-PR-10003 | F72AG467 Off Alarm | Misc | Alarm |  |  | 5 | LIC72439.PV ≤ A Lo _ | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Restart agitator as soon as possible if safe to do so. | 1
LIME1 FTS ALM _ _ | 2000-F72-PID-PR-10001 | F72PK402 Lime 1 Seq FTS | Misc | Alarm |  |  | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Lime auto sequence failed to start or stop. Check sequence permissives are healthy | C
LIME2 FTS ALM _ _ | 2000-F72-PID-PR-10002 | F72PK402 Lime 2 Seq FTS | Misc | Alarm |  |  | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Lime auto sequence failed to start or stop. Check sequence permissives are healthy | C
F72PS419 NA _ | 2000-F72-PID-PR-10003 | F72PS419 Not Auto | Misc | Alarm |  |  | 30 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Set F72PS419 and XV72464 to auto to ensure line is flushed | 1
F72PS466 NA _ | 2000-F72-PID-PR-10003 | F72PS466 Not Auto | Misc | Alarm |  |  | 30 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Set F72PS466 and XV72465 to auto to ensure line is flushed | 1
F72PS467 NA _ | 2000-F72-PID-PR-10003 | F72PS467 Not Auto | Misc | Alarm |  |  | 30 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Set F72PS467 and XV72466 to auto to ensure line is flushed | 1
F72LU411 T3A _ | 2000-F72-PID-PR-10001 | F72MB411 Grease Fail | Misc | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Failed greasing cycle. Check pump is in AUT, attempt manual grease cycle, investigate in field. | 1
F72LU412 T3A _ | 2000-F72-PID-PR-10002 | F72MB412 Grease Fail | Misc | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Failed greasing cycle. Check pump is in AUT, attempt manual grease cycle, investigate in field. | 1
TI72412 | 2000-F72-PID-PR-10001 | F72HP411 Temperature | Analogue Input | SS-DUAL DV | 5 | °C | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Dual redundancy deviation between temperature transmitter process variables. Investigate differential. | 1
TI72432 | 2000-F72-PID-PR-10001 | F72HP412 Temperature | Analogue Input | SS-DUAL DV | 5 | °C | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Dual redundancy deviation between temperature transmitter process variables. Investigate differential. | 1
LI72531 | 2000-F72-PID-PR-10005 | F72TK437 Cyanide Level | Analogue Input | SS-DUAL DV | 5 | % | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Dual redundancy deviation between level transmitter process variables. Investigate differential. | 1
LI72535 | 2000-F72-PID-PR-10005 | F72TK439 Cyanide Level | Analogue Input | SS-DUAL DV | 5 | % | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Dual redundancy deviation between level transmitter process variables. Investigate differential. | 1
LI72591 | 2000-F72-PID-PR-10006 | F72TK434 Caustic Level | Analogue Input | SS-DUAL DV | 5 | % | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Dual redundancy deviation between level transmitter process variables. Investigate differential. | 1
LI72602 | 2000-F72-PID-PR-10007 | F72TK435 Acid Storage | Analogue Input | SS-DUAL DV | 5 | % | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Dual redundancy deviation between level transmitter process variables. Investigate differential. | 1
LI72612 | 2000-F72-PID-PR-10007 | F72TK424 Acid Dilution | Analogue Input | SS-DUAL DV | 5 | % | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Dual redundancy deviation between level transmitter process variables. Investigate differential. | 1
FIC72407 | 2000-F72-PID-PR-10001 | F72XM658 Prewetter Water | Analogue PID | DV | 10 | % of range | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Setpoint deviation. Check controller / valve mode in appropriate mode. Investigate deviation. | 1
FIC72408 | 2000-F72-PID-PR-10001 | F72HP411 Feed Water | Analogue PID | DV | 10 | % of range | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Setpoint deviation. Check controller / valve mode in appropriate mode. Investigate deviation. | 1
FIC72427 | 2000-F72-PID-PR-10002 | F72XM659 Prewetter Water | Analogue PID | DV | 10 | % of range | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Setpoint deviation. Check controller / valve mode in appropriate mode. Investigate deviation. | 1
FIC72428 | 2000-F72-PID-PR-10002 | F72HP412 Feed Water | Analogue PID | DV | 10 | % of range | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Setpoint deviation. Check controller / valve mode in appropriate mode. Investigate deviation. | 1
FAH72168 | 2000-F24-PID-PR-10028 | F72SE424 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
FAH72169 | 2000-F24-PID-PR-10028 | F72SE425 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
FAH72170 | 2000-F24-PID-PR-10028 | F72SE426 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
FAH72177 | 2000-F24-PID-PR-10028 | F72SE454 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
FAH72178 | 2000-F24-PID-PR-10028 | F72SE455 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
FAH72179 | 2000-F24-PID-PR-10028 | F72SE456 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
FAH72180 | 2000-F24-PID-PR-10028 | F72SE457 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
FAH72181 | 2000-F24-PID-PR-10028 | F72SE458 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
FAH72182 | 2000-F24-PID-PR-10028 | F72SE459 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
FAH72183 | 2000-F24-PID-PR-10028 | F72SE460 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
FAH72184 | 2000-F24-PID-PR-10028 | F72SE461 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
FAH72185 | 2000-F24-PID-PR-10028 | F72SE462 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
FAH72186 | 2000-F24-PID-PR-10028 | F72SE504 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
FAH72187 | 2000-F24-PID-PR-10028 | F72SE466 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 2
TI72633 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Feed | Analogue Input | A_Lo | 5 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check cooling water Chiller capacity and that Chillers are healthy | 1
TI72633 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Feed | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check cooling water Chiller capacity and that Chillers are healthy | 1
PI72634 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Feed | Analogue Input | A_Lo | 160 | kPa | 5 | Mask A Lo if F72-PK-405 Not Running (XI72629 inactive) _ for > 1 minute | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check that the cooling water circuit and pumps are operating as required. Advise Field Operator / Maintenance to investigate in the field. | 1
PI72634 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Feed | Analogue Input | A_Hi | 360 | kPa | 5 | Mask A Lo if F72-PK-405 Not Running (XI72629 inactive) _ for > 1 minute | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check that the cooling water circuit and pumps are operating as required. Advise Field Operator / Maintenance to investigate in the field. | 1
PI72634 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Feed | Analogue Input | A_HH | 990 | kPa | 5 | Mask A Lo if F72-PK-405 Not Running (XI72629 inactive) _ for > 1 minute | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check that the cooling water circuit and pumps are operating as required. Advise Field Operator / Maintenance to investigate in the field. | 1
TI72635 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Rturn | Analogue Input | A_Lo | 5 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check cooling water Chiller capacity and that Chillers are healthy | 1
TI72635 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Rturn | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check cooling water Chiller capacity and that Chillers are healthy | 1
PI72636 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Rturn | Analogue Input | A_Lo | 100 | kPa | 5 | Mask A Lo if F72-PK-405 Not Running (XI72629 inactive) _ for > 1 minute | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check that the cooling water circuit and pumps are operating as required. Advise Field Operator / Maintenance to investigate in the field. | 1
PI72636 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Rturn | Analogue Input | A_Hi | 275 | kPa | 5 | Mask A Lo if F72-PK-405 Not Running (XI72629 inactive) _ for > 1 minute | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check that the cooling water circuit and pumps are operating as required. Advise Field Operator / Maintenance to investigate in the field. | 1
PI72636 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Rturn | Analogue Input | A_HH | 990 | kPa | 5 | Mask A Lo if F72-PK-405 Not Running (XI72629 inactive) _ for > 1 minute | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check that the cooling water circuit and pumps are operating as required. Advise Field Operator / Maintenance to investigate in the field. | 1
FIC72632 | 2000-F72-PID-PR-10011 | F72PK405 Cool Wtr Feed | Analogue PID | DV | 10 | % of range | 0 | Mask deviation alarm if F72-PK-405 Not Running (XI72629 inactive) for > 1 minute | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check controller operating mode is in auto. Else, advise Field Operator / Maintenance to check instrumentation and valve in the field. | 1
XA72630 | 2000-F72-PID-PR-10011 | F72PK405 Fault | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Oxygen plant general fault. Liaise with Linde team. | 1
XA72631 | 2000-F72-PID-PR-10011 | F72PK405 Fire | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel to evacuate area. | 1
F72RIO004 PS1 _ | - | F72RIO004 PS1 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure. | 1
F72RIO004 PS2 _ | - | F72RIO004 PS2 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure. | 1
F72LU411 PS _ | - | F72LU411 PS 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure. | 1
F72LU412 PS _ | - | F72LU412 PS 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure. | 1
F72TR072 WTH _ | - | F72TR072 Temp Hi | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrician to investigate high transformer winding temperature alarm | 1
PI72638 | 2000-F72-PID-PR-10007 | F72PP424 Discharge | Analogue Input | A_Lo | 200 | kPa | 5 | Mask A Lo if F72-PP-424 not running _ Mask A Lo for 10 seconds of F72-PP-424 start _ | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operating off pump curve. Advise Field Operator to check for spillage. Advise Maintenance to check pump health. | 1
PI72638 | 2000-F72-PID-PR-10007 | F72PP424 Discharge | Analogue Input | A_Hi | 400 | kPa | 5 | Mask A Lo if F72-PP-424 not running _ Mask A Lo for 10 seconds of F72-PP-424 start _ | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operating above normal operating pressure. Investigate in field. Check for deadhead. | 1
PI72638 | 2000-F72-PID-PR-10007 | F72PP424 Discharge | Analogue Input | A_HH | 460 | kPa | 5 | Mask A Lo if F72-PP-424 not running _ Mask A Lo for 10 seconds of F72-PP-424 start _ | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Pump tripped. Investigate in field. Check for deadhead. | 1
F72GE172CBTRP | - | F72-GE-172 GEN CB TRP | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to manually change over generator | 1