## Revisions
PROCESS CONTROL TABLES
REVISION HISTORY
KCGM GROWTH PROJECT
2000-F13-LST-PR-10001
NORTHERN STAR RESOURCES LIMITED
Revision | Document Changes | Date
A for Internal Review | - Vendor Data TBC highlighted yellow or in red-text
2024-07-15
B for Client Review | - Vendor Data TBC highlighted yellow or in red-text
2024-09-06
0 for Design | - Vendor Data TBC highlighted yellow or in red-text
0 for Design |  | 2025-01-22
1 - Post software FAT update | - Updated with post-software FAT punch items (Jira)
| - Updated with change requests (internal document) | 2025-11-18
- Changed transitions / steps are highlighted orange
2 - Prepared for SAT | - Strikthrough text and highlighting removed

## 1. Analogue Input
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - MILLING & CLASSIFICATION (F13)
2000-F13-LST-PR-10001
ANALOGUE INSTRUMENTS (AI)
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [12 empty] | C1 Sign Off |  | C2 Sign Off |  | C1 Comments
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Comments | Rev | Change Date | Change Reference | OK | Date | OK | Date
|  |  |  | LT13036 | LI13036 | 2000-F13-PID-PR-10001 | F13-BN-402 Emergency Feed Bin Level Transmitter | F13BN402 Level | 1 | 0 | 100 | % | [12 empty] | 20 | 5 | 30 | 5 | 80 | 5 | 90 | 5 | Mask A_Lo AND A_LL if Emergency Feeder is not selected for Duty operation on faceplate, F13FA400_FP1. | Alarm setpoints TBC during commissioning. A_LL = Trip F13-FA-414 | B
|  |  |  | TE13003A | TI13003A | 2000-F13-PID-PR-10001 | F13-FA-411 Coarse Ore Reclaim Feeder 1 Motor Phase U RTD | F13FA411 U RTD | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 180 | 5 |  | 2000-ME004-F13-10001 2000-ME004-F13-10002 A_Hi = Alarm A_HH = Trip F13-FA-411 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | TE13003B | TI13003B | 2000-F13-PID-PR-10001 | F13-FA-411 Coarse Ore Reclaim Feeder 1 Motor Phase V RTD | F13FA411 V RTD | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 180 | 5 |  | 2000-ME004-F13-10001 2000-ME004-F13-10002 A_Hi = Alarm A_HH = Trip F13-FA-411 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | TE13003C | TI13003C | 2000-F13-PID-PR-10001 | F13-FA-411 Coarse Ore Reclaim Feeder 1 Motor Phase W RTD | F13FA411 W RTD | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 180 | 5 |  | 2000-ME004-F13-10001 2000-ME004-F13-10002 A_Hi = Alarm A_HH = Trip F13-FA-411 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | TE13003D | TI13003D | 2000-F13-PID-PR-10001 | F13-FA-411 Coarse Ore Reclaim Feeder 1 Motor DE Bearing RTD | F13FA411 DE Brg RTD | 1 | -5 | 200 | °C | [16 empty] | 110 | 5 | 120 | 5 |  | 2000-ME004-F13-10001 2000-ME004-F13-10002 A_Hi = Alarm A_HH = Trip F13-FA-411 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | TE13003E | TI13003E | 2000-F13-PID-PR-10001 | F13-FA-411 Coarse Ore Reclaim Feeder 1 Motor NDE Bearing RTD | F13FA411 NDE Brg RTD | 1 | -5 | 200 | °C | [16 empty] | 110 | 5 | 120 | 5 |  | 2000-ME004-F13-10001 2000-ME004-F13-10002 A_Hi = Alarm A_HH = Trip F13-FA-411 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | TE13012 | TI13012 | 2000-F13-PID-PR-10001 | F13-FA-411 Coarse Ore Reclaim Feeder 1 Gearboox Sump RTD | F13FA411 G/box Sump | 1 | -5 | 200 | °C | [6 empty] | 70 | 5 | [10 empty] | 90 | 5 |  | 2000-ME004-M01-10002 A_HH = Trip F13-FA-411 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | TE13013 | TI13013 | 2000-F13-PID-PR-10001 | F13-FA-411 Coarse Ore Reclaim Feeder 1 Gearboox High Speed Bearing RTD | F13FA411 G/box HS Brg | 1 | -5 | 200 | °C | [16 empty] | 60 | 5 | 90 | 5 |  | 2000-ME004-M01-10002 A_Hi = Alarm A_HH = Trip F13-FA-411 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691 |  |  |  |  | tested by disconnection for IOP. No tester available for range test. Range test completed 15/05/2026 LR
|  |  |  | TE13004A | TI13004A | 2000-F13-PID-PR-10001 | F13-FA-412 Coarse Ore Reclaim Feeder 2 Motor Phase U RTD | F13FA412 U RTD | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 180 | 5 |  | 2000-ME004-F13-10001 2000-ME004-F13-10003 A_Hi = Alarm A_HH = Trip F13-FA-412 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | TE13004B | TI13004B | 2000-F13-PID-PR-10001 | F13-FA-412 Coarse Ore Reclaim Feeder 2 Motor Phase V RTD | F13FA412 V RTD | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 180 | 5 |  | 2000-ME004-F13-10001 2000-ME004-F13-10003 A_Hi = Alarm A_HH = Trip F13-FA-412 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | TE13004C | TI13004C | 2000-F13-PID-PR-10001 | F13-FA-412 Coarse Ore Reclaim Feeder 2 Motor Phase W RTD | F13FA412 W RTD | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 180 | 5 |  | 2000-ME004-F13-10001 2000-ME004-F13-10003 A_Hi = Alarm A_HH = Trip F13-FA-412 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | TE13004D | TI13004D | 2000-F13-PID-PR-10001 | F13-FA-412 Coarse Ore Reclaim Feeder 2 Motor DE Bearing RTD | F13FA412 DE Brg RTD | 1 | -5 | 200 | °C | [16 empty] | 110 | 5 | 120 | 5 |  | 2000-ME004-F13-10001 2000-ME004-F13-10003 A_Hi = Alarm A_HH = Trip F13-FA-412 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | TE13004E | TI13004E | 2000-F13-PID-PR-10001 | F13-FA-412 Coarse Ore Reclaim Feeder 2 Motor NDE Bearing RTD | F13FA412 NDE Brg RTD | 1 | -5 | 200 | °C | [16 empty] | 110 | 5 | 120 | 5 |  | 2000-ME004-F13-10001 2000-ME004-F13-10003 A_Hi = Alarm A_HH = Trip F13-FA-412 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | TE13022 | TI13022 | 2000-F13-PID-PR-10001 | F13-FA-412 Coarse Ore Reclaim Feeder 2 Gearboox Sump RTD | F13FA412 G/box Sump | 1 | -5 | 200 | °C | [6 empty] | 70 | 5 | [10 empty] | 90 | 5 |  | 2000-ME004-M01-10002 A_HH = Trip F13-FA-412 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | TE13023 | TI13023 | 2000-F13-PID-PR-10001 | F13-FA-412 Coarse Ore Reclaim Feeder 2 Gearboox High Speed Bearing RTD | F13FA412 G/box HS Brg | 1 | -5 | 200 | °C | [16 empty] | 60 | 5 | 90 | 5 |  | 2000-ME004-M01-10002 A_Hi = Alarm A_HH = Trip F13-FA-412 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691 |  |  |  |  | Only tested the IOP and ambient temp reading. Range Tested 15/05/2026 LR
|  |  |  | TE13032 | TI13032 | 2000-F13-PID-PR-10001 | F13-FA-414 Emergency Feeder Gearboox Sump RTD | F13FA414 G/box Sump | 1 | -5 | 200 | °C | [6 empty] | 70 | 5 | [10 empty] | 90 | 5 |  | 2000-ME004-M01-10003 A_HH = Trip F13-FA-414 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | TE13033 | TI13033 | 2000-F13-PID-PR-10001 | F13-FA-414 Emergency Feeder Gearboox High Speed Bearing RTD | F13FA414 G/box HS Brg | 1 | -5 | 200 | °C | [16 empty] | 60 | 5 | 90 | 5 |  | 2000-ME004-M01-10003 A_Hi = Alarm A_HH = Trip F13-FA-414 | 1 | 2025-04-30 | No actioned required. https://pastech-2955.atlassian.net/browse/KAN-1691
|  |  |  | LT13037 | LI13037 | 2000-F13-PID-PR-10001 | F13-BN-403 Sag Mill Ball Charger Feed Bin Level Transmitter | F13BN403 Level | 1 | 0 | 100 | % | [12 empty] | 10 | 5 | 30 | 5 | 80 | 5 | 90 | 5 |  | Alarm setpoints TBC during commissioning. A_LL = Trip F13-BLC-401 | B
|  |  |  | PDIT13067 | PDI13067 | 2000-F13-PID-PR-10001 | F13DC402 Reclaim Tunnel Dust Collector Air Chambers Differential Pressure Indicating Transmitter | F13DC402 Pressure Delta | 1 | 0 | 2500 | Pa |  |  |  | 800 | 5 |  | 1300 | 5 |  |  |  |  | 300 | 5 |  |  |  |  | 1800 | 5 | Mask if F13-DC-402 Not Running Mask for 10 seconds (TBC) on F13-DC-402 start-up | A_HH for more than 1 hour = Trip F13-FN-402 P_Hi = Logging Event (pulse cleaning started by Dust Collector Controller) P_Lo = Logging Event (pulse cleaning stopped by Dust Collector Controller) A_LL = Warning (investigate F13-DC-402 and PDIT for faults) | 1 | 2025-04-10 | https://pastech-2955.atlassian.net/browse/KAN-1669 |  |  |  |  | Instrument cannot test range Range and alarms tested - JM
|  |  |  | F13CALC10001 | WI13035 | 2000-F13-PID-PR-10001 | F13BLC401 SAG Mill Ball Charger Instantaneous Mill Ball Tonnage | F13BLC401 Ball Tonnage | 1 | 0 | 30 | t/h | [21 empty] | Range calculated as 2880*8.03/1000 rounded up Design charger addition rate = 2880 balls/h (2000-ME087-M02-10001) Weight per ball = 8.04 kg/ball (2000-F00-DSH-ME-11087) | 0
|  |  |  | ZE13310A | ZI13310A | 2000-F13-PID-PR-10004 | F19-CR-431 Trolley Position | F13CR453 TrolleyPosition | 1 | 0 | 8000 | mm | [21 empty] | To be calibrated during commissioning. | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | justin checking things
|  |  |  | ZE13310B | ZI13310B | 2000-F13-PID-PR-10004 | F19-CR-431 Hoist Position | F13CR453 HoistPosition | 1 | 0 | 23300 | mm | [9 empty] | 23200 | [11 empty] | To be calibrated during commissioning. | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | justin checking things MSH 15/08/2026: based on field input, need to limit how far hoist can go down not to slam on ground, will change PLO in DCS to PHH since it is not used
|  |  |  | AT13285A | EI13285A | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Magnet Voltage Transmitter | F13BLC402 Voltage | 1 | 0 | 300 | V DC | [16 empty] | 285 | 5 |  |  |  | Vendor Reference : K1_DC_V K1 – DC Voltage Transducer. 0-300 V DC 4-20 mA A_Hi = Alarm | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876
|  |  |  | AT13285B | II13285B | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Magnet Current Transmitter | F13BLC402 Current | 1 | 0 | 50 | A DC | [16 empty] | 47.5 | 5 |  |  |  | Vendor Reference : K2_DC_I K2 – DC Current Transducer. 0-50 A DC 4-20 mA A_Hi = Alarm | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876
|  |  |  | AT13285C | WI13285C | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Load Cell Output Transmitter | F13BLC402 Load Cell | 1 | 0 | 2500 | kg |  |  |  | 1110 | 5 | [11 empty] | x = 1575 y = 1125 See comments for logic | 5 | x = 1750 y = 1250 See comments for logic | 5 |  | Vendor Reference : U1_LC U1 Load Cell Transmitter 0-2500 kg 4-20 mA A_Hi = Alarm A_HH = F13-CR-453 Hoist interlock P_Lo = F13-BLC-402 Max Duty Cycle interlock condition Value TBC during commissioning Alarm setpoints to be confirmed during commissioning P_Lo needs to be set to weight when magnet is unloaded (TBC during commissioning) Logic: If XC13230A, XC13230B, XC13234A, XC13234B OR XC13234C = Energised AND WI13285C.PV >= x A_Hi or x A_HH then Alarm If XC13230A, XC13230B, XC13234A, XC13234B AND XC13234C = De-energised AND WI13285C.PV >= y A_Hi or y A_HH then Alarm | 1 | 2025-05-27 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | 15/08/26 MSH: unloaded magnet weighs 1089, PLO set to 1110
|  |  |  | YI13059AS | YI13059A | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Rock Ore Camera p80 | F13CV403 p80 | 1 | 0 | 260 | mm | [16 empty] | 130 | 30 |  |  | Mask if F13-CV-403 is Not Running | SoftTag From PVX Camera OPC Server. Hold last known process variable if YI13059C = FAULT The high alarm from FLS calculated max p80 (Stage 1 PDC source 51) | 0
|  |  |  | YI13059BS | YI13059B | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Rock Ore Camera Top Size | F13CV403 Top Size | 1 | 0 | 480 | mm | [16 empty] | 240 | 30 |  |  | Mask if F13-CV-403 is Not Running | SoftTag From PVX Camera OPC Server. Hold last known process variable if YI13059C = FAULT The high alarm from FLS simulated max p100 (Stage 1 PDC source 51) | 0
|  |  |  | VT13060A | VI13060A | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Drive Pulley Vibration Transmitter 1 | F13CV403 Drive Pulley | 1 | 0 | 45 | mm/s | [16 empty] | 7 | 5 | 10 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | B
|  |  |  | VT13060B | VI13060B | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Drive Pulley Vibration Transmitter 2 | F13CV403 Drive Pulley | 1 | 0 | 45 | mm/s | [16 empty] | 7 | 5 | 10 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | B
|  |  |  | TT13060A | TI13060A | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Drive Pulley Vibration Transmitter 1 | F13CV403 Drive Pulley | 1 | -5 | 80 | °C | [16 empty] | 60 | 5 | 70 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | B
|  |  |  | TT13060B | TI13060B | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Drive Pulley Vibration Transmitter 2 | F13CV403 Drive Pulley | 1 | -5 | 80 | °C | [16 empty] | 60 | 5 | 70 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | B
|  |  |  | WIT13055 | WI13055 | 2000-F13-PID-PR-10001 | F13WD403 SAG Mill Feed Weightometer Weightometer Transmitter | F13CV403 SAG Feed Wet | 1 | 0 | 3500 | t/h |  |  |  | 10 | 5 | [9 empty] | 1200 | 5 | 2180 | 5 |  |  | 1. Mask A_Lo if F13-FA-411, F13-FA-412 AND F13-FA-414 Not Running 2. Mask A_Lo for 120 seconds (TBC) after F13-FA-411, F13-FA-412 OR F13-FA-414 Start Signal | A_Hi = F13-WD-403 Design Capacity 2000-F00-DSH-ME-11021 A_Lo = Warning A_Hi = Warning P_Lo = F13-SEQ-0021 Transition 6 Condition Alarm setpoints and delays TBC during commissioning. | B | [6 empty] | F13-SEQ-0024 Updates
|  |  |  | TE13991A | TI13991A | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Motor Phase U RTD | F13CV403 U RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Teco Maxe3 Motor Catalogue A_Lo = Alarm A_LL = Trip F13-CV-403 | B
|  |  |  | TE13991B | TI13991B | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Motor Phase V RTD | F13CV403 V RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Teco Maxe3 Motor Catalogue A_Lo = Alarm A_LL = Trip F13-CV-403 | B
|  |  |  | TE13991C | TI13991C | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Motor Phase W RTD | F13CV403 W RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Teco Maxe3 Motor Catalogue A_Lo = Alarm A_LL = Trip F13-CV-403 | B
|  |  |  | TE13991D | TI13991D | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Motor DE Bearing RTD | F13CV403 DE Brg RTD | 1 | -5 | 200 | °C | [16 empty] | 90 | 5 | 95 | 5 |  | Teco Maxe3 Motor Catalogue A_Lo = Alarm A_LL = Trip F13-CV-403 | B
|  |  |  | TE13991E | TI13991E | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Motor NDE Bearing RTD | F13CV403 NDE Brg RTD | 1 | -5 | 200 | °C | [16 empty] | 90 | 5 | 95 | 5 |  | Teco Maxe3 Motor Catalogue A_Lo = Alarm A_LL = Trip F13-CV-403 | B
|  |  |  | SS-DUAL LIT13076 AND LIT13086 | LI13076 | 2000-F13-PID-PR-10002 | F13-HP-401 Primary Cyclone Feed Hopper Level Indicating Transmitter | F13HP401 Level | 1 | 0 | 100 | % | [21 empty] | Set up as SS-DUAL with LIT13076 and LIT13086 Deviation (DL) = 10% (TBC during commissioning) Set up to 'Maintain PV Value' on deviation and alarm | 1 | 7/04/2025 20/05/2025 | Cyclones design change following F28 FAT. https://pastech-2955.atlassian.net/browse/KAN-1909 |  |  |  |  | PL: Need HMI indication of fialed instrument as well as operator selector option, DV alarm configured for both this block and LIC block per Justin's request | 1 | 45754 | Design change. Cyclone update following F28 FAT
|  |  |  | LIT13086 Used above (SS_DUAL). Line duplicated for test record |  | 2000-F13-PID-PR-10002 | F13-HP-401 Primary Cyclone Feed Hopper Level Indicating Transmitter | F13HP401 Level | 1 | 0 | 100 | % | [21 empty] | Set up as SS-DUAL with LIT13076 and LIT13086 Deviation (DL) = 10% (TBC during commissioning) Set up to 'Maintain PV Value' on deviation and alarm | 1 | 7/04/2025 20/05/2025 | Cyclones design change following F28 FAT. https://pastech-2955.atlassian.net/browse/KAN-1909 | [5 empty] | 1 | 45754 | Design change. Cyclone update following F28 FAT
|  |  |  | DIT13090 | DI13090 | 2000-F13-PID-PR-10002 | F13-PP-401 Cyclone Feed Pump Discharge Density Indicating Transmitter | F13CY401 Feed Density | 1 | 1 | 3 | t/m3 | [22 empty] | 1 | 2025-03-06 | PCT alignment action register (density transmitters to align with F16,17,18)
|  |  |  | F13CALC10006 | WI13090 | 2000-F13-PID-PR-10002 | F13CY401 Primary Cyclone Cluster Feed Solids | F13CY401 Feed Solids | 1 | 0 | 20000 | t/h | [21 empty] | 2000-F00-CAL-PR-10001 | 0
|  |  |  | FIT13112 | FI13112 | 2000-F13-PID-PR-10002 | F14-CY-411 Gravity Cyclone 1 Feed Flow Indicating Transmitter | F14CY411 Feed | 1 | 0 | 2170 | m3/h | [14 empty] | 500 | 10 | 1500 | 10 |  |  | For A_Lo alarms: 1. Mask if XV13110 closed or F13-PP-401 stopped. 2. Mask for 5 seconds after XV13110 is opened. 3. Mask for 10 seconds on F13-PP-401 start-up. | 2000-F00-CAL-PR-10001. Alarm setpoints to be confirmed during commissioning. | 2 | 2025-04-08 | https://pastech-2955.atlassian.net/browse/KAN-1661 |  |  |  |  | JDM: Configured for A_Lo alarm only. Accepted
|  |  |  | FIT13113 | FI13113 | 2000-F13-PID-PR-10002 | F14-CY-412 Gravity Cyclone 2 Feed Flow Indicating Transmitter | F14CY412 Feed | 1 | 0 | 2170 | m3/h | [14 empty] | 500 | 10 | 1500 | 10 |  |  | For A_Lo alarms: 1. Mask if XV13111 closed or F13-PP-401 stopped. 2. Mask for 5 seconds after XV13111 is opened. 3. Mask for 10 seconds on F13-PP-401 start-up. | 2000-F00-CAL-PR-10001. Alarm setpoints to be confirmed during commissioning. | 2 | 2025-04-08 | https://pastech-2955.atlassian.net/browse/KAN-1661 |  |  |  |  | JDM: Configured for A_Lo alarm only. Accepted
|  |  |  | F13CY401A_VS | VI13120A | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 1 RMS Vibration | F13CY401A Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone01RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401A_RS | F13CY401A_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 1 Roping Index | F13CY401A Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone01RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401A_AS | F13CY401A_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 1 Active Mode Number | F13CY401A Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone01ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401B_VS | VI13120B | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 2 RMS Vibration | F13CY401B Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone02RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401B_RS | F13CY401B_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 2 Roping Index | F13CY401B Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone02RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401B_AS | F13CY401B_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 2 Active Mode Number | F13CY401B Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone02ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401C_VS | VI13120C | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 3 RMS Vibration | F13CY401C Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone03RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401C_RS | F13CY401C_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 3 Roping Index | F13CY401C Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone03RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401C_AS | F13CY401C_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 3 Active Mode Number | F13CY401C Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone03ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401D_VS | VI13120D | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 4 RMS Vibration | F13CY401D Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone04RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401D_RS | F13CY401D_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 4 Roping Index | F13CY401D Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone04RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401D_AS | F13CY401D_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 4 Active Mode Number | F13CY401D Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone04ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401E_VS | VI13120E | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 5 RMS Vibration | F13CY401E Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone05RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401E_RS | F13CY401E_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 5 Roping Index | F13CY401E Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone05RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401E_AS | F13CY401E_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 5 Active Mode Number | F13CY401E Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone05ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401F_VS | VI13120F | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 6 RMS Vibration | F13CY401F Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone06RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401F_RS | F13CY401F_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 6 Roping Index | F13CY401F Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone06RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401F_AS | F13CY401F_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 6 Active Mode Number | F13CY401F Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone06ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401G_VS | VI13120G | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 7 RMS Vibration | F13CY401G Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone07RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401G_RS | F13CY401G_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 7 Roping Index | F13CY401G Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone07RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401G_AS | F13CY401G_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 7 Active Mode Number | F13CY401G Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone07ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401H_VS | VI13120H | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 8 RMS Vibration | F13CY401H Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone08RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401H_RS | F13CY401H_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 8 Roping Index | F13CY401H Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone08RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401H_AS | F13CY401H_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 8 Active Mode Number | F13CY401H Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone08ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401J_VS | VI13120J | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 9 RMS Vibration | F13CY401J Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone09RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401J_RS | F13CY401J_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 9 Roping Index | F13CY401J Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone09RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401J_AS | F13CY401J_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 9 Active Mode Number | F13CY401J Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone09ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401K_VS | VI13120K | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 10 RMS Vibration | F13CY401K Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone10RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401K_RS | F13CY401K_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 10 Roping Index | F13CY401K Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone10RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401K_AS | F13CY401K_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 10 Active Mode Number | F13CY401K Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone10ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401M_VS | VI13120M | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 11 RMS Vibration | F13CY401M Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone11RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401M_RS | F13CY401M_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 11 Roping Index | F13CY401M Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone11RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401M_AS | F13CY401M_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 11 Active Mode Number | F13CY401M Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone11ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401N_VS | VI13120N | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 12 RMS Vibration | F13CY401N Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone12RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401N_RS | F13CY401N_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 12 Roping Index | F13CY401N Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone12RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401N_AS | F13CY401N_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 12 Active Mode Number | F13CY401N Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone12ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401P_VS | VI13120P | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 13 RMS Vibration | F13CY401P Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone13RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401P_RS | F13CY401P_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 13 Roping Index | F13CY401P Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone13RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401P_AS | F13CY401P_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 13 Active Mode Number | F13CY401P Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone13ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401Q_VS | VI13120Q | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 14 RMS Vibration | F13CY401Q Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone14RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401Q_RS | F13CY401Q_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 14 Roping Index | F13CY401Q Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone14RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401Q_AS | F13CY401Q_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 14 Active Mode Number | F13CY401Q Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone14ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401R_VS | VI13120R | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 15 RMS Vibration | F13CY401R Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone15RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0 | [6 empty] | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F13CY401R_RS | F13CY401R_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 15 Roping Index | F13CY401R Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone15RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401R_AS | F13CY401R_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 15 Active Mode Number | F13CY401R Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone15ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F14CY411_VS | VI13120S | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 16 RMS Vibration | F14CY411 Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone16RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 1 | 2025-06-25 | PL-317 |  |  |  |  | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F14CY411_RS | F14CY411_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 16 Roping Index | F14CY411 Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone16RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 1 | 2025-06-25 | PL-317
|  |  |  | F14CY411_AS | F14CY411_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 16 Active Mode Number | F14CY411 Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone16ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 1 | 2025-06-25 | PL-317
|  |  |  | F14CY412_VS | VI13120T | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 17 RMS Vibration | F14CY412 Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone17RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 1 | 2025-06-25 | PL-317 |  |  |  |  | Soft tag via Modbus. Tested in field by tapping to simulate vibration. Was previously tested in field to VSD with vendor
|  |  |  | F14CY412_RS | F14CY412_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 17 Roping Index | F14CY412 Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone17RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 1 | 2025-06-25 | PL-317
|  |  |  | F14CY412_AS | F14CY412_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 17 Active Mode Number | F14CY412 Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone17ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 1 | 2025-06-25 | PL-317
|  |  |  | F13CY401U_VS | VI13120U | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 18 RMS Vibration | F13CY401U Vibration | 1 | 0 | 10 | G | [21 empty] | SoftTag Synertrex Ref: Cyclone18RMSVibrationValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401U_RS | F13CY401U_RIV | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 18 Roping Index | F13CY401U Roping Index | 1 | 0 | 125 | % | [21 empty] | SoftTag Synertrex Ref: Cyclone18RopingIndexValue Alarm setpoints TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | F13CY401U_AS | F13CY401U_AMN | 2000-F13-PID-PR-10002 | F13CY401CP01 Primary Cyclone Cluster Synertrix Rope Detection Panel Cyclone 18 Active Mode Number | F13CY401U Active Mode | 1 | 0 | 4 | - | [21 empty] | SoftTag Synertrex Ref: Cyclone18ActiveModeNumberValue 0 = OFF 1 = ROPING 2 = ROPING TRANSITION 3 = SEMI ROPING 4 = SPLASH Alarm details TBC by Weir From Cyclone Cluster Weir Synertex controller. 2000-ME005-F18-10001 | 0
|  |  |  | LT13130 | LI13130 | 2000-F13-PID-PR-10003 | F13PS404 Mill Discharge End Sump Pump Remote Level Indicating Transmitter | F13PS404 Level | 1 | 0 | 100 | % |  |  |  | 20 15 | 5 |  | 75 60 | 5 | [8 empty] | 80 | 5 | 90 | 5 |  | Alarm setpoints TBC during commissioning. | 2
|  |  |  | VT13172A | VI13172A | 2000-F13-PID-PR-10005 | F13-CV-404 Recycle Conveyor 1 Drive Pulley Vibration Transmitter 1 | F13CV404 Drive Pulley | 1 | 0 | 45 | mm/s | [16 empty] | 7 | 5 | 10 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | A
|  |  |  | VT13172B | VI13172B | 2000-F13-PID-PR-10005 | F13-CV-404 Recycle Conveyor 1 Drive Pulley Vibration Transmitter 2 | F13CV404 Drive Pulley | 1 | 0 | 45 | mm/s | [16 empty] | 7 | 5 | 10 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | A | [6 empty] | As per Manesh, x'ter range need to be configured by communicator - done
|  |  |  | TT13172A | TI13172A | 2000-F13-PID-PR-10005 | F13CV404 Recycle Conveyor 1 Drive Pulley Vibration Transmitter 2 | F13CV404 Drive Pulley | 1 | -5 | 80 | °C | [16 empty] | 60 | 5 | 70 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | B
|  |  |  | TT13172B | TI13172B | 2000-F13-PID-PR-10005 | F13CV404 Recycle Conveyor 1 Drive Pulley Vibration Transmitter 2 | F13CV404 Drive Pulley | 1 | -5 | 80 | °C | [16 empty] | 60 | 5 | 70 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | B | [6 empty] | As per Manesh, x'ter range need to be configured by communicator - done
|  |  |  | VT13199A | VI13199A | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Drive Pulley Vibration Transmitter 1 | F13CV405 Drive Pulley | 1 | 0 | 45 | mm/s | [16 empty] | 7 | 5 | 10 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | A
|  |  |  | VT13199B | VI13199B | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Drive Pulley Vibration Transmitter 2 | F13CV405 Drive Pulley | 1 | 0 | 45 | mm/s | [16 empty] | 7 | 5 | 10 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | A
|  |  |  | TT13199A | TI13199A | 2000-F13-PID-PR-10005 | F13CV405 Recycle Conveyor 2 Drive Pulley Vibration Transmitter 2 | F13CV405 Drive Pulley | 1 | -5 | 80 | °C | [16 empty] | 60 | 5 | 70 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | B
|  |  |  | TT13199B | TI13199B | 2000-F13-PID-PR-10005 | F13CV405 Recycle Conveyor 2 Drive Pulley Vibration Transmitter 2 | F13CV405 Drive Pulley | 1 | -5 | 80 | °C | [16 empty] | 60 | 5 | 70 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | B
|  |  |  | WIT13195 | WI13195 | 2000-F13-PID-PR-10005 | F13WD405 Recycle Conveyor 2 Weightometer Transmitter | F13CV405 RC Feed Wet | 1 | 0 | 1400 | t/h |  |  |  | 10 | 5 | [11 empty] | 610 | 20 |  |  |  | A_Hi = F13-WD-405 Design Capacity 2000-F00-DSH-ME-11021 | 2 | [6 empty] | F13-SEQ-0024 Updates
|  |  |  | LT13221 | LI13221 | 2000-F13-PID-PR-10006 | F13-BN-411 Recycle Crusher Feed Bin Level Transmitter 1 | F13BN411 Crusher C | 1 | 0 | 100 | % |  | 35 | 5 | 50 | 5 |  | 55 | 5 |  | 60 | 5 |  | 20 | 5 | 30 | 5 | 85 | 5 | 90 | 5 |  | Alarm setpoints and process switchpoints to be confirmed during commissioning. Set A_Hi and A_HH to be above overflow chute. A_HH = F13-CV-405 Tripped A_Hi = Open condition for XV13220 to bypass feed from F13-BN-411 A_Lo = Warning A_LL = F13-FV-401 Tripped P_HH = Auto start condition for F13-FV-401 P_Hi = Close condition for XV13220 to direct feed to F13-BN-411 P_Lo = Auto stop condition for F13-FV-401 | B | [6 empty] | Tested A_HH = F13-CV-405 Tripped A_Lo = Warning Not Tested A_Hi = Open condition for XV13220 to bypass feed from F13-BN-411 due to 13CV406 Interlock P_HH = Auto start condition for F13-FV-402 due to FV402 in Interlock P_Lo = Auto stop condition for F13-FV-402 due to FV402 in Interlock P_Hi = Close condition for XV13220 to direct feed to F13-BN-411 due to 13MD401 Not On
|  |  |  | LT13222 | LI13222 | 2000-F13-PID-PR-10006 | F13-BN-411 Recycle Crusher Feed Bin Level Transmitter 2 | F13BN411 Crusher D | 1 | 0 | 100 | % |  | 35 | 5 | 50 | 5 |  | 55 | 5 |  | 60 | 5 |  | 20 | 5 | 30 | 5 | 85 | 5 | 90 | 5 |  | Alarm setpoints and process switchpoints to be confirmed during commissioning. Set A_Hi and A_HH to be above overflow chute. A_HH = F13-CV-405 Tripped A_Hi = Open condition for XV13220 to bypass feed from F13-BN-411 A_Lo = Warning A_LL = F13-FV-402 Tripped P_HH = Auto start condition for F13-FV-402 P_Hi = Close condition for XV13220 to direct feed to F13-BN-411 P_Lo = Auto stop condition for F13-FV-402 | B | [6 empty] | Tested A_HH = F13-CV-405 Tripped A_Lo = Warning Not Tested A_Hi = Open condition for XV13220 to bypass feed from F13-BN-411 due to 13CV406 Interlock P_HH = Auto start condition for F13-FV-402 due to FV402 in Interlock P_Lo = Auto stop condition for F13-FV-402 due to FV402 in Interlock P_Hi = Close condition for XV13220 to direct feed to F13-BN-411 due to 13MD401 Not On
|  |  |  | VT13357A | VI13357A | 2000-F13-PID-PR-10006 | F13-CV-406 Recycle Crusher Discharge Conveyor Drive Pulley Vibration Transmitter 1 | F13CV406 Drive Pulley | 1 | 0 | 45 | mm/s | [16 empty] | 7 | 5 | 10 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | A
|  |  |  | VT13357B | VI13357B | 2000-F13-PID-PR-10006 | F13-CV-406 Recycle Crusher Discharge Conveyor Drive Pulley Vibration Transmitter 2 | F13CV406 Drive Pulley | 1 | 0 | 45 | mm/s | [16 empty] | 7 | 5 | 10 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | A
|  |  |  | TT13357A | TI13357A | 2000-F13-PID-PR-10006 | F13CV406 Recycle Crusher Discharge Conveyor Drive Pulley Vibration Transmitter 2 | F13CV406 Drive Pulley | 1 | -5 | 80 | °C | [16 empty] | 60 | 5 | 70 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | B
|  |  |  | TT13357B | TI13357B | 2000-F13-PID-PR-10006 | F13CV406 Recycle Crusher Discharge Conveyor Drive Pulley Vibration Transmitter 2 | F13CV406 Drive Pulley | 1 | -5 | 80 | °C | [16 empty] | 60 | 5 | 70 | 5 |  | Alarm setpoints and delays TBC during commissioning. Range ref: Vibration sensor VVB001 | B
|  |  |  | FIT13363 | FI13363 | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Process Water Flow Indicating Transmitter | F13SL401 PW Spray | 1 | 0 | 100 | m3/h | [14 empty] | 25 | 5 | 75 | 5 |  |  | Mask A_Lo if F13-SL-401 Not Running Mask A_Lo for 10 seconds on F13-SL-401 start-up | A_Lo = Warning A_Hi = Warning | B
|  |  |  | FIT13373 | FI13373 | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Process Water Flow Indicating Transmitter | F13SL402 PW Spray | 1 | 0 | 100 | m3/h | [14 empty] | 25 | 5 | 75 | 5 |  |  | Mask A_Lo if F13-SL-402 Not Running Mask A_Lo for 10 seconds on F13-SL-402 start-up | A_Lo = Warning A_Hi = Warning | B
|  |  |  | FIT13403 | FI13403 | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Process Water Flow Indicating Transmitter | F13SL403 PW Spray | 1 | 0 | 100 | m3/h | [14 empty] | 25 | 5 | 75 | 5 |  |  | Mask A_Lo if F13-SL-403 Not Running Mask A_Lo for 10 seconds on F13-SL-403 start-up | A_Lo = Warning A_Hi = Warning | B
|  |  |  | FIT13393 | FI13393 | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Process Water Flow Indicating Transmitter | F13SL404 PW Spray | 1 | 0 | 100 | m3/h | [14 empty] | 25 | 5 | 75 | 5 |  |  | Mask A_Lo if F13-SL-404 Not Running Mask A_Lo for 10 seconds on F13-SL-404 start-up | A_Lo = Warning A_Hi = Warning | B
|  |  |  | FIT13359 | FI13359 | 2000-F13-PID-PR-10008 | F13-BX-415 Trash Screens Final Collection Box Process Water Addition Flow Indicating Transmitter | F13BX415 Motive PW | 1 | 0 | 650 | m3/h | [21 empty] | 2000-F00-CAL-PR-10001 | A
|  |  |  | LIT13426 | LI13426 | 2000-F13-PID-PR-10012 | F13TK408 Cooling Water Tank 1 Level Indicating Transmitter | F13TK408 Level | 1 | 0 | 100 | % | [12 empty] | 20 | 5 | 30 | 5 | 80 | 5 | 90 | 5 |  | A_HH = Close tank fill valve XV13418 A_Hi = Warning A_Lo = Warning A_LL = Trip F13-PW-413/414 Alarm setpoints TBC during commissioning. | B
|  |  |  | LIT13430 | LI13430 | 2000-F13-PID-PR-10012 | F13TK407 Chiller Tank Level Indicating Transmitter | F13TK407 Level | 1 | 0 | 100 | % | [12 empty] | 20 | 5 | 30 | 5 | 80 | 5 | 90 | 5 |  | A_HH = Close tank fill valve XV13419 A_Hi = Warning A_Lo = Warning A_LL = Trip F13-PW-415/416 Alarm setpoints TBC during commissioning. | B
|  |  |  | TIT13437 | TI13437 | 2000-F13-PID-PR-10012 | F13HE420 Chiller Heat Exchanger Chilled Water Inlet Temperature Indicating Transmitter | F13HE420 Chill Water In | 1 | -5 | 100 | °C | [14 empty] | 5 | 5 | 25 | 5 |  |  |  | Alarms and process switchpoints estimated from 2000-F00-DSH-ME-11034 and Cooling Water Requirements Rev C Chilled Water Temperature nominal is 20degC A_Hi = Warning A_Lo = Warning Alarm setpoints TBC during commissioning. | B
|  |  |  | TIT13427 | TI13427 | 2000-F13-PID-PR-10012 | F13HE420 Chiller Heat Exchanger Chilled Water Outlet Temperature Indicating Transmitter | F13HE420 Chill Water Out | 1 | -5 | 100 | °C | [14 empty] | 5 | 5 | 30 | 5 |  |  |  | Alarms and process switchpoints estimated from 2000-F00-DSH-ME-11034 and Cooling Water Requirements Rev C Chilled Water Temperature nominal is 20degC A_Hi = Warning A_Lo = Warning Alarm setpoints TBC during commissioning. | B
|  |  |  | TIT13420 | TI13420 | 2000-F13-PID-PR-10012 | Cooling Water Return Temperature Indicating Transmitter | F13HE420 Cool Water In | 1 | -5 | 100 | °C | [14 empty] | 5 | 5 | 45 | 5 |  |  |  | Alarms estimated from 2000-F13-DSH-ME-20002 / 3 Cooling Water Temperature range ideally 0-38 degC according to SAG and Ball Mill Datasheets (VSD / Motor). Confirm ranges are suitable Cyclone Feed Pump VSD / Motor A_Hi = Warning A_Lo = Warning Alarm setpoints TBC during commissioning. | B
|  |  |  | TIT13421 | TI13421 | 2000-F13-PID-PR-10012 | Cooling Water Outgoing Temperature Indicating Transmitter | F13HE420 Cool Water Out | 1 | -5 | 100 | °C | [14 empty] | 5 | 5 | 38 | 5 |  |  |  | Alarms estimated from 2000-F13-DSH-ME-20002 / 3 Cooling Water Temperature range ideally 0-38 degC according to SAG and Ball Mill Datasheets (VSD / Motor). Confirm ranges are suitable Cyclone Feed Pump VSD / Motor A_Hi = Warning A_Lo = Warning Alarm setpoints TBC during commissioning. | B
|  |  |  | TIT13117 | TI13117 | 2000-F13-PID-PR-10009 | F13CU407 SAG Mill VSD Cooling System Cabinet Cooling Water Return Temperature | F13CU407 Cool Wtr Rturn | 1 | -5 | 100 | °C | [14 empty] | 5 | 5 | 43 | 5 |  |  |  | A_Hi = Warning A_Lo = Warning Range and alarms estimated. Cooling Water Temperature range ideally 0-38 degC according to SAG and Ball Mill Datasheets (VSD / Motor). TBC during commissioning. | B
|  |  |  | TIT13118 | TI13118 | 2000-F13-PID-PR-10009 | F13CU408 Ball Mill VSD Cooling System Cabinet Cooling Water Return Temperature | F13CU408 Cool Wtr Rturn | 1 | -5 | 100 | °C | [14 empty] | 5 | 5 | 43 | 5 |  |  |  | A_Hi = Warning A_Lo = Warning Range and alarms estimated. Cooling Water Temperature range ideally 0-38 degC according to SAG and Ball Mill Datasheets (VSD / Motor). TBC during commissioning. | B
|  |  |  | TIT13119 | TI13119 | 2000-F13-PID-PR-10009 | F13CU409 Cyclone Feed Pump VSD Cooling System Cabinet Cooling Water Return Temperature | F13CU409 Cool Wtr Rturn | 1 | -5 | 100 | °C | [14 empty] | 15 | 5 | 37 | 5 |  |  |  | A_Hi = Warning A_Lo = Warning Range and alarms estimated. Cooling Water Temperature range ideally 10-32deg C according to Cyclone Feed Pump VSD / Motor Cooling Datasheet 2000-ME063A-F14-10002 TBC during commissioning. | B
|  |  |  | TIT13129 | TI13129 | 2000-F13-PID-PR-10009 |  | F13PP401 Cool Wtr Rturn | 1 | -5 | 100 | °C | [14 empty] | 5 | 5 | 41 | 5 |  |  |  | A_Hi = Warning A_Lo = Warning Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. Range and alarms estimated. Cooling Water Temperature range ideally 10-36deg C according to Cyclone Feed Pump VSD / Motor Cooling Datasheet 2000-ME063A-F14-10002. TBC during commissioning. | 2 | 2026-05-27 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=rgupXp
|  |  |  | TIT13412 | TI13412 | 2000-F13-PID-PR-10010 | F13-MS-401B SAG Mill Motor 2 Cooling Water Return Temperature | F13MS401B Cool Wtr Rturn | 1 | -5 | 100 | °C | [14 empty] | 5 | 5 | 43 | 5 |  |  |  | A_Hi = Warning A_Lo = Warning Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. Range and alarms estimated. Cooling Water Temperature range ideally 0-38 degC according to SAG and Ball Mill Datasheets (VSD / Motor). TBC during commissioning. | 2 | 2026-05-27 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=rgupXp
|  |  |  | TIT13410 | TI13410 | 2000-F13-PID-PR-10010 | F13-MS-401A SAG Mill Motor 1 Cooling Water Return Temperature | F13MS401A Cool Wtr Rturn | 1 | -5 | 100 | °C | [14 empty] | 5 | 5 | 43 | 5 |  |  |  | A_Hi = Warning A_Lo = Warning Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. Range and alarms estimated. Cooling Water Temperature range ideally 0-38 degC according to SAG and Ball Mill Datasheets (VSD / Motor). TBC during commissioning. | 2 | 2026-05-27 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=rgupXp
|  |  |  | TIT13414 | TI13414 | 2000-F13-PID-PR-10011 | F13-MB-401A Ball Mill Motor 1 Cooling Water Return Temperature | F13MB401A Cool Wtr Rturn | 1 | -5 | 100 | °C | [14 empty] | 5 | 5 | 43 | 5 |  |  |  | A_Hi = Warning A_Lo = Warning Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. Range and alarms estimated. Cooling Water Temperature range ideally 0-38 degC according to SAG and Ball Mill Datasheets (VSD / Motor). TBC during commissioning. | 2 | 2026-05-27 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=rgupXp |  |  |  |  | Received advice from Ben that these Tx have been tested and working. Checked the 2-day trend and reading is accurate
|  |  |  | TIT13416 | TI13416 | 2000-F13-PID-PR-10011 | F13-MB-401B Ball Mill Motor 2 Cooling Water Return Temperature | F13MB401B Cool Wtr Rturn | 1 | -5 | 100 | °C | [14 empty] | 5 | 5 | 43 | 5 |  |  |  | A_Hi = Warning A_Lo = Warning Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. Range and alarms estimated. Cooling Water Temperature range ideally 0-38 degC according to SAG and Ball Mill Datasheets (VSD / Motor). TBC during commissioning. | 2 | 2026-05-27 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=rgupXp |  |  |  |  | Received advice from Ben that these Tx have been tested and working. Checked the 2-day trend and reading is accurate
|  |  |  | FIT13128 | FI13128 | 2000-F13-PID-PR-10009 | F13CU409 Cyclone Feed Pump Motor Cooling Water Supply | F13PP401 Cool Wtr Spply | 1 | 0 | 150 | m3/h | [14 empty] | 50 | 5 |  |  |  |  | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-PP-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Cooling Requirements Calc Rev C Nominal = 60m3/h Range as per instrument datasheet, max = 150 m3/h A_Lo = F13-PP-401 Start Permissive | 1 | 7/05/2025 27/05/2026 | https://pastech-2955.atlassian.net/browse/KAN-1809 https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=rgupXp |  |  |  |  | IOP not tested due to simulator cannot inject more current.
|  |  |  | FIT13411 | FI13411 | 2000-F13-PID-PR-10010 | F13-MS-401B SAG Mill Motor 2 Cooling Water Feed Flow Indicating Transmitter | F13MS401B Cool Wtr Feed | 1 | 0 | 150 | m3/h | [14 empty] | 55 | 5 |  |  |  |  | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MS-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | 2000-F13-TQY-ME-10023 Nominal = 64m3/h A_Lo = Confirm flow for VSD start sequence F13-SEQ-0021B and SAG Mill Main Motor inching interlocks | 1 | 7/05/2025 27/05/2026 | https://pastech-2955.atlassian.net/browse/KAN-1809 https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=rgupXp |  |  |  |  | IOP not tested due to simulator cannot inject more current. LO alarm not tested due to Alarm masking
|  |  |  | FIT13409 | FI13409 | 2000-F13-PID-PR-10010 | F13-MS-401A SAG Mill Motor 1 Cooling Water Feed Flow Indicating Transmitter | F13MS401A Cool Wtr Feed | 1 | 0 | 150 | m3/h | [14 empty] | 55 | 5 |  |  |  |  | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MS-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | 2000-F13-TQY-ME-10023 Nominal = 64m3/h A_Lo = Confirm flow for VSD start sequence F13-SEQ-0021B and SAG Mill Main Motor inching interlocks | 1 | 7/05/2025 27/05/2026 | https://pastech-2955.atlassian.net/browse/KAN-1809 https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=rgupXp |  |  |  |  | Becomes FIC instead of FI
|  |  |  | FIT13413 | FI13413 | 2000-F13-PID-PR-10011 | F13-MB-401A Ball Mill Motor 1 Cooling Water Feed Flow Indicating Transmitter | F13MB401A Cool Wtr Feed | 1 | 0 | 150 | m3/h | [14 empty] | 55 | 5 |  |  |  |  | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MB-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | 2000-F13-TQY-ME-10023 Nominal = 64m3/h A_Lo = Confirm flow for VSD start sequence F13-SEQ-0015B and Ball Mill Main Motor inching interlocks | 1 | 7/05/2025 27/05/2026 | https://pastech-2955.atlassian.net/browse/KAN-1809 https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=rgupXp
|  |  |  | FIT13415 | FI13415 | 2000-F13-PID-PR-10011 | F13-MB-401B Ball Mill Motor 2 Cooling Water Feed Flow Indicating Transmitter | F13MB401B Cool Wtr Feed | 1 | 0 | 150 | m3/h | [14 empty] | 55 | 5 |  |  |  |  | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MB-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | 2000-F13-TQY-ME-10023 Nominal = 64m3/h A_Lo = Confirm flow for VSD start sequence F13-SEQ-0015B and Ball Mill Main Motor inching interlocks | 1 | 7/05/2025 27/05/2026 | https://pastech-2955.atlassian.net/browse/KAN-1809 https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=rgupXp
|  |  |  | FIT13461 | FI13461 | 2000-F24-PID-PR-10004 | F13-PP-401 Cyclone Feed Pump Gland Water Flow Indicating Transmitter | F13PP401 Gland Water | 1 | 0 | 7.2 | m3/h | [12 empty] | 1 | 10 | 1.2 | 10 |  | 13.89 | 16.67 |  | 1. F13-PP-401 Not Running 2. Mask for 10 seconds (TBC) after F13-PP-401 start signal | 2000-F00-DSH-ME-11063A New Gland Seal = 1.2m3/h (20L/min) Worn Gland Seal = 3.6m3/h (60L/min) | A | [6 empty] | Could not see alarms in the alarm banner
|  |  |  | FIT13187 | FI13187 | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Seal Water Supply Flowmeter | F13CC401 Seal Water Flow | 1 | 0 | 5 | m3/h |  |  |  | 1.8 | 3 | [7 empty] | 1.32 | 3 | 1.56 | 3 |  |  |  |  | Mask if SV13185 closed | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 A_Lo = F13-FV-401 Tripped. P_Lo = Warning A_LL = F13-CC-401 Tripped Include P_Lo as logging alarm | B
|  |  |  | TE13255A | TI13255A | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Main Motor Winding U RTD | F13CC401 U RTD 1 | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 165 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 A_HH = F13-CC-401 Tripped A_Hi = Warning | B
|  |  |  | TE13255B | TI13255B | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Main Motor Winding V RTD | F13CC401 V RTD 1 | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 165 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 A_HH = F13-CC-401 Tripped A_Hi = Warning | B
|  |  |  | TE13255C | TI13255C | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Main Motor Winding W RTD | F13CC401 W RTD 1 | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 165 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 A_HH = F13-CC-401 Tripped A_Hi = Warning | B
|  |  |  | TE13255D | TI13255D | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Main Motor NDE Bearing RTD | F13CC401 NDE RTD | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 165 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 A_HH = F13-CC-401 Tripped A_Hi = Warning | B
|  |  |  | TE13255E | TI13255E | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Main Motor DE Bearing RTD | F13CC401 DE RTD | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 165 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 A_HH = F13-CC-401 Tripped A_Hi = Warning | B
|  |  |  | VT13254A | VI13254A | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Main Motor NDE Bearing Vibration Transmitter | F13CC401 Drive DE | 1 | 0 | 300 | mm/s | [16 empty] | 6 | 5 | 8 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 Range from FLS instrument list. Alarm setpoints TBC. A_HH = F13-CC-401 Tripped A_Hi = Warning | 0
|  |  |  | VT13254B | VI13254B | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Main Motor DE Bearing Vibration Transmitter | F13CC401 Drive NDE | 1 | 0 | 300 | mm/s | [16 empty] | 6 | 5 | 8 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 Range from FLS instrument list. Alarm setpoints TBC. A_HH = F13-CC-401 Tripped A_Hi = Warning | 0
|  |  |  | FIT13244 | FI13244 | 2000-F13-PID-PR-10006 | F13LU403 Recycle Crusher C Lubrication Unity Supply Lube Oil Flowmeter | F13CC401 Lube Oil Supply | 1 | 0 | 30 | m3/h |  |  |  | 11.4 | 3 | [7 empty] | 10.2 | 3 | 12.48 | 3 |  |  |  |  | 1. F13-PO-401/402 Not Running 2. Mask for 10 seconds (TBC) after F13-PO-401 OR 402 start signal | 2000-ME001.6-F16-50001 2000-ME001.6-E04-50001 Range 15-500L/min converted to m3/h Nominal F13-PO-401/402 flowrate = 281 L/min A_Lo = Warning P_Lo = Trip F13-FV-401 A_LL = Trip F13-CC-401 | B
|  |  |  | PT13233 | PI13233 | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Lube Oil Supply Pressure Transmitter | F13CC401 Lube Oil Supply | 1 | 0 | 500 | kPa |  |  |  | 27 | 3 | [7 empty] | 13 | 3 | 41 | 3 |  |  |  |  | 1. F13-PO-401/402 Not Running 2. Mask for 10 seconds (TBC) after F13-PO-401 OR 402 start signal | 2000-ME001.6-F16-50001 A_Lo = Warning P_Lo = Trip F13-FV-401 A_LL = Trip F13-CC-401 | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | ST13253 | SI13253 | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Countershaft Speed Transmitter | F13CC401 C/Shaft Speed | 1 | 0 | 100 | % |  |  |  | 97 | 3 | [7 empty] | 90 | 18 | 95 | 10 |  |  |  |  | 1. F13-CC-401 Not Running 2. Mask for 10 45seconds (TBC) after F13-CC-401 start signal | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 P_Lo = Warning A_Lo = F13-FV-401 Tripped A_LL = F13-CC-401 Tripped P_Lo requires a logging alarm | B
|  |  |  | TT13232 | TI13232 | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Countershaft Temperature Transmitter | F13CC401 C/Shaft Temp | 1 | 0 | 100 | °C | [6 empty] | 49 | 3 | [8 empty] | 54 | 3 | 59 | 3 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-CC-401 Tripped A_Hi = F13-FV-401 Tripped P_Hi = F13-SEQ-0028 Condition | B | [6 empty] | MOC-775 - changed DCS range from -5 to 90 degC to 0 to 100 degC (DE 04/08/2026)
|  |  |  | VT13256 | VI13256 | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Vibration Transmitter 1 | F13CC401 Adj. Ring 1 | 1 | 0 | 50 | mm/s | [16 empty] | 6 | 10 | 8 | 10 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-FV-401 Tripped A_Hi = Warning | B
|  |  |  | VT13257 | VI13257 | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Vibration Transmitter 2 | F13CC401 Adj. Ring 2 | 1 | 0 | 50 | mm/s | [16 empty] | 6 | 10 | 8 | 10 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-FV-401 Tripped A_Hi = Warning | B
|  |  |  | VT13258 | VI13258 | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Vibration Transmitter 3 | F13CC401 Adj. Ring 3 | 1 | 0 | 50 | mm/s | [16 empty] | 6 | 10 | 8 | 10 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-FV-401 Tripped A_Hi = Warning | B
|  |  |  | VT13259 | VI13259 | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Vibration Transmitter 4 | F13CC401 Adj. Ring 4 | 1 | 0 | 50 | mm/s | [16 empty] | 6 | 10 | 8 | 10 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-FV-401 Tripped A_Hi = Warning | B
|  |  |  | TT13242 | TI13242 | 2000-F13-PID-PR-10006 | F13-LU-403 Recycle Crusher C Lubrication Unit Lube Oil Tank Temperature Transmitter | F13LU403 Lube Oil Tank | 1 | -5 0 | -150 100 | °C |  |  |  | 30 | 3 |  | 35 | 3 |  |  |  |  | 15 | 3 | 27 | 3 | 38 | 3 | 42 | 3 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-HT-403/404/451/452 Tripped A_Hi = Warning A_Lo = Warning A_LL = F13-PO-401/402 Tripped P_Hi = Auto stop F13-HT-403/404/451/452 P_Lo = Auto start F13-HT-403/404/451/452 | B | [6 empty] | MOC-768 - Updated DCS Range from -5 to 150 to 5 to 100. Retested on 2/8/2026
|  |  |  | PT13237 | PI13237 | 2000-F13-PID-PR-10006 | F13-LU-403 Recycle Crusher C Lubrication Unit Lube Oil Supply (Pressure Adjusted) Pressure Transmitter | F13LU403 Fltr Upstream | 1 | 0 | 500 | kPa | [21 empty] | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PT13236 | PI13236 | 2000-F13-PID-PR-10006 | F13-LU-403 Recycle Crusher C Lubrication Unit Lube Oil Supply Pressure Transmitter | F13LU403 Fltr Downstream | 1 | 0 | 500 | kPa | [21 empty] | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | TT13247 | TI13247 | 2000-F13-PID-PR-10006 | F13-FN-458 RECYCLE CRUSHER C LUBRICATION AIR COOLER 2 Outlet Temperature Transmitter | F13LU403 Lube Oil Supply | 1 | -5 0 | -160 100 | °C | [14 empty] | 20 | 3 | [5 empty] | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_Lo = Warning | B | [6 empty] | MOC-768 - Updated DCS Range from -5 to 160 to 5 to 100. Retested on 2/8/2026
|  |  |  | TT13243 | TI13243 | 2000-F13-PID-PR-10006 | F13-LU-403 Recycle Crusher C Lubrication Unit Return Lube Oil Temperature Transmitter | F13LU403 Lube Oil Return | 1 | 0 | 100 | °C |  |  |  | 38 | 3 |  | 43 | 3 |  | 57 | 3 | [5 empty] | 55 | 3 | 60 | 3 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-CC-401 Tripped (3 second on-delay) A_Hi = F13-CC-401 Tripped (60 second on-delay) P_HH = F13-FV-401 Tripped P_Hi = Auto start F13-FN-457/458 P_Lo = Auto stop F13-FN-457/458 | B | [6 empty] | MOC-768 - Updated DCS Range from -5 to 160 to 5 to 100. Retested on 2/8/2026
|  |  |  | LT13241 | LI13241 | 2000-F13-PID-PR-10006 | F13-LU-403 Recycle Crusher C Lubrication Unit Lube Oil Tank Level Transmitter | F13LU403 Lube Oil Tank | 1 | 0 | 100 | % |  |  |  | 40 | 5 | [7 empty] | 10 | 60 | 50 | 3 |  |  | 90 | 3 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = Warning A_Lo = F13-FV-401 & F13-HT-403/404/451/452 Tripped P_Lo = F13-CC-401 Tripped A_LL = F13-PO-401/402 Tripped P_Lo requires a logging alarm | B
|  |  |  | F13CALC10010 | TDI13247 | 2000-F13-PID-PR-10006 | F13LU403 Recycle Crusher C Lubrication Unit Lube Oil Supply & Return Differential Temperature | F13LU403 Lube Oil dT 1 | 1 | 0 | 160 | °C | [16 empty] | 17 | 3 | 17 | 600 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-FV-401 Tripped A_Hi = Warning | 0
|  |  |  | F13CALC10012 | PDI13237 | 2000-F13-PID-PR-10006 | F13LU403 Recycle Crusher C Lubrication Unit Lube Oil Filter Differential Pressure | F13LU403 Lube Filter dP | 1 | 0 | 500 | kPa | [16 empty] | 241 | 5 |  |  |  | 2000-ME001.6-F16-50001 A_Hi = Warning | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | LT13268 | LI13268 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Hydraulic Reservoir Level Transmitter | F13HU403 Hyd. Oil Tank | 1 | 0 | 100 | % |  |  |  | 37 | 5 | [7 empty] | 15 | 60 | 47 | 3 | 90 | 3 |  |  |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_Hi = Warning A_Lo = F13-FV-401 Tripped P_Lo = F13-CC-401 Tripped A_LL = F13-PO-408 Tripped P_Lo requires a logging alarm | B | [6 empty] | No logging alarm for P Lo - used only as a PIL on 13CC401 so FO should capture it.
|  |  |  | TT13267 | TI13267 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Hydraulic Reservoir Temperature Transmitter | F13HU403 Hyd. Oil Tank | 1 | 0 | 100 | °C | [6 empty] | 63 | 5 | [10 empty] | 65 | 5 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-PO-408 & F13-FV-401 Tripped P_Hi = F13-SEQ-0028 Condition | B | [6 empty] | MOC-780 - Updated DCS Range from -5 to 150 to 5 to 100. Retested on 2/8/2026
|  |  |  | PT13261 | PI13261 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Pump Discharge 1 Pressure Transmitter | F13HU403 Pump Disch. | 1 | 0 | 25000 | kPa | [21 empty] | 2000-ME001.6-F16-50001 Used in F13CALC10028 for PDI13261 calculation | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PT13262 | PI13262 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Pump Discharge 2 Pressure Transmitter | F13HU403 System Pressure | 1 | 0 | 25000 | kPa | [21 empty] | 2000-ME001.6-F16-50001 Used in F13CALC10028 for PDI13261 calculation | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | F13CALC10028 | PDI13261 | 2000-F13-PID-PR-10006 | F13HU403 Recycle Crusher C Hydraulic Unit Hydraulic Supply Filter Pressure Differential | F13HU403 Hyd. Filter dP | 1 | 0 | 25000 | kPa | [16 empty] | 8600 | 3 |  |  |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_Hi = Warning | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PT13263 | PI13263 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Clamping Pressure Transmitter | F13HU403 Clamping | 1 | 0 | 25000 | kPa |  |  |  | 17900 | 3 |  | 19300 | 3 |  |  |  |  | 16500 | 5 | 17900 | 10 |  |  |  |  | 1. F13CC401_CLMP Inactive | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_Lo = F13-FV-401 Tripped (180 second ondelay) A_LL = F13-FV-401 Tripped (5 second ondelay) & Mask F13CC401_CRP P_Hi = See below P_Lo = See below IF F13CC401_CLMP = Active (Refer to Misc tab, F13CC401_CLMP), then: Activate YS13273 when PI13263 < P_Lo (see Misc tab) Deactivate YS13273 when PI13263 > P_Hi (see Misc tab) Alarm delays to be confirmed during commissioning | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1468 PCT alignment action register (kPa units)
|  |  |  | PT13264 | PI13264 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Tramp Pressure Transmitter | F13HU403 Tramp | 1 | 0 | 25000 | kPa |  |  |  | 11000 | 3 |  | 12400 | 3 |  |  |  |  | 9600 | 5 | 11000 | 60 |  |  |  |  | 1. F13CC401_TRMP Inactive | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_Lo = F13-FV-401 Tripped (300 second ondelay) A_LL = F13-FV-401 Tripped (5 second ondelay) P_Hi = See below P_Lo = See below IF F13CC401_TRMP = Active (Refer to Misc tab, F13CC401_TRMP), then: Activate YS13276 when PI13264 < P_Lo (See Misc tab) Deactivate YS13276 when PI13264 > P_Hi (See Misc tab) Alarm delays to be confirmed during commissioning | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1468 PCT alignment action register (kPa units)
|  |  |  | F13CALC10030 | F13CC401_CSS | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Closed Side Setting | F13CC401 Crusher CSS | 1 | 0 | 40 | mm | [12 empty] | F13CC401_MIN | 5 | 1.1 * F13CC401_MIN | 5 | 0.9 * F13CC401_MAX | 5 | F13CC401_MAX | 5 | 1. Mask if F13CC401_CAL (See Misc sheet) is ACTIVE | F13CC401_MIN and F13CC401_MAX are configurable with Engineer level access (see Misc sheet). The LOW and HIGH alarms are calculated as F13CC401_MIN and F13CC401_MAX +/ 10% of set value | 0
|  |  |  | FIT13294 | FI13294 | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Seal Water Supply Flowmeter | F13CC402 Seal Water Flow | 1 | 0 | 5 | m3/h |  |  |  | 1.8 | 3 | [7 empty] | 1.32 | 3 | 1.56 | 3 |  |  |  |  | Mask if SV13292 closed | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 A_Lo = F13-FV-402 Tripped. P_Lo = Warning / Logging Alarm A_LL = F13-CC-402 Tripped Include P_Lo as logging alarm | B
|  |  |  | TE13315A | TI13315A | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Main Motor Winding U1 RTD | F13CC402 U RTD 1 | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 165 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 A_HH = F13-CC-402 Tripped A_Hi = Warning | B
|  |  |  | TE13315B | TI13315B | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Main Motor Winding V1 RTD | F13CC402 V RTD 1 | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 165 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 A_HH = F13-CC-402 Tripped A_Hi = Warning | B
|  |  |  | TE13315C | TI13315C | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Main Motor Winding W1 RTD | F13CC402 W RTD 1 | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 165 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 A_HH = F13-CC-402 Tripped A_Hi = Warning | B
|  |  |  | TE13315D | TI13315D | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Main Motor NDE Bearing RTD | F13CC402 NDE RTD | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 165 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 A_HH = F13-CC-402 Tripped A_Hi = Warning | B
|  |  |  | TE13315E | TI13315E | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Main Motor DE Bearing RTD | F13CC402 DE RTD | 1 | -5 | 200 | °C | [16 empty] | 155 | 5 | 165 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 A_HH = F13-CC-402 Tripped A_Hi = Warning | B
|  |  |  | VT13314A | VI13314A | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Main Motor DE Bearing Vibration Transmitter | F13CC402 Drive DE | 1 | 0 | 300 | mm/s | [16 empty] | 6 | 5 | 8 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 Range from FLS instrument list. Alarm setpoints TBC. A_HH = F13-CC-402 Tripped A_Hi = Warning | B
|  |  |  | VT13314B | VI13314B | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Main Motor NDE Bearing Vibration Transmitter | F13CC402 Drive NDE | 1 | 0 | 300 | mm/s | [16 empty] | 6 | 5 | 8 | 5 |  | 2000-ME001.6-F16-50001 2000-ME001.6-F14-50001 Range from FLS instrument list. Alarm setpoints TBC. A_HH = F13-CC-402 Tripped A_Hi = Warning | B
|  |  |  | FIT13304 | FI13304 | 2000-F13-PID-PR-10006 | F13LU404 Recycle Crusher D Lubrication Unity Supply Lube Oil Flowmeter | F13CC402 Lube Oil Supply | 1 | 0 | 30 | m3/h |  |  |  | 11.4 | 3 | [7 empty] | 10.2 | 3 | 12.48 | 3 |  |  |  |  | 1. F13-PO-406/407 Not Running 2. Mask for 10 seconds (TBC) after F13-PO-406 OR 407 start signal | 2000-ME001.6-F16-50001 2000-ME001.6-E04-50001 Range 15-500L/min converted to m3/h Nominal F13-PO-406/407 flowrate = 281 L/min A_Lo = Warning P_Lo = Trip F13-FV-402 A_LL = Trip F13-CC-402 | B
|  |  |  | PT13283 | PI13283 | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Lube Oil Supply Pressure Transmitter | F13CC402 Lube Oil Supply | 1 | 0 | 500 | kPa |  |  |  | 27 | 3 | [7 empty] | 13 | 3 | 41 | 3 |  |  |  |  | 1. F13-PO-406/407 Not Running 2. Mask for 10 seconds (TBC) after F13-PO-406 OR 407 start signal | 2000-ME001.6-F16-50001 A_Lo = Warning P_Lo = Trip F13-FV-402 A_LL = Trip F13-CC-402 | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | ST13313 | SI13313 | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Countershaft Speed Transmitter | F13CC402 C/Shaft Speed | 1 | 0 | 100 | % |  |  |  | 97 | 3 | [7 empty] | 90 | 18 | 95 | 10 |  |  |  |  | 1. F13-CC-402 Not Running 2. Mask for 10 seconds (TBC) after F13-CC-402 start signal | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 P_Lo = Warning A_Lo = F13-FV-402 Tripped A_LL = F13-CC-402 Tripped P_Lo requires a logging alarm | B
|  |  |  | TT13282 | TI13282 | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Countershaft Temperature Transmitter | F13CC402 C/Shaft Temp | 1 | 0 | 100 | °C | [6 empty] | 49 | 3 | [8 empty] | 54 | 3 | 59 | 3 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-CC-402 Tripped A_Hi = F13-FV-402 Tripped P_Hi = F13-SEQ-0033 Condition | B | [6 empty] | interlocks are correct, check for process switchpoint in sequence MOC-775 - changed DCS range from -5 to 90 degC to 0 to 100 degC (DE 04/08/2026)
[7 empty] | 0 | [27 empty] | B | 2025-08-19 | CR-044
|  |  |  | VT13316 | VI13316 | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Vibration Transmitter 1 | F13CC402 Adj. Ring 1 | 1 | 0 | 50 | mm/s | [16 empty] | 6 | 10 | 8 | 10 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-FV-402 Tripped A_Hi = Warning | B
|  |  |  | VT13317 | VI13317 | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Vibration Transmitter 2 | F13CC402 Adj. Ring 2 | 1 | 0 | 50 | mm/s | [16 empty] | 6 | 10 | 8 | 10 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-FV-402 Tripped A_Hi = Warning | B
|  |  |  | VT13318 | VI13318 | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Vibration Transmitter 3 | F13CC402 Adj. Ring 3 | 1 | 0 | 50 | mm/s | [16 empty] | 6 | 10 | 8 | 10 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-FV-402 Tripped A_Hi = Warning | B
|  |  |  | VT13319 | VI13319 | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Vibration Transmitter 4 | F13CC402 Adj. Ring 4 | 1 | 0 | 50 | mm/s | [16 empty] | 6 | 10 | 8 | 10 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-FV-402 Tripped A_Hi = Warning | B
|  |  |  | TT13302 | TI13302 | 2000-F13-PID-PR-10006 | F13-LU-404 Recycle Crusher D Lubrication Unit Lube Oil Tank Temperature Transmitter | F13LU404 Lube Oil Tank | 1 | 0 | 100 | °C |  |  |  | 30 | 3 |  | 35 | 3 |  |  |  |  | 15 | 3 | 27 | 3 | 38 | 3 | 42 | 3 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-HT-405/406/453/454 Tripped A_Hi = Warning A_Lo = Warning A_LL = F13-PO-406/407 Tripped P_Hi = Auto stop F13-HT-405/406/453/454 P_Lo = Auto start F13-HT-405/406/453/454 | B | [6 empty] | MOC-768 - Updated DCS Range from -5 to 150 to 5 to 100. Retested on 2/8/2026
|  |  |  | PT13297 | PI13297 | 2000-F13-PID-PR-10006 | F13-LU-404 Recycle Crusher D Lubrication Unit Lube Oil Supply (Pressure Adjusted) Pressure Transmitter | F13LU404 Fltr Upstream | 1 | 0 | 500 | kPa | [21 empty] | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PT13296 | PI13296 | 2000-F13-PID-PR-10006 | F13-LU-404 Recycle Crusher D Lubrication Unit Lube Oil Supply Pressure Transmitter | F13LU404 Fltr Downstream | 1 | 0 | 500 | kPa | [21 empty] | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | TT13307 | TI13307 | 2000-F13-PID-PR-10006 | F13-FN-460 RECYCLE CRUSHER D LUBRICATION AIR COOLER 2 Outlet Temperature Transmitter | F13LU404 Lube Oil Supply | 1 | 0 | 100 | °C | [14 empty] | 20 | 3 | [5 empty] | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_Lo = Warning | B | [6 empty] | MOC-768 - Updated DCS Range from -5 to 160 to 5 to 100. Retested on 2/8/2026
|  |  |  | TT13303 | TI13303 | 2000-F13-PID-PR-10006 | F13-LU-404 Recycle Crusher D Lubrication Unit Return Lube Oil Temperature Transmitter | F13LU404 Lube Oil Return | 1 | 0 | 100 | °C |  |  |  | 38 | 3 |  | 43 | 3 |  | 57 | 3 | [5 empty] | 55 | 3 | 60 | 3 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-CC-402 Tripped (3 second on-delay) A_Hi = F13-CC-402 Tripped (60 second on-delay) P_HH = F13-FV-402 Tripped P_Hi = Auto start F13-FN-459/460 P_Lo = Auto stop F13-FN-459/460 | B | [6 empty] | MOC-768 - Updated DCS Range from -5 to 160 to 5 to 100. Retested on 2/8/2026
|  |  |  | LT13301 | LI13301 | 2000-F13-PID-PR-10006 | F13-LU-404 Recycle Crusher D Lubrication Unit Lube Oil Tank Level Transmitter | F13LU404 Lube Oil Tank | 1 | 0 | 100 | % |  |  |  | 40 | 5 | [7 empty] | 10 | 60 | 50 | 3 |  |  | 90 | 3 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = Warning A_Lo = F13-FV-402 & F13-HT-405/406/453/454 Tripped P_Lo = F13-CC-402 Tripped A_LL = F13-PO-406/407 Tripped P_Lo requires a logging alarm | B
|  |  |  | F13CALC10013 | TDI13307 | 2000-F13-PID-PR-10006 | F13LU404 Recycle Crusher D Lubrication Unit Lube Oil Supply & Return Differential Temperature | F13LU404 Lube Oil dT 1 | 1 | 0 | 160 | °C | [16 empty] | 17 | 3 | 17 | 600 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-FV-402 Tripped A_Hi = Warning | 0
|  |  |  | F13CALC10015 | PDI13296 | 2000-F13-PID-PR-10006 | F13LU404 Recycle Crusher D Lubrication Unit Lube Oil Filter Differential Pressure | F13LU404 Lube Filter dP | 1 | 0 | 500 | kPa | [16 empty] | 241 | 5 |  |  |  | 2000-ME001.6-F16-50001 A_Hi = Warning | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | LT13328 | LI13328 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Hydraulic Reservoir Level Transmitter | F13HU404 Hyd. Oil Tank | 1 | 0 | 100 | % |  |  |  | 37 | 5 | [7 empty] | 15 | 60 | 47 | 3 | 90 | 3 |  |  |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_Hi = Warning A_Lo = F13-FV-402 Tripped P_Lo = F13-CC-402 Tripped A_LL = F13-PO-409 Tripped P_Lo requires a logging alarm | B
|  |  |  | TT13327 | TI13327 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Hydraulic Reservoir Temperature Transmitter | F13HU404 Hyd. Oil Tank | 1 | 0 | 100 | °C | [6 empty] | 63 | 5 | [10 empty] | 65 | 5 |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_HH = F13-PO-409 & F13-FV-402 Tripped P_Hi = F13-SEQ-0033 Condition | B | [6 empty] | MOC-780 - Updated DCS Range from -5 to 150 to 5 to 100. Retested on 2/8/2026
|  |  |  | PT13321 | PI13321 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Pump Discharge Pressure Transmitter | F13HU404 Pump Disch. | 1 | 0 | 25000 | kPa | [21 empty] | 2000-ME001.6-F16-50001 Used in F13CALC10029 for PDI13321 calculation | 1 | 2025-03-06 | PCT alignment action register (kPa units) |  |  |  |  | was configured as 4-wire, it is 2-wire
|  |  |  | PT13322 | PI13322 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Oil Filter Discharge Pressure Transmitter | F13HU404 System Pressure | 1 | 0 | 25000 | kPa | [21 empty] | 2000-ME001.6-F16-50001 Used in F13CALC10029 for PDI13321 calculation | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | F13CALC10029 | PDI13321 | 2000-F13-PID-PR-10006 | F13HU404 Recycle Crusher D Hydraulic Unit Hydraulic Supply Filter Pressure Differential | F13HU404 Hyd. Filter dP | 1 | 0 | 25000 | kPa | [16 empty] | 8600 | 3 |  |  |  | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_Hi = Warning | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PT13323 | PI13323 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Clamping Cylinder Pressure Transmitter | F13HU404 Clamping | 1 | 0 | 25000 | kPa |  |  |  | 17900 | 3 |  | 19300 | 3 |  |  |  |  | 16500 | 5 | 17900 | 10 |  |  |  |  | 1. F13CC402_CLMP Inactive | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_Lo = F13-FV-402 Tripped (180 second ondelay) A_LL = F13-FV-402 Tripped (5 second ondelay) & Mask F13CC402_CRP P_Hi = See below P_Lo = See below IF F13CC402_CLMP = Active (Refer to Misc tab, F13CC402_CLMP), then: Activate YS13333 when PI13323 < P_Lo (see Misc tab) Deactivate YS13333 when PI13323 > P_Hi (see Misc tab) | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1468 PCT alignment action register (kPa units)
|  |  |  | PT13324 | PI13324 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Clearing Pressure Transmitter | F13HU404 Tramp | 1 | 0 | 25000 | kPa |  |  |  | 11000 | 3 |  | 12400 | 3 |  |  |  |  | 9600 | 5 | 11000 | 60 |  |  |  |  | 1. F13CC402_TRMP Inactive | 2000-ME001.6-M02-50001 2000-ME001.6-F16-50001 A_Lo = F13-FV-402 Tripped (300 second ondelay) A_LL = F13-FV-402 Tripped (5 second ondelay) P_Hi = See below P_Lo = See below IF F13CC402_TRMP = Active (Refer to Misc tab, F13CC402_TRMP), then: Activate YS13336 when PI13324 < P_Lo (see Misc tab) Deactivate YS13336 when PI13324 > P_Hi (see Misc tab) | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1468 PCT alignment action register (kPa units)
|  |  |  | F13CALC10032 | F13CC402_CSS | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Closed Side Setting | F13CC402 Crusher CSS | 1 | 0 | 40 | mm | [12 empty] | F13CC402_MIN | 5 | 1.1 * F13CC402_MIN | 5 | 0.9 * F13CC402_MAX | 5 | F13CC402_MAX | 5 | 1. Mask if F13CC402_CAL (See Misc sheet) is ACTIVE | F13CC402_MIN and F13CC402_MAX are configurable with Engineer level access (see Misc sheet). The LOW and HIGH alarms are calculated as F13CC402_MIN and F13CC402_MAX +/ 10% of set value | 0
|  |  |  | F13CALC10035 | MS_FD_WT | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Feed End Trunnion Bearing Weight | F13MS401 DschTrunBrg Wt | 1 | 0 | 2000 | t | [21 empty] | Range calculated as 1.5x operating conditions (12911kN) and rounded to closest multiple of 100 2000-ME001.2-M01-50001 2000-ME001.3-F20-50003 | 0
|  |  |  | F13CALC10036 | MS_DSCH_WT | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Discharge End Trunnion Bearing Weight | F13MS401 FeedTrunBrg Wt | 1 | 0 | 1700 | t | [21 empty] | Range calculated as 1.5x operating conditions (11234kN) and rounded to closest multiple of 100 2000-ME001.2-M01-50001 2000-ME001.3-F20-50003 | 0
|  |  |  | F13CALC10037 | MB_FD_WT | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Feed End Trunnion Bearing Weight | F13MB401 DschTrunBrg Wt | 1 | 0 | 2200 | t | [21 empty] | Range calculated as 1.5x operating conditions (14235kN) and rounded to closest multiple of 100 2000-ME001.3-M01-50001 2000-ME001.3-F20-50003 | 0
|  |  |  | F13CALC10038 | MB_DSCH_WT | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Discharge End Trunnion Bearing Weight | F13MB401 FeedTrunBrg Wt | 1 | 0 | 1900 | t | [21 empty] | Range calculated as 1.5x operating conditions (12653kN) and rounded to closest multiple of 100 2000-ME001.3-M01-50001 2000-ME001.3-F20-50003 | 0
|  |  |  | MSINTENSITY | MS_INTENSITY | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill LoadIQ Intensity | F13MS401 IQ Intensity | 1 | 0 | 10000 | - | [21 empty] | SoftTag From LoadIQ OPC Server. | 1 | 2025-06-25 | No action required. TBC removed.
|  |  |  | MSTOE | MS_TOE | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill LoadIQ Toe | F13MS401 IQ Toe | 1 | 0 | 360 | ° | [21 empty] | SoftTag From LoadIQ OPC Server. | 1 | 2025-06-25 | No action required. TBC removed.
|  |  |  | MSTHROW | MS_THROW | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill LoadIQ Throw | F13MS401 IQ Throw | 1 | 0 | 360 | ° | [21 empty] | SoftTag From LoadIQ OPC Server. | 1 | 2025-06-25 | No action required. TBC removed.
|  |  |  | MSWIDTH | MS_WIDTH | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill LoadIQ Width | F13MS401 IQ Width | 1 | 0 | 360 | ° | [21 empty] | SoftTag From LoadIQ OPC Server. | 1 | 2025-06-25 | No action required. TBC removed.
|  |  |  | MSIMPACTS | MS_IMPACTS | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill LoadIQ Impacts | F13MS401 IQ Impacts | 1 | 0 | 10000 | - | [21 empty] | SoftTag From LoadIQ OPC Server. | 1 | 2025-06-25 | No action required. TBC removed.
|  |  |  | MSSPEED | MS_SPEED | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill LoadIQ Speed | F13MS401 IQ Speed | 1 | 0 | 20 | RPM | [21 empty] | SoftTag From LoadIQ OPC Server. | 1 | 2025-06-25 | No action required. TBC removed.
|  |  |  | F13CALC10043 | MS_TORQUE | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Total Torque | F13MS401 Total Torque | 1 | 0 | 2500 | kNm | [21 empty] | 2000-ME001.2-F14-50008 | 0 | [6 empty] | Range high modified from 25000 to 2500.
|  |  |  | F13CALC10045 | MS_CURRENT | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Total Current | F13MS401 Total Current | 1 | 0 | 4000 | Amps | [21 empty] | 2000-ME001.2-F14-50008 | 0
|  |  |  | MSMSTRSPD | SI13137A | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Master Motor Speed Feedback | F13MS401 Master Speed | 1 | -7.5 | 165 | RPM |  |  |  | 90 | 5 | [7 empty] | 115 | 5 | 120 | 5 | 160 | 5 | 164 | 5 | 1. Mask if F13-MS-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MS-401 start signal 3. MS_OP_MODE = Inching | SoftTag. Modbus signal from SAG Mill VSD Include DV+/- alarm if less than or greater than 2% from setpoint. 2000-ME001.2-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | 1 | 6/03/2025 12/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1411 https://pastech-2955.atlassian.net/browse/KAN-1811
|  |  |  | MSMSTRI | MS_MSTR_I | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Master Motor Current | F13MS401 Master Current | 1 | 0 | 2550 | Amps | [18 empty] | 1700 | 5 |  | SoftTag. Modbus signal from SAG Mill VSD 2000-ME001.2-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | B
|  |  |  | MSMSTRT | MS_MSTR_T | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Master Motor Torque | F13MS401 Master Torque | 1 | 0 | 954.881 | kNm | [18 empty] | 700 | 5 |  | SoftTag. Modbus signal from SAG Mill VSD 2000-ME001.2-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | B
|  |  |  | MSMSTRPWR | JI13136A | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Master Motor Power | F13MS401 Master Power | 1 | 0 | 15000 | kW | [16 empty] | 9900 | 5 | 10000 | 5 |  | SoftTag. Modbus signal from SAG Mill VSD 2000-ME001.2-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=511&pa=1&e=hmg2b6
|  |  |  | MSSLVESPD | SI13137B | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Slave Motor Speed Feedback | F13MS401 Slave Speed | 1 | -7.5 | 165 | RPM | [12 empty] | 115 | 5 | 120 | 5 | 160 | 5 | 164 | 5 | 1. Mask if F13-MS-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MS-401 start signal 3. MS_OP_MODE = Inching | SoftTag. Modbus signal from SAG Mill VSD Include DV+/- alarm if less than or greater than 2% from setpoint. 2000-ME001.2-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1411
|  |  |  | MSSLVEI | MS_SLVE_I | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Slave Motor Current | F13MS401 Slave Current | 1 | 0 | 2550 | Amps | [18 empty] | 1700 | 5 |  | SoftTag. Modbus signal from SAG Mill VSD 2000-ME001.2-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | B
|  |  |  | MSSLVET | MS_SLVE_T | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Slave Motor Torque | F13MS401 Slave Torque | 1 | 0 | 954.881 | kNm | [16 empty] | 700 | 5 |  |  |  | SoftTag. Modbus signal from SAG Mill VSD 2000-ME001.2-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | B
|  |  |  | MSSLVEPWR | JI13136B | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Slave Motor Power | F13MS401 Slave Power | 1 | 0 | 15000 | kW | [16 empty] | 9900 | 5 | 10000 | 5 |  | SoftTag. Modbus signal from SAG Mill VSD 2000-ME001.2-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=511&pa=1&e=hmg2b6
|  |  |  | MSCOOLCOND | MS_COOL_COND | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Pure Water Conductivity | F13MS401 Pure Water Cond | 1 | 0 | 3 | µS/cm | [16 empty] | 0.8 | 5 |  |  |  | SoftTag. Modbus signal from SAG Mill VSD 2000-ME001.2-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | B
|  |  |  | F13CALC10040 | WI13148 | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Mill Weight | F13MB401 Mill Weight | 1 | 0 | 2000 | t | [16 empty] | 1495 | 5 | 1525 | 5 |  | Range & alarms inferred from nominal Mill operating weight of 1456t (2000-ME001.3-F20-50003). Range and alarm setpoints to be confirmed during commissioning. | 0
|  |  |  | F13CALC10042 | JI13149 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Total Power | F13MB401 Total Power | 1 | 0 | 25000 | kW | [21 empty] | 2000-ME001.2-F14-50008 | 0 | 2025-10-30 | CR-052
|  |  |  | F13CALC10044 | MB_TORQUE | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Total Torque | F13MB401 Total Torque | 1 | 0 | 2500 | kNm | [21 empty] | 2000-ME001.2-F14-50008 | 0 | [6 empty] | Range high modified from 25000 to 2500.
|  |  |  | F13CALC10046 | MB_CURRENT | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Total Current | F13MB401 Total Current | 1 | 0 | 4000 | Amps | [21 empty] | 2000-ME001.2-F14-50008 | 0
|  |  |  | MBMSTRSPD | SI13150A | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Master Motor Speed Feedback | F13MB401 Master Speed | 1 | -7.5 | 165 | RPM |  |  |  | 90 | 5 | [7 empty] | 115 | 5 | 120 | 5 | 160 | 5 | 164 | 5 | 1. Mask if F13-MB-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MB-401 start signal | SoftTag. Modbus signal from Ball Mill VSD Include DV+/- alarm if less than or greater than 2RPM from setpoint. 2000-ME001.3-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | 1 | 6/03/2025 12/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1411 https://pastech-2955.atlassian.net/browse/KAN-1811
|  |  |  | MBMSTRI | MB_MSTR_I | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Master Motor Current | F13MB401 Master Current | 1 | 0 | 2550 | Amps | [18 empty] | 1700 | 5 |  | SoftTag. Modbus signal from Ball Mill VSD 2000-ME001.3-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | B | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1411
|  |  |  | MBMSTRT | MB_MSTR_T | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Master Motor Torque | F13MB401 Master Torque | 1 | 0 | 954.881 | kNm | [18 empty] | 700 | 5 |  | SoftTag. Modbus signal from Ball Mill VSD 2000-ME001.3-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | B | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1411
|  |  |  | MBMSTRPWR | JI13149A | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Master Motor Power | F13MB401 Master Power | 1 | 0 | 15000 | kW | [16 empty] | 9900 | 5 | 10000 | 5 |  | SoftTag. Modbus signal from Ball Mill VSD 2000-ME001.3-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | 2 | 6/03/2025 20/05/2026 | https://pastech-2955.atlassian.net/browse/KAN-1411 https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=511&pa=1&e=hmg2b6
|  |  |  | MBSLVESPD | SI13150B | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Slave Motor Speed Feedback | F13MB401 Slave Speed | 1 | -7.5 | 165 | RPM | [12 empty] | 115 | 5 | 120 | 5 | 160 | 5 | 164 | 5 | 1. Mask if F13-MB-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MB-401 start signal | SoftTag. Modbus signal from Ball Mill VSD Include DV+/- alarm if less than or greater than 2RPM from setpoint. 2000-ME001.3-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1411
|  |  |  | MBSLVEI | MB_SLVE_I | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Slave Motor Current | F13MB401 Slave Current | 1 | 0 | 2550 | Amps | [18 empty] | 1700 | 5 |  | SoftTag. Modbus signal from Ball Mill VSD 2000-ME001.3-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | B
|  |  |  | MBSLVET | MB_SLVE_T | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Slave Motor Torque | F13MB401 Slave Torque | 1 | 0 | 954.881 | kNm | [16 empty] | 700 | 5 |  |  |  | SoftTag. Modbus signal from Ball Mill VSD 2000-ME001.3-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | B
|  |  |  | MBSLVEPWR | JI13149B | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Slave Motor Power | F13MB401 Slave Power | 1 | 0 | 15000 | kW | [16 empty] | 9900 | 5 | 10000 | 5 |  | SoftTag. Modbus signal from Ball Mill VSD 2000-ME001.3-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=511&pa=1&e=hmg2b6
|  |  |  | MBCOOLCOND | MB_COOL_COND | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Pure Water Conductivity | F13MB401 Pure Water Cond | 1 | 0 | 3 | µS/cm | [16 empty] | 0.8 | 5 |  |  |  | SoftTag. Modbus signal from Ball Mill VSD 2000-ME001.3-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | B
|  |  |  | TE13716A | TI13716A | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End Trunnion Bearing (Right Side) Outboard Temperature Element | F13MS401 Dsch Trn R OB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13716B | TI13716B | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End Trunnion Bearing (Right Side) Centre Temperature Element | F13MS401 Dsch Trn R Ctr | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13716C | TI13716C | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End Trunnion Bearing (Right Side) Inboard Temperature Element | F13MS401 Dsch Trn R IB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13717A | TI13717A | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End Trunnion Bearing (Left Side) Outboard Temperature Element | F13MS401 Dsch Trn L OB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13717B | TI13717B | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End Trunnion Bearing (Left Side) Centre Temperature Element | F13MS401 Dsch Trn L Ctr | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13717C | TI13717C | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End Trunnion Bearing (Left Side) Inboard Temperature Element | F13MS401 Dsch Trn L IB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13714A | TI13714A | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Feed End Trunnion Bearing (Left Side) Outboard Temperature Element | F13MS401 Feed Trn L OB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13714B | TI13714B | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Feed End Trunnion Bearing (Left Side) Centre Temperature Element | F13MS401 Feed Trn L Ctr | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13714C | TI13714C | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Feed End Trunnion Bearing (Left Side) Inboard Temperature Element | F13MS401 Feed Trn L IB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13712A | TI13712A | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Feed End Trunnion Bearing (Right Side) Outboard Temperature Element | F13MS401 Feed Trn R OB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13712B | TI13712B | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Feed End Trunnion Bearing (Right Side) Centre Temperature Element | F13MS401 Feed Trn R Ctr | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13712C | TI13712C | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Feed End Trunnion Bearing (Right Side) Inboard Temperature Element | F13MS401 Feed Trn R IB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13715A | TI13715A | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End Thrust Bearing (Left Side) Outboard Temperature Element | F13MS401 Dsch Thst L OB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13715B | TI13715B | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End Thrust Bearing (Left Side) Inboard Temperature Element | F13MS401 Dsch Thst L IB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13713A | TI13713A | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End Thrust Bearing (Right Side) Outboard Temperature Element | F13MS401 Dsch Thst R OB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13713B | TI13713B | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End Thrust Bearing (Right Side) Inboard Temperature Element | F13MS401 Dsch Thst R IB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13706 | TI13706 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Feed End (Floating) Pinion Right Side Bearing Temperature Element | F13MS401 Feed Fl. Pin. R | 1 | -5 | 100 | °C | [16 empty] | 70 | 5 | 75 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | TE13704 | TI13704 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End (Fixed) Pinion Right Side Bearing Temperature Element | F13MS401 Dsch Fxd Pin. R | 1 | -5 | 100 | °C | [16 empty] | 70 | 5 | 75 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | F13CALC10018 | TDI13712 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Feed Trunnion Bearing (Right) Differential Temperature | F13MS401 Fd TrnBrgR dT | 1 | 0 | 100 | °C | [16 empty] | 5 | 5 |  |  |  | A_Hi = Warning 2000-ME001.2-F17-50001 | 0
|  |  |  | F13CALC10019 | TDI13716 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge Trunnion Bearing (Right) Differential Temperature | F13MS401 Dsch TrnBrgR dT | 1 | 0 | 100 | °C | [16 empty] | 5 | 5 |  |  |  | A_Hi = Warning 2000-ME001.2-F17-50001 | 0
|  |  |  | F13CALC10020 | TDI13714 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Feed Trunnion Bearing (Left) Differential Temperature | F13MS401 Fd TrnBrgL dT | 1 | 0 | 100 | °C | [16 empty] | 5 | 5 |  |  |  | A_Hi = Warning 2000-ME001.2-F17-50001 | 0
|  |  |  | F13CALC10021 | TDI13717 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge Trunnion Bearing (Left) Differential Temperature | F13MS401 Dsch TrnBrgL dT | 1 | 0 | 100 | °C | [16 empty] | 5 | 5 |  |  |  | A_Hi = Warning 2000-ME001.2-F17-50001 | 0
|  |  |  | TT13511 | TI13511 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Pinion Gear Flank (Right) Temperature Transmitter 1 | F13MS401 Pin. Flank R 1 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MS-401A/B (Normal mode) A_HH = Trip F13-MS-401A/B (Normal mode) 2000-ME001.2-F17-50001 | B
|  |  |  | TT13512 | TI13512 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Pinion Gear Flank (Right) Temperature Transmitter 2 | F13MS401 Pin. Flank R 2 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MS-401A/B (Normal mode) A_HH = Trip F13-MS-401A/B (Normal mode) 2000-ME001.2-F17-50001 | B
|  |  |  | TT13513 | TI13513 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Pinion Gear Flank (Right) Temperature Transmitter 3 | F13MS401 Pin. Flank R 3 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MS-401A/B (Normal mode) A_HH = Trip F13-MS-401A/B (Normal mode) 2000-ME001.2-F17-50001 | B
|  |  |  | TT13514 | TI13514 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Pinion Gear Flank (Right) Temperature Transmitter 4 | F13MS401 Pin. Flank R 4 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MS-401A/B (Normal mode) A_HH = Trip F13-MS-401A/B (Normal mode) 2000-ME001.2-F17-50001 | B
|  |  |  | F13CALC10016 | TDI13511 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Pinion Gear Flank (Right) Differential Temperature | F13MS401 Pin. Gear R dT | 1 | 0 | 100 | °C | [16 empty] | 8 | 5 | 17 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.2-M02-50001 | 0
|  |  |  | VT13710 | VI13710 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Feed End (Floating) Pinion Right Side Bearing Vibration Transmitter | F13MS401 Feed Fl. Pin. R | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.2-F17-50001 | B |  | MOC-493
|  |  |  | VT13708 | VI13708 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End (Fixed) Pinion Right Side Bearing Vibration Transmitter | F13MS401 Feed Fxd Pin. R | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.2-F17-50001 | B |  | MOC-493 |  |  |  |  | Field transmitter has been replaced with new range of 0 - 20 mm/s
|  |  |  | TE13707 | TI13707 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Feed End (Floating) Pinion Left Side Bearing Temperature Element | F13MS401 Feed Fl. Pin. L | 1 | -5 | 100 | °C | [16 empty] | 70 | 5 | 75 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.3-F17-50001 | B
|  |  |  | TE13705 | TI13705 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End (Fixed) Pinion Left Side Bearing Temperature Element | F13MS401 Dsch Fxd Pin. L | 1 | -5 | 100 | °C | [16 empty] | 70 | 5 | 75 | 5 |  | A_Hi = Start permissive for F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.3-F17-50001 | B
|  |  |  | TT13515 | TI13515 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Pinion Gear Flank (Left) Temperature Transmitter 1 | F13MS401 Pin. Flank L 1 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MS-401A/B (Normal mode) A_HH = Trip F13-MS-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B
|  |  |  | TT13516 | TI13516 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Pinion Gear Flank (Left) Temperature Transmitter 2 | F13MS401 Pin. Flank L 2 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MS-401A/B (Normal mode) A_HH = Trip F13-MS-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B | [6 empty] | Loop test completed, however, the transmitter has been water damage as per E&I Manesh. Jwho - 1/5/2026 Field issue resolved
|  |  |  | TT13519 | TI13519 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Pinion Gear Flank (Left) Temperature Transmitter 3 | F13MS401 Pin. Flank L 3 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MS-401A/B (Normal mode) A_HH = Trip F13-MS-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B
|  |  |  | TT13520 | TI13520 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Pinion Gear Flank (Left) Temperature Transmitter 4 | F13MS401 Pin. Flank L 4 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MS-401A/B (Normal mode) A_HH = Trip F13-MS-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B
|  |  |  | F13CALC10017 | TDI13515 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Pinion Gear Flank (Left) Differential Temperature | F13MS401 Pin. Gear L dT | 1 | 0 | 100 | °C | [16 empty] | 8 | 5 | 17 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.2-M02-50001 | 0
|  |  |  | VT13711 | VI13711 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Feed End (Floating) Pinion Left Side Bearing Vibration Transmitter | F13MS401 Feed Fl. Pin. L | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.2-F17-50001 | B |  | MOC-493
|  |  |  | VT13709 | VI13709 | 2000-F13-PID-PR-10010 | F13-MS-401 SAG Mill Discharge End (Fixed) Pinion Left Side Bearing Vibration Transmitter | F13MS401 Feed Fxd Pin. L | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.2-F17-50001 | B |  | MOC-493
|  |  |  | PT13572 | PI13572 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Motor 1 Drive End Pressure Transmitter | F13MS401A Motor DE Lube | 1 | 0 | 25000 | kPa | [12 empty] | 6200 | 5 | 8500 | 5 | 15000 | 5 | 17500 | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | A_LL = Warning A_Lo = Warning A_Hi = Warning A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 250 barg MAX range converted | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PT13573 | PI13573 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Motor 1 Non-Drive End Pressure Transmitter | F13MS401A Motor NDE Lube | 1 | 0 | 25000 | kPa | [12 empty] | 6200 | 5 | 8500 | 5 | 15000 | 5 | 17500 | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | A_LL = Warning A_Lo = Warning A_Hi = Warning A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 250 barg MAX range converted | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PT13574 | PI13574 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Motor 2 Drive End Pressure Transmitter | F13MS401B Motor DE Lube | 1 | 0 | 25000 | kPa | [12 empty] | 6200 | 5 | 8500 | 5 | 15000 | 5 | 17500 | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | A_LL = Warning A_Lo = Warning A_Hi = Warning A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 250 barg MAX range converted | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PT13575 | PI13575 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Motor 2 Non-Drive End Pressure Transmitter | F13MS401B Motor NDE Lube | 1 | 0 | 25000 | kPa | [12 empty] | 6200 | 5 | 8500 | 5 | 15000 | 5 | 17500 | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | A_LL = Warning A_Lo = Warning A_Hi = Warning A_HH = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 250 barg MAX range converted | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | FT13576 | FI13576 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Motor 1 Drive End Flow Transmitter | F13MS401A Motor DE Lube | 1 | 0 | 5 | L/min | [12 empty] | 0.6 | 5 | 0.9 | 5 |  |  |  |  | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | A_LL = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_Lo = Warning & start permissive F13-MS-401A/B (Normal mode) 2000-ME001.2-F17-50001 2000-ME001.2-M01-50001 | B | [6 empty] | Changed the range from 0 - 3 to 0 - 5
|  |  |  | FT13577 | FI13577 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Motor 1 Non-Drive End Flow Transmitter | F13MS401A Motor NDE Lube | 1 | 0 | 5 | L/min | [12 empty] | 0.6 | 5 | 0.9 | 5 |  |  |  |  | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | A_LL = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_Lo = Warning & start permissive F13-MS-401A/B (Normal mode) 2000-ME001.2-F17-50001 2000-ME001.2-M01-50001 | B | [6 empty] | Changed the range from 0 - 3 to 0 - 5
|  |  |  | FT13578 | FI13578 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Motor 2 Drive End Flow Transmitter | F13MS401B Motor DE Lube | 1 | 0 | 5 | L/min | [12 empty] | 0.6 | 5 | 0.9 | 5 |  |  |  |  | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | A_LL = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_Lo = Warning & start permissive F13-MS-401A/B (Normal mode) 2000-ME001.2-F17-50001 2000-ME001.2-M01-50001 | B | [6 empty] | Changed the range from 0 - 3 to 0 - 5
|  |  |  | FT13579 | FI13579 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Motor 2 Non-Drive End Flow Transmitter | F13MS401B Motor NDE Lube | 1 | 0 | 5 | L/min | [12 empty] | 0.6 | 5 | 0.9 | 5 |  |  |  |  | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | A_LL = Trip F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_Lo = Warning & start permissive F13-MS-401A/B (Normal mode) 2000-ME001.2-F17-50001 2000-ME001.2-M01-50001 | B | [6 empty] | Changed the range from 0 - 3 to 0 - 5
|  |  |  | TT13570 | TI13570 | 2000-F13-PID-PR-10010 |  | F13LU411 Tank Temp. | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Warning A_HH = Warning & start permissive F13-MS-401A/B (Normal mode) 2000-ME001.2-M01-50001 | B
|  |  |  | LT13571 | LI13571 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Reservoir Level Transmitter | F13LU411 Tank Level | 1 | 0 | 100 | % | [12 empty] | 25 | 5 | 35 | 5 | [5 empty] | A_LL = Warning A_Lo = Warning % Level based on below: A_Lo = 92mm, A_LL = 130mm 4mA = 0mm 20mA = 370mm 2000-ME001.2-F17-50001 | B
|  |  |  | VT13517 | VI13517 | 2000-F13-PID-PR-10010 | F13-MS-401A SAG Mill Motor 1 NDE Bearing Vibration Transmitter | F13MS401A Motor NDE Brg | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Trip F13-MS-401A/B (Normal mode) 2000-ME001.2-F17-50001 | B |  | MOC-493
|  |  |  | VT13518 | VI13518 | 2000-F13-PID-PR-10010 | F13-MS-401A SAG Mill Motor 1 DE Bearing Vibration Transmitter | F13MS401A Motor DE Brg | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Trip F13-MS-401A/B (Normal mode) 2000-ME001.2-F17-50001 | B |  | MOC-493
|  |  |  | VT13539 | VI13539 | 2000-F13-PID-PR-10010 | F13-MS-401B SAG Mill Motor 2 NDE Bearing Vibration Transmitter | F13MS401B Motor NDE Brg | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Trip F13-MS-401A/B (Normal mode) 2000-ME001.2-F17-50001 | B |  | MOC-493
|  |  |  | VT13540 | VI13540 | 2000-F13-PID-PR-10010 | F13-MS-401B SAG Mill Motor 2 DE Bearing Vibration Transmitter | F13MS401B Motor DE Brg | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Trip F13-MS-401A/B (Normal mode) 2000-ME001.2-F17-50001 | B |  | MOC-493
|  |  |  | LIT13608 | LI13608 | 2000-F13-PID-PR-10013 | F13-LU-416 SAG Mill Seal Grease System SAG Mill Seal Grease Drum Level indicating Transmitter | F13LU416 Grease Level | 1 | 0 | 100 | % | [14 empty] | 25 | 5 | [5 empty] | A_Lo = Warning 2000-ME001.2-F17-50001 | 1 | 2025-05-28 | https://pastech-2955.atlassian.net/browse/KAN-1938
|  |  |  | PIT13648 | PI13648 | 2000-F13-PID-PR-10013 | F13-LU-413 SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Indicating Transmitter 1 | F13LU413 Dsch Trn Brg 1 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13649 | PI13649 | 2000-F13-PID-PR-10013 | F13-LU-413 SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Indicating Transmitter 2 | F13LU413 Dsch Trn Brg 2 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13650 | PI13650 | 2000-F13-PID-PR-10013 | F13-LU-413 SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Indicating Transmitter 3 | F13LU413 Dsch Trn Brg 3 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13651 | PI13651 | 2000-F13-PID-PR-10013 | F13-LU-413 SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Indicating Transmitter 4 | F13LU413 Dsch Trn Brg 4 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13644 | PI13644 | 2000-F13-PID-PR-10013 | F13-LU-413 SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure Indicating Transmitter 1 | F13LU413 Feed Trn Brg 1 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13645 | PI13645 | 2000-F13-PID-PR-10013 | F13-LU-413 SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure Indicating Transmitter 2 | F13LU413 Feed Trn Brg 2 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13646 | PI13646 | 2000-F13-PID-PR-10013 | F13-LU-413 SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure Indicating Transmitter 3 | F13LU413 Feed Trn Brg 3 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13647 | PI13647 | 2000-F13-PID-PR-10013 | F13-LU-413 SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure Indicating Transmitter 4 | F13LU413 Feed Trn Brg 4 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PDIT13628 | PDI13628 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication System Main Bearings Lube Oil Pump 4 Differential Pressure indicating Transmitter | F13LU413 LP Lube Fltr dP | 1 | 0 | 700 | kPa | [16 empty] | 207 | 5 | 345 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.2-F17-50001 | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | ZT13629 | ZI13629 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication System Lube Oil Heat Exchanger Cooling Water Temperature Control Valve Limit Switch Opened Limit Switch Closed Position Transmitter | TCV13629 Position | 1 | 0 | 100 | % | [21 empty] | 2000-ME001.2-F17-50001 Position indication for TCV13629 (see Control Valves tab) | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  |  | FIT13630 | FI13630 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication System Conditioned Circuit Flow Indicating Transmitter | F13LU413 LP Lube Flow | 1 | 0 | 90 | m3/h | [12 empty] | 22 | 5 | 40 | 5 |  |  |  |  | 1. F13-PO-427 AND F13-PO-428 Not Running 2. Mask for 20 seconds (TBC) on Pump (F13-PO-427 OR 428) start-up | A_LL = Trip F13-PO-427/428/429/430/431 A_Lo = Start permissive F13-PO-429/430/431 2000-ME001.2-F17-50001 | B
|  |  |  | FIT13641 | FI13641 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication System Thrust Rail Lubrication Flow Indicating Transmitter | F13LU413 Thrst Rail Flow | 1 | 0 | 89.94 | m3/h | [12 empty] | 12.24 | 5 | 12.96 | 5 |  |  |  |  | 1. F13-PO-429, 430 AND 431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-PO-429/430/431 and F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) Converted from LPM (IO List) to m3/h 2000-ME001.2-F17-50001 | B
|  |  |  | FIT13657 | FI13657 | 2000-F13-PID-PR-10010 | F13LU413 SAG Mill Main Bearings Lubrication System Floating Pinion Bearing (Right Side) Flow Indicating Transmitter | F13LU413 Float. Pinion R | 1 | 0 | 17 | L/min | [12 empty] | 9 | 5 | 9.5 | 5 |  |  |  |  | 1. F13-PO-434 Not Running AND F13-PO-435 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-434 OR 435) start-up | A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | FIT13658 | FI13658 | 2000-F13-PID-PR-10010 | F13LU413 SAG Mill Main Bearings Lubrication System Fixed Pinion Bearing (Right Side) Flow Indicating Transmitter | F13LU413 Fxd Pinion R | 1 | 0 | 17 | L/min | [12 empty] | 9 | 5 | 9.5 | 5 |  |  |  |  | 1. F13-PO-434 Not Running AND F13-PO-435 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-434 OR 435) start-up | A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | FIT13659 | FI13659 | 2000-F13-PID-PR-10010 | F13LU413 SAG Mill Main Bearings Lubrication System Floating Pinion Bearing (Left Side) Flow Indicating Transmitter | F13LU413 Float. Pinion L | 1 | 0 | 17 | L/min | [12 empty] | 9 | 5 | 9.5 | 5 |  |  |  |  | 1. F13-PO-434 Not Running AND F13-PO-435 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-434 OR 435) start-up | A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | FIT13660 | FI13660 | 2000-F13-PID-PR-10010 | F13LU413 SAG Mill Main Bearings Lubrication System Fixed Pinion Bearing (Left Side) Flow Indicating Transmitter | F13LU413 Fxd Pinion L | 1 | 0 | 17 | L/min | [12 empty] | 9 | 5 | 9.5 | 5 |  |  |  |  | 1. F13-PO-434 Not Running AND F13-PO-435 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-434 OR 435) start-up | A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) 2000-ME001.2-F17-50001 | B
|  |  |  | LIT13619 | LI13619 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication System Suction Compartment Level Indicating Transmitter | F13LU413 Lube Set. Comp. | 1 | 0 | 100 | % | [12 empty] | 10 | 5 | 38 | 5 | [5 empty] | A_Lo = Start permissive for F13-MS-401A/B (Normal mode), F13-PO-427/428/434/435 A_LL = Trip F13-PO-427/428/434/435 and F13-HT-433/434 4mA = 0.25mm 20mA = 1346mm From vendor doc, A_LL = 1219mm, 10% (130/1346), A_Lo = 838mm, 38% (508/1346) 2000-ME001.2-F17-50001 | B
|  |  |  | LIT13620 | LI13620 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication System Conditioned Compartment Level Indicating Transmitter | F13LU413 Lube Cond. Comp | 1 | 0 | 100 | % | [12 empty] | 25 | 5 | 76 | 5 | [5 empty] | A_Lo = Start permissive for F13-MS-401A/B (Normal mode), F13-PO-445/429/430/431 A_LL = Trip F13-PO-445/429/430/431 and F13-HT-435/436 4mA = 0.25m 20mA = 1346mm From vendor doc, A_LL = 1016mm, 25% (330/1346), A_Lo = 330mm, 75% (1016/1346) 2000-ME001.2-F17-50001 | B
|  |  |  | FIT13640 | FI13640 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication System Flow Divider Feed Flow Indicating Transmitter | F13LU413 Flow Divider | 1 | 0 | 89.94 | m3/h | [12 empty] | 12.24 | 5 | 12.96 | 5 |  |  |  |  | 1. F13-PO-429, 430 AND 431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | A_Lo = Start permissive for F13-MS-401A/B (Inching & Normal mode) or F13-HU-413 (SAG Mill HPU Inching) A_LL = Trip F13-PO-429/430/431 and F13-MS-401A/B (Inching & Normal mode) and F13-HU-413 (SAG Mill HPU Inching) UoM converted to m3/h from L/min 2000-ME001.2-F17-50001 | B
|  |  |  | TIT13623 | TI13623 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication System Conditioned Compartment Temperature Indicating Transmitter | F13LU413 Lube Cond. Comp | 1 | -5 | 100 | °C |  |  |  | 34 | 5 |  | 37 | 5 |  |  |  |  | 26.6 | 5 | 32 | 5 | 45 | 5 | 47 | 5 |  | A_LL = Trip F13-PO-445/429/430/431 A_Lo = Start permissive for F13-MS-401A/B (Normal mode) and F13-PO-445/429/430/431 A_Hi = Start permissive F13-MS-401A/B (Normal mode) and F13-HT-435/436 A_HH = Trip F13-HT-435/436 and F13-PO-429/430/431 P_Lo = Start F13-HT-435 & 436 P_Hi = Stop F13-HT-435 & 436 2000-ME001.2-F17-50001 | MOC-460
|  |  |  | TIT13615 | TI13615 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication System Suction Compartment Temperature Indicating Transmitter | F13LU413 Lube Set. Comp. | 1 | -5 | 100 | °C |  |  |  | 34 | 5 |  | 37 | 5 |  |  |  |  | 26.6 | 5 | 32 | 5 | 45 | 5 | 47 | 5 |  | A_LL = Trip F13-PO-427/428 A_Lo = Start permissive for F13-MS-401A/B (Normal mode) and F13-PO-427/428/435/434 A_Hi = Start permissive F13-MS-401A/B (Normal mode) and F13-HT-433/434 A_HH = Trip F13-HT-433/434 and F13-PO-427/428 P_Lo = Start F13-HT-433 & 434 P_Hi = Stop F13-HT-433 & 434 2000-ME001.2-F17-50001 | MOC-460
|  |  |  | F13LU413STSS | F13LU413_STS | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Oil Status | F13LU413 OCM Status | 1 | 0 | 3 | - | [21 empty] | SoftTag Register 30 0 = NOT READY 1 = READY 2 = TESTING 3 = WAITING Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics | 0
|  |  |  | F13LU413RHS | F13LU413_RH | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Oil %RH | F13LU413 OCM %RH | 1 | 0 | 100 | % | [21 empty] | SoftTag Register 34 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics | 0
|  |  |  | F13LU413TEMPS | F13LU413_TEMP | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Oil Temperature | F13LU413 OCM Temperature | 1 | -5 | 100 | °C | [21 empty] | SoftTag Register 33 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics | 0
|  |  |  | F13LU413_4US | F13LU413_4U | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU413 Count > 4µm | 1 | 0 | 2000000 | µm/100mL | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 4 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 2025-03-18 | Calculation comment deleted - unnecassary
|  |  |  | F13LU413_6US | F13LU413_6U | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU413 Count >6µm | 1 | 0 | 2000000 | µm/100mL | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 6 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 2025-03-18 | Calculation comment deleted - unnecassary
|  |  |  | F13LU413_14US | F13LU413_14U | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU413 Count >14µm | 1 | 0 | 2000000 | µm/100mL | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 14 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 2025-03-18 | Calculation comment deleted - unnecassary
|  |  |  | F13LU413_21US | F13LU413_21U | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU413 Count >21µm | 1 | 0 | 2000000 | µm/100mL | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 21 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 2025-03-18 | Calculation comment deleted - unnecassary
|  |  |  | F13LU413_25US | F13LU413_25U | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU413 Count >25µm | 1 | 0 | 2000000 | µm/100mL | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 25 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 2025-03-18 | Calculation comment deleted - unnecassary
|  |  |  | F13LU413_38US | F13LU413_38U | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU413 Count >38µm | 1 | 0 | 2000000 | µm/100mL | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 38 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 2025-03-18 | Calculation comment deleted - unnecassary
|  |  |  | F13LU413_50US | F13LU413_50U | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU413 Count >50µm | 1 | 0 | 2000000 | µm/100mL | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 50 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 2025-03-18 | Calculation comment deleted - unnecassary
|  |  |  | F13LU413_70US | F13LU413_70U | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU413 Count >70µm | 1 | 0 | 2000000 | µm/100mL | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 70 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 2025-03-18 | Calculation comment deleted - unnecassary
|  |  |  | LT13142 | LI13142 | 2000-F13-PID-PR-10004 | F13-BN-404 Ball Mill Ball Charger Feed Bin Level Transmitter | F13BN404 MB Ball Lvl | 1 | 0 | 100 | % | [12 empty] | 20 | 5 | 30 | 5 | 80 | 5 | 90 | 5 |  | Alarm setpoints to be confirmed during commissioning. | B | [6 empty] | can't check IOP-
|  |  |  | TE13966A | TI13966A | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Feed End Trunnion Bearing (Left Side) Temperature Element Outboard | F13MB401 Feed Trn L OB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B | [6 empty] | can't check IOP-, 200+c won't trigger IOP, otherwise OK
|  |  |  | TE13966B | TI13966B | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Feed End Trunnion Bearing (Left Side) Temperature Element Centre | F13MB401 Feed Trn L Ctr | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B | [6 empty] | can't check IOP-, 200+c won't trigger IOP, otherwise OK
|  |  |  | TE13966C | TI13966C | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Feed End Trunnion Bearing (Left Side) Temperature Element Inboard | F13MB401 Feed Trn L IB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B | [6 empty] | can't check IOP-, 200+c won't trigger IOP, otherwise OK
|  |  |  | TE13964A | TI13964A | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Feed End Trunnion Bearing (Right Side) Temperature Element Outboard | F13MB401 Feed Trn R OB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B | [6 empty] | can't check IOP-, 200+c won't trigger IOP, otherwise OK
|  |  |  | TE13964B | TI13964B | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Feed End Trunnion Bearing (Right Side) Temperature Element Centre | F13MB401 Feed Trn R Ctr | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B | [6 empty] | can't check IOP-, 200+c won't trigger IOP, otherwise OK
|  |  |  | TE13964C | TI13964C | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Feed End Trunnion Bearing (Right Side) Temperature Element Inboard | F13MB401 Feed Trn R IB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B | [6 empty] | can't check IOP-, 200+c won't trigger IOP, otherwise OK
|  |  |  | TE13960A | TI13960A | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Discharge End Trunnion Bearing (Left Side) Temperature Element Outboard | F13MB401 Dsch Trn L OB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B
|  |  |  | TE13960B | TI13960B | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Discharge End Trunnion Bearing (Left Side) Temperature Element Centre | F13MB401 Dsch Trn L Ctr | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B
|  |  |  | TE13960C | TI13960C | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Discharge End Trunnion Bearing (Left Side) Temperature Element Inboard | F13MB401 Dsch Trn L IB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B
|  |  |  | TE13958A | TI13958A | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Discharge End Trunnion Bearing (Right Side) Temperature Element Outboard | F13MB401 Dsch Trn R OB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B
|  |  |  | TE13958B | TI13958B | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Discharge End Trunnion Bearing (Right Side) Temperature Element Centre | F13MB401 Dsch Trn R Ctr | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B
|  |  |  | TE13958C | TI13958C | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Discharge End Trunnion Bearing (Right Side) Temperature Element Inboard | F13MB401 Dsch Trn R IB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B
|  |  |  | TE13967A | TI13967A | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Thrust Bearing Discharge End (Left Side) Temperature Element Inboard | F13MB401 Dsch Thst L OB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B
|  |  |  | TE13967B | TI13967B | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Thrust Bearing Discharge End (Left Side) Temperature Element Outboard | F13MB401 Dsch Thst L IB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B | [6 empty] | can't check IOP-, 200+c won't trigger IOP, otherwise OK
|  |  |  | TE13962A | TI13962A | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Thrust Bearing Discharge End (Right Side) Temperature Element Outboard | F13MB401 Dsch Thst R OB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B
|  |  |  | TE13962B | TI13962B | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Thrust Bearing Discharge End (Right Side) Temperature Element Inboard | F13MB401 Dsch Thst R IB | 1 | -5 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B
|  |  |  | TE13955 | TI13955 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Feed End Floating Pinion Bearing (Right Side) Temperature Element | F13MB401 Feed Fl. Pin. R | 1 | -5 | 100 | °C | [16 empty] | 70 | 5 | 75 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B | [6 empty] | can't check IOP-, 200+c won't trigger IOP, otherwise OK
|  |  |  | TE13957 | TI13957 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Discharge End Fixed Pinion Bearing (Right Side) Temperature Element | F13MB401 Dsch Fxd Pin. R | 1 | -5 | 100 | °C | [16 empty] | 70 | 5 | 75 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B | [6 empty] | can't check IOP-, 200+c won't trigger IOP, otherwise OK
|  |  |  | F13CALC10024 | TDI13964 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Feed Trunnion Bearing (Right) Differential Temperature | F13MB401 Fd TrnBrgR dT | 1 | 0 | 100 | °C | [16 empty] | 5 | 5 |  |  |  | A_Hi = Warning 2000-ME001.3-F17-50001 | 0
|  |  |  | F13CALC10025 | TDI13958 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Discharge Trunnion Bearing (Right) Differential Temperature | F13MB401 Dsch TrnBrgR dT | 1 | 0 | 100 | °C | [16 empty] | 5 | 5 |  |  |  | A_Hi = Warning 2000-ME001.3-F17-50001 | 0
|  |  |  | F13CALC10026 | TDI13966 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Feed Trunnion Bearing (Left) Differential Temperature | F13MB401 Fd TrnBrgL dT | 1 | 0 | 100 | °C | [16 empty] | 5 | 5 |  |  |  | A_Hi = Warning 2000-ME001.3-F17-50001 | 0
|  |  |  | F13CALC10027 | TDI13960 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Discharge Trunnion Bearing (Left) Differential Temperature | F13MB401 Dsch TrnBrgL dT | 1 | 0 | 100 | °C | [16 empty] | 5 | 5 |  |  |  | A_Hi = Warning 2000-ME001.3-F17-50001 | 0
|  |  |  | TT13763 | TI13763 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Pinion Gear Flank (Right) Temperature Transmitter 1 | F13MB401 Pin. Flank R 1 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MB-401A/B (Normal mode) A_HH = Trip F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B
|  |  |  | TT13764 | TI13764 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Pinion Gear Flank (Right) Temperature Transmitter 2 | F13MB401 Pin. Flank R 2 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MB-401A/B (Normal mode) A_HH = Trip F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B
|  |  |  | TT13765 | TI13765 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Pinion Gear Flank (Right) Temperature Transmitter 3 | F13MB401 Pin. Flank R 3 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MB-401A/B (Normal mode) A_HH = Trip F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B
|  |  |  | TT13766 | TI13766 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Pinion Gear Flank (Right) Temperature Transmitter 4 | F13MB401 Pin. Flank R 4 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MB-401A/B (Normal mode) A_HH = Trip F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B
|  |  |  | F13CALC10022 | TDI13763 | 2000-F13-PID-PR-10011 | F13-MB-401A Ball Mill Pinion Gear Flank (Right) Differential Temperature | F13MB401A Pin. Gear R dT | 1 | 0 | 100 | °C | [16 empty] | 8 | 5 | 17 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.3-M02-50001 | 1 | 2025-06-25 | No action required. Aligned with DCS
|  |  |  | VT13972 | VI13972 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Feed End Floating Pinion Bearing (Right Side) Vibration Transmitter | F13MB401 Feed Fl. Pin. R | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.3-F17-50001 | B |  | MOC-493
|  |  |  | VT13974 | VI13974 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Discharge End Fixed Pinion Bearing (Right Side) Vibration Transmitter | F13MB401 Feed Fxd Pin. R | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.3-F17-50001 | B |  | MOC-493
|  |  |  | TE13954 | TI13954 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Feed End Floating Pinion Bearing (Left Side) Temperature Element | F13MB401 Feed Fl. Pin. L | 1 | -5 | 100 | °C | [16 empty] | 70 | 5 | 75 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B | [6 empty] | can't check IOP-, 200+c won't trigger IOP, otherwise OK
|  |  |  | TE13956 | TI13956 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Discharge End Fixed Pinion Bearing (Left Side) Temperature Element | F13MB401 Dsch Fxd Pin. L | 1 | -5 | 100 | °C | [16 empty] | 70 | 5 | 75 | 5 |  | A_Hi = Start permissive for F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | B | [6 empty] | can't check IOP-, 200+c won't trigger IOP, otherwise OK
|  |  |  | TT13783 | TI13783 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Pinion Gear Flank (Left) Temperature Transmitter 1 | F13MB401 Pin. Flank L 1 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MB-401A/B (Normal mode) A_HH = Trip F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B
|  |  |  | TT13784 | TI13784 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Pinion Gear Flank (Left) Temperature Transmitter 2 | F13MB401 Pin. Flank L 2 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MB-401A/B (Normal mode) A_HH = Trip F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B
|  |  |  | TT13785 | TI13785 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Pinion Gear Flank (Left) Temperature Transmitter 3 | F13MB401 Pin. Flank L 3 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MB-401A/B (Normal mode) A_HH = Trip F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B
|  |  |  | TT13786 | TI13786 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Pinion Gear Flank (Left) Temperature Transmitter 4 | F13MB401 Pin. Flank L 4 | 1 | -20 | 600 | °C | [16 empty] | 90 | 5 | 100 | 5 |  | A_Hi = Start permissive F13-MB-401A/B (Normal mode) A_HH = Trip F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B
|  |  |  | F13CALC10023 | TDI13786 | 2000-F13-PID-PR-10011 | F13-MB-401B Ball Mill Pinion Gear Flank (Left) Differential Temperature | F13MB401B Pin. Gear L dT | 1 | 0 | 100 | °C | [16 empty] | 8 | 5 | 17 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.3-M02-50001 | 1 | 2025-06-25 | No action required. Aligned with DCS
|  |  |  | VT13971 | VI13971 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Feed End Floating Pinion Bearing (Left Side) Vibration Transmitter | F13MB401 Feed Fl. Pin. L | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.3-F17-50001 | B |  | MOC-493
|  |  |  | VT13973 | VI13973 | 2000-F13-PID-PR-10011 | F13-MB-401 Ball Mill Discharge End Fixed Pinion Bearing (Left Side) Vibration Transmitter | F13MB401 Feed Fxd Pin. L | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.3-F17-50001 | B |  | MOC-493
|  |  |  | PT13823 | PI13823 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Motor 1 Drive End Pressure Transmitter | F13MB401A Motor DE Lube | 1 | 0 | 25000 | kPa | [12 empty] | 6200 | 5 | 8500 | 5 | 15000 | 5 | 17500 | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | A_LL = Warning A_Lo = Warning A_Hi = Warning A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 250 barg MAX range converted | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PT13824 | PI13824 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Motor 1 Non-Drive End Pressure Transmitter | F13MB401A Motor NDE Lube | 1 | 0 | 25000 | kPa | [12 empty] | 6200 | 5 | 8500 | 5 | 15000 | 5 | 17500 | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | A_LL = Warning A_Lo = Warning A_Hi = Warning A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 250 barg MAX range converted | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PT13825 | PI13825 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Motor 2 Drive End Pressure Transmitter | F13MB401B Motor DE Lube | 1 | 0 | 25000 | kPa | [12 empty] | 6200 | 5 | 8500 | 5 | 15000 | 5 | 17500 | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | A_LL = Warning A_Lo = Warning A_Hi = Warning A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 250 barg MAX range converted | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PT13826 | PI13826 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Motor 2 Non-Drive End Pressure Transmitter | F13MB401B Motor NDE Lube | 1 | 0 | 25000 | kPa | [12 empty] | 6200 | 5 | 8500 | 5 | 15000 | 5 | 17500 | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | A_LL = Warning A_Lo = Warning A_Hi = Warning A_HH = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 250 barg MAX range converted | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | FT13827 | FI13827 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Motor 1 Drive End Flow Transmitter | F13MB401A Motor DE Lube | 1 | 0 | 3 5 | L/min | [12 empty] | 0.6 | 5 | 0.9 | 5 |  |  |  |  | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | A_LL = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_Lo = Warning & start permissive F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 2000-ME001.3-M01-50001 | B
|  |  |  | FT13828 | FI13828 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Motor 1 Non-Drive End Flow Transmitter | F13MB401A Motor NDE Lube | 1 | 0 | 3 5 | L/min | [12 empty] | 0.6 | 5 | 0.9 | 5 |  |  |  |  | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | A_LL = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_Lo = Warning & start permissive F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 2000-ME001.3-M01-50001 | B
|  |  |  | FT13829 | FI13829 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Motor 2 Drive End Flow Transmitter | F13MB401B Motor DE Lube | 1 | 0 | 3 5 | L/min | [12 empty] | 0.6 | 5 | 0.9 | 5 |  |  |  |  | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | A_LL = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_Lo = Warning & start permissive F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 2000-ME001.3-M01-50001 | B
|  |  |  | FT13830 | FI13830 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Motor 2 Non-Drive End Flow Transmitter | F13MB401B Motor NDE Lube | 1 | 0 | 3 5 | L/min | [12 empty] | 0.6 | 5 | 0.9 | 5 |  |  |  |  | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | A_LL = Trip F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_Lo = Warning & start permissive F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 2000-ME001.3-M01-50001 | B
|  |  |  | TT13821 | TI13821 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Reservoir Temperature Transmitter | F13LU421 Tank Temp. | 1 | -5 0 | 100 | °C | [16 empty] | 55 | 5 | 60 | 5 |  | A_Hi = Warning A_HH = Warning & start permissive F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B
|  |  |  | LT13822 | LI13822 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Reservoir Level Transmitter | F13LU421 Tank Level | 1 | 0 | 100 | % | [12 empty] | 25 | 5 | 35 | 5 | [5 empty] | A_LL = Warning A_Lo = Warning % Level based on below: A_Lo = 92mm, A_LL = 130mm 4mA = 0mm 20mA = 370mm 2000-ME001.3-F17-50001 | B
|  |  |  | VT13767 | VI13767 | 2000-F13-PID-PR-10011 | F13-MB-401A Ball Mill Motor 1 NDE Bearing Vibration Transmitter | F13MB401A Motor NDE Brg | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Trip F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B |  | MOC-493
|  |  |  | VT13770 | VI13770 | 2000-F13-PID-PR-10011 | F13-MB-401A Ball Mill Motor 1 DE Bearing Vibration Transmitter | F13MB401A Motor DE Brg | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Trip F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B |  | MOC-493
|  |  |  | VT13789 | VI13789 | 2000-F13-PID-PR-10011 | F13-MB-401B Ball Mill Motor 2 Non Drive End Bearing Vibration Transmitter | F13MB401B Motor NDE Brg | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Trip F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B |  | MOC-493
|  |  |  | VT13792 | VI13792 | 2000-F13-PID-PR-10011 | F13-MB-401B Ball Mill Motor 2 DE Bearing Vibration Transmitter | F13MB401B Motor DE Brg | 1 | 0 | 20 | mm/s | [16 empty] | 4.5 | 5 | 7.1 | 5 |  | A_Hi = Warning A_HH = Trip F13-MB-401A/B (Normal mode) 2000-ME001.3-F17-50001 | B |  | MOC-493
|  |  |  | LIT13859 | LI13859 | 2000-F13-PID-PR-10013 | F13-LU-426 Ball Mill Seal Grease System Ball Mill Seal Grease Drum Level Indicating Transmitter | F13LU426 Grease Level | 1 | 0 | 100 | % | [14 empty] | 25 | 5 | [5 empty] | A_Lo = Warning 2000-ME001.3-F17-50001 | 1 | 2025-05-28 | https://pastech-2955.atlassian.net/browse/KAN-1938
|  |  |  | PIT13899 | PI13899 | 2000-F13-PID-PR-10013 | F13-LU-423 Ball Mill Main Bearings Lubrication System Discharge End Bearing Pressure Indicating Transmitter 1 | F13LU423 Dsch Trn Brg 1 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13900 | PI13900 | 2000-F13-PID-PR-10013 | F13-LU-423 Ball Mill Main Bearings Lubrication System Discharge End Bearing Pressure Indicating Transmitter 2 | F13LU423 Dsch Trn Brg 2 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13901 | PI13901 | 2000-F13-PID-PR-10013 | F13-LU-423 Ball Mill Main Bearings Lubrication System Discharge End Bearing Pressure Indicating Transmitter 3 | F13LU423 Dsch Trn Brg 3 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13902 | PI13902 | 2000-F13-PID-PR-10013 | F13-LU-423 Ball Mill Main Bearings Lubrication System Discharge End Bearing Pressure Indicating Transmitter 4 | F13LU423 Dsch Trn Brg 4 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13895 | PI13895 | 2000-F13-PID-PR-10013 | F13-LU-423 Ball Mill Main Bearings Lubrication System Feed End Bearing Pressure Indicating Transmitter 1 | F13LU423 Feed Trn Brg 1 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13896 | PI13896 | 2000-F13-PID-PR-10013 | F13-LU-423 Ball Mill Main Bearings Lubrication System Feed End Bearing Pressure Indicating Transmitter 2 | F13LU423 Feed Trn Brg 2 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13897 | PI13897 | 2000-F13-PID-PR-10013 | F13-LU-423 Ball Mill Main Bearings Lubrication System Feed End Bearing Pressure Indicating Transmitter 3 | F13LU423 Feed Trn Brg 3 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PIT13898 | PI13898 | 2000-F13-PID-PR-10013 | F13-LU-423 Ball Mill Main Bearings Lubrication System Feed End Bearing Pressure Indicating Transmitter 4 | F13LU423 Feed Trn Brg 4 | 1 | 0 | 25000 | kPa | [12 empty] | 3300 | 10 | 3400 | 10 | 8900 | 10 | 9000 | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | A_HH = Warning A_Hi = Warning A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | 2 | 6/03/2025 20/05/2026 | PCT alignment action register (kPa units) https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=h8crdx |  |  |  |  | VG 21/05/26: Modified A_LL and A_Lo as per Rev 2
|  |  |  | PDIT13879 | PDI13879 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Low Pressure Pump Filters No. 1 and No.2 Differential Pressure Indicating Transmitter | F13LU423 LP Lube Fltr dP | 1 | 0 | 700 | kPa | [16 empty] | 207 | 5 | 345 | 5 |  | A_Hi = Warning A_HH = Warning 2000-ME001.3-F17-50001 | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | ZT13880 | ZI13880 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Oil Heat Exchanger Cooling Water Solenoid Position Transmitter | TCV13880 Position | 1 | 0 | 100 | % | [21 empty] | 2000-ME001.3-F17-50001 Position indication for TCV13880 (see Control Valves tab) | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  |  | FIT13881 | FI13881 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Oil Heat Exchanger Discharge Flow Indicating Transmitter | F13LU423 LP Lube Flow | 1 | 0 | 90 | m3/h | [12 empty] | 22 | 5 | 40 | 5 |  |  |  |  | F13-PO-527 AND F13-PO-528 Not Running Mask alarms for 20 seconds on Pump (F13-PO-527 OR 528) start-up | A_LL = Trip F13-PO-527/528/529/530/531 A_Lo = Start permissive F13-PO-529/530/531 2000-ME001.3-F17-50001 | B
|  |  |  | FIT13892 | FI13892 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Flow Dividing Cabinet Flow Indicating Transmitter 2 | F13LU423 Thrst Rail Flow | 1 | 0 | 89.94 | m3/h | [12 empty] | 12.24 | 5 | 12.96 | 5 |  |  |  |  | F13-PO-529, 530 AND 531 Not Running Mask alarms for 10 seconds on Pump (F13-PO-529 OR 530 OR 531) start-up | A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-PO-529/530/531 and F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) Converted from LPM (IO List) to m3/h 2000-ME001.3-F17-50001 | B
|  |  |  | FIT13908 | FI13908 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Feed Floating Pinion Bearing (Right Side) Flow Indicating Transmitter | F13LU423 Float. Pinion R | 1 | 0 | 17 | L/min | [12 empty] | 9 | 5 | 9.5 | 5 |  |  |  |  | F13-PO-534 Not Running AND F13-PO-535 Not Running Mask alarms for 10 seconds on Pump (F13-PO-534 OR 535) start-up | A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | 1 | 2025-05-29 | https://pastech-2955.atlassian.net/browse/KAN-1941
|  |  |  | FIT13909 | FI13909 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Feed Fixed Pinion Bearing (Right Side) Flow Indicating Transmitter | F13LU423 Fxd Pin. Brg R | 1 | 0 | 17 | L/min | [12 empty] | 9 | 5 | 9.5 | 5 |  |  |  |  | F13-PO-534 Not Running AND F13-PO-535 Not Running Mask alarms for 10 seconds on Pump (F13-PO-534 OR 535) start-up | A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | 1 | 2025-05-29 | https://pastech-2955.atlassian.net/browse/KAN-1941
|  |  |  | FIT13910 | FI13910 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Feed Floating Pinion Bearing (Left Side) Flow Indicating Transmitter | F13LU423 Float. Pinion L | 1 | 0 | 17 | L/min | [12 empty] | 9 | 5 | 9.5 | 5 |  |  |  |  | F13-PO-534 Not Running AND F13-PO-535 Not Running Mask alarms for 10 seconds on Pump (F13-PO-534 OR 535) start-up | A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | 1 | 2025-05-29 | https://pastech-2955.atlassian.net/browse/KAN-1941
|  |  |  | FIT13911 | FI13911 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Feed Fixed Pinion Bearing (Left Side) Flow Indicating Transmitter | F13LU423 Fxd Pin. Brg L | 1 | 0 | 17 | L/min | [12 empty] | 9 | 5 | 9.5 | 5 |  |  |  |  | F13-PO-534 Not Running AND F13-PO-535 Not Running Mask alarms for 10 seconds on Pump (F13-PO-534 OR 535) start-up | A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) 2000-ME001.3-F17-50001 | 1 | 2025-05-29 | https://pastech-2955.atlassian.net/browse/KAN-1941
|  |  |  | LIT13874 | LI13874 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Tank Settling Compartment Level Indicating Transmitter | F13LU423 Lube Set. Comp. | 1 | 0 | 100 | % | [12 empty] | 10 | 5 | 38 | 5 | [5 empty] | A_Lo = Start permissive for F13-MB-401A/B (Normal mode), F13-PO-527/528/534/535 A_LL = Trip F13-PO-527/528/534/535 and F13-HT-529/530 4mA = 0.25mm 20mA = 1346mm From vendor doc, A_LL = 1219mm, 10% (130/1346), A_Lo = 838mm, 38% (508/1346) 2000-ME001.3-F17-50001 | B
|  |  |  | LIT13872 | LI13872 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Oil Tank Conditioned Compartment Level Indicating Transmitter | F13LU423 Lube Cond. Comp | 1 | 0 | 100 | % | [12 empty] | 25 | 5 | 75 | 5 | [5 empty] | A_Lo = Start permissive for F13-MB-401A/B (Normal mode), F13-PO-446/529/530/531 A_LL = Trip F13-PO-446/529/530/531 and F13-HT-531/532 4mA = 0.25m 20mA = 1346mm From vendor doc, A_LL = 1016mm, 25% (330/1346), A_Lo = 330mm, 75% (1016/1346) 2000-ME001.3-F17-50001 | B
|  |  |  | FIT13891 | FI13891 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Flow Dividing Cabinet Flow Indicating Transmitter 1 | F13LU423 Flow Divider | 1 | 0 | 89.94 | m3/h | [12 empty] | 12.24 | 5 | 12.96 | 5 |  |  |  |  | F13-PO-529, 530 AND 531 Not Running Mask alarms for 10 seconds on Pump (F13-PO-529 OR 530 OR 531) start-up | A_Lo = Start permissive for F13-MB-401A/B (Inching & Normal mode) or F13-HU-413 (Ball Mill HPU Inching) A_LL = Trip F13-PO-529/530/531 and F13-MB-401A/B (Inching & Normal mode) and F13-HU-413 (Ball Mill HPU Inching) UoM converted to m3/h from L/min 2000-ME001.3-F17-50001 | B
|  |  |  | TIT13873 | TI13873 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Oil Tank Conditioned Compartment Temperature Indicating Transmitter | F13LU423 Lube Cond. Comp | 1 | -5 | 100 | °C |  |  |  | 34 | 5 |  | 37 | 5 |  |  |  |  | 26.6 | 5 | 32 | 5 | 45 | 5 | 47 | 5 |  | A_LL = Trip F13-PO-446 and F13-PO-529/530/531 A_Lo = Start permissive for F13-MB-401A/B (Normal mode) and F13-PO-529/530/531 A_Hi = Start permissive F13-MB-401A/B (Normal mode) and F13-HT-531/532 A_HH = Trip F13-HT-531/532 and F13-PO-529/530/531 P_Lo = Start F13-HT-531 & 532 P_Hi = Stop F13-HT-531 & 532 2000-ME001.3-F17-50001 | B
|  |  |  | TIT13866 | TI13866 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Tank Settling Compartment Temperature Indicating Transmitter | F13LU423 Lube Set. Comp. | 1 | -5 | 100 | °C |  |  |  | 34 | 5 |  | 37 | 5 |  |  |  |  | 26.6 | 5 | 32 | 5 | 45 | 5 | 47 | 5 |  | A_LL = Trip F13-PO-527/528 A_Lo = Start permissive for F13-MB-401A/B (Normal mode) and F13-PO-527/528/534/535 A_Hi = Start permissive F13-MB-401A/B (Normal mode) and F13-HT-529/530 A_HH = Trip F13-HT-529/530 and F13-PO-527/528 P_Lo = Start F13-HT-529 & 530 P_Hi = Stop F13-HT-529 & 530 2000-ME001.3-F17-50001 | B
|  |  |  | F13LU423STSS | F13LU423_STS | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Oil Status | F13LU423 OCM Status | 1 | 0 | 3 | - | [21 empty] | SoftTag Register 30 0 = NOT READY 1 = READY 2 = TESTING 3 = WAITING Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics | 0
|  |  |  | F13LU423RHS | F13LU423_RH | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Oil %RH | F13LU423 OCM %RH | 1 | 0 | 100 | % | [21 empty] | SoftTag Register 34 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics | 0
|  |  |  | F13LU423TEMPS | F13LU423_TEMP | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Oil Temperature | F13LU423 OCM Temperature | 1 | -5 | 100 | °C | [21 empty] | SoftTag Register 33 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics | 0
|  |  |  | F13LU423_4US | F13LU423_4U | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU423 Count > 4µm | 1 | 0 | 2000000 | # | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 4 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 18/03/2025 03/06/2025 | Calculation comment deleted - unnecassary https://pastech-2955.atlassian.net/browse/KAN-1940
|  |  |  | F13LU423_6US | F13LU423_6U | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU423 Count >6µm | 1 | 0 | 2000000 | # | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 6 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 18/03/2025 03/06/2025 | Calculation comment deleted - unnecassary https://pastech-2955.atlassian.net/browse/KAN-1940
|  |  |  | F13LU423_14US | F13LU423_14U | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU423 Count >14µm | 1 | 0 | 2000000 | # | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 14 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 18/03/2025 03/06/2025 | Calculation comment deleted - unnecassary https://pastech-2955.atlassian.net/browse/KAN-1940
|  |  |  | F13LU423_21US | F13LU423_21U | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU423 Count >21µm | 1 | 0 | 2000000 | # | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 21 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 18/03/2025 03/06/2025 | Calculation comment deleted - unnecassary https://pastech-2955.atlassian.net/browse/KAN-1940
|  |  |  | F13LU423_25US | F13LU423_25U | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU423 Count >25µm | 1 | 0 | 2000000 | # | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 25 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 18/03/2025 03/06/2025 | Calculation comment deleted - unnecassary https://pastech-2955.atlassian.net/browse/KAN-1940
|  |  |  | F13LU423_38US | F13LU423_38U | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU423 Count >38µm | 1 | 0 | 2000000 | # | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 38 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 18/03/2025 03/06/2025 | Calculation comment deleted - unnecassary https://pastech-2955.atlassian.net/browse/KAN-1940
|  |  |  | F13LU423_50US | F13LU423_50U | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU423 Count >50µm | 1 | 0 | 2000000 | # | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 50 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 18/03/2025 03/06/2025 | Calculation comment deleted - unnecassary https://pastech-2955.atlassian.net/browse/KAN-1940
|  |  |  | F13LU423_70US | F13LU423_70U | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Oil Particle Counts | F13LU423 Count >70µm | 1 | 0 | 2000000 | # | [21 empty] | SoftTag Particle count (contaminants in oil) greater than 70 microns Ensure result format on OCM15 set to ISO4406:1999 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics Ranges and alarms to be confirmed during commissioning by FLS. | 1 | 18/03/2025 03/06/2025 | Calculation comment deleted - unnecassary https://pastech-2955.atlassian.net/browse/KAN-1940
|  |  |  | WE13834 | WI13834 | 2000-F13-PID-PR-10013 | F13-LU-424 Mills Ring Gear Spray System Ring Gear Spray System Container IBC Weightometer Indicating Transmitter | F13LU424 IBC Weight | 1 | 0 | 100 | % | [14 empty] | 15 | 5 | [5 empty] | A_Lo = Warning | B
|  |  |  | PIT13845 | PI13845 | 2000-F13-PID-PR-10013 | F13-LU-424 Ball Mill Ring Gear Spray System Gear Grease Supply Assembly Pressure Indicating Transmitter | F13LU424 MB Rng Spry Oil | 1 | 0 | 27579 | kPa | [14 empty] | 8273 | 5 | 11032 | 5 |  |  | SV13838 Deenergised (see OnOff Valves tab) | A_Lo = Warning A_Hi = Warning 2000-ME001.3-F17-50001 | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PIT13842 | PI13842 | 2000-F13-PID-PR-10013 | F13-LU-424 Ball Mill Ring Gear Spray System Nozzle Air Supply Assembly Pressure Indicating Transmitter | F13LU424 MB Rng Spry Air | 1 | 0 | 1034 | kPa | [14 empty] | 310 | 5 | 415 | 5 |  |  | SV13841 Deenergised (see OnOff Valves tab) | A_Lo = Warning A_Hi = Warning 2000-ME001.3-F17-50001 | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PIT13595 | PI13595 | 2000-F13-PID-PR-10013 | F13-LU-424 SAG Mill Ring Gear Spray System Gear Grease Supply Assembly Pressure Indicating Transmitter | F13LU424 MS Rng Spry Oil | 1 | 0 | 27579 | kPa | [14 empty] | 8273 | 5 | 11032 | 5 |  |  | SV13588 Deenergised (see OnOff Valves tab) | A_Lo = Warning A_Hi = Warning 2000-ME001.3-F17-50001 | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | PIT13592 | PI13592 | 2000-F13-PID-PR-10013 | F13-LU-424 SAG Mill Ring Gear Spray System Grease System Nozzle Air Supply Assembly Pressure Indicating Transmitter | F13LU424 MS Rng Spry Air | 1 | 0 | 1034 | kPa | [14 empty] | 310 | 5 | 415 | 5 |  |  | SV13591 Deenergised (see OnOff Valves tab) | A_Lo = Warning A_Hi = Warning 2000-ME001.3-F17-50001 | 1 | 2025-03-06 | PCT alignment action register (kPa units)
|  |  |  | UT00010 | TI00010 | N/A | F00-SR-001 33kV Switchroom Temperature | F00SR001 33kV SR Temp | 1 | 0 | 50 | °C | [16 empty] | 30 | 600 |  |  |  |  | 1 | 2025-04-08 | https://pastech-2955.atlassian.net/browse/KAN-1660
|  |  |  | UT13040 | TI13040 | N/A | SAG Mill 415V Switchroom Temperature | F13SR001 415V SR Temp | 1 | 0 | 50 | °C | [16 empty] | 30 | 600 |  |  |  |  | 1 | 2025-04-08 | https://pastech-2955.atlassian.net/browse/KAN-1660
|  |  |  | UT13041 | TI13041 | N/A | F13-SR-001 SAG Mill 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | F13SR001 415V SR TF | 1 | 0 | 50 | °C | [16 empty] | 30 | 600 |  |  |  |  | 1 | 2025-04-08 | https://pastech-2955.atlassian.net/browse/KAN-1660
|  |  |  | UT13042 | TI13042 | N/A | Ball Mill 415V Switchroom Temperature | F13SR002 415V SR Temp | 1 | 0 | 50 | °C | [16 empty] | 30 | 600 |  |  |  |  | 1 | 2025-04-08 | https://pastech-2955.atlassian.net/browse/KAN-1660
|  |  |  | UT13043 | TI13043 | N/A | F13-SR-002 Ball Mill 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | F13SR002 415V SR TF | 1 | 0 | 50 | °C | [16 empty] | 30 | 600 |  |  |  |  | 1 | 2025-04-08 | https://pastech-2955.atlassian.net/browse/KAN-1660
|  |  |  | UT13044 | TI13044 | N/A | F13-SR-003 SAG and Ball Mill VSD Switchroom Temperature | F13SR003 VSD SR Temp | 1 | 0 | 50 | °C | [16 empty] | 30 | 600 |  |  |  |  | 1 | 2025-04-08 | https://pastech-2955.atlassian.net/browse/KAN-1660 |  |  |  |  | Need to test alarm (10min delay) rest all good PH-24/05
|  |  |  | UT13045 | TI13045 | N/A | F13-SR-004 Recycle Crushing 415V Switchroom Temperature | F13SR004 415V SR Temp | 1 | 0 | 50 | °C | [16 empty] | 30 | 600 |  |  |  |  | 1 | 2025-04-08 | https://pastech-2955.atlassian.net/browse/KAN-1660
|  |  |  | UT13046 | TI13046 | N/A | F13-SR-004 Recycle Crushing 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | F13SR004 415V SR TF | 1 | 0 | 50 | °C | [16 empty] | 30 | 600 |  |  |  |  | 1 | 2025-04-08 | https://pastech-2955.atlassian.net/browse/KAN-1660
|  |  |  | UT13047 | TI13047 | N/A | F13-SR-005 Mill Chillers & Reagents 415V Switchroom Temperature | F13SR005 415V SR Temp | 1 | 0 | 50 | °C | [16 empty] | 30 | 600 |  |  |  |  | 1 | 2025-04-08 | https://pastech-2955.atlassian.net/browse/KAN-1660
|  |  |  | UT13048 | TI13048 | N/A | F13-SR-005 Mill Chillers & Reagents 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | F13SR005 415V SR Temp TF | 1 | 0 | 50 | °C | [16 empty] | 30 | 600 |  |  |  |  | 1 | 2025-04-08 | https://pastech-2955.atlassian.net/browse/KAN-1660
|  |  |  | PIT13535 | PI13535 | 2000-F13-PID-PR-10002 | F13-HU-407 Cyclone Feed Pump Suction Valve HPU Pressure Indicating Transmitter | F13HU407 Hyd Supply | 1 | 0 | 50000 | kPa | [16 empty] | 15000 | 5 | 16000 | 5 |  |  | 2 | 6/03/2025 2/07/2025 | PCT alignment action register (kPa units) CR-021
|  |  |  | TIT13536 | TI13536 | 2000-F13-PID-PR-10002 | F13-HU-407 Cyclone Feed Pump Suction Valve HPU Temperature Indicating Transmitter | F13HU407 Hyd Reservoir | 1 | 0 | 100 | °C | [16 empty] | 65 | 5 | 70 | 5 |  |  | 1 | 2025-07-02 | CR-021
|  |  |  | LIT13537 | LI13537 | 2000-F13-PID-PR-10002 | F13-HU-407 Cyclone Feed Pump Suction Valve HPU Level Indicating Transmitter | F13HU407 Hyd Reservoir | 1 | 0 | 100 | % | [12 empty] | 50 | 5 | 60 | 5 | [6 empty] | 1 | 2025-07-02 | CR-021
|  |  |  | F13CV403TEMPS | F13CV403TEMP | 2000-F13-PID-PR-10001 | F13-CV-403 SAG MILL FEED CONVEYOR BELT RIP AMBIENT TEMPERATURE | F13CV403 Ambient Temp | 1 | -5 | 50 | °C | [21 empty] | SoftTag Display on level 4 graphic Variation NOFD153 | 1 | 2025-05-28 | Variation NOFD153
|  |  |  | F13CV403MFLOS | F13CV403MFLO | 2000-F13-PID-PR-10001 | F13-CV-403 SAG MILL FEED CONVEYOR BELT RIP MASS FLOW | F13CV403 Mass Flow | 1 | 0 | 100 | % | [21 empty] | SoftTag Display on level 4 graphic Variation NOFD153 | 1 | 2025-05-28 | Variation NOFD153
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 427 | 426

## 2. Analogue Output
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - MILLING & CLASSIFICATION (F13)
2000-F13-LST-PR-10001
ANALOGUE INSTRUMENTS (AO)
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  |  |  | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | Comments | Rev | OK | Date | OK | Date
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 0 | 0

## 3. Digital Input
KCGM GROWTH PROJECT
|  |  | PROCESS CONTROL TABLES - MILLING & CLASSIFICATION (F13) |  |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)*
2000-F13-LST-PR-10001
DIGITAL INSTRUMENTS (DI)
[18 empty] | C1 Sign Off |  | C2 Sign Off |  | C1 Comments
Area | Type | Loop No. | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Source | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | Change Date | Change Reference | OK | Date | OK | Date
|  |  | F00BC001FL2 | F00BC001_FL2 | N/A | F00-BC-001 48VDC Charger Common Alarm | F00BC001 48VDCChargeCom | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F00BC001FL3 | F00BC001_FL3 | N/A | F00-BC-001 48VDC Charger Earth Fault | F00BC001 48VDCChrgeEarth | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F00BC001FL1 | F00BC001_FL1 | N/A | F00-BC-001 48VDC Charger Mains Fail | F00BC001 48VDCChargeMain | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F00FIP001ALM | F00FIP001_ALM | N/A | F00-FIP-001 Alarm | F00-FIP-001 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-20 | MOC103
|  |  | F00FIP001FLT | F00FIP001_FLT | N/A | F00-FIP-001 Fault | F00-FIP-001 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F00FIP001ISL | F00FIP001_ISL | N/A | F00-FIP-001 Isolated | F00-FIP-001 Isolated | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-20 | MOC103
|  |  | F00RIO100PS1 | F00RIO100_PS1 | N/A | F00-RIO-100 PS1 24VDC HEALTHY | F00RIO100 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F00RIO100PS2 | F00RIO100_PS2 | N/A | F00-RIO-100 PS2 24VDC HEALTHY | F00RIO100 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F00SR001ESTP | F00SR001_ESTP | N/A | F00-SR-001 SWITCHROOM EMERGENCY SHUTDOWN DCS INPUT | F00SR001 SR ESHUT DCS IN | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | SW10BT1SW1OP | SW10BT1SW1_O | N/A | F00-SW-010 Bus-Tie 1 3-Position Switch 1 Open Status | F00SW010 BT1 3PosSw1Open | N_Open | Open |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT1SW2OP | SW10BT1SW2_O | N/A | F00-SW-010 Bus-Tie 1 3-Position Switch 2 Open Status | F00SW010 BT1 3PosSw2Open | N_Open | Open |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT1CBCS | SW10BT1CB_CS | N/A | F00-SW-010 Bus-Tie 1 Circuit Breaker Closed Status | F00SW010 BusTie1CB Close | N_Closed | Closed |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT1CBOS | SW10BT1CB_OS | N/A | F00-SW-010 Bus-Tie 1 Circuit Breaker Open Status | F00SW010 BusTie1 CB Open | N_Open | Open |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT1DS1CL | SW10BT1DS1_C | N/A | F00-SW-010 Bus-Tie 1 Disconnector Switch 1 Closed Status | F00SW010 BT1DiscSw1Close | N_Closed | Closed |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT1DS2CL | SW10BT1DS2_C | N/A | F00-SW-010 Bus-Tie 1 Disconnector Switch 2 Closed Status | F00SW010 BT1DiscSw2Close | N_Closed | Closed |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT1ES1CL | SW10BT1ES1_C | N/A | F00-SW-010 Bus-Tie 1 Earth Switch 1 Closed Status | F00SW010 BT1EarthSw1Clse | N_Closed | Closed |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT1ES2CL | SW10BT1ES2_C | N/A | F00-SW-010 Bus-Tie 1 Earth Switch 2 Closed Status | F00SW010 BT1EarthSw2Clse | N_Closed | Closed |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT2SW1OP | SW10BT2SW1_O | N/A | F00-SW-010 Bus-Tie 2 3-Position Switch 1 Open Status | F00SW010 BT2 3PosSw1Open | N_Open | Open |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT2SW2OP | SW10BT2SW2_O | N/A | F00-SW-010 Bus-Tie 2 3-Position Switch 2 Open Status | F00SW010 BT2 3PosSw2Open | N_Open | Open |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT2CBCS | SW10BT2CB_CS | N/A | F00-SW-010 Bus-Tie 2 Circuit Breaker Closed Status | F00SW010 BusTie1CB Close | N_Closed | Closed |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT2CBOS | SW10BT2CB_OS | N/A | F00-SW-010 Bus-Tie 2 Circuit Breaker Open Status | F00SW010 BusTie1 CB Open | N_Open | Open |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT2DS1CL | SW10BT2DS1_C | N/A | F00-SW-010 Bus-Tie 2 Disconnector Switch 1 Closed Status | F00SW010 BT2DiscSw1Close | N_Closed | Closed |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT2DS2CL | SW10BT2DS2_C | N/A | F00-SW-010 Bus-Tie 2 Disconnector Switch 2 Closed Status | F00SW010 BT2DiscSw2Close | N_Closed | Closed |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT2ES1CL | SW10BT2ES1_C | N/A | F00-SW-010 Bus-Tie 2 Earth Switch 1 Closed Status | F00SW010 BT2EarthSw1Clse | N_Closed | Closed |  | Hardwired to DCS | - |  |  | 0
|  |  | SW10BT2ES2CL | SW10BT2ES2_C | N/A | F00-SW-010 Bus-Tie 2 Earth Switch 2 Closed Status | F00SW010 BT2EarthSw2Clse | N_Closed | Closed |  | Hardwired to DCS | - |  |  | 0
|  |  | ZS13035 | ZI13035 | 2000-F13-PID-PR-10001 | F13-BLC-401 SAG Mill Ball Charger Ball Counting Proximity Switch | F13BLC401 Index | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | ZSC13038 | ZIC13038 | 2000-F13-PID-PR-10001 | F13-BLC-401 SAG Mill Ball Charger Isolation Gate Position Position Switch Closed | F13BLC401 IsolationClose | Active (Closed) | N_Active (N_Closed) |  | Hardwired to DCS | - |  |  | B
|  |  | ZSO13038 | ZIO13038 | 2000-F13-PID-PR-10001 | F13-BLC-401 SAG Mill Ball Charger Isolation Gate Position Position Switch Opened | F13BLC401 Isolation Open | Active (Open) | N_Active (N_Open) |  | Hardwired to DCS | - |  |  | B
|  |  | HS13179A | HS13179ASTT | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Auto Start Push Button | F13BLC402 Auto Start | N_Active | Active (Start) |  | Hardwired to DCS | - |  | Vendor Reference: AUTO_START S2 Auto Start N/O push button on LCP to start auto ball loading. Refer to 2000-ME057-M01-10001 Activates F13BLC402_SEQ_EN (Misc tab) in auto mode (HS13140AAUT) only | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | ZS13229A | ZI13229A | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Dump Position Signal | F13BLC402 Dump Position | N_Active | Active |  | Hardwired to DCS | - |  | F13-CH-442 Position Reduce to 1 second debounce | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | XS13206C | XI13206C | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Earth Fault Signal | F13BLC402 Earth Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  | Vendor Reference: EARTH_FLT Earth Leak Detect Open on Fault. The Bender relay will open its ELD-K1 contact on fault as an advisory to the DCS. | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | XS13206A | XI13206A | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Emergency Stop Contact Signal | F13BLC402 E-Stop | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  | Vendor Reference: E_STOP LOS01 ESTOP ADVISORY CONTACT N/C emergency stop push button shuts down power to magnet and hoist/trolley system | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | HS13144B | HS13144BFST | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Fast Switch | F13CR453 Fast | N_Active | Active (Fast) |  | Hardwired to DCS | - |  | Vendor Reference: TRO_FST PB used for Manual mode only, L_MANUAL (HS13140BMAN) = Active (see Digital Output tab) | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | HS13203B | HS13203BDN | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Hoist Down Push Button | F13CR453H Hoist Down | N_Active | Active (Down) |  | Hardwired to DCS | - |  | Vendor Reference: HST_DWN S7 Hoist Down N/O hoist down push button on LCP will lower hoist when signal is high via output XC13280B PB used for Manual mode only, L_MANUAL (HS13140BMAN) = Active (see Digital Output tab) | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | HS13203A | HS13203AUP | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Hoist Up Push Button | F13CR453H Hoist Up | N_Active | Active (Up) |  | Hardwired to DCS | - |  | Vendor Reference: HST_UP S6 Hoist Up N/O hoist up push button on LCP will raise hoist when signal is active via output XC13280A PB used for Manual mode only, L_MANUAL (HS13140BMAN) = Active (see Digital Output tab) | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | ZS13229B | ZI13229B | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Lift Position Signal | F13BLC402 Lift Position | N_Active | Active |  | Hardwired to DCS | - |  | F13-BN-404 Position Reduce to 1 second debounce | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | HS13140B | HS13140BMAN | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Local - Manual Switch | F13BLC402 Local Manual | N_Active | Active (Manual) |  | Hardwired to DCS | - |  | Vendor Reference: L_MANUAL S1 Selector switch Pos 3 Local Manual mode Allows for manual controls via LCP (see HS13189AFWD, HS13189BREV, HS13203AUP, HS13203BDN, HS13144ASLW and HS13144BFST in Digital Input tab). | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | ZS13226A | ZI13226A | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Maintenance Position 1 Signal | F13BLC402 Maint. Pos 1 | N_Active | Active |  | Hardwired to DCS | - |  | Maintenance position south Reduce to 1 second debounce | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | ZS13226B | ZI13226B | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Maintenance Position 2 Signal | F13BLC402 Maint. Pos 2 | N_Active | Active |  | Hardwired to DCS | - |  | Maintenance position north Reduce to 1 second debounce | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | XS13206B | XI13206B | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger MCB Tripped Signal | F13BLC402 MCB Trip | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  | Vendor Reference: MAG_FLT MCB Trip Open on Fault Auxiliary NO contact for Trans CB, Lift AC CB, Dump AC CB or Lift DC CB | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only | [5 empty] | MSH 15/08/26: MCB is actually NC, logic in 13BLC402LC1 inverted to enable trolly operation
|  |  | HS13140A | HS13140AAUT | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Remote - Auto Switch | F13BLC402 Auto | N_Active | Active (Auto) |  | Hardwired to DCS | - |  | Vendor Reference: R_AUTO S1 Selector switch Pos 2 Local/Remote Auto mode. Allows for Auto-Start remotely or locally (see F13BLC402_SEQ_EN in Misc tab). | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | HS13144A | HS13144ASLW | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Slow Switch | F13CR453T Slow | N_Active | Active (Slow) |  | Hardwired to DCS | - |  | PB used for Manual mode only, L_MANUAL (HS13140BMAN) = Active (see Digital Output tab) | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | HS13179B | HS13179BSTP | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Stop Push Button | F13BLC402 Stop | N_Active | Active (Stop) |  | Hardwired to DCS | - |  | Vendor Reference: STOP S3 Stop N/O push button on LCP to stop the auto ball loading sequence at the end of the current cycle. Refer to 2000-ME057-M01-10001 Deactivates/unlatches F13BLC402_SEQ_EN (Misc tab) in any mode (Auto, Local Manual) | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | HS13189A | HS13189AFWD | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Trolley Forward Push Button | F13CR453T Trolley Fwd | N_Active | Active (Forward) |  | Hardwired to DCS | - |  | Vendor Reference: TRO_FWD S4 Normal Press. Trolley Forward N/O local push button on LCP drives trolley forward towards when signal is high via output XC13251A PB used for Manual mode only, L_MANUAL (HS13140BMAN) = Active (see Digital Output tab) | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | HS13189B | HS13189BREV | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Trolley Reverse Push Button | F13CR453T Trolley Rev | N_Active | Active (Reverse) |  | Hardwired to DCS | - |  | Vendor Reference: TRO_REV S5 Normal Press. Trolley Reverse N/O local push button on LCP drives trolley in reverse towards south when signal is high via output XC13251B PB used for Manual mode only, L_MANUAL (HS13140BMAN) = Active (see Digital Output tab) | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC by vendor comment removed only
|  |  | ZS13252A | ZA13252A | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Bowl Adjustment 1 Limit Switch | F13CC401 Bowl Adj. 1 | N_Active | Active |  | Hardwired to DCS | - |  | Refer F13CC401_DUP and F13CC401_DIR_DOWN in Misc tab for details | B
|  |  | ZS13252B | ZA13252B | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Bowl Adjustment 2 Limit Switch | F13CC401 Bowl Adj. 2 | N_Active | Active |  | Hardwired to DCS | - |  | Refer F13CC401_DUP and F13CC401_DIR_DOWN in Misc tab for details | B
|  |  | ZS13312A | ZA13312A | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Bowl Adjustment 1 Limit Switch | F13CC402 Bowl Adj. 1 | N_Active | Active |  | Hardwired to DCS | - |  | Refer F13CC402_DUP and F13CC402_DIR_DOWN in Misc tab for details | B
|  |  | ZS13312B | ZA13312B | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Bowl Adjustment 2 Limit Switch | F13CC402 Bowl Adj. 2 | N_Active | Active |  | Hardwired to DCS | - |  | n | B
|  |  | LSH13011 | LAH13011 | 2000-F13-PID-PR-10001 | F13-CH-422 Crushed Ore Reclaim Feeder 1 Discharge Chute Blocked Chute Receive | F13CH422 Blocked Chute | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | LSH13021 | LAH13021 | 2000-F13-PID-PR-10001 | F13-CH-425 Coarse Ore Reclaim Feeder 2 Discharge Chute Blocked Chute Receive | F13CH425 Blocked Chute | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | LSH13058 | LAH13058 | 2000-F13-PID-PR-10003 | F13-CH-430 SAG Mill Feed Conveyor Head Chute Blocked Chute Receive | F13CH430 Blocked Chute | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  |  | LAHH13073 | 2000-F13-PID-PR-10002 | F13-CH-433 SAG Mill Discharge Screen Oversize Chute Blocked Chute Switch | F13CH433 Blocked Chute | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | LSH13031 | LAH13031 | 2000-F13-PID-PR-10001 | F13-CH-440 Emergency Feeder Discharge Chute Blocked Chute Receive | F13CH440 Blocked Chute | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | LSH13171 | LAH13171 | 2000-F13-PID-PR-10005 | F13-CH-452 Recycle Conveyor 1 Head Chute Blocked Chute Receive | F13CH452 Blocked Chute | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | LSH13198 | LAH13198 | 2000-F13-PID-PR-10005 | F13-CH-455 Recycle Conveyor 2 Head Chute Blocked Chute Receive | F13CH455 Blocked Chute | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | LSH13356 | LAH13356 | 2000-F13-PID-PR-10006 | F13-CH-463 Recycle Crusher Discharge Conveyor Head Chute Blocked Chute Receive | F13CH463 Blocked Chute | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | XS13470C | XA13470C | 2000-F13-PID-PR-10012 | F13-CU-402 Chiller 1 Alarm Relay | F13CU402 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Ref: 2000-ME034-M01-10002 | 0 |  | 11/05/2026 - AP : chiller NO contact
|  |  | ZSC13442 | ZIC13442 | 2000-F13-PID-PR-10012 | F13-CU-402 Chiller 1 Discharge Valve Position Switch Closed | F13CU402 Discharge Close | N_Closed | Closed |  | Hardwired to DCS | - |  | HV13442 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | ZSO13442 | ZIO13442 | 2000-F13-PID-PR-10012 | F13-CU-402 Chiller 1 Discharge Valve Position Switch Opened | F13CU402 Discharge Open | N_Open | Open |  | Hardwired to DCS | - |  | HV13442 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | XS13470B | XI13470B | 2000-F13-PID-PR-10012 | F13-CU-402 Chiller 1 Ready Status Relay | F13CU402 Ready | N_Active | Active |  | Hardwired to DCS | - |  | Ref: 2000-ME034-M01-10002 | B
|  |  | XS13470A | XI13470A | 2000-F13-PID-PR-10012 | F13-CU-402 Chiller 1 Run Status Relay | F13CU402 Running | N_Running | Running |  | Hardwired to DCS | - |  | Ref: 2000-ME034-M01-10002 | B
|  |  | XS13471C | XA13471C | 2000-F13-PID-PR-10012 | F13-CU-403 Chiller 2 Alarm Relay | F13CU403 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Ref: 2000-ME034-M01-10002 | 0
|  |  | ZSC13444 | ZIC13444 | 2000-F13-PID-PR-10012 | F13-CU-403 Chiller 2 Discharge Valve Position Switch Closed | F13CU403 Discharge Close | N_Closed | Closed |  | Hardwired to DCS | - |  | HV13444 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | ZSO13444 | ZIO13444 | 2000-F13-PID-PR-10012 | F13-CU-403 Chiller 2 Discharge Valve Position Switch Opened | F13CU403 Discharge Open | N_Open | Open |  | Hardwired to DCS | - |  | HV13444 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | XS13471B | XI13471B | 2000-F13-PID-PR-10012 | F13-CU-403 Chiller 2 Ready Status Relay | F13CU403 Ready | N_Active | Active |  | Hardwired to DCS | - |  | Ref: 2000-ME034-M01-10002 | B
|  |  | XS13471A | XI13471A | 2000-F13-PID-PR-10012 | F13-CU-403 Chiller 2 Run Status Relay | F13CU403 Running | N_Running | Running |  | Hardwired to DCS | - |  | Ref: 2000-ME034-M01-10002 | B
|  |  | XS13472C | XA13472C | 2000-F13-PID-PR-10012 | F13-CU-404 Chiller 3 Alarm Relay | F13CU404 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Ref: 2000-ME034-M01-10002 | 0
|  |  | ZSC13446 | ZIC13446 | 2000-F13-PID-PR-10012 | F13-CU-404 Chiller 3 Discharge Valve Position Switch Closed | F13CU404 Discharge Close | N_Closed | Closed |  | Hardwired to DCS | - |  | HV13446 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | ZSO13446 | ZIO13446 | 2000-F13-PID-PR-10012 | F13-CU-404 Chiller 3 Discharge Valve Position Switch Opened | F13CU404 Discharge Open | N_Open | Open |  | Hardwired to DCS | - |  | HV13446 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | XS13472B | XI13472B | 2000-F13-PID-PR-10012 | F13-CU-404 Chiller 3 Ready Status Relay | F13CU404 Ready | N_Active | Active |  | Hardwired to DCS | - |  | Ref: 2000-ME034-M01-10002 | B
|  |  | XS13472A | XI13472A | 2000-F13-PID-PR-10012 | F13-CU-404 Chiller 3 Run Status Relay | F13CU404 Running | N_Running | Running |  | Hardwired to DCS | - |  | Ref: 2000-ME034-M01-10002 | B
|  |  | XS13473C | XA13473C | 2000-F13-PID-PR-10012 | F13-CU-405 Chiller 4 Alarm Relay | F13CU405 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Ref: 2000-ME034-M01-10002 | 0
|  |  | ZSC13448 | ZIC13448 | 2000-F13-PID-PR-10012 | F13-CU-405 Chiller 4 Discharge Valve Position Switch Closed | F13CU405 Discharge Close | N_Closed | Closed |  | Hardwired to DCS | - |  | HV13448 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | ZSO13448 | ZIO13448 | 2000-F13-PID-PR-10012 | F13-CU-405 Chiller 4 Discharge Valve Position Switch Opened | F13CU405 Discharge Open | N_Open | Open |  | Hardwired to DCS | - |  | HV13448 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | XS13473B | XI13473B | 2000-F13-PID-PR-10012 | F13-CU-405 Chiller 4 Ready Status Relay | F13CU405 Ready | N_Active | Active |  | Hardwired to DCS | - |  | Ref: 2000-ME034-M01-10002 | B
|  |  | XS13473A | XI13473A | 2000-F13-PID-PR-10012 | F13-CU-405 Chiller 4 Run Status Relay | F13CU405 Running | N_Running | Running |  | Hardwired to DCS | - |  | Ref: 2000-ME034-M01-10002 | B
|  |  | BRS13054 | BRA13054 | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Belt Rip Switch | F13CV403 Belt Rip | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | F13CV403BRS1 | F13CV403_BRS1 | 2000-F13-PID-PR-10001 | F13-CV-403 SAG MILL FEED CONVEYOR BELT RIP SWITCH ANOMALY DETECTED | F13CV403 BRS Anomaly | Inactive | Active |  | SoftTag |  |  | Variation NOFD153 Display on level 4 graphic | 1 | 2025-05-28 | Variation NOFD153
|  |  | F13CV403BRS2 | F13CV403_BRS2 | 2000-F13-PID-PR-10001 | F13-CV-403 SAG MILL FEED CONVEYOR BELT RIP SWITCH BELT RIP INDICATION | F13CV403 BRS Rip | Inactive | Active |  | SoftTag |  |  | Variation NOFD153 Display on level 4 graphic | 1 | 2025-05-28 | Variation NOFD153
|  |  | F13CV403BRS3 | F13CV403_BRS3 | 2000-F13-PID-PR-10001 | F13-CV-403 SAG MILL FEED CONVEYOR BELT RIP SWITCH BELT RUNNING STATUS | F13CV403 BRS Running | Inactive | Active |  | SoftTag |  |  | Variation NOFD153 Display on level 4 graphic | 1 | 2025-05-28 | Variation NOFD153
|  |  | F13CV403ALM3 | XA13000C | 2000-F13-PID-PR-10001 | F13-CV-403 SAG MILL FEED CONVEYOR BELT RIP SWITCH CRITICAL ALARM | F13CV403 BRS Critical | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | Variation NOFD153 Display on level 3 & 4 graphic | 1 | 2025-05-28 | Variation NOFD153
|  |  | F13CV403ALM2 | XA13000B | 2000-F13-PID-PR-10001 | F13-CV-403 SAG MILL FEED CONVEYOR BELT RIP SWITCH FAULT ALARM | F13CV403 BRS Fault | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | Variation NOFD153 Display on level 3 & 4 graphic | 1 | 2025-05-28 | Variation NOFD153
|  |  | F13CV403BRS4 | F13CV403_BRS4 | 2000-F13-PID-PR-10001 | F13-CV-403 SAG MILL FEED CONVEYOR BELT RIP SWITCH MOTOR STATUS | F13CV403 BRS Motor Sts | Inactive | Active |  | SoftTag |  |  | Variation NOFD153 Display on level 4 graphic | 1 | 2025-05-28 | Variation NOFD153
|  |  | F13CV403BRS5 | F13CV403_BRS5 | 2000-F13-PID-PR-10001 | F13-CV-403 SAG MILL FEED CONVEYOR BELT RIP SWITCH NETWORK ANALYSIS STATUS | F13CV403 BRS Network Sts | Inactive | Active |  | SoftTag |  |  | Variation NOFD153 Display on level 4 graphic | 1 | 2025-05-28 | Variation NOFD153
|  |  | F13CV403ALM1 | XA13000A | 2000-F13-PID-PR-10001 | F13-CV-403 SAG MILL FEED CONVEYOR BELT RIP SWITCH STATUS ALARM | F13CV403 BRS Status | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | Variation NOFD153 Display on level 4 graphic | 1 | 2025-05-28 | Variation NOFD153
|  |  | ZE13052 | SAL13052 | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Drive Motor Speed Encoder | F13CV403 FE Underspeed | Normal | Alarm | Alarm | SoftTag | 3 | 1. F13-CV-403 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-403 start-up | Alarm masking duration to be confirmed during commissioning. Wired to VSD | 1 | 2025-03-06 | [KAN-1469] Soft Tag VSD Underspeeds - Jira |  |  |  |  | MOC563 Comments - remove underspeed soft tags from DCS.
|  |  | BDS13053F | BDA13053F | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Front Quarter Belt Drift Switch LHS | F13CV403 FQ Drift LHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-403 Not Running |  | B
|  |  | BDS13053E | BDA13053E | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Front Quarter Belt Drift Switch RHS | F13CV403 FQ Drift RHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-403 Not Running |  | B
|  |  | BDS13053H | BDA13053H | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Head End Belt Drift Switch LHS | F13CV403 HE Drift LHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-403 Not Running |  | B
|  |  | BDS13053G | BDA13053G | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Head End Belt Drift Switch RHS | F13CV403 HE Drift RHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-403 Not Running |  | B
|  |  | PWS13050B | PWA13050B | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Pull-Wire Switch 1 LHS | F13CV403 Pullwire1 LHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | PWS13050A | PWA13050A | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Pull-Wire Switch 1 RHS | F13CV403 Pullwire1 RHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | PWS13050D | PWA13050D | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Pull-Wire Switch 2 LHS | F13CV403 Pullwire2 LHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | PWS13050C | PWA13050C | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Pull-Wire Switch 2 RHS | F13CV403 Pullwire2 RHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | PWS13050F | PWA13050F | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Pull-Wire Switch 3 LHS | F13CV403 Pullwire3 LHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | PWS13050H | PWA13050H | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Pull-Wire Switch 3 LHS | F13CV403 Pullwire4 LHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | 2 | 2026-01-31 | CR-065, MOC-237
|  |  | PWS13050E | PWA13050E | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Pull-Wire Switch 3 RHS | F13CV403 Pullwire3 RHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | PWS13050G | PWA13050G | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Pull-Wire Switch 3 RHS | F13CV403 Pullwire4 RHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | 2 | 2026-01-31 | CR-065, MOC-237
|  |  | BDS13053D | BDA13053D | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Rear Quarter Belt Drift Switch LHS | F13CV403 RQ Drift LHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-403 Not Running |  | B
|  |  | BDS13053C | BDA13053C | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Rear Quarter Belt Drift Switch RHS | F13CV403 RQ Drift RHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-403 Not Running |  | B
|  |  | YI13059CS | YI13059C | 2000-F13-PID-PR-10001 | F13CV403 SAG Mill Feed Conveyor Rock Ore Camera | F13CAM101 Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From PVX Camera OPC Server. | 0
|  |  | BDS13053B | BDA13053B | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Tail End Belt Drift Switch LHS | F13CV403 TE Drift LHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-403 Not Running |  | B
|  |  | BDS13053A | BDA13053A | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Tail End Belt Drift Switch RHS | F13CV403 TE Drift RHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-403 Not Running |  | B
|  |  | SSL13051 | SAL13051 | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Tail End Underspeed Switch | F13CV403 TE Underspeed | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-CV-403 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-403 start-up | Speed monitoring from instrument (signal active when underspeed) Alarm masking duration to be confirmed during commissioning. | B
|  |  | ZS13057B | ZSA13057B | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Take-Up Lower Limit Limit Switch | F13CV403 TakeUp RHS | Normal | Alarm | Alarm | Hardwired to DCS | 3 | F13-CV-403 Not Running |  | B | 2026-05-11 | MOC-459 - AP
|  |  | ZS13057A | ZSA13057A | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Take-Up Upper Limit Limit Switch | F13CV403 TakeUp LHS | Normal | Alarm | Alarm | Hardwired to DCS | 3 | F13-CV-403 Not Running |  | B | 2026-05-11 | MOC-459 - AP
|  |  | BRS13169 | BRA13169 | 2000-F13-PID-PR-10005 | F13-CV-404 Recycle Conveyor 1 Belt Rip Switch | F13CV404 Belt Rip | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | ZE13167 | SAL13167 | 2000-F13-PID-PR-10005 | F13-CV-404 Recycle Conveyor 1 Drive Motor Speed Encoder | F13CV404 Underspeed 2 | Normal | Alarm | Alarm | SoftTag | 3 | 1. F13-CV-404 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-404 start-up | Alarm masking duration to be confirmed during commissioning. Wired to VSD | 1 | 2025-03-06 | [KAN-1469] Soft Tag VSD Underspeeds - Jira |  |  |  |  | MOC563 Comments - remove underspeed soft tags from DCS.
|  |  | BDS13168B | BDA13168B | 2000-F13-PID-PR-10005 | F13-CV-404 Recycle Conveyor 1 Head End Belt Drift Switch LHS | F13CV404 HE Drift LHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-404 Not Running |  | B
|  |  | BDS13168A | BDA13168A | 2000-F13-PID-PR-10005 | F13-CV-404 Recycle Conveyor 1 Head End Belt Drift Switch RHS | F13CV404 HE Drift RHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-404 Not Running |  | B
|  |  | PWS13165B | PWA13165B | 2000-F13-PID-PR-10005 | F13-CV-404 Recycle Conveyor 1 Pull-Wire Switch LHS | F13CV404 Pullwire LHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | PWS13165A | PWA13165A | 2000-F13-PID-PR-10005 | F13-CV-404 Recycle Conveyor 1 Pull-Wire Switch RHS | F13CV404 Pullwire RHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | SSL13166 | SAL13166 | 2000-F13-PID-PR-10005 | F13-CV-404 Recycle Conveyor 1 Tail End Underspeed Switch | F13CV404 Underspeed 1 | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-CV-404 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-404 start-up | Speed monitoring from instrument (signal active when underspeed) Alarm masking duration to be confirmed during commissioning. | B
|  |  | BRS13194 | BRA13194 | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Belt Rip Switch | F13CV405 Belt Rip | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | ZE13192 | SAL13192 | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Drive Motor Speed Encoder | F13CV405 DE Underspeed | Normal | Alarm | Alarm | SoftTag | 3 | 1. F13-CV-405 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-405 start-up | Alarm masking duration to be confirmed during commissioning. Wired to VSD | 1 | 2025-03-06 | [KAN-1469] Soft Tag VSD Underspeeds - Jira |  |  |  |  | MOC563 Comments - remove underspeed soft tags from DCS.
|  |  | BDS13193F | BDA13193F | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Head End Belt Drift Switch LHS | r | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-405 Not Running |  | B
|  |  | BDS13193E | BDA13193E | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Head End Belt Drift Switch RHS | F13CV405 HE Drift RHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-405 Not Running |  | B
|  |  | BDS13193D | BDA13193D | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Mid End Belt Drift Switch LHS | F13CV405 ME Drift LHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-405 Not Running |  | B
|  |  | BDS13193C | BDA13193C | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Mid End Belt Drift Switch RHS | F13CV405 ME Drift RHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-405 Not Running |  | B
|  |  | PWS13190B | PWA13190B | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Pull-Wire Switch 1 LHS | F13CV405 Pullwire1 LHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | PWS13190A | PWA13190A | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Pull-Wire Switch 1 RHS | F13CV405 Pullwire1 RHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | PWS13190D | PWA13190D | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Pull-Wire Switch 2 LHS | F13CV405 Pullwire2 LHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | PWS13190C | PWA13190C | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Pull-Wire Switch 2 RHS | F13CV405 Pullwire2 RHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | BDS13193B | BDA13193B | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Tail End Belt Drift Switch LHS | F13CV405 TE Drift LHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-405 Not Running |  | B
|  |  | BDS13193A | BDA13193A | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Tail End Belt Drift Switch RHS | F13CV405 TE Drift RHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-405 Not Running |  | B
|  |  | SSL13191 | SAL13191 | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Tail Pulley Underspeed Switch | F13CV405 TE Underspeed | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-CV-405 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-405 start-up | Speed monitoring from instrument (signal active when underspeed) Activate alarm on underspeed. Alarm masking duration to be confirmed during commissioning. | B
|  |  | ZS13197B | ZSA13197B | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Take-Up Lower Limit Limit Switch | F13CV405 TakeUp RHS | Normal | Alarm | Alarm | Hardwired to DCS | 3 | F13-CV-405 Not Running |  | B | 2026-05-11 | MOC-459 - AP |  |  |  |  | Removed inversion, NO contacts - AP 11/05/2026
|  |  | ZS13197A | ZSA13197A | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Take-Up Upper Limit Limit Switch | F13CV405 TakeUp LHS | Normal | Alarm | Alarm | Hardwired to DCS | 3 | F13-CV-405 Not Running |  | B | 2026-05-11 | MOC-459 - AP |  |  |  |  | Removed inversion, NO contacts - AP 11/05/2026
|  |  | BRS13354 | BRA13354 | 2000-F13-PID-PR-10006 | F13-CV-406 Recycle Crusher Discharge Conveyor Belt Rip Switch | F13CV406 Belt Rip | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | ZE13352 | SAL13352 | 2000-F13-PID-PR-10006 | F13-CV-406 Recycle Crusher Discharge Conveyor Drive Motor Speed Encoder | F13CV406 Underspeed | Normal | Alarm | Alarm | SoftTag | 3 | 1. F13-CV-406 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-406 start-up | Alarm masking duration to be confirmed during commissioning. Wired to VSD | 1 | 2025-03-06 | [KAN-1469] Soft Tag VSD Underspeeds - Jira |  |  |  |  | MOC563 Comments - remove underspeed soft tags from DCS.
|  |  | BDS13353B | BDA13353B | 2000-F13-PID-PR-10006 | F13-CV-406 Recycle Crusher Discharge Conveyor Head End Belt Drift Switch LHS | F13CV406 Drift LHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-406 Not Running |  | B | [6 empty] | tested input back to DCS. Drive not ready for alarm test.
|  |  | BDS13353A | BDA13353A | 2000-F13-PID-PR-10006 | F13-CV-406 Recycle Crusher Discharge Conveyor Head End Belt Drift Switch RHS | F13CV406 Drift RHS | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-CV-406 Not Running |  | B | [6 empty] | tested input back to DCS. Drive not ready for alarm test. This instrument is broken on the field
|  |  | PWS13350B | PWA13350B | 2000-F13-PID-PR-10006 | F13-CV-406 Recycle Crusher Discharge Conveyor Pull-Wire Switch LHS | F13CV406 Pullwire LHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-04-12 | MOC-237. Alarm state must be set when signal is INACTIVE
|  |  | PWS13350A | PWA13350A | 2000-F13-PID-PR-10006 | F13-CV-406 Recycle Crusher Discharge Conveyor Pull-Wire Switch RHS | F13CV406 Pullwire RHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-04-12 | MOC-237. Alarm state must be set when signal is INACTIVE
|  |  | SSL13351 | SAL13351 | 2000-F13-PID-PR-10006 | F13-CV-406 Recycle Crusher Discharge Conveyor Underspeed Switch | F13CV406 Underspeed | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-CV-406 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-406 start-up | Speed monitoring from instrument (signal active when underspeed) Alarm masking duration to be confirmed during commissioning. | B | [6 empty] | Unable to test the alarm due to Alarm Masking condition where 13CV406 must be running.
|  |  | XS13078 | XA13078 | 2000-F13-PID-PR-10001 | F13-DC-402 Reclaim Tunnel Dust Collector Controller Alarm | F13DC402 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  | Dwyer Dust Collector controller alarm Refer to 2000-ME012-F16-10001 | B
|  |  | SSL13070 | SAL13070 | 2000-F13-PID-PR-10001 | F13-DC-402 Reclaim Tunnel Dust Collector Rotary Valve Underspeed Switch | F13DC402 Rotary Vlv U/S | Inactive | Active | Alarm (see Comments) | Hardwired to DCS | 3 | 1. F13-VR-402 Not Running 2. Mask for 10 seconds (TBC) on F23-VR-402 start-up | Speed monitoring from DCS (signal active per rotation) Alarm to activate on underspeed. Setpoint TBC during commissioning - set to 5RPM initially. Alarm masking duration to be confirmed during commissioning. | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390 |  |  |  |  | I think SSL13070 is overestimating speed. Gain of 0.2 doesn't seem right? I would expect a 0.25 or a 4 as one of the data values since 4 pulses=1 rotation? JM - I changed the gain to 0.15 as the techs in the fiels were counting the RPMs at 15 at 100Hz (pulses)
|  |  | F13DCS402PS1 | F13DCS402_PS1 | N/A | F13-DCS-402 PS1 24VDC HEALTHY | F13DCS402 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13DCS402PS2 | F13DCS402_PS2 | N/A | F13-DCS-402 PS2 24VDC HEALTHY | F13DCS402 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13DCS403PS1 | F13DCS403_PS1 | N/A | F13-DCS-403 PS1 24VDC HEALTHY | F13DCS403 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13DCS403PS2 | F13DCS403_PS2 | N/A | F13-DCS-403 PS2 24VDC HEALTHY | F13DCS403 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13DCS404PS1 | F13DCS404_PS1 | N/A | F13-DCS-404 PS1 24VDC HEALTHY | F13DCS404 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13DCS404PS2 | F13DCS404_PS2 | N/A | F13-DCS-404 PS2 24VDC HEALTHY | F13DCS404 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13DCS405PS1 | F13DCS405_PS1 | N/A | F13-DCS-405 PS1 24VDC HEALTHY | F13DCS405 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13DCS405PS2 | F13DCS405_PS2 | N/A | F13-DCS-405 PS2 24VDC HEALTHY | F13DCS405 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13DCS406PS1 | F13DCS406_PS1 | N/A | F13-DCS-406 PS1 24VDC HEALTHY | F13DCS406 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13DCS406PS2 | F13DCS406_PS2 | N/A | F13-DCS-406 PS2 24VDC HEALTHY | F13DCS406 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13DCS407PS1 | F13DCS407_PS1 | N/A | F13-DCS-407 PS1 24VDC HEALTHY | F13DCS407 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13DCS407PS2 | F13DCS407_PS2 | N/A | F13-DCS-407 PS2 24VDC HEALTHY | F13DCS407 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | HS13220A | HS13220AOP | 2000-F13-PID-PR-10005 | F13-DG-467 RECYCLE CRUSHER BYPASS GATE FORWARD PUSH BUTTON | F13DG467 Open | Inactive | Active |  | Hardwired to DCS |  |  | LCP push button for XV13220. Refer to On/Off Valve tab for logic. | 1 | 2025-07-22 | CR-031
|  |  | HS13220B | HS13220BCL | 2000-F13-PID-PR-10005 | F13-DG-467 RECYCLE CRUSHER BYPASS GATE REVERSE PUSH BUTTON | F13DG467 Close | Inactive | Active |  | Hardwired to DCS |  |  | LCP push button for XV13220. Refer to On/Off Valve tab for logic. | 1 | 2025-07-22 | CR-031
|  |  | PS13225 | PAL13225 | 2000-F13-PID-PR-10006 | F13DG467-CP Recycle Crusher Bypass Gate Control Panel Main Air Isolated Position Switch | F13DG467-CP Air | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 1 | 24/03/2025 30/04/2025 | IO List updates Alarm added https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-296?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
|  |  | PWS13005B | PWA13005B | 2000-F13-PID-PR-10001 | F13-FA-411 Coarse Ore Reclaim Feeder 1 Pull-Wire Switch LHS | F13FA411 Pullwire LHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | PWS13005A | PWA13005A | 2000-F13-PID-PR-10001 | F13-FA-411 Coarse Ore Reclaim Feeder 1 Pull-Wire Switch RHS | F13FA411 Pullwire RHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | ZE13006 | SAL13006 | 2000-F13-PID-PR-10001 | F13-FA-411 Coarse Ore Reclaim Feeder 1 Speed Encoder | F13FA411 Underspeed | Normal | Alarm | Alarm | SoftTag | 3 | 1. F13-FA-411 Not Running 2. Mask for 10 seconds (TBC) on F13-FA-411 start-up | Source: 2000-ME004-M01-10002 Alarm masking duration to be confirmed during commissioning. Wired to VSD | 1 | 2025-03-06 | [KAN-1469] Soft Tag VSD Underspeeds - Jira |  |  |  |  | MOC563 Comments - remove underspeed soft tags from DCS.
|  |  | TS13995 | TSH13995 | 2000-F13-PID-PR-10001 | F13-FA-412 Coarse Ore Reclaim Feeder 2 Gearboox Fan Cooler Temperature Switch | F13FA412 G/box Clr Temp | Active | N_Active |  | Hardwired to DCS | - |  | Apron Feeder Cooler Temperature Switch. When activated, air-oil cooler fan will switch on (at temperatures greater than 50C). Fan will switch off when temperature is < 35C. Source: 2000-ME004-M01-10002. | B
|  |  | PWS13015B | PWA13015B | 2000-F13-PID-PR-10001 | F13-FA-412 Coarse Ore Reclaim Feeder 2 Pull-Wire Switch LHS | F13FA412 Pullwire LHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | PWS13015A | PWA13015A | 2000-F13-PID-PR-10001 | F13-FA-412 Coarse Ore Reclaim Feeder 2 Pull-Wire Switch RHS | F13FA412 Pullwire RHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | ZE13016 | SAL13016 | 2000-F13-PID-PR-10001 | F13-FA-412 Coarse Ore Reclaim Feeder 2 Speed Encoder | F13FA412 Underspeed | Normal | Alarm | Alarm | SoftTag | 3 | 1. F13-FA-412 Not Running 2. Mask for 10 seconds (TBC) on F13-FA-412 start-up | Source: 2000-ME004-M01-10002 Alarm masking duration to be confirmed during commissioning. Wired to VSD | 1 | 2025-03-06 | [KAN-1469] Soft Tag VSD Underspeeds - Jira |  |  |  |  | MOC563 Comments - remove underspeed soft tags from DCS.
|  |  | TS13996 | TSH13996 | 2000-F13-PID-PR-10001 | F13-FA-414 Emergency Feeder Gearboox Fan Cooler Temperature Switch | F13FA414 G/box Clr Temp | Active | N_Active |  | Hardwired to DCS | - |  | Apron Feeder Cooler Temperature Switch. When activated, air-oil cooler fan will switch on (at temperatures greater than 50C). Fan will switch off when temperature is < 35C. Source: 2000-ME004-M01-10003. | B
|  |  | PWS13025B | PWA13025B | 2000-F13-PID-PR-10001 | F13-FA-414 Emergency Feeder Pull-Wire Switch LHS | F13FA414 Pullwire LHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | PWS13025A | PWA13025A | 2000-F13-PID-PR-10001 | F13-FA-414 Emergency Feeder Pull-Wire Switch RHS | F13FA414 Pullwire RHS | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B |  | MOC-237
|  |  | ZE13026 | SAL13026 | 2000-F13-PID-PR-10001 | F13-FA-414 Emergency Feeder Tail Pulley Speed Encoder | F13FA414 Underspeed | Normal | Alarm | Alarm | SoftTag | 3 | 1. F13-FA-442 Not Running 2. Mask for 10 seconds (TBC) on F13-FA-442 start-up | Source: 2000-ME004-M01-10002 Alarm masking duration to be confirmed during commissioning. Wired to VSD | 1 | 2025-03-06 | [KAN-1469] Soft Tag VSD Underspeeds - Jira |  |  |  |  | MOC563 Comments - remove underspeed soft tags from DCS.
|  |  | PDSH13362 | PDAH13362 | 2000-F13-PID-PR-10007 | F13-FI-404 Trash Screen 1 Water Filter Process Water Pressure Differential Switch High | F13FI404 DP Switch | Alarm | Normal | Alarm | Hardwired to DCS | 3 | Mask if XV13361 Closed |  | B
|  |  | PDSH13372 | PDAH13372 | 2000-F13-PID-PR-10007 | F13-FI-405 Trash Screen 2 Water Filter Process Water Pressure Differential Switch High | F13FI405 DP Switch | Alarm | Normal | Alarm | Hardwired to DCS | 3 | Mask if XV13371 Closed |  | B
|  |  | PDSH13402 | PDAH13402 | 2000-F13-PID-PR-10008 | F13-FI-406 Trash Screen 3 Water Filter Process Water Pressure Differential Switch High | F13FI406 DP Switch | Alarm | Normal | Alarm | Hardwired to DCS | 3 | Mask if XV13401 Closed |  | B
|  |  | PDSH13392 | PDAH13392 | 2000-F13-PID-PR-10008 | F13-FI-407 Trash Screen 4 Water Filter Process Water Pressure Differential Switch High | F13FI407 DP Switch | Alarm | Normal | Alarm | Hardwired to DCS | 3 | Mask if XV13391 Closed |  | B
|  |  | F13FIP001ALM | F13FIP001_ALM | N/A | F13-FIP-001 Alarm | F13-FIP-001 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-20 | MOC103
|  |  | F13FIP001FLT | F13FIP001_FLT | N/A | F13-FIP-001 Fault | F13-FIP-001 Fault | Alarm | f | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13FIP001ISL | F13FIP001_ISL | N/A | F13-FIP-001 Isolated | F13-FIP-001 Isolated | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-20 | MOC103
|  |  | F13FIP002ALM | F13FIP002_ALM | N/A | F13-FIP-002 Alarm | F13-FIP-002 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-20 | MOC103
|  |  | F13FIP002FLT | F13FIP002_FLT | N/A | F13-FIP-002 Fault | F13-FIP-002 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13FIP002ISL | F13FIP002_ISL | N/A | F13-FIP-002 Isolated | F13-FIP-002 Isolated | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-20 | MOC103
|  |  | F13FIP003ALM | F13FIP003_ALM | N/A | F13-FIP-003 Alarm | F13-FIP-003 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-20 | MOC103
|  |  | F13FIP003FLT | F13FIP003_FLT | N/A | F13-FIP-003 Fault | F13-FIP-003 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13FIP003ISL | F13FIP003_ISL | N/A | F13-FIP-003 Isolated | F13-FIP-003 Isolated | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-20 | MOC103
|  |  | F13FIP004ALM | F13FIP004_ALM | N/A | F13-FIP-004 Alarm | F13-FIP-004 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-20 | MOC103
|  |  | F13FIP004FLT | F13FIP004_FLT | N/A | F13-FIP-004 Fault | F13-FIP-004 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13FIP004ISL | F13FIP004_ISL | N/A | F13-FIP-004 Isolated | F13-FIP-004 Isolated | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-20 | MOC103
|  |  | F13FIP005ALM | F13FIP005_ALM | N/A | F13-FIP-005 Alarm | F13-FIP-005 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-20 | MOC103
|  |  | F13FIP005FLT | F13FIP005_FLT | N/A | F13-FIP-005 Fault | F13-FIP-005 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13FIP005ISL | F13FIP005_ISL | N/A | F13-FIP-005 Isolated | F13-FIP-005 Isolated | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-20 | MOC103
|  |  | ZSC13218 | ZIC13218 | 2000-F13-PID-PR-10006 | F13-GA-411 Recycle Crusher C Isolation Gates Close Position Switch | F13GA411 C Closed | Closed | N_Closed |  | Hardwired to DCS | - |  |  | B
|  |  | HS13218B | HS13218BCL | 2000-F13-PID-PR-10006 | F13-GA-411 Recycle Crusher C Isolation Gates Close Push Button | F13GA411 Close PB | N_Active | Close |  | Hardwired to DCS | - |  | Pressing this button will energise SV13218B to close F13GA411 Cannot be energised at the same time as HS13218AOP Refer to OnOff Valves tab for solenoid valve details | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
|  |  | ZSO13218 | ZIO13218 | 2000-F13-PID-PR-10006 | F13-GA-411 Recycle Crusher C Isolation Gates Open Position Switch | F13GA411 C Opened | N_Open | Open |  | Hardwired to DCS | - |  |  | B
|  |  | HS13218A | HS13218AOP | 2000-F13-PID-PR-10006 | F13-GA-411 Recycle Crusher C Isolation Gates Open Push Button | F13GA411 Open PB | N_Active | Open |  | Hardwired to DCS | - |  | Pressing this button will energise SV13218A to open F13GA411 Cannot be energised at the same time as HS13218BCL Refer to OnOff Valves tab for solenoid valve details | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
|  |  | ZSC13219 | ZIC13219 | 2000-F13-PID-PR-10006 | F13-GA-412 Recycle Crusher D Isolation Gates Close Position Switch | F13GA412 D Closed | Closed | N_Closed |  | Hardwired to DCS | - |  |  | B
|  |  | HS13219B | HS13219BCL | 2000-F13-PID-PR-10006 | F13-GA-412 Recycle Crusher D Isolation Gates Close Push Button | F13GA412 Close PB | N_Active | Close |  | Hardwired to DCS | - |  |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
|  |  | ZSO13219 | ZIO13219 | 2000-F13-PID-PR-10006 | F13-GA-412 Recycle Crusher D Isolation Gates Open Position Switch | F13GA412 D Opened | N_Open | Open |  | Hardwired to DCS | - |  |  | B
|  |  | HS13219A | HS13219AOP | 2000-F13-PID-PR-10006 | F13-GA-412 Recycle Crusher D Isolation Gates Open Push Button | F13GA412 Open PB | N_Active | Open |  | Hardwired to DCS | - |  | Pressing this button will energise SV13219A to open F13GA412 Cannot be energised at the same time as HS13219BCL Refer to OnOff Valves tab for solenoid valve details | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
|  |  | LSH13039 | LAH13039 | N/A | F13-GE-103 Mills Essential Supply 415V Generator Fuel Level Switch High | F13-GE-103 Gen Fuel Hi | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | LSL13039 | LAL13039 | N/A | F13-GE-103 Mills Essential Supply 415V Generator Fuel Level Switch Low | F13-GE-103 Gen Fuel Lo | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | LSH13049 | LAH13049 | N/A | F13-GE-114 Recycle Crushing Essential Supply 415V Generator Fuel Level Switch High | F13-GE-114 Gen Fuel Hi | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | LSL13049 | LAL13049 | N/A | F13-GE-114 Recycle Crushing Essential Supply 415V Generator Fuel Level Switch Low | F13-GE-114 Gen Fuel Lo | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | LSH13438 | LAH13438 | N/A | F13-GE-120 Mill Chillers and Reagents Essential Supply 415V Generator Fuel Level Switch High | F13-GE-120 Gen Fuel Hi | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | LSL13438 | LAL13438 | N/A | F13-GE-120 Mill Chillers and Reagents Essential Supply 415V Generator Fuel Level Switch Low | F13-GE-120 Gen Fuel Lo | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | PS13266 | PAH13266 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Bowl Close Pressure Switch | F13HU403 Bowl Open | Open | N_Open | Open | Hardwired to DCS | 3 |  | Inactive when bowl is fully closed | B | [6 empty] | Should be PAL according to vendor drawing BOWL OPEN IN\\in PCT and BOWL CLOSED in FACEPLATE. No info in vedor pack
|  |  | PDSH13260 | PDAH13260 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Bowl Close Pressure Switch | F13HU403 Filter Blocked | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Hydraulic filter DP switch. Filter blockage = alarm | B
|  |  | PDSH13320 | PDAH13320 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Bowl Close Pressure Switch | F13HU404 Filter Blocked | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Hydraulic filter DP switch. Filter blockage = alarm | B
|  |  | PS13265 | PAH13265 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Bowl Open Pressure Switch | F13HU403 Bowl Close | Closed | N_Closed | Closed | Hardwired to DCS | 3 |  | Inactive when bowl is fully open | B
|  |  | HS13279D | HS13279DCL | 2000-F13-PID-PR-10006 | F13HU403-CP Recycle Crusher C Hydraulic Unit Control Panel Bowl Close Selector Switch | F13HU403-CP BowlClose | N_Active | Active |  | Hardwired to DCS | - |  | HS13279D is the F13-CC-401 Recycle Crusher C Hydraulic Unit F13-HU-403 Control Panel Bowl Close Selector Switch. F13HU403-CP push buttons and switches will only work when F13CC401_HPU is Active. When F13CC401_HPU ACTIVE and HS13279DCL ACTIVE and HS13279EFAST ACTIVE (Fast): • Activate YS13272B (Misc tab for detail) When F13CC401_HPU ACTIVE and HS13279DCL ACTIVE and HS13279FSLOW ACTIVE (Slow): • Activate YS13272A (Misc tab for detail) | 0
|  |  | HS13279C | HS13279COP | 2000-F13-PID-PR-10006 | F13HU403-CP Recycle Crusher C Hydraulic Unit Control Panel Bowl Open Selector Switch | F13HU403-CP Bowl Open | N_Active | Active |  | Hardwired to DCS | - |  | HS13279C is the F13-CC-401 Recycle Crusher C Hydraulic Unit F13-HU-403 Control Panel Bowl Open Selector Switch. F13HU403-CP push buttons and switches will only work when F13CC401_HPU is Active. When F13CC401_HPU ACTIVE and HS13279COP ACTIVE and HS13279EFAST ACTIVE (Fast): • Activate YS13271B (see Misc tab for detail) When F13CC401_HPU ACTIVE and HS13279COP ACTIVE and HS13279FSLOW ACTIVE (Slow): • Activate YS13271A (see Misc tab for detail) | 0
|  |  | HS13279E | HS13279EFAST | 2000-F13-PID-PR-10006 | F13HU403-CP Recycle Crusher C Hydraulic Unit Control Panel High Speed Selector Switch | F13HU403-CP Bowl Fast | N_Active | Active |  | Hardwired to DCS | - |  | HS13279E is the F13-CC-401 Recycle Crusher C Hydraulic Unit F13-HU-403 Control Panel High Speed (high flow for bowl adjustment) Selector Switch. F13HU403-CP push buttons and switches will only work when F13CC401_HPU is Active. Refer to HS13279C and HS13279D | 0
|  |  | HS13279F | HS13279FSLOW | 2000-F13-PID-PR-10006 | F13HU403-CP Recycle Crusher C Hydraulic Unit Control Panel Low Speed Selector Switch | F13HU403-CP Bowl Slow | N_Active | Active |  | Hardwired to DCS | - |  | HS13279F is the F13-CC-401 Recycle Crusher C Hydraulic Unit F13-HU-403 Control Panel Low Speed (low flow for bowl adjustment) Selector Switch. F13HU403-CP push buttons and switches will only work when F13CC401_HPU is Active. Refer to HS13279C and HS13279D | 0
|  |  | HS13279A | HS13279ASTT | 2000-F13-PID-PR-10006 | F13HU403-CP Recycle Crusher C Hydraulic Unit Control Panel Start Push Button | F13HU403-CP Start | N_Active | Active |  | Hardwired to DCS | - | adam gay | HS13279A is the F13-CC-401 Recycle Crusher C Hydraulic Unit F13-HU-403 Control Panel Start Push Button. If F13CC401_HPU and HS13279ASTT = active: start F13-PO-408 See F13CC401_HPU in Misc tab for details. | 1 | 2025-04-09 | https://pastech-2955.atlassian.net/browse/KAN-1654?linkSource=email
|  |  | HS13279B | HS13279BSTP | 2000-F13-PID-PR-10006 | F13HU403-CP Recycle Crusher C Hydraulic Unit Control Panel Stop Push Button | F13HU403-CP Stop | Active | N_Active |  | Hardwired to DCS | - |  | HS13279B is the F13-CC-401 Recycle Crusher C Hydraulic Unit F13-HU-403 Control Panel Stop Push Button. If F13CC401_HPU and HS13279BSTP = active: stop F13-PO-408 | 1 | 2025-04-07 | https://pastech-2955.atlassian.net/browse/KAN-1654?linkSource=email |  |  |  |  | MSH 17/07/26: Wired as NC in the field, probably because it is considered as E-stop when it is not, logic reversed accordingly
|  |  | HS13279H | HS13279HCLR | 2000-F13-PID-PR-10006 | F13HU403-CP Recycle Crusher C Hydraulic Unit Control Panel Tramp Pressure Clear Selector Switch | F13HU403-CP Clear Press. | N_Active | Active |  | Hardwired to DCS | - |  | HS13279H is the F13-CC-401 Recycle Crusher C Hydraulic Unit F13-HU-403 Control Panel Clearing Pressure Selector Switch. F13HU403-CP push buttons and switches will only work when F13CC401_HPU is Active. When F13CC401_HPU ACTIVE and HS13279HCLR ACTIVE: • Activate YS13275 (Misc tab for detail) | 0
|  |  | HS13279G | HS13279GTRP | 2000-F13-PID-PR-10006 | F13HU403-CP Recycle Crusher C Hydraulic Unit Control Panel Tramp Pressure Reset Selector Switch | F13HU403-CP Tramp Press. | N_Active | Active |  | Hardwired to DCS | - |  | HS13279G is the F13-CC-401 Recycle Crusher C Hydraulic Unit F13-HU-403 Control Panel Tramp Pressure Reset Selector Switch. F13HU403-CP push buttons and switches will only work when F13CC401_HPU is Active. When F13CC401_HPU ACTIVE and HS13279GTRP ACTIVE: • Activate YS13276 as per Process Switchpoints (Misc tab for detail) | 0
|  |  | PS13325 | PAH13325 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Bowl Close Pressure Switch | F13HU404 Bowl Close | Closed | N_Closed | Closed | Hardwired to DCS | 3 |  | Inactive when bowl is fully closed | B
|  |  | PS13326 | PAH13326 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Bowl Open Pressure Switch | F13HU404 Bowl Open | Open | N_Open | Open | Hardwired to DCS | 3 |  | Inactive when bowl is fully open | B
|  |  | HS13343D | HS13343DCL | 2000-F13-PID-PR-10006 | F13HU404-CP Recycle Crusher D Hydraulic Unit Control Panel Bowl Close Selector Switch | F13HU404-CP BowlClose | N_Active | Active |  | Hardwired to DCS | - |  | HS13343D is the F13-CC-402 Recycle Crusher D Hydraulic Unit F13-HU-404 Control Panel Bowl Close Selector Switch. F13HU404-CP push buttons and switches will only work when F13CC402_HPU is Active. When F13CC402_HPU ACTIVE and HS13343DCL ACTIVE and HS13343EFAST ACTIVE (Fast): • Activate YS13272B (Misc tab for detail) When F13CC402_HPU ACTIVE and HS13343DCL ACTIVE and HS13343FSLOW ACTIVE (Slow): • Activate YS13334A (Misc tab for detail) | 0
|  |  | HS13343C | HS13343COP | 2000-F13-PID-PR-10006 | F13HU404-CP Recycle Crusher D Hydraulic Unit Control Panel Bowl Open Selector Switch | F13HU404-CP Bowl Open | N_Active | Active |  | Hardwired to DCS | - |  | HS13343C is the F13-CC-402 Recycle Crusher D Hydraulic Unit F13-HU-404 Control Panel Bowl Open Selector Switch. F13HU404-CP push buttons and switches will only work when F13CC402_HPU is Active. When F13CC402_HPU ACTIVE and HS13343COP ACTIVE and HS13343EFAST ACTIVE (Fast): • Activate YS13331B (Misc tab for detail) When F13CC402_HPU ACTIVE and HS13343COP ACTIVE and HS13343FSLOW ACTIVE (Slow): • Activate YS13331A (Misc tab for detail) | 0
|  |  | HS13343E | HS13343EFAST | 2000-F13-PID-PR-10006 | F13HU404-CP Recycle Crusher D Hydraulic Unit Control Panel High Speed Selector Switch | F13HU404-CP Bowl Fast | N_Active | Active |  | Hardwired to DCS | - |  | HS13343E is the F13-CC-402 Recycle Crusher D Hydraulic Unit F13-HU-404 Control Panel High Speed (high flow for bowl adjustment) Selector Switch. F13HU404-CP push buttons and switches will only work when F13CC402_HPU is Active. Refer to HS13343C and HS13343D | 0
|  |  | HS13343F | HS13343FSLOW | 2000-F13-PID-PR-10006 | F13HU404-CP Recycle Crusher D Hydraulic Unit Control Panel Low Speed Selector Switch | F13HU404-CP Bowl Slow | N_Active | Active |  | Hardwired to DCS | - |  | HS13343F is the F13-CC-402 Recycle Crusher D Hydraulic Unit F13-HU-404 Control Panel Low Speed (low flow for bowl adjustment) Selector Switch. F13HU404-CP push buttons and switches will only work when F13CC402_HPU is Active. Refer to HS13343C and HS13343D | 0
|  |  | HS13343A | HS13343ASTT | 2000-F13-PID-PR-10006 | F13HU404-CP Recycle Crusher D Hydraulic Unit Control Panel Start Push Button | F13HU404-CP Start | N_Active | Active |  | Hardwired to DCS | - |  | HS13343A is the F13-CC-402 Recycle Crusher D Hydraulic Unit F13-HU-404 Control Panel Start Push Button. If F13CC402_HPU and HS13343ASTT = active: start F13-PO-409 See F13CC402_HPU in Misc tab for details. | 2 | 2025-04-09 | https://pastech-2955.atlassian.net/browse/KAN-1654?linkSource=email
|  |  | f | HS13343BSTP | 2000-F13-PID-PR-10006 | F13HU404-CP Recycle Crusher D Hydraulic Unit Control Panel Stop Push Button | F13HU404-CP Stop | Active | N_Active |  | Hardwired to DCS | - |  | HS13343B is the F13-CC-402 Recycle Crusher D Hydraulic Unit F13-HU-404 Control Panel Stop Push Button. If F13CC402_HPU and HS13343BSTP = active: stop F13-PO-409 | 2 | 2025-04-07 | https://pastech-2955.atlassian.net/browse/KAN-1654?linkSource=email |  |  |  |  | MSH 17/07/26: Wired as NC in the field, probably because it is considered as E-stop when it is not, logic reversed accordingly
|  |  | HS13343H | HS13343HCLR | 2000-F13-PID-PR-10006 | F13HU404-CP Recycle Crusher D Hydraulic Unit Control Panel Tramp Pressure Clear Selector Switch | F13HU404-CP Clear Press. | N_Active | Active |  | Hardwired to DCS | - |  | HS13343H is the F13-CC-402 Recycle Crusher D Hydraulic Unit F13-HU-404 Control Panel Clearing Pressure Selector Switch. F13HU404-CP push buttons and switches will only work when F13CC402_HPU is Active. When F13CC402_HPU ACTIVE and HS13343HCLR ACTIVE: • Activate YS13335 (Misc tab for detail) | 0
|  |  | HS13343G | HS13343GTRP | 2000-F13-PID-PR-10006 | F13HU404-CP Recycle Crusher D Hydraulic Unit Control Panel Tramp Pressure Reset Selector Switch | F13HU404-CP Tramp Press. | N_Active | Active |  | Hardwired to DCS | - |  | HS13343G is the F13-CC-402 Recycle Crusher D Hydraulic Unit F13-HU-404 Control Panel Tramp Pressure Reset Selector Switch. F13HU404-CP push buttons and switches will only work when F13CC402_HPU is Active. When F13CC402_HPU ACTIVE and HS13343GTRP ACTIVE: • Activate YS13336 as per Process Switchpoints (Misc tab for detail) | 0
|  |  |  | PDAH13217 | 2000-F13-PID-PR-10006 | F13-HU-405 Recycle Crusher Isolation Gates Hydraulic Unit Filter Pressure Differential Switch High | F13HU405 HPU Res Fltr | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | LSL13216 | LAL13216 | 2000-F13-PID-PR-10006 | F13-HU-405 Recycle Crusher Isolation Gates Hydraulic Unit Oil Level Low Alarm | F13HU405 HPU Res Lvl Lo | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-04-29 | https://pastech-2955.atlassian.net/browse/KAN-1674
|  |  | LSLL13216 | LALL13216 | 2000-F13-PID-PR-10006 | F13-HU-405 Recycle Crusher Isolation Gates Hydraulic Unit Oil Level Low Low Alarm | F13HU405 HPU Res Lvl LL | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | TSH13216 | TAH13216 | 2000-F13-PID-PR-10006 | F13-HU-405 Recycle Crusher Isolation Gates Hydraulic Unit Oil Temperature High Alarm | F13HU405 HPU Res Temp Hi | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-04-29 | https://pastech-2955.atlassian.net/browse/KAN-1674
|  |  | TSHH13216 | TAHH13216 | 2000-F13-PID-PR-10006 | F13-HU-405 Recycle Crusher Isolation Gates Hydraulic Unit Oil Temperature High High Alarm | F13HU405 HPU Res Temp HH | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | ZSH13542 | ZSH13542 | 2000-F13-PID-PR-10002 | F13-HU-407 CYCLONE FEED PUMP SUCTION VALVE HPU LIMIT SWITCH HIGH | F13HU407 Suction Valve | N_Open | Open |  | Hardwired to DCS |  |  |  | 1 | 2/07/2025 28/08/2025 | CR-021 Updated based on vendor document update
|  |  | PSH13538 | PAH13538 | 2000-F13-PID-PR-10002 | F13-HU-407 CYCLONE FEED PUMP SUCTION VALVE HPU RETURN FILTER PRESSURE SWITCH HIGH | F13HU407 Filter Blocked | Alarm (see comment) | N_Active | Alarm (see comment) | Hardwired to DCS | 3 |  | Logic: Latch PAH13538 alarm Unlatch if (PSH13538 active and F13HU407 running) for > 10 seconds | 1 | 2025-07-02 | CR-021
|  |  | HS13544B | HS13544BCL | 2000-F13-PID-PR-10002 | F13HU407-CP CYCLONE FEED PUMP SUCTION VALVE HYDRAULIC POWER UNIT CONTROL PANEL CLOSE VALVE PUSH BUTTON | F13HU407 Close Valve | N_Active | Close |  | Hardwired to DCS |  |  | Refer to HS13543_LOGIC for logic | 1 | 2025-07-02 | CR-021
|  |  | HS13543A | HS13543ALOC | 2000-F13-PID-PR-10002 | F13HU407-CP CYCLONE FEED PUMP SUCTION VALVE HYDRAULIC POWER UNIT CONTROL PANEL LOCAL SELECTED | F13HU407 Local Mode | N_Active | Local |  | Hardwired to DCS |  |  | 2 selector switch, HS13543A/B Refer to HS13543_LOGIC for logic | 1 | 2025-07-02 | CR-021
|  |  | HS13544A | HS13544AOP | 2000-F13-PID-PR-10002 | F13HU407-CP CYCLONE FEED PUMP SUCTION VALVE HYDRAULIC POWER UNIT CONTROL PANEL OPEN VALVE PUSH BUTTON | F13HU407 Open Valve | N_Active | Open |  | Hardwired to DCS |  |  | Refer to HS13543_LOGIC for logic | 1 | 2025-07-02 | CR-021
|  |  | HS13543B | HS13543BREM | 2000-F13-PID-PR-10002 | F13HU407-CP CYCLONE FEED PUMP SUCTION VALVE HYDRAULIC POWER UNIT CONTROL PANEL REMOTE SELECTED | F13HU407 Remote Mode | N_Active | Remote |  | Hardwired to DCS |  |  | 2 selector switch, HS13543A/B Refer to HS13543_LOGIC for logic | 1 | 2025-07-02 | CR-021
|  |  | XS13759 | XI13759 | 2000-F13-PID-PR-10003 | F13-HU-413 PORTABLE MILLS INCHING DRIVE HYDRAULIC POWER UNIT MOTOR RUN FEEDBACK | F13HU413 Running FB | Inactive | Active |  | Hardwired to DCS |  |  |  | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
|  |  | PSH13555 | PAH13555 | 2000-F13-PID-PR-10013 | F13-HU-416 Sag Mill Brake Hydraulic Power Unit Accumulator Pressure Switch High | F13HU416 Accu Pressure | Active | N_Active |  | Hardwired to DCS | - |  |  | B
|  |  | ZSH13545 | ZAH13545 | 2000-F13-PID-PR-10013 | F13-HU-416 Sag Mill Brake Hydraulic Power Unit Brake #1 On/Off Proximity Switch | F13HU416 Brake 1 On/Off | On | Off |  | Hardwired to DCS | - |  | On = Brake Engaged Off = Brake Released | B
|  |  | ZSH13546 | ZAH13546 | 2000-F13-PID-PR-10013 | F13-HU-416 Sag Mill Brake Hydraulic Power Unit Brake #1 Pad Wear Proximity Switch | F13HU416 Brake 1 Wear | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Alarm = Worn Normal = Not Worn | A
|  |  | ZSH13547 | ZAH13547 | 2000-F13-PID-PR-10013 | F13-HU-416 Sag Mill Brake Hydraulic Power Unit Brake #2 On/Off Proximity Switch | F13HU416 Brake 2 On/Off | On | Off |  | Hardwired to DCS | - |  | On = Brake Engaged Off = Brake Released | B
|  |  | ZSH13548 | ZAH13548 | 2000-F13-PID-PR-10013 | F13-HU-416 Sag Mill Brake Hydraulic Power Unit Brake #2 Pad Wear Proximity Switch | F13HU416 Brake 2 Wear | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Alarm = Worn Normal = Not Worn | A
|  |  | LSL13551 | LAL13551 | 2000-F13-PID-PR-10013 | F13-HU-416 Sag Mill Brake Hydraulic Power Unit Brake Hydraulic Fluid Reservoir Level Switch Low | F13HU416 Hyd Res Lvl | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | TSH13552 | TAH13552 | 2000-F13-PID-PR-10013 | F13-HU-416 Sag Mill Brake Hydraulic Power Unit Brake Hydraulic Fluid Reservoir Temperature Switch high | F13HU416 Hyd Res Temp | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | A
|  |  | HS13739 | HS13739STT | 2000-F13-PID-PR-10013 | F13HU416-CP SAG Mill Brake System Local Control Panel Jog Pump Indicator Light | F13HU416 Jog Pump PB | N_Active | Active |  | Hardwired to DCS | - |  | Pressing this button will jog F13-PO-432 in Local mode only for the duration that the pushbutton is held down if HS13737 is in LOCAL selection. | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1939
|  |  | HS13736 | HS13736TEST | 2000-F13-PID-PR-10013 | F13HU416-CP SAG Mill Brake System Local Control Panel Lamp Test Indicator Light | F13HU416 Lamp Test PB | N_Active | Active |  | Hardwired to DCS | - |  | Holding down push button will light up all indicators on the F13-HU-416 control panel for testing purposes. Refer to Digital Output tab | A
|  |  | HS13737 | HS13737MODE | 2000-F13-PID-PR-10013 | F13HU416-CP SAG Mill Brake System Local Control Panel Local/Auto Selector Switch | F13HU416CP Loc/Auto Sel. | Local | Automatic |  | Hardwired to DCS | - |  | Local / Automatic selector switch. If LOCAL then control as per HS13738. In LOCAL, F13-PO-432 shall be forced into LOCAL If AUTOMATIC then control as per MS_2S_BRK and MS_RL_BRK | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1939
|  |  | HS13738 | HS13738BRK | 2000-F13-PID-PR-10013 | F13HU416-CP SAG Mill Brake System Local Control Panel Manual Brake Release / Apply Selector Switch | F13HU416CP Man Brk Sel. | Release | Engage |  | Hardwired to DCS | - |  | Release / Apply brake selector switch. IF HS13737MODE = LOCAL AND HS13738BRK = RELEASE: • ACTIVATE MS_RL_BRK IF HS13737MODE = LOCAL AND HS13738BRK = ENGAGE: • ACTIVATE MS_EN_BRK | A
|  |  | ZSH13795 | ZAH13795 | 2000-F13-PID-PR-10013 | F13-HU-417 Ball Mill Brake Hydraulic Power Unit Brake #1 On/Off Proximity Switch | F13HU417 Brake 1 On/Off | On | Off |  | Hardwired to DCS | - |  | On = Brake Engaged Off = Brake Released | A
|  |  | ZSH13796 | ZAH13796 | 2000-F13-PID-PR-10013 | F13-HU-417 Ball Mill Brake Hydraulic Power Unit Brake #1 Pad Wear Proximity Switch | F13HU417 Brake 1 Wear | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Alarm = Worn Normal = Not Worn | B
|  |  | ZSH13797 | ZAH13797 | 2000-F13-PID-PR-10013 | F13-HU-417 Ball Mill Brake Hydraulic Power Unit Brake #2 On/Off Proximity Switch | F13HU417 Brake 2 On/Off | On | Off |  | Hardwired to DCS | - |  | On = Brake Engaged Off = Brake Released | A
|  |  | ZSH13798 | ZAH13798 | 2000-F13-PID-PR-10013 | F13-HU-417 Ball Mill Brake Hydraulic Power Unit Brake #2 Pad Wear Proximity Switch | F13HU417 Brake 2 Wear | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Alarm = Worn Normal = Not Worn | B
|  |  | LSL13802 | LAL13802 | 2000-F13-PID-PR-10013 | F13-HU-417 Ball Mill Brake Hydraulic Power Unit Brake Fluid Reservoir Level Switch Low | F13HU417 Hyd Res Lvl | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | TSH13803 | TAH13803 | 2000-F13-PID-PR-10013 | F13-HU-417 Ball Mill Brake Hydraulic Power Unit Brake Fluid Reservoir Temperature Switch High | F13HU417 Hyd Res Temp | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PSH13806 | PAH13806 | 2000-F13-PID-PR-10013 | F13-HU-417 Ball Mill Brake Hydraulic Power Unit Hydraulic Brake System Pump Discharge Pressure Switch High | F13HU417 Accu Pressure | Active | N_Active |  | Hardwired to DCS | 3 |  |  | B
|  |  | HS13749 | HS13749BRK | 2000-F13-PID-PR-10013 | F13HU417-CP Ball Mill Brake System Local Control Panel Brake Release/Apply Selector Switch | F13HU417CP Man Brk Sel. | Release | Engage |  | Hardwired to DCS | - |  | Release / Apply brake selector switch. IF HS13748MODE = LOCAL AND HS13749BRK = RELEASE: • ACTIVATE MB_RL_BRK IF HS13748MODE = LOCAL AND HS13749BRK = ENGAGE: • ACTIVATE MB_EN_BRK | A
|  |  | HS13750 | HS13750STT | 2000-F13-PID-PR-10013 | F13HU417-CP Ball Mill Brake System Local Control Panel Jog Pump Indicator Light | F13HU417 Jog Pump PB | N_Active | Active |  | Hardwired to DCS | - |  | Pressing this button will jog F13-PO-532 in Local mode for the duration that the pushbutton is held down if HS13748 is in LOCAL selection | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1939
|  |  | HS13747 | HS13747TEST | 2000-F13-PID-PR-10013 | F13HU417-CP Ball Mill Brake System Local Control Panel Lamp Test Indicator Light | F13HU417 Lamp Test PB | N_Active | Active |  | Hardwired to DCS | - |  | Holding down push button will light up all indicators on the F13-HU-417 control panel for testing purposes. Refer to Digital Output tab | A
|  |  | HS13748 | HS13748MODE | 2000-F13-PID-PR-10013 | F13HU417-CP Ball Mill Brake System Local Control Panel Local/Auto Selector Switch | F13HU417CP Loc/Auto Sel. | Local | Automatic |  | Hardwired to DCS | - |  | Local / Automatic selector switch. If LOCAL then control as per HS13749. In LOCAL, F13-PO-532 shall be forced into LOCAL. If AUTOMATIC then control as per MB_2S_BRK and MB_RL_BRK | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1939
|  |  | ZSO13238 | ZAO13238 | 2000-F13-PID-PR-10006 | F13-LU-403 Recycle Crusher C Lubrication Unit Valve 1 Position Switch Opened | F13LU403 Pump 1 Disch. | N_Open | Open | N_Open | Hardwired to DCS | 3 | Mask if F13-PO-401 is Standby on F13CC401_FP2 | HV13238 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | ZSO13239 | ZAO13239 | 2000-F13-PID-PR-10006 | F13-LU-403 Recycle Crusher C Lubrication Unit Valve 2 Position Switch Opened | F13LU403 Pump 2 Disch. | N_Open | Open | N_Open | Hardwired to DCS | 3 | Mask if F13-PO-402 is Standby on F13CC401_FP2 | HV13239 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | ZSO13298 | ZAO13298 | 2000-F13-PID-PR-10006 | F13-LU-404 Recycle Crusher D Lubrication Unit Valve 1 Position Switch Opened | F13LU404 Pump 1 Disch. | N_Open | Open | N_Open | Hardwired to DCS | 3 | Mask if F13-PO-406 is Standby on F13CC402_FP2 | HV13298 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | ZSO13299 | ZAO13299 | 2000-F13-PID-PR-10006 | F13-LU-404 Recycle Crusher D Lubrication Unit Valve 2 Position Switch Opened | F13LU404 Pump 2 Disch. | N_Open | Open | N_Open | Hardwired to DCS | 3 | Mask if F13-PO-407 is Standby on F13CC402_FP2 | HV13299 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | PDSH13565 | PDAH13565 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Cooling Filter Blocked Pressure Differential Switch High | F13LU411 Lbe Fltr 2 Hi | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-04-29 | https://pastech-2955.atlassian.net/browse/KAN-1674 |  |  |  |  | Field (Vendor Drawing) 0=Normal 1=Alarm Need MOC approval [update] reverting MOC changes, wired as fail-safe in the field now [update] MSH 06/05/26, this can't be fail-safe in the field, 1 is Alarm
|  |  | PDSHH13565 | PDAHH13565 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Cooling Filter Blocked Pressure Differential Switch High High | F13LU411 LbeFltr 2 Sw HH | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PDSH13566 | PDAH13566 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Filter Pressure Differential Switch High | F13LU411 Lbe Fltr 1 Hi | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-04-29 | https://pastech-2955.atlassian.net/browse/KAN-1674 |  |  |  |  | Field (Vendor Drawing) 0=Normal 1=Alarm Need MOC approval [update] reverting MOC changes, wired as fail-safe in the field now [update] MSH 06/05/26, this can't be fail-safe in the field, 1 is Alarm | Loop tested, however, the pressure switch need replacement as per the E&I
|  |  | PDSHH13566 | PDAHH13566 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Filter Pressure Differential Switch High High | F13LU411 LbeFltr 1 Sw HH | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [7 empty] | Loop tested, however, the pressure switch need replacement as per the E&I
|  |  | PSL13572 | PAL13572 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Motor 1 Drive End Pressure Switch | F13LU411 A Lube Sup. DE | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | As found: SP1 = 50bar, RES = 49bar As left: SP1 = 41bar, RES =40bar | 2 | [6 empty] | MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
|  |  | PSL13573 | PAL13573 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Motor 1 Non-Drive End Pressure Switch | F13LU411 A Lube Sup. NDE | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
|  |  | PSL13574 | PAL13574 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Motor 2 Drive End Pressure Switch | F13LU411 B Lube Sup. DE | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
|  |  | PSL13575 | PAL13575 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Motor 2 Non-Drive End Pressure Switch | F13LU411 B Lube Sup. NDE | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
|  |  | LSL13568 | LAL13568 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Reservoir Level Switch Low | F13LU411 Lube Res Lvl L | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | Field (Vendor Drawing) 0=Normal 1=Alarm Need MOC approval [update] reverting MOC changes, wired as fail-safe in the field now
|  |  | LSLL13568 | LALL13568 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Reservoir Level Switch Low Low | F13LU411 Lube Res Lvl LL | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [9 empty] | 13
|  |  | TSH13569 | TAH13569 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Reservoir Temperature Switch High | F13LU411 Lube Res Tmp Hi | Active | N_Active |  | Hardwired to DCS | - |  |  | 1 | 29/04/2025 4/06/2025 | https://pastech-2955.atlassian.net/browse/KAN-1674 https://pastech-2955.atlassian.net/browse/KAN-1984
|  |  | TSL13569 | TAL13569 | 2000-F13-PID-PR-10010 | F13-LU-411 SAG Mill Motors Lubrication Unit Reservoir Temperature Switch Low | F13LU411 Lube Res Tmp Lo | N_Active | Active |  | Hardwired to DCS | - |  |  | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1674
|  |  | SSL13693 | SAL13693 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG MILL HIGH PRESSURE LUBE PUMP 1 Motor Underspeed Switch | F13LU413 HP Lube P1 U/S | Alarm | Normal | Alarm | Hardwired to DCS | 10 | 1. F13-PO-429 Not Running 2. Mask for 60 seconds (TBC) on F13-PO-429 start-up | Speed monitoring from instrument (signal inactive when underspeed) Alarm masking duration to be confirmed during commissioning. | 0
|  |  | SSL13694 | SAL13694 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG MILL HIGH PRESSURE LUBE PUMP 2 Motor Underspeed Switch | F13LU413 HP Lube P2 U/S | Alarm | Normal | Alarm | Hardwired to DCS | 10 | 1. F13-PO-430 Not Running 2. Mask for 60 seconds (TBC) on F13-PO-430 start-up | Speed monitoring from instrument (signal inactive when underspeed) Alarm masking duration to be confirmed during commissioning. | 0
|  |  | SSL13695 | SAL13695 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG MILL HIGH PRESSURE LUBE PUMP 3 Motor Underspeed Switch | F13LU413 HP Lube P3 U/S | Alarm | Normal | Alarm | Hardwired to DCS | 10 | 1. F13-PO-431 Not Running 2. Mask for 60 seconds (TBC) on F13-PO-431 start-up | Speed monitoring from instrument (signal inactive when underspeed) Alarm masking duration to be confirmed during commissioning. | 0
|  |  | ZSO13629 | ZIO13629 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication System Lube Oil Heat Exchanger Cooling Water Temperature Control Valve Limit Switch Opened | TCV13629 Opened | N_Open | Open |  | Hardwired to DCS | - |  | Open position switch for TCV13629 (see Control Valves tab) | 1 | 2025-03-06 | PCT alignment action register (non standard valves defined) |  |  |  |  | State 1 = Open; 0 = N_Open
|  |  | ZSC13629 | ZIC13629 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication System Lube Oil Heat Exchanger Cooling Water Temperature Control Valve Limit Switch Opened Limit Switch Closed | TCV13629 Closed | N_Closed | Closed |  | Hardwired to DCS | - |  | Closed position switch for TCV13629 (see Control Valves tab) | 1 | 2025-03-06 | PCT alignment action register (non standard valves defined) |  |  |  |  | State 1 = Close; 0 = N_Close
|  |  | XS13200 | XA13200 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Alarm | F13LU413 OCM Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 0 | 2025-03-18 | Should be XA not XI
|  |  | HS13733A | HS13733AAUT | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Conditioned Heaters Test/Off/Auto Switch | F13LU413 Cond Htr Auto | N_Active | Active (Automatic) |  | Hardwired to DCS | - |  | 3 Selector switch: Auto / Off / Test AUTO selected: One shot F13-HT-43XX to AUT mode | 1 | 2025-07-01
|  |  | HS13733B | HS13733BOFF | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Conditioned Heaters Test/Off/Auto Switch | F13LU413 Cond Htr Off | N_Active | Active (Off) | Active (Off) | Hardwired to DCS | 0 |  | 3 Selector switch: Auto / Off / Test OFF selected: Causes F13-HT-43XX to interlock (see Drives tab) | 1 | 2025-07-01
|  |  | HS13733C | HS13733CTEST | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Conditioned Heaters Test/Off/Auto Switch | F13LU413 Cond Htr Test | N_Active | Active (Test) | Active (Test) | Hardwired to DCS | 0 |  | 3 Selector switch: Auto / Off / Test TEST selected: Set F13-HT-43XX = RUNNING | 1 | 2025-06-12 | RE: Sag Mill lube oil heater control
|  |  | HS13634B | HS13634BSTT | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel High Pressure Pump 1 Motor Start Push Button | F13LU413 HP P1 Start PB | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will start F13-PO-429. | B
|  |  | HS13634C | HS13634CSTP | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel High Pressure Pump 1 Motor Stop Push Button | F13LU413 HP P1 Stop PB | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will stop F13-PO-429. | B
|  |  | HS13636B | HS13636BSTT | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel High Pressure Pump 2 Motor Start Push Button | F13LU413 HP P2 Start PB | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will start F13-PO-430. | B
|  |  | HS13636C | HS13636CSTP | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel High Pressure Pump 2 Motor Stop Push Button | F13LU413 HP P2 Stop PB | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will stop F13-PO-430. | B
|  |  | HS13638B | HS13638BSTT | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel High Pressure Pump 3 Motor Start Push Button | F13LU413 HP P3 Start PB | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will start F13-PO-431. | B
|  |  | HS13638C | HS13638CSTP | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel High Pressure Pump 3 Motor Stop Push Button | F13LU413 HP P3 Stop PB | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will stop F13-PO-431. | B
|  |  | HS13663 | HS13663TEST | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Local Panel Lamp Test Push Button | F13LU413 Panel Lamp Test | N_Active | Active |  | Hardwired to DCS | - |  | Holding down push button will light up all indicators on the F13-LU-413 control panel for testing purposes. Refer to Digital Output tab | A
|  |  | HS13664 | HS13664AUT | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Local Panel Local Release Push Button | F13LU413 Local Rlease PB | N_Active | Active |  | Hardwired to DCS | - |  | IF HS13664AUT = ACTIVE (One Shot, Rising-Edge Trigger), Prompt CRO: Set "SAG Mill Lubrication System Local Release Request Pushbutton Activated. Set F13-LU-413 Package to AUTO mode?" (YES / NO) If YES is selected, set to AUTO mode: F13-HT-433, F13-HT-434, F13-HT-435, F13-HT-436, , F13-PO-445, F13-PO-427, F13-PO-428, F13-PO-429, F13-PO-430, F13-PO-431, F13-PO-434, F13-PO-435, F13-PO-421, F13-PO-422. Individual equipment can be set to Auto without the use of the Local Release Push Button. | 1 | 2025-07-01 | Valve cannot be local. Removed. No action on DCS PL-329
|  |  | HS13662 | HS13662LOC | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Local Panel Local Request Push Button | F13LU413 Local Req Btn | N_Active | Active |  | Hardwired to DCS | - |  | IF HS13662LOC = ACTIVE (One Shot, Rising-Edge Trigger), Prompt CRO: Set "SAG Mill Lubrication System Local Request Pushbutton Activated. Set F13-LU-413 Package to LOCAL mode?" (YES / NO) If YES is selected, set to LOCAL mode: F13-HT-433, F13-HT-434, F13-HT-435, F13-HT-436, , F13-PO-445, F13-PO-427, F13-PO-428, F13-PO-429, F13-PO-430, F13-PO-431, F13-PO-434, F13-PO-435, F13-PO-421, F13-PO-422. Individual equipment can be set to Local without the use of the Local Request Push Button. | 1 | 2025-07-01 | Valve cannot be local. Removed. No action on DCS PL-329
|  |  | HS13625B | HS13625BSTT | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Low Pressure Pump 1 Start Push Button | F13LU413 Brg LP P1 Start | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will start F13-PO-427. | B
|  |  | HS13625C | HS13625CSTP | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Low Pressure Pump 1 Stop Push Button | F13LU413 Brg LP P1 Stop | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will stop F13-PO-427. | B
|  |  | HS13627B | HS13627BSTT | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Low Pressure Pump 2 Start Push Button | F13LU413 Brg LP P2 Strt | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will start F13-PO-428. | B
|  |  | HS13627C | HS13627CSTP | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Low Pressure Pump 2 Stop Push Button | F13LU413 Brg LP P2 Stp | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will stop F13-PO-428. | B
|  |  | HS13652B | HS13652BSTT | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Pinion Bearing Lube Oil Pump 1 Start Push Button | F13LU413 Pin Lbe P1 Strt | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will start F13-PO-434. | B
|  |  | HS13652C | HS13652CSTP | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Pinion Bearing Lube Oil Pump 1 Stop Push Button | F13LU413 Pin Lbe P1 Stop | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will stop F13-PO-434. | B
|  |  | HS13654B | HS13654BSTT | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Pinion Bearing Lube Oil Pump 2 Start Push Button | F13LU413 Pin Lbe P2 Strt | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will start F13-PO-435. | B
|  |  | HS13654C | HS13654CSTP | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Pinion Bearing Lube Oil Pump 2 Stop Push Button | F13LU413 Pin Lbe P2 Stop | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-413 Must be in Local Mode via HS13662LOC. If in LOCAL mode, pressing this PB will stop F13-PO-435. | B
|  |  | HS13678A | HS13678AAUT | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Suction Heaters Test/Auto/Off Selector Switch | F13LU413 Res Htr Auto | N_Active | Active (Automatic) |  | Hardwired to DCS | - |  | 3 Selector switch: Auto / Off / Test AUTO selected: One shot F13-HT-43X to AUT mode | 1 | 2025-07-01 | [5 empty] | LOGIC is OR'ed with Field Auto Group HS13664AUT to switch 13HT43X to AUTO
|  |  | HS13678B | HS13678BOFF | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Suction Heaters Test/Auto/Off Selector Switch | F13LU413 Res Htr Off | N_Active | Active (Off) | Active (Off) | Hardwired to DCS | 0 |  | 3 Selector switch: Auto / Off / Test OFF selected: Causes F13-HT-43X to interlock (see Drives tab) | 1 | 2025-07-01
|  |  | HS13678C | HS13678CTEST | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Suction Heaters Test/Auto/Off Selector Switch | F13LU413 Res Htr Test | N_Active | Active (Test) | Active (Test) | Hardwired to DCS | 0 |  | 3 Selector switch: Auto / Off / Test TEST selected: Set F13-HT-43X = RUNNING | 1 | 2025-06-12 | RE: Sag Mill lube oil heater control
|  |  | KS13596 | KI13596 | 2000-F13-PID-PR-10013 | F13-LU-414 SAG Mill Ring Gear Spray System Gear Spray Panel Timer Switch | F13LU424 MS Spray Pulse | N_Active | Active |  | Hardwired to DCS | - |  | Utilised for F13MS401_C2 (see Misc tab) | A
|  |  | HS13600 | HS13600MAN | 2000-F13-PID-PR-10013 | F13LU414-CP SAG Mill Ring Gear Spray System Control Panel F13LU424 Manual Spray Cycle Push Button | F13LU424 MS Man Spry PB | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | Pressing this PB will initiate F13-SEQ-0020 in all modes (AUTO, MAN, LOCAL) This button can be used to attempt a Spray Cycle on demand to stop F13MS401_T8. | B
|  |  | KS13489 | KI13489 | 2000-F13-PID-PR-10010 | F13-LU-416 SAG Mill Seal Grease System Discharge End Grease Divider (Left Side) Cycle Switch | F13LU416 DE Grse Div. L | N_Active | Active |  | Hardwired to DCS | - |  |  | A
|  |  | KS13490 | KI13490 | 2000-F13-PID-PR-10010 | F13-LU-416 SAG Mill Seal Grease System Discharge End Grease Divider (Right Side) Cycle Switch | F13LU416 DE Grse Div. R | N_Active | Active |  | Hardwired to DCS | - |  |  | A
|  |  | KS13487 | KI13487 | 2000-F13-PID-PR-10010 | F13-LU-416 SAG Mill Seal Grease System Feed End Grease Divider (Left Side) Cycle Switch | F13LU416 FE Grse Div. L | N_Active | Active |  | Hardwired to DCS | - |  |  | A
|  |  | KS13488 | KI13488 | 2000-F13-PID-PR-10010 | F13-LU-416 SAG Mill Seal Grease System Feed End Grease Divider (Right Side) Cycle Switch | F13LU416 FE Grse Div. R | N_Active | Active |  | Hardwired to DCS | - |  |  | A
|  |  | KS13611 | KI13611 | 2000-F13-PID-PR-10013 | F13-LU-416 SAG Mill Seal Grease System SAG Mill Seal Grease Flow Divider Cycle Switch | F13LU416 Divider Pulse | N_Active | Active |  | Hardwired to DCS | - |  |  | A
|  |  | HS13854 | HS13854MAN | 2000-F13-PID-PR-10013 | F13LU416-CP Mills Seal Grease System Control Panel F13LU426 Ball Mill Manual Seal Grease Cycle Pushbutton | F13LU426 MB Man Grse PB | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | Pressing this PB will initiate F13-SEQ-0013 in all modes (AUTO, MAN, LOCAL) This button is used to attempt a Grease Cycle on demand to stop F13MB401_T6. | B
|  |  | HS13604B | HS13604DWN | 2000-F13-PID-PR-10013 | F13LU416-CP Mills Seal Grease System Control Panel Pneumatic Barrel Elevator Selector Switch Lower | F13LU416/426 Elvtr Lower | N_Active | Active |  | Hardwired to DCS | - |  |  | 1 | 2025-04-30 | https://pastech-2955.atlassian.net/browse/KAN-1681
|  |  | HS13604A | HS13604UP | 2000-F13-PID-PR-10013 | F13LU416-CP Mills Seal Grease System Control Panel Pneumatic Barrel Elevator Selector Switch Raise | F13LU416/426 Elvtr Raise | N_Active | Active |  | Hardwired to DCS | - |  |  | 1 | 2025-04-30 | https://pastech-2955.atlassian.net/browse/KAN-1681
|  |  | HS13603 | HS13603MAN | 2000-F13-PID-PR-10013 | F13LU416-CP Mills Seal Grease System Control Panel SAG Mill Manual Seal Grease Cycle Push Button | F13LU416 MS Man Grse PB | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | Pressing this PB will initiate F13-SEQ-0019 in all modes (AUTO, MAN, LOCAL) This button can be used to attempt a Grease Cycle on demand to stop F13MS401_T6. | B
|  |  | PDSHH13816 | PDAHH13816 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Cooling Filter Blocked Pressure Differential High High Switch 2 | F13LU421 LbeFltr 2 Sw HH | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PDSH13816 | PDAH13816 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Cooling Filter Blocked Pressure Differential High Switch 1 | F13LU421 Lbe Fltr 2 Hi | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-04-29 | https://pastech-2955.atlassian.net/browse/KAN-1674 |  |  |  |  | MOC-384 Invert the signal
|  |  | PDSHH13817 | PDAHH13817 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Filter Pressure Differential High High Switch 2 | F13LU421 LbeFltr 1 Sw HH | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PDSH13817 | PDAH13817 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Filter Pressure Differential High Switch 1 | F13LU421 Lbe Fltr 1 Hi | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-04-29 | https://pastech-2955.atlassian.net/browse/KAN-1674 |  |  |  |  | MOC-384 Invert the signal
|  |  | PSL13823 | PAL13823 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Motor 1 Drive End Pressure Switch Low | F13LU421 A Lube Sup. DE | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
|  |  | PSL13824 | PAL13824 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Motor 1 Non-Drive End Pressure Switch | F13LU421 A Lube Sup. NDE | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
|  |  | PSL13825 | PAL13825 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Motor 2 Drive End Pressure Switch | F13LU421 B Lube Sup. DE | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
|  |  | PSL13826 | PAL13826 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Motor 2 Non-Drive End Pressure Switch | F13LU421 B Lube Sup. NDE | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
|  |  | LSL13819 | LAL13819 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Reservoir Level Switch 1 | F13LU421 Lube Res Lvl Lo | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-04-29 | https://pastech-2955.atlassian.net/browse/KAN-1674 |  |  |  |  | MOC-384 Invert the signal [update, reverted MOC-384]
|  |  | LSLL13819 | LALL13819 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Reservoir Level Switch 2 | F13LU421 LubeRes. Lvl LL | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | TSH13820 | TAH13820 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Reservoir Temperature Switch 1 | F13LU421 Lube Res Tmp Hi | Active | N_Active |  | Hardwired to DCS |  |  |  | 1 | 29/04/2025 04/06/2025 | https://pastech-2955.atlassian.net/browse/KAN-1674 https://pastech-2955.atlassian.net/browse/KAN-1984
|  |  | TSL13820 | TAL13820 | 2000-F13-PID-PR-10011 | F13-LU-421 Ball Mill Motors Lubrication Unit Reservoir Temperature Switch 2 | F13LU421 Lube Res Tmp Lo | N_Active | Active |  | Hardwired to DCS |  |  |  | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1674 https://pastech-2955.atlassian.net/browse/KAN-1984
|  |  | ZSC13880 | ZIC13880 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Oil Heat Exchanger Cooling Water Solenoid Limit Switch Closed | TCV13880 Closed | N_Closed | Closed |  | Hardwired to DCS | - |  | Closed position switch for TCV13880 (see Control Valves tab) | 1 | 2025-03-06 | PCT alignment action register (non standard valves defined)
|  |  | ZSO13880 | ZIO13880 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Oil Heat Exchanger Cooling Water Solenoid Limit Switch Opened | TCV13880 Opened | N_Open | Open |  | Hardwired to DCS | - |  | Open position switch for TCV13880 (see Control Valves tab) | 1 | 2025-03-06 | PCT alignment action register (non standard valves defined)
|  |  | XS13201 | XA13201 | 2000-F13-PID-PR-10010 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Alarm | F13LU423 OCM Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 0 | 2025-03-18 | Should be XA not XI
|  |  | HS13968A | HS13968AAUT | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Conditioned Heaters Test/Off/Auto Selector Switch | F13LU423 Cond Htr Auto | N_Active | Active (Automatic) |  | Hardwired to DCS | - |  | 3 Selector switch: Auto / Off / Test AUTO selected: One shot F13-HT-53XX to AUT mode | 1 | 2025-07-01 | [5 empty] | Field switch only has 2 contacts instead of the required 3, electrical is aware and finding out what to do about it. LR 29/04/26 Rewiring has been completed - JM - 30/04/2026
|  |  | HS13968B | HS13968BOFF | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Conditioned Heaters Test/Off/Auto Selector Switch | F13LU423 Cond Htr Off | N_Active | Active (Off) | Active (Off) | Hardwired to DCS | 0 |  | 3 Selector switch: Auto / Off / Test OFF selected: Causes F13-HT-53XX to interlock (see Drives tab) | 1 | 2025-07-01 | [5 empty] | Field switch only has 2 contacts instead of the required 3, electrical is aware and finding out what to do about it. LR 29/04/26 Rewiring has been completed - JM - 30/04/2026
|  |  | HS13968C | HS13968CTEST | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Conditioned Heaters Test/Off/Auto Selector Switch | F13LU423 Cond Htr Test | N_Active | Active (Test) | Active (Test) | Hardwired to DCS | 0 |  | 3 Selector switch: Auto / Off / Test TEST selected: Set F13-HT-53XX = RUNNING | 1 | 2025-06-12 | RE: Sag Mill lube oil heater control |  |  |  |  | Field switch only has 2 contacts instead of the required 3, electrical is aware and finding out what to do about it. LR 29/04/26 Rewiring has been completed - JM - 30/04/2026
|  |  | HS13885B | HS13885BSTT | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel High Pressure Pump 1 Start Push Button | F13LU423 HP P1 Start PB | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will start F13-PO-529. | B
|  |  | HS13885C | HS13885CSTP | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel High Pressure Pump 1 Stop Push Button | F13LU423 HP P1 Stop PB | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will stop F13-PO-529. | B
|  |  | HS13887B | HS13887BSTT | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel High Pressure Pump 2 Start Push Button | F13LU423 HP P2 Start PB | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will start F13-PO-530. | B
|  |  | HS13887C | HS13887CSTP | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel High Pressure Pump 2 Stop Push Button | F13LU423 HP P2 Stop PB | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will stop F13-PO-530. | B
|  |  | HS13889B | HS13889BSTT | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel High Pressure Pump 3 Start Push Button | F13LU423 HP P3 Start PB | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will start F13-PO-531. | B
|  |  | HS13889C | HS13889CSTP | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel High Pressure Pump 3 Stop Push Button | F13LU423 HP P3 Stop PB | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will stop F13-PO-531. | B
|  |  | HS13914 | HS13914TEST | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Local Panel Lamp Test Push Button | F13LU423 Panel Lamp Test | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | Holding down push button will light up all indicators on the F13-LU-423 control panel for testing purposes. Refer to Digital Output tab | B
|  |  | HS13915 | HS13915AUT | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Local Panel Local Release Push Button | F13LU423 Local Rlease PB | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | IF HS13915AUT = ACTIVE (One Shot, Rising-Edge Trigger), Prompt CRO: Set "Ball Mill Lubrication System Local Release Request Pushbutton Activated. Set F13-LU-423 Package to AUTO mode?" (YES / NO) If YES is selected, set to AUTO mode: F13-HT-529, F13-HT-530, F13-HT-531, F13-HT-532, F13-PO-446, F13-PO-527, F13-PO-528, F13-PO-529, F13-PO-530, F13-PO-531, F13-PO-534, F13-PO-535, F13-PO-521, F13-PO-522 Individual equipment can be set to Auto without the use of the Local Release Push Button. | 1 | 2025-07-01 | Valve cannot be local. Removed. No action on DCS PL-328
|  |  | HS13913 | HS13913LOC | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Local Panel Local Request Push Button | F13LU423 Local Req Btn | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | IF HS13913LOC = ACTIVE (One Shot, Rising-Edge Trigger), Prompt CRO: Set "Ball Mill Lubrication System Local Request Pushbutton Activated. Set F13-LU-423 Package to LOCAL mode?" (YES / NO) If YES is selected, set to LOCAL mode: F13-HT-529, F13-HT-530, F13-HT-531, F13-HT-532, F13-PO-446, F13-PO-527, F13-PO-528, F13-PO-529, F13-PO-530, F13-PO-531, F13-PO-534, F13-PO-535, F13-PO-521, F13-PO-522 Individual equipment can be set to Local without the use of the Local Request Push Button. | 1 | 2025-07-01 | Valve cannot be local. Removed. No action on DCS PL-328
|  |  | HS13875B | HS13875BSTT | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Low Pressure Pump 1 Start Push Button | F13LU423 Brg LP P1 Start | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will start F13-PO-527. | B
|  |  | HS13875C | HS13875CSTP | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Low Pressure Pump 1 Stop Push Button | F13LU423 Brg LP P1 Stop | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will stop F13-PO-527. | B
|  |  | HS13877B | HS13877BSTT | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Low Pressure Pump 2 Start Push Button | F13LU423 Brg LP P2 Strt | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will start F13-PO-528. | B
|  |  | HS13877C | HS13877CSTP | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Low Pressure Pump 2 Stop Push Button | F13LU423 Brg LP P2 Stp | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will stop F13-PO-528. | B
|  |  | HS13903B | HS13903BSTT | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Pinion Pump 1 Start Push Button | F13LU423 Pin Lbe P1 Strt | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will start F13-PO-534. | B
|  |  | HS13903C | HS13903CSTP | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Pinion Pump 1 Stop Push Button | F13LU423 Pin Lbe P1 Stop | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will stop F13-PO-534. | B
|  |  | HS13905B | HS13905BSTT | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Pinion Pump 2 Start Push Button | F13LU423 Pin Lbe P2 Strt | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will start F13-PO-535. | B
|  |  | HS13905C | HS13905CSTP | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Pinion Pump 2 Stop Push Button | F13LU423 Pin Lbe P2 Stop | Active (pressed) | N_Active (not pressed) |  | Hardwired to DCS | - |  | F13-LU-423 Must be in Local Mode via HS13915AUT. If in LOCAL mode, pressing this PB will stop F13-PO-535. | B
|  |  | HS13925A | HS13925AAUT | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Reservoir Heater Test/Off/Auto Selector Switch | F13LU423 Res Htr Auto | N_Active | Active (Automatic) |  | Hardwired to DCS | - |  | 3 Selector switch: Auto / Off / Test AUTO selected: One shot F13-HT-53X to AUT mode | 1 | 2025-07-01 | [5 empty] | Field switch only has 2 contacts instead of the required 3, electrical is aware and finding out what to do about it. LR 29/04/26 Rewiring has been completed - JM - 30/04/2026
|  |  | HS13925B | HS13925BOFF | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Reservoir Heater Test/Off/Auto Selector Switch | F13LU423 Res Htr Off | N_Active | Active (Off) | Active (Off) | Hardwired to DCS | 0 |  | 3 Selector switch: Auto / Off / Test OFF selected: Causes F13-HT-F13-HT-53X to interlock (see Drives tab) | 1 | 2025-07-01 | [5 empty] | Field switch only has 2 contacts instead of the required 3, electrical is aware and finding out what to do about it. LR 29/04/26 Rewiring has been completed - JM - 30/04/2026
|  |  | HS13925C | HS13925CTEST | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Reservoir Heater Test/Off/Auto Selector Switch | F13LU423 Res Htr Test | N_Active | Active (Test) | Active (Test) | Hardwired to DCS | 0 |  | 3 Selector switch: Auto / Off / Test TEST selected: Set F13-HT-53X = RUNNING | 1 | 2025-06-12 | RE: Sag Mill lube oil heater control |  |  |  |  | Field switch only has 2 contacts instead of the required 3, electrical is aware and finding out what to do about it. LR 29/04/26 Rewiring has been completed - JM - 30/04/2026
|  |  | KS13847 | KI13847 | 2000-F13-PID-PR-10013 | F13-LU-424 Ball Mill Ring Gear Spray System Gear Spray Panel Timer Switch | F13LU424 MB Spray Pulse | N_Active | Active |  | Hardwired to DCS | - |  | Utilised for F13MB401_C2 (see Misc tab) | A
|  |  | HS13851 | HS13851MAN | 2000-F13-PID-PR-10013 | F13LU424-CP Ball Mill Ring Gear Spray System Control Panel Manual Gear Spray Cycle Pushbutton | F13LU424 MB Man Spry PB | N_Active (not pressed) | Active (pressed) |  | Hardwired to DCS | - |  | Pressing this PB will initiate As per F13-SEQ-0014 in all modes (AUTO, MAN, LOCAL) This button can be used to attempt a Spray Cycle on demand to stop F13MB401_T8. | B
|  |  | KS13862 | KI13862 | 2000-F13-PID-PR-10013 | F13-LU-426 Ball Mill Seal Grease System Ball Mill Seal Grease Flow Divider Cycle Switch | F13LU426 Divider Pulse | N_Active | Active |  | Hardwired to DCS | - |  |  | A
|  |  | KS13493 | KI13493 | 2000-F13-PID-PR-10013 | F13-LU-426 Ball Mill Seal Grease System Discharge End Grease Divider (Left Side) Cycle Switch | F13LU426 DE Grse Div. L | N_Active | Active |  | Hardwired to DCS | - |  |  | A
|  |  | KS13494 | KI13494 | 2000-F13-PID-PR-10013 | F13-LU-426 Ball Mill Seal Grease System Discharge End Grease Divider (Right Side) Cycle Switch | F13LU426 DE Grse Div. R | N_Active | Active |  | Hardwired to DCS | - |  |  | A
|  |  | KS13491 | KI13491 | 2000-F13-PID-PR-10013 | F13-LU-426 Ball Mill Seal Grease System Feed End Grease Divider (Left Side) Cycle Switch | F13LU426 FE Grse Div. L | N_Active | Active |  | Hardwired to DCS | - |  |  | A
|  |  | KS13492 | KI13492 | 2000-F13-PID-PR-10013 | F13-LU-426 Ball Mill Seal Grease System Feed End Grease Divider (Right Side) Cycle Switch | F13LU426 FE Grse Div. R | N_Active | Active |  | Hardwired to DCS | - |  |  | A
|  |  | XS13008 | XA13008 | 2000-F13-PID-PR-10001 | F13-LU-451 Coarse Ore Reclaim Feeder 1 Autolube Grease System End Cycle Position Switch | F13FA411 Lube Cycle | Inactive | Active |  | Hardwired to DCS |  | Mask if F13-LU-451 Not Running | Switch to pulse when Grease Pump (F13-LU-451) is running. Refer to 2000-ME004-M01-10002 for further details. | 1 | 2025-04-30 | https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-295?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
|  |  | LSL13009 | LAL13009 | 2000-F13-PID-PR-10001 | F13-LU-451 Coarse Ore Reclaim Feeder 1 Autolube Grease System Lube Level Switch Low | F13FA411 Lube Level | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | XS13018 | XA13018 | 2000-F13-PID-PR-10001 | F13-LU-452 Coarse Ore Reclaim Feeder 2 Autolube Grease System End Cycle Position Switch | F13FA412 Lube Cycle | Inactive | Active |  | Hardwired to DCS |  | Mask if F13-LU-452 Not Running | Switch to pulse when Grease Pump (F13-LU-452) is running. Refer to 2000-ME004-M01-10002 for further details. | 1 | 2025-04-30 | https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-295?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
|  |  | LSL13019 | LAL13019 | 2000-F13-PID-PR-10001 | F13-LU-452 Coarse Ore Reclaim Feeder 2 Autolube Grease System Lube Level Switch Low | F13FA412 Lube Level | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | XS13028 | XA13028 | 2000-F13-PID-PR-10001 | F13-LU-453 Emergency Feeder Autolube Grease System End Cycle Position Switch | F13FA414 Lube Cycle | Inactive | Active |  | Hardwired to DCS |  | Mask if F13-LU-453 Not Running | Switch to pulse when Grease Pump (F13-LU-453) is running. Refer to 2000-ME004-M01-10003 for further details. | 1 | 2025-04-30 | https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-295?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC |  |  |  |  | masking not tested due to pump not ready
|  |  | LSL13029 | LAL13029 | 2000-F13-PID-PR-10001 | F13-LU-453 Emergency Feeder Autolube Grease System Lube Level Switch Low | F13FA414 Lube Level | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PDSH13981 | PDAH13981 | 2000-F13-PID-PR-10013 | F13-MB-401 Ball Mill Discharge End Trunnion Filter Pressure Differential Switch High 1 | F13MB401 Dsch Trn DP1 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PDSH13982 | PDAH13982 | 2000-F13-PID-PR-10013 | F13-MB-401 Ball Mill Discharge End Trunnion Filter Pressure Differential Switch High 2 | F13MB401 Dsch Trn DP2 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PDSH13983 | PDAH13983 | 2000-F13-PID-PR-10013 | F13-MB-401 Ball Mill Discharge End Trunnion Filter Pressure Differential Switch High 3 | F13MB401 Dsch Trn DP3 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PDSH13984 | PDAH13984 | 2000-F13-PID-PR-10013 | F13-MB-401 Ball Mill Discharge End Trunnion Filter Pressure Differential Switch High 4 | F13MB401 Dsch Trn DP4 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PDSH13985 | PDAH13985 | 2000-F13-PID-PR-10013 | F13-MB-401 Ball Mill Feed End Thrust Bearing Supply Filter Pressure Differential Switch High 1 | F13MB401 Dsch ThrBrg DP1 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-07-07 | CR-018
|  |  | PDSH13986 | PDAH13986 | 2000-F13-PID-PR-10013 | F13-MB-401 Ball Mill Feed End Thrust Bearing Supply Filter Pressure Differential Switch High 2 | F13MB401 Dsch ThrBrg DP2 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-07-07 | CR-018
|  |  | PDSH13987 | PDAH13987 | 2000-F13-PID-PR-10013 | F13-MB-401 Ball Mill Feed End Thrust Bearing Supply Filter Pressure Differential Switch High 3 | F13MB401 Dsch ThrBrg DP3 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-07-07 | CR-018
|  |  | PDSH13988 | PDAH13988 | 2000-F13-PID-PR-10013 | F13-MB-401 Ball Mill Feed End Thrust Bearing Supply Filter Pressure Differential Switch High 4 | F13MB401 Dsch ThrBrg DP4 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-07-07 | CR-018
|  |  | PDSH13977 | PDAH13977 | 2000-F13-PID-PR-10013 | F13-MB-401 Ball Mill Feed End Trunnion Filter Pressure Differential Switch High 1 | F13MB401 Fd Trn DP1 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PDSH13978 | PDAH13978 | 2000-F13-PID-PR-10013 | F13-MB-401 Ball Mill Feed End Trunnion Filter Pressure Differential Switch High 2 | F13MB401 Fd Trn DP2 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PDSH13979 | PDAH13979 | 2000-F13-PID-PR-10013 | F13-MB-401 Ball Mill Feed End Trunnion Filter Pressure Differential Switch High 3 | F13MB401 Fd Trn DP3 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PDSH13980 | PDAH13980 | 2000-F13-PID-PR-10013 | F13-MB-401 Ball Mill Feed End Trunnion Filter Pressure Differential Switch High 4 | F13MB401 Fd Trn DP4 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | MB33KVSTS | MB_33KV_STS | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD 33kV HVCB Feedback | F13MB401 33kV HVCB Posn | Open | Close |  | SoftTag | - |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBCOMALARM | MB_COM_ALARM | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Common Alarm | F13MB401 Common Alarm | Alarm | Normal | Alarm | SoftTag | 3 |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBFAULT | XA13147 | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Common Fault | F13MB401 Common Fault | Alarm | Normal | Alarm | SoftTag | 3 |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | B
|  |  | MBCONVRDY | MB_CONV_RDY | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Converter Ready to Start | F13MB401 Conv. Ready | N_Ready | Ready |  | SoftTag | - |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBFRZNCHRG | MB_FRZN_CHRG | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Frozen Charge Detected | F13MB401 Frozen Charge | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBMINVALM | MB_M_INV_ALM | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Master VSD lnverter Alarm | F13MB401 M.Inverter Alrm | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBMINVFLT | MB_M_INV_FLT | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Master VSD lnverter Fault | F13MB401 M.Inverter Flt | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBESTOP | MB_ESTOP | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Mill Emergency Stop Status | F13MB401 E-Stop | Alarm | Normal | Alarm | SoftTag | 0 |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | 1 | 2025-07-01 | https://pastech-2955.atlassian.net/browse/PL-343
|  |  | MBFUNCFLT | MB_FUNC_FLT | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Mill Function Module | F13MB401 Function Module | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBFUNCALM | MB_FUNC_ALM | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Mill Function Module Alarm | F13MB401 Function Alarm | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBOPMODE | MB_OP_MODE | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Mill in inching mode (Field Selection) | F13MB401 Norm/Inch Mode | Normal | Inching |  | SoftTag | - |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBREADY | MB_READY | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Mill Ready to Start | F13MB401 Ready | N_Ready | Ready |  | SoftTag | - |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBRUNNING | MB_RUNNING | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Mill Running on VSD | F13MB401 Running | N_Running | Running |  | SoftTag | - |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBSTARTING | MB_STARTING | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Mill Starting | F13MB401 Starting | N_Starting | Starting |  | SoftTag | - |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBSTOPPING | MB_STOPPING | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Mill Stopping | F13MB401 Stopping | N_Stopping | Stopping |  | SoftTag | - |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBDCSHBEAT | MB_DCS_HBEAT | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD PLC Heartbeat | F13MB401 PLC Heartbeat | Off | On |  | SoftTag | - |  | Heatbeat Pulse On/Off Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBREMOTE | MB_REMOTE | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Remote mode selected (HMI) | F13MB401 Remote Mode | Local | Remote |  | SoftTag | - |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBSINVALM | MB_S_INV_ALM | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Slave VSD lnverter Alarm | F13MB401 S.Inverter Alrm | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | MBSINVFLT | MB_S_INV_FLT | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Slave VSD lnverter Fault | F13MB401 S.Inverter Flt | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | A
|  |  | XS13204 | XA13204 | 2000-F13-PID-PR-10005 | F13-MD-401 Recycle Crusher Metal Detector Fault Signal | F13MD401 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | XS13202 | XA13202 | 2000-F13-PID-PR-10005 | F13-MD-401 Recycle Crusher Metal Detector Metal Detected Signal | F13MD401 Metal Detect | Alarm (Detected) | Normal | Alarm (Detected) | Hardwired to DCS | 0 |  | When XA13202 is Normal, the Recycle Crusher Bypass Gate remains closed (no bypass). When XA13202 is in the Detected state, the Recycle Crusher Bypass Gate will open to bypass the tramp metal instead of it reporting to the Recycle Crushers. | B
|  |  | XS13182 | XA13182 | 2000-F13-PID-PR-10005 | F13-MG-403 Recycle Crusher Tramp Magnet 1 System Fault | F13MG403 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | States are set electrically by the F13-MG-403 control wiring. Feedback to DCS. | B | [6 empty] | loop tested only, need to revisit the functionality
|  |  | XS13180 | XI13180 | 2000-F13-PID-PR-10005 | F13-MG-403 Recycle Crusher Tramp Magnet 1 System Ready | F13MG403 Ready | N_Active (N_Ready) | Active (Ready) |  | Hardwired to DCS | - |  | States are set electrically by the F13-MG-403 control wiring. Feedback to DCS. | 0 | [6 empty] | loop tested only, need to revisit the functionality
|  |  | XS13181 | XI13181 | 2000-F13-PID-PR-10005 | F13-MG-403 Recycle Crusher Tramp Magnet 1 System Running | F13MG403 Running | N_Active (N_Running) | Active (Running) |  | Hardwired to DCS | - |  | States are set electrically by the F13-MG-403 control wiring. Feedback to DCS. | B | [6 empty] | loop tested only, need to revisit the functionality
|  |  | XS13212 | XA13212 | 2000-F13-PID-PR-10005 | F13-MG-404 Recycle Crusher Tramp Magnet 2 System Fault | F13MG404 Fault | Fault | Normal | Fault | Hardwired to DCS | 3 |  | States are set electrically by the F13-MG-404 control wiring. Feedback to DCS. | B
|  |  | XS13210 | XI13210 | 2000-F13-PID-PR-10005 | F13-MG-404 Recycle Crusher Tramp Magnet 2 System Ready | F13MG404 Ready | N_Active (N_Ready) | Active (Ready) |  | Hardwired to DCS | - |  | States are set electrically by the F13-MG-404 control wiring. Feedback to DCS. | B
|  |  | XS13211 | XI13211 | 2000-F13-PID-PR-10005 | F13-MG-404 Recycle Crusher Tramp Magnet 2 System Running | F13MG404 Running | N_Active (N_Running) | Active (Running) |  | Hardwired to DCS | - |  | States are set electrically by the F13-MG-404 control wiring. Feedback to DCS. | B
|  |  | PDSH13724 | PDAH13724 | 2000-F13-PID-PR-10013 | F13-MS-401 SAG Mill Discharge End Trunnion Filter Pressure Differential Switch High 1 | F13MS401 Dsch Trn DP1 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | Loop has been tested however, DP switch contact to be confirmed
|  |  | PDSH13725 | PDAH13725 | 2000-F13-PID-PR-10013 | F13-MS-401 SAG Mill Discharge End Trunnion Filter Pressure Differential Switch High 2 | F13MS401 Dsch Trn DP2 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | Loop has been tested however, DP switch contact to be confirmed
|  |  | PDSH13726 | PDAH13726 | 2000-F13-PID-PR-10013 | F13-MS-401 SAG Mill Discharge End Trunnion Filter Pressure Differential Switch High 3 | F13MS401 Dsch Trn DP3 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PDSH13727 | PDAH13727 | 2000-F13-PID-PR-10013 | F13-MS-401 SAG Mill Discharge End Trunnion Filter Pressure Differential Switch High 4 | F13MS401 Dsch Trn DP4 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | PDSH13720 | PDAH13720 | 2000-F13-PID-PR-10013 | F13-MS-401 SAG Mill Feed End Trunnion Filter Pressure Differential Switch High 1 | F13MS401 Fd Trn DP1 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | Loop has been tested however, DP switch contact to be confirmed
|  |  | PDSH13721 | PDAH13721 | 2000-F13-PID-PR-10013 | F13-MS-401 SAG Mill Feed End Trunnion Filter Pressure Differential Switch High 2 | F13MS401 Fd Trn DP2 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | Loop has been tested however, DP switch contact to be confirmed
|  |  | PDSH13722 | PDAH13722 | 2000-F13-PID-PR-10013 | F13-MS-401 SAG Mill Feed End Trunnion Filter Pressure Differential Switch High 3 | F13MS401 Fd Trn DP3 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | Loop has been tested however, DP switch contact to be confirmed
|  |  | PDSH13723 | PDAH13723 | 2000-F13-PID-PR-10013 | F13-MS-401 SAG Mill Feed End Trunnion Filter Pressure Differential Switch High 4 | F13MS401 Fd Trn DP4 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B | [6 empty] | Loop has been tested however, DP switch contact to be confirmed
|  |  | PDSH13728 | PDAH13728 | 2000-F13-PID-PR-10013 | F13-MS-401 SAG Mill Feed End Trunnion Thrust Bearing Supply Filter Pressure Differential Switch High 1 | F13MS401 Dsch ThrBrg DP1 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-07-07 | CR-018 |  |  |  |  | Loop has been tested however, DP switch contact to be confirmed
|  |  | PDSH13729 | PDAH13729 | 2000-F13-PID-PR-10013 | F13-MS-401 SAG Mill Feed End Trunnion Thrust Bearing Supply Filter Pressure Differential Switch High 2 | F13MS401 Dsch ThrBrg DP2 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-07-07 | CR-018 |  |  |  |  | Loop has been tested however, DP switch contact to be confirmed
|  |  | PDSH13730 | PDAH13730 | 2000-F13-PID-PR-10013 | F13-MS-401 SAG Mill Feed End Trunnion Thrust Bearing Supply Filter Pressure Differential Switch High 3 | F13MS401 Dsch ThrBrg DP3 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-07-07 | CR-018 |  |  |  |  | Loop has been tested however, DP switch contact to be confirmed
|  |  | PDSH13731 | PDAH13731 | 2000-F13-PID-PR-10013 | F13-MS-401 SAG Mill Feed End Trunnion Thrust Bearing Supply Filter Pressure Differential Switch High 4 | F13MS401 Dsch ThrBrg DP4 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 1 | 2025-07-07 | CR-018 |  |  |  |  | Loop has been tested however, DP switch contact to be confirmed
|  |  | MSSTATUS | MS_STATUS | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill LoadIQ Status | F13MS401 IQ Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From LoadIQ OPC Server. | A
|  |  | MS33KVSTS | MS_33KV_STS | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD 33kV HVCB Feedback | F13MS401 33kV HVCB Posn | Open | Close |  | SoftTag | - |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSCOMALARM | MS_COM_ALARM | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Common Alarm | F13MS401 Common Alarm | Alarm | Normal | Alarm | SoftTag | 3 |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | B
|  |  | MSFAULT | XA13139 | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Common Fault | F13MS401 Common Fault | Alarm | Normal | Alarm | SoftTag | 3 |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | B
|  |  | MSCONVRDY | MS_CONV_RDY | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Converter Ready to Start | F13MS401 Conv. Ready | N_Ready | Ready |  | SoftTag | - |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSFRZNCHRG | MS_FRZN_CHRG | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Frozen Charge Detected | F13MS401 Frozen Charge | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSMINVALM | MS_M_INV_ALM | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Master VSD lnverter Alarm | F13MS401 M.Inverter Alrm | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | 0
|  |  | MSMINVFLT | MS_M_INV_FLT | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Master VSD lnverter Fault | F13MS401 M.Inverter Flt | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSESTOP | MS_ESTOP | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Mill Emergency Stop Status | F13MS401 E-Stop | Alarm | Normal | Alarm | SoftTag | 0 |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | 1 | 2025-07-01 | https://pastech-2955.atlassian.net/browse/PL-343
|  |  | MSFUNCFLT | MS_FUNC_FLT | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Mill Function Module | F13MS401 Function Module | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSFUNCALM | MS_FUNC_ALM | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Mill Function Module Alarm | F13MS401 Function Alarm | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSOPMODE | MS_OP_MODE | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Mill in inching mode (Field Selection) | F13MS401 Norm/Inch Mode | Normal | Inching |  | SoftTag | - |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSREADY | MS_READY | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Mill Ready to Start | F13MS401 Ready | N_Ready | Ready |  | SoftTag | - |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSRUNNING | MS_RUNNING | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Mill Running on VSD | F13MS401 Running | N_Running | Running |  | SoftTag | - |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSSTARTING | MS_STARTING | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Mill Starting | F13MS401 Starting | N_Starting | Starting |  | SoftTag | - |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSSTOPPING | MS_STOPPING | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Mill Stopping | F13MS401 Stopping | N_Stopping | Stopping |  | SoftTag | - |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSDCSHBEAT | MS_DCS_HBEAT | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD PLC Heartbeat | F13MS401 PLC Heartbeat | Off | On |  | SoftTag | - |  | Heatbeat Pulse On/Off Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSREMOTE | MS_REMOTE | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Remote mode selected (HMI) | F13MS401 Remote Mode | Local | Remote |  | SoftTag | - |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSSINVALM | MS_S_INV_ALM | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Slave VSD lnverter Alarm | F13MS401 S.Inverter Alrm | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | MSSINVFLT | MS_S_INV_FLT | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Slave VSD lnverter Fault | F13MS401 S.Inverter Flt | Normal | Alarm | Alarm | SoftTag | 3 |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | A
|  |  | PDSH13014 | PDAH13014 | 2000-F13-PID-PR-10001 | F13-PO-437 Coarse Ore Reclaim Feeder 1 Gearbox Cooler Oil Pump Filter Pressure Differential Switch High | F13FA411 G/box Clr Fltr | Alarm | Normal | Alarm | Hardwired to DCS | 3 | Mask if F13-PO-437 Not Running | Gearbox Cooler Filter Clogging Indicator. Differential pressure is above 1.5 bar. | B
|  |  | PS13156 | PAL13156 | 2000-F13-PID-PR-10001 | F13-PO-437 Coarse Ore Reclaim Feeder 1 Gearbox Cooler Oil Pump Pressure Switch | F13FA411 G/box Clr Pump | Alarm | Normal | Alarm | Hardwired to DCS | 30 | Mask if F13-PO-437 Not Running | Gearbox Oil Cooler Pressure Switch. Oil pump fault. Discharge pressure < 0.7 bar. | 0
|  |  | TS13994 | TSH13994 | 2000-F13-PID-PR-10001 | F13-PO-437 Coarse Ore Reclaim Feeder 1 Gearbox Cooler Oil Pump Pressure Switch | F13FA411 G/box Clr Temp | Active | N_Active |  | Hardwired to DCS | - |  | Apron Feeder Cooler Temperature Switch. When activated, air-oil cooler fan will switch on (at temperatures greater than 50C). Fan will switch off when temperature is < 35C. Source: 2000-ME004-M01-10002. | B
|  |  | PDSH13024 | PDAH13024 | 2000-F13-PID-PR-10001 | F13-PO-438 Coarse Ore Reclaim Feeder 2 Gearbox Cooler Oil Pump Filter Pressure Differential Switch High | F13FA412 G/box Clr Fltr | Alarm | Normal | Alarm | Hardwired to DCS | 3 | Mask if F13-PO-438 Not Running | Gearbox Cooler Filter Clogging Indicator. Differential pressure is above 1.5 bar. | B | [6 empty] | masking not tested due to pump not ready
|  |  | PS13159 | PAL13159 | 2000-F13-PID-PR-10001 | F13-PO-438 Coarse Ore Reclaim Feeder 2 Gearbox Cooler Oil Pump Pressure Switch | F13FA412 G/box Clr Pump | Alarm | Normal | Alarm | Hardwired to DCS | 30 | Mask if F13-PO-438 Not Running | Gearbox Oil Cooler Pressure Switch. Oil pump fault. Discharge pressure < 0.7 bar. | 0 | [6 empty] | masking not tested due to pump not ready
|  |  | PDSH13034 | PDAH13034 | 2000-F13-PID-PR-10001 | F13-PO-439 Emergency Feeder 2 Gearbox Cooler Oil Pump Filter Pressure Differential Switch High | F13FA414 G/box Clr Fltr | Alarm | Normal | Alarm | Hardwired to DCS | 3 | Mask if F13-PO-439 Not Running | Gearbox Cooler Filter Clogging Indicator. Differential pressure is above 1.5 bar. | B | [6 empty] | masking not tested due to pump not ready
|  |  | PS13162 | PAL13162 | 2000-F13-PID-PR-10001 | F13-PO-439 Emergency Feeder 2 Gearbox Cooler Oil Pump Pressure Switch | F13FA414 G/box Clr Pump | Alarm | Normal | Alarm | Hardwired to DCS | 30 | Mask if F13-PO-439 Not Running | Gearbox Oil Cooler Pressure Switch. Oil pump fault. Discharge pressure < 0.7 bar. | 0
|  |  | SSL13863 | SAL13863 | 2000-F13-PID-PR-10011 | F13-PO-529 BALL MILL HIGH PRESSURE LUBE PUMP 1 Motor Underspeed Switch | F13LU423 HP Lube P1 U/S | Alarm | Normal | Alarm | Hardwired to DCS | 10 | F13-PO-529 Not Running Mask for 60 seconds (TBC) on F13-PO-529 start-up | Speed monitoring from instrument (signal active when underspeed) Alarm masking duration to be confirmed during commissioning. | 0
|  |  | SSL13864 | SAL13864 | 2000-F13-PID-PR-10011 | F13-PO-530 BALL MILL HIGH PRESSURE LUBE PUMP 2 Motor Underspeed Switch | F13LU423 HP Lube P2 U/S | Alarm | Normal | Alarm | Hardwired to DCS | 10 | F13-PO-530 Not Running Mask for 60 seconds (TBC) on F13-PO-530 start-up | Speed monitoring from instrument (signal active when underspeed) Alarm masking duration to be confirmed during commissioning. | 0
|  |  | SSL13865 | SAL13865 | 2000-F13-PID-PR-10011 | F13-PO-531 BALL MILL HIGH PRESSURE LUBE PUMP 3 Motor Underspeed Switch | F13LU423 HP Lube P3 U/S | Alarm | Normal | Alarm | Hardwired to DCS | 10 | F13-PO-531 Not Running Mask for 60 seconds (TBC) on F13-PO-531 start-up | Speed monitoring from instrument (signal active when underspeed) Alarm masking duration to be confirmed during commissioning. | 0
|  |  | FSL13465 | FAL13465 | 2000-F13-PID-PR-10007 | F13-PP-403 Trash Dewatering Screen Underflow Pump Gland Water Flow Switch | F13PP403 Flow Switch | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-PP-403 Not Running |  | B
|  |  | LSH13064 | LAH13064 | 2000-F13-PID-PR-10001 | F13-PS-402 Coarse Ore Stockpile 2 Sump Pump Level Switch High | F13PS402 Level | Normal | Alarm | Alarm | SoftTag | 3 |  |  | B
|  |  | LSH13209 | LAH13209 | 2000-F13-PID-PR-10005 | F13-PS-403 Recycle Crusher Area Sump Pump Level Switch High | F13PS403 Level | Normal | Alarm | Alarm | SoftTag | 3 |  |  | B
|  |  | LSH13131 | LAH13131 | 2000-F13-PID-PR-10003 | F13-PS-405 Mill Feed End Sump Pump Level Switch High | F13PS405 Level | Normal | Alarm | Alarm | SoftTag | 3 |  |  | B
|  |  | LSH13385 | LAH13385 | 2000-F13-PID-PR-10007 | F13-PS-409 Trash Screen Area Sump Pump 1 Level Switch High | F13PS409 Level | Normal | Alarm | Alarm | SoftTag | 3 |  |  | B
|  |  | ZSC13423 | ZIC13423 | 2000-F13-PID-PR-10012 | F13-PW-413 Cooling Water Pump 1 Discharge Valve Position Switch Closed | F13PW413 Discharge Close | N_Closed | Closed |  | Hardwired to DCS | - |  | HV13423 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches) |  |  |  |  | Compared against OnOff Valve tab. BAH signed off
|  |  | ZSO13423 | ZIO13423 | 2000-F13-PID-PR-10012 | F13-PW-413 Cooling Water Pump 1 Discharge Valve Position Switch Opened | F13PW413 Discharge Open | N_Open | Open |  | Hardwired to DCS | - |  | HV13423 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches) |  |  |  |  | Compared against OnOff Valve tab. BAH signed off
|  |  | ZSC13422 | ZIC13422 | 2000-F13-PID-PR-10012 | F13-PW-413 Cooling Water Pump 1 Suction Valve Position Switch Closed | F13PW413 Suction Close | N_Closed | Closed |  | Hardwired to DCS | - |  | HV13422 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches) |  |  |  |  | Compared against OnOff Valve tab. BAH signed off
|  |  | ZSO13422 | ZIO13422 | 2000-F13-PID-PR-10012 | F13-PW-413 Cooling Water Pump 1 Suction Valve Position Switch Opened | F13PW413 Suction Open | N_Open | Open |  | Hardwired to DCS | - |  | HV13422 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches) |  |  |  |  | Compared against OnOff Valve tab. BAH signed off
|  |  | FSLL13436 | FALL13436 | 2000-F13-PID-PR-10012 | F13-PW-413/413 Cooling Water Pump 1/2 Discharge Flow Switch Low Low | F13PW413/414 Flow LL | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-PW-413 AND F13-PW-414 Not Running Mask for 10 seconds on F13-PW-413 OR 414 start |  | B
|  |  | ZSC13425 | ZIC13425 | 2000-F13-PID-PR-10012 | F13-PW-414 Cooling Water Pump 2 Discharge Valve Position Switch Closed | F13PW414 Discharge Close | N_Closed | Closed |  | Hardwired to DCS | - |  | HV13425 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches) |  |  |  |  | Compared against OnOff Valve tab. BAH signed off
|  |  | ZSO13425 | ZIO13425 | 2000-F13-PID-PR-10012 | F13-PW-414 Cooling Water Pump 2 Discharge Valve Position Switch Opened | F13PW414 Discharge Open | N_Open | Open |  | Hardwired to DCS | - |  | HV13425 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches) |  |  |  |  | Compared against OnOff Valve tab. BAH signed off
|  |  | ZSC13424 | ZIC13424 | 2000-F13-PID-PR-10012 | F13-PW-414 Cooling Water Pump 2 Suction Valve Position Switch Closed | F13PW414 Suction Close | N_Closed | Closed |  | Hardwired to DCS | - |  | HV13424 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches) |  |  |  |  | Compared against OnOff Valve tab. BAH signed off
|  |  | ZSO13424 | ZIO13424 | 2000-F13-PID-PR-10012 | F13-PW-414 Cooling Water Pump 2 Suction Valve Position Switch Opened | F13PW414 Suction Open | N_Open | Open |  | Hardwired to DCS | - |  | HV13424 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches) |  |  |  |  | Compared against OnOff Valve tab. BAH signed off
|  |  | ZSC13432 | ZIC13432 | 2000-F13-PID-PR-10012 | F13-PW-415 Chiller Recirculating Water Pump 1 Discharge Valve Position Switch Closed | F13PW415 Discharge Close | N_Closed | Closed |  | Hardwired to DCS | - |  | HV13432 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | ZSO13432 | ZIO13432 | 2000-F13-PID-PR-10012 | F13-PW-415 Chiller Recirculating Water Pump 1 Discharge Valve Position Switch Opened | F13PW415 Discharge Open | N_Open | Open |  | Hardwired to DCS | - |  | HV13432 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | ZSC13431 | ZIC13431 | 2000-F13-PID-PR-10012 | F13-PW-415 Chiller Recirculating Water Pump 1 Suction Valve Position Switch Closed | F13PW415 Suction Close | N_Closed | Closed |  | Hardwired to DCS | - |  | HV13431 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | ZSO13431 | ZIO13431 | 2000-F13-PID-PR-10012 | F13-PW-415 Chiller Recirculating Water Pump 1 Suction Valve Position Switch Opened | F13PW415 Suction Open | N_Open | Open |  | Hardwired to DCS | - |  | HV13431 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | FSLL13435 | FALL13435 | 2000-F13-PID-PR-10012 | F13-PW-415/416 Chiller Recirculating Pump 1/2 Discharge Flow Switch Low Low | F13PW415/416 Flow LL | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-PW-415 AND F13-PW-416 Not Running Mask for 10 seconds on F13-PW-415 OR 416 start |  | B
|  |  | ZSC13434 | ZIC13434 | 2000-F13-PID-PR-10012 | F13-PW-416 Chiller Recirculating Water Pump 2 Discharge Valve Position Switch Closed | F13PW416 Discharge Close | N_Closed | Closed |  | Hardwired to DCS | - |  | HV13434 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | ZSO13434 | ZIO13434 | 2000-F13-PID-PR-10012 | F13-PW-416 Chiller Recirculating Water Pump 2 Discharge Valve Position Switch Opened | F13PW416 Discharge Open | N_Open | Open |  | Hardwired to DCS | - |  | HV13434 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | ZSC13433 | ZIC13433 | 2000-F13-PID-PR-10012 | F13-PW-416 Chiller Recirculating Water Pump 2 Suction Valve Position Switch Closed | F13PW416 Suction Close | N_Closed | Closed |  | Hardwired to DCS | - |  | HV13433 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | ZSO13433 | ZIO13433 | 2000-F13-PID-PR-10012 | F13-PW-416 Chiller Recirculating Water Pump 2 Suction Valve Position Switch Opened | F13PW416 Suction Open | N_Open | Open |  | Hardwired to DCS | - |  | HV13433 See On/Off tab | 1 | 2025-03-06 | PCT alignment action register (man valves with posn switches)
|  |  | F13RIO001PS1 | F13RIO001_PS1 | N/A | F13-RIO-001 PS1 24VDC HEALTHY | F13RIO001 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO001PS2 | F13RIO001_PS2 | N/A | F13-RIO-001 PS2 24VDC HEALTHY | F13RIO001 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO011PS1 | F13RIO011_PS1 | N/A | F13-RIO-011 PS1 24VDC HEALTHY | F13RIO011 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO011PS2 | F13RIO011_PS2 | N/A | F13-RIO-011 PS2 24VDC HEALTHY | F13RIO011 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO012PS1 | F13RIO012_PS1 | N/A | F13-RIO-012 PS1 24VDC HEALTHY | F13RIO012 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO012PS2 | F13RIO012_PS2 | N/A | F13-RIO-012 PS2 24VDC HEALTHY | F13RIO012 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO013PS1 | F13RIO013_PS1 | N/A | F13-RIO-013 PS1 24VDC HEALTHY | F13RIO013 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO013PS2 | F13RIO013_PS2 | N/A | F13-RIO-013 PS2 24VDC HEALTHY | F13RIO013 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO021PS1 | F13RIO021_PS1 | N/A | F13-RIO-021 PS1 24VDC HEALTHY | F13RIO021 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO021PS2 | F13RIO021_PS2 | N/A | F13-RIO-021 PS2 24VDC HEALTHY | F13RIO021 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO022PS1 | F13RIO022_PS1 | N/A | F13-RIO-022 PS1 24VDC HEALTHY | F13RIO022 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO022PS2 | F13RIO022_PS2 | N/A | F13-RIO-022 PS2 24VDC HEALTHY | F13RIO022 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO031PS1 | F13RIO031_PS1 | N/A | F13-RIO-031 PS1 24VDC HEALTHY | F13RIO031 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO031PS2 | F13RIO031_PS2 | N/A | F13-RIO-031 PS2 24VDC HEALTHY | F13RIO031 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO032PS1 | F13RIO032_PS1 | N/A | F13-RIO-032 PS1 24VDC HEALTHY | F13RIO032 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO032PS2 | F13RIO032_PS2 | N/A | F13-RIO-032 PS2 24VDC HEALTHY | F13RIO032 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO041PS1 | F13RIO041_PS1 | N/A | F13-RIO-041 PS1 24VDC HEALTHY | F13RIO041 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO041PS2 | F13RIO041_PS2 | N/A | F13-RIO-041 PS2 24VDC HEALTHY | F13RIO041 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO042PS1 | F13RIO042_PS1 | N/A | F13-RIO-042 PS1 24VDC HEALTHY | F13RIO042 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO042PS2 | F13RIO042_PS2 | N/A | F13-RIO-042 PS2 24VDC HEALTHY | F13RIO042 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO051PS1 | F13RIO051_PS1 | N/A | F13-RIO-051 PS1 24VDC HEALTHY | F13RIO051 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13RIO051PS2 | F13RIO051_PS2 | N/A | F13-RIO-051 PS2 24VDC HEALTHY | F13RIO051 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | FSL13364 | FAL13364 | 2000-F13-PID-PR-10007 | F13-SC-403 Trash Dewatering Screen Sprays Flow Switch | F13SC403 Spray Flow | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-SC-403 Not Running |  | B | [6 empty] | checked historical, toggling
|  |  | FSH13207 | FAH13207 | 2000-F24-PID-PR-10005 | F13-SE-404 GROUND FLOOR ILR SAFETY SHOWER | F13SE404 Alarm | Alarm | Normal | Alarm | Hardwired | 30 |  | tested by simulating, no actual water in the field | 1 | 2025-07-01 | CR-019
|  |  | FSH13208 | FAH13208 | 2000-F24-PID-PR-10005 | F13-SE-408 MILL DECK SAFETY SHOWER | F13SE408 Alarm | Alarm | Normal | Alarm | Hardwired | 30 |  |  | 1 | 2025-07-01 | CR-019
|  |  | BDS13367A | BDA13367A | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Cloth Track Belt Drift Switch LHS Alarm | F13SL401 Drift LHS Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-401 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-401 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
|  |  | BDS13367C | BDA13367C | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Cloth Track Belt Drift Switch LHS Trip | F13SL401 Drift LHS Trip | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-401 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-401 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
|  |  | BDS13367B | BDA13367B | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Cloth Track Belt Drift Switch RHS Alarm | F13SL401 Drift RHS Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-401 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-401 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
|  |  | BDS13367D | BDA13367D | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Cloth Track Belt Drift Switch RHS Trip | F13SL401 Drift RHS Trip | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-401 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-401 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
|  |  | PSL13370 | PAL13370 | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Cloth Wash (Standby) Pressure Switch Low | F13SL401 PW Sprays Lo | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-SL-401 Not Running | Allow 10 s alarm delay for trash screen start-up | B | [6 empty] | VV 02/06/2026. As per Tech Misha socket is broken on the pressure switch body. To revisit
|  |  | PSL13368 | PAL13368 | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Cloth Wash (Working) Pressure Switch Low | F13SL401 PW Sprays Lo | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-SL-401 Not Running | Allow 10 s alarm delay for trash screen start-up | B
|  |  | PSL13369 | PAL13369 | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Instrument Air Pressure Switch Low | F13SL401 Instr. Air Lo | Alarm | Normal | Alarm | Hardwired to DCS | 300 | F13-SL-401 Not Running | Alarm delay as per 2000-ME018-M01-10001 | B
|  |  | PWS13365C | PWA13365C | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Pull-Wire Switch LHS Lower | F13SL401 PW Lower LHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237
|  |  | PWS13365A | PWA13365A | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Pull-Wire Switch LHS Upper | F13SL401 PW Upper LHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354, MOC-237
|  |  | PWS13365D | PWA13365D | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Pull-Wire Switch RHS Lower | F13SL401 PW Lower RHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237
|  |  | PWS13365B | PWA13365B | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Pull-Wire Switch RHS Upper | F13SL401 PW Upper RHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237
|  |  | SSL13366 | SAL13366 | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Tail Pulley Underspeed Switch | F13SL401 Underspeed | Inactive | Active | Alarm (see Comments) | Hardwired to DCS | 3 | 1. F13-SL-401 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-401 start-up |  | 1 | 6/03/2025 26/06/2025 | https://pastech-2955.atlassian.net/browse/KAN-1390 Updated comments to includeTBC required inputs to RPM logic |  |  |  |  | JM - Loop check only Pulse and Underspeed alarm settings to TBC when vendor is on site
|  |  | BDS13377A | BDA13377A | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Cloth Track Belt Drift Switch LHS Alarm | F13SL402 Drift LHS Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-402 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-402 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 |  |  |  |  | Digital input good. Need to check alarm function PH 12/08/2026 |  | MSH checked alarm function on FCS 20/08
|  |  | BDS13377C | BDA13377C | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Cloth Track Belt Drift Switch LHS Trip | F13SL402 Drift LHS Trip | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-402 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-402 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 |  |  |  |  | Digital input good. Need to check alarm function PH 12/08/2026 |  | MSH checked alarm function on FCS 20/08
|  |  | BDS13377B | BDA13377B | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Cloth Track Belt Drift Switch RHS Alarm | F13SL402 Drift RHS Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-402 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-402 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 |  |  |  |  | Digital input good. Need to check alarm function PH 12/08/2026 |  | MSH checked alarm function on FCS 20/08
|  |  | BDS13377D | BDA13377D | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Cloth Track Belt Drift Switch RHS Trip | F13SL402 Drift RHS Trip | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-402 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-402 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 |  |  |  |  | Digital input good. Need to check alarm function PH 12/08/2026 |  | MSH checked alarm function on FCS 20/08
|  |  | PSL13380 | PAL13380 | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Cloth Wash (Standby) Pressure Switch Low | F13SL402 PW Sprays Lo | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-SL-402 Not Running | Allow 10 s alarm delay for trash screen start-up | B
|  |  | PSL13378 | PAL13378 | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Cloth Wash (Working) Pressure Switch Low | F13SL402 PW Sprays Lo | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-SL-402 Not Running | Allow 10 s alarm delay for trash screen start-up | B
|  |  | PSL13379 | PAL13379 | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Instrument Air Pressure Switch Low | F13SL402 Instr. AirLo | Alarm | Normal | Alarm | Hardwired to DCS | 300 | F13-SL-402 Not Running | Alarm delay as per 2000-ME018-M01-10001 | B
|  |  | PWS13375C | PWA13375C | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Pull-Wire Switch LHS Lower | F13SL402 PW Lower LHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237 Reverted
|  |  | PWS13375A | PWA13375A | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Pull-Wire Switch LHS Upper | F13SL402 PW Upper LHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237 Reverted
|  |  | PWS13375D | PWA13375D | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Pull-Wire Switch RHS Lower | F13SL402 PW Lower RHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237 Reverted
|  |  | PWS13375B | PWA13375B | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Pull-Wire Switch RHS Upper | F13SL402 PW Upper RHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237 Reverted
|  |  | SSL13376 | SAL13376 | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Tail Pulley Underspeed Switch | F13SL402 Underspeed | Inactive | Active | Alarm (see Comments) | Hardwired to DCS | 3 | 1. F13-SL-402 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-402 start-up | Speed monitoring from DCS (signal active per rotation) Alarm to activate on 'zero speed'. Estimate as < 0.1RPM (TBC during commissioning) SSL13376HZ Pulse Rate at full speed to be confirmed during commissioning SSL13376 Conversion Gain to be confirmed during commissioning (Hz to RPM conversion) Alarm masking duration to be confirmed during commissioning. | 1 | 6/03/2025 26/06/2025 | https://pastech-2955.atlassian.net/browse/KAN-1390 Updated comments to includeTBC required inputs to RPM logic |  |  |  |  | JM - Loop check only Pulse and Underspeed alarm settings to TBC when vendor is on site
|  |  | BDS13397A | BDA13397A | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Cloth Track Belt Drift Switch LHS Alarm | F13SL403 Drift LHS Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-403 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-403 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
|  |  | BDS13397C | BDA13397C | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Cloth Track Belt Drift Switch LHS Trip | F13SL403 Drift LHS Trip | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-403 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-403 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
|  |  | BDS13397B | BDA13397B | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Cloth Track Belt Drift Switch RHS Alarm | F13SL403 Drift RHS Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-403 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-403 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
|  |  | BDS13397D | BDA13397D | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Cloth Track Belt Drift Switch RHS Trip | F13SL403 Drift RHS Trip | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-403 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-403 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
|  |  | PSL13400 | PAL13400 | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Cloth Wash (Standby) Pressure Switch Low | F13SL403 PW Sprays Lo | Active | Normal | Active | Hardwired to DCS | 3 | F13-SL-403 Not Running | Allow 10 s alarm delay for trash screen start-up | B
|  |  | PSL13398 | PAL13398 | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Cloth Wash (Working) Pressure Switch Low | F13SL403 PW Sprays Lo | Active | Normal | Active | Hardwired to DCS | 3 | F13-SL-403 Not Running | Allow 10 s alarm delay for trash screen start-up | B
|  |  | PSL13399 | PAL13399 | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Instrument Air Pressure Switch Low | F13SL403 Instr. Air Lo | Active | Normal | Active | Hardwired to DCS | 300 | F13-SL-403 Not Running | Alarm delay as per 2000-ME018-M01-10001 | B
|  |  | PWS13395C | PWA13395C | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Pull-Wire Switch LHS Lower | F13SL403 PW Lower LHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237(Reverted)
|  |  | PWS13395A | PWA13395A | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Pull-Wire Switch LHS Upper | F13SL403 PW Upper LHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237(Reverted)
|  |  | PWS13395D | PWA13395D | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Pull-Wire Switch RHS Lower | F13SL403 PW Lower RHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237(Reverted)
|  |  | PWS13395B | PWA13395B | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Pull-Wire Switch RHS Upper | F13SL403 PW Upper RHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237(Reverted)
|  |  | SSL13396 | SAL13396 | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Tail Pulley Underspeed Switch | F13SL403 Underspeed | Inactive | Active | Alarm (see Comments) | Hardwired to DCS | 3 | 1. F13-SL-403 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-403 start-up | Speed monitoring from DCS (signal active per rotation) Alarm to activate on 'zero speed'. Estimate as < 0.1RPM (TBC during commissioning) SSL13396HZ Pulse Rate at full speed to be confirmed during commissioning SSL13396 Conversion Gain to be confirmed during commissioning (Hz to RPM conversion) Alarm masking duration to be confirmed during commissioning. | 1 | 6/03/2025 26/06/2025 | https://pastech-2955.atlassian.net/browse/KAN-1390 Updated comments to includeTBC required inputs to RPM logic |  |  |  |  | JM - Loop check only Pulse and Underspeed alarm settings to TBC when vendor is on site
|  |  | BDS13407A | BDA13407A | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Cloth Track Belt Drift Switch LHS Alarm | F13SL404 Drift LHS Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-404 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-404 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
|  |  | BDS13407C | BDA13407C | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Cloth Track Belt Drift Switch LHS Trip | F13SL404 Drift LHS Trip | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-404 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-404 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
|  |  | BDS13407B | BDA13407B | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Cloth Track Belt Drift Switch RHS Alarm | F13SL404 Drift RHS Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-404 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-404 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
|  |  | BDS13407D | BDA13407D | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Cloth Track Belt Drift Switch RHS Trip | F13SL404 Drift RHS Trip | Alarm | Normal | Alarm | Hardwired to DCS | 3 | 1. F13-SL-404 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-404 start-up |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
|  |  | PSL13394 | PAL13394 | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Cloth Wash (Standby) Pressure Switch Low | F13SL404 PW Sprays Lo | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-SL-404 Not Running | Allow 10 s alarm delay for trash screen start-up | B
|  |  | PSL13408 | PAL13408 | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Cloth Wash (Working) Pressure Switch Low | F13SL404 PW Sprays Lo | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F13-SL-404 Not Running | Allow 10 s alarm delay for trash screen start-up | B |  | MOC may be required for masking logic for this pressure switch upon trash screen start up. This is how the alarm is configured and there should also be interlock masking otherwise you will never be healthy to start the screen
|  |  | PSL13404 | PAL13404 | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Instrument Air Pressure Switch Low | F13SL404 Instr. Air Lo | Alarm | Normal | Alarm | Hardwired to DCS | 300 | F13-SL-404 Not Running | Alarm delay as per 2000-ME018-M01-10001 | B
|  |  | PWS13405C | PWA13405C | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Pull-Wire Switch LHS Lower | F13SL404 PW Lower LHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237 (Reverted)
|  |  | PWS13405A | PWA13405A | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Pull-Wire Switch LHS Upper | F13SL404 PW Upper LHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237 (Reverted)
|  |  | PWS13405D | PWA13405D | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Pull-Wire Switch RHS Lower | F13SL404 PW Lower RHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237 (Reverted)
|  |  | PWS13405B | PWA13405B | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Pull-Wire Switch RHS Upper | F13SL404 PW Upper RHS | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354 , MOC-237 (Reverted)
|  |  | SSL13406 | SAL13406 | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Tail Pulley Underspeed Switch | F13SL404 Underspeed | Inactive | Active | Alarm (see Comments) | Hardwired to DCS | 3 | 1. F13-SL-404 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-404 start-up | Speed monitoring from DCS (signal active per rotation) Alarm to activate on 'zero speed'. Estimate as < 0.1RPM (TBC during commissioning) SSL13406HZ Pulse Rate at full speed to be confirmed during commissioning SSL13406 Conversion Gain to be confirmed during commissioning (Hz to RPM conversion) Alarm masking duration to be confirmed during commissioning. | 1 | 6/03/2025 26/06/2025 | https://pastech-2955.atlassian.net/browse/KAN-1390 Updated comments to includeTBC required inputs to RPM logic |  |  |  |  | JM - Loop check only Pulse and Underspeed alarm settings to TBC when vendor is on site
|  |  | F13SR001ESTP | F13SR001_ESTP | N/A | F13-SR-001 SWITCHROOM EMERGENCY SHUTDOWN DCS INPUT | F13SR001 SR ESHUT DCS IN | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SR002ESTP | F13SR002_ESTP | N/A | F13-SR-002 SWITCHROOM EMERGENCY SHUTDOWN DCS INPUT | F13SR002 SR ESHUT DCS IN | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-04-16
|  |  | F13SR003ESTP | F13SR003_ESTP | N/A | F13-SR-003 SWITCHROOM EMERGENCY SHUTDOWN DCS INPUT | F13SR003 SR ESHUT DCS IN | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SR005ESTP | F13SR005_ESTP | N/A | F13-SR-005 SWITCHROOM EMERGENCY SHUTDOWN DCS INPUT | F13SR005 SR ESHUT DCS IN | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SR004ESTP | F13SR004_ESTP | N/A | F13-SR-014 SWITCHROOM EMERGENCY SHUTDOWN DCS INPUT | F13SR014 SR ESHUT DCS IN | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SW002PS | F13SW002_PS | N/A | F13-SW-002 ACB SHUNT TRIP 24VDC OK | F13SW002 ACBShunt 24V OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | WIP | 2025-10-23 | 24VD added to description
|  |  | F13SW002AF | F13SW002_AF | N/A | F13-SW-002 ARC FLASH DETECTION SYSTEM ALARM | F13SW002 ARC FLASH | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-28 | MOC-125
|  |  | F13SW002CL | F13SW002_CL | N/A | F13-SW-002 CIRCUIT BREAKER CLOSED | F13SW002 C BREAKER CLOSE | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW002OP | F13SW002_OP | N/A | F13-SW-002 CIRCUIT BREAKER OPENED | F13SW002 C BREAKER OPEN | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW002TRP | F13SW002_TRP | N/A | F13-SW-002 CIRCUIT BREAKER TRIPPED | F13SW002 C BREAKER TRIP | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-28 | MOC-125
|  |  | F13SW002SD | F13SW002_SD | N/A | F13-SW-002 INCOMER SURGE DIVERTER OK | F13SW002 INC SURGE DIV | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-28 | MOC-125
|  |  | F13SW002PS1 | F13SW002_PS1 | N/A | F13-SW-002 PS1 24VDC HEALTHY | F13SW002 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SW002PS2 | F13SW002_PS2 | N/A | F13-SW-002 PS2 24VDC HEALTHY | F13SW002 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SW003PS | F13SW003_PS | N/A | F13-SW-003 ACB SHUNT TRIP 24VDC OK | F13SW003 ACBShunt 24V OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | WIP | 2025-10-23 | 24V added to description
|  |  | F13SW003AF | F13SW003_AF | N/A | F13-SW-003 ARC FLASH DETECTION SYSTEM ALARM | F13-SW-003 ARC FLASH | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-28 | MOC-125
|  |  | F13SW003CL | F13SW003_CL | N/A | F13-SW-003 CIRCUIT BREAKER CLOSED | F13SW003 C BREAKER CLOSE | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW003OP | F13SW003_OP | N/A | F13-SW-003 CIRCUIT BREAKER OPENED | F13SW003 C BREAKER OPEN | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW003TRP | F13SW003_TRP | N/A | F13-SW-003 CIRCUIT BREAKER TRIPPED | F13SW003 C BREAKER TRIP | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-28 | MOC-125
|  |  | F13SW003SD | F13SW003_SD | N/A | F13-SW-003 INCOMER SURGE DIVERTER OK | F13SW003 INC SURGE DIV | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-28 | MOC-125
|  |  | F13SW003PS1 | F13SW003_PS1 | N/A | F13-SW-003 PS1 24VDC HEALTHY | F13SW003 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SW003PS2 | F13SW003_PS2 | N/A | F13-SW-003 PS2 24VDC HEALTHY | F13SW003 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SW014PS | F13SW014_PS | N/A | F13-SW-014 ACB SHUNT TRIP 24VDC OK | F13SW014 ACBShunt 24V OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | WIP | 2025-10-23 | Add 24V to description
|  |  | F13SW014AF | F13SW014_AF | N/A | F13-SW-014 ARC FLASH DETECTION SYSTEM ALARM | F13-SW-014 ARC FLASH | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  | Wiring changed in field, signal not tested yet (JM 29/03/2026) | B | 2026-02-28 | MOC-125
|  |  | F13SW014CL | F13SW014_CL | N/A | F13-SW-014 CIRCUIT BREAKER CLOSED | F13SW014 C BREAKER CLOSE | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW014OP | F13SW014_OP | N/A | F13-SW-014 CIRCUIT BREAKER OPENED | F13SW014 C BREAKER OPEN | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW014TRP | F13SW014_TRP | N/A | F13-SW-014 CIRCUIT BREAKER TRIPPED | F13SW014 C BREAKER TRIP | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-28 | MOC-125
|  |  | F13SW014SD | F13SW014_SD | N/A | F13-SW-014 INCOMER SURGE DIVERTER OK | F13SW014 INC SURGE DIVOK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-28 | MOC-125
|  |  | F13SW014PS1 | F13SW014_PS1 | N/A | F13-SW-014 PS1 24VDC HEALTHY | F13SW014 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SW014PS2 | F13SW014_PS2 | N/A | F13-SW-014 PS2 24VDC HEALTHY | F13SW014 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SW020PS | F13SW020_PS | N/A | F13-SW-020 ACB SHUNT TRIP 24VDC OK | F13SW020 ACBShunt 24V OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | WIP | 2025-10-23 | description
|  |  | F13SW020AF | F13SW020_AF | N/A | F13-SW-020 ARC FLASH DETECTION SYSTEM ALARM | F13-SW-020 ARC FLASH | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-28 | MOC-125
|  |  | F13SW020CL | F13SW020_CL | N/A | F13-SW-020 CIRCUIT BREAKER CLOSED | F13SW020 C BREAKER CLOSE | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW020OP | F13SW020_OP | N/A | F13-SW-020 CIRCUIT BREAKER OPENED | F13SW020 C BREAKER OPEN | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW020TRP | F13SW020_TRP | N/A | F13-SW-020 CIRCUIT BREAKER TRIPPED | F13SW020 C BREAKER TRIP | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-28 | MOC-125
|  |  | F13SW020SD | F13SW020_SD | N/A | F13-SW-020 INCOMER SURGE DIVERTER OK | F13SW020 INC SURGE DIVOK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B | 2026-02-28 | MOC-125
|  |  | F13SW020PS1 | F13SW020_PS1 | N/A | F13-SW-020 PS1 24VDC HEALTHY | F13SW020 PS1 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SW020PS2 | F13SW020_PS2 | N/A | F13-SW-020 PS2 24VDC HEALTHY | F13SW020 PS2 24VDC HTHY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SW102Q2CL | F13SW102Q2_CL | N/A | F13-SW-102 Generator Supply CB Closed | F13SW102 GenSup CB Close | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW102Q2OP | F13SW102Q2_OP | N/A | F13-SW-102 Generator Supply CB Opened | F13SW102 Gen Sup CB Open | N_Active | Active |  | Hardwired to DCS | - |  |  | 1 | 2025-06-05 | IO List updated in April. Variation to be raised in register
|  |  | F13SW102Q1CL | F13SW102Q1_CL | N/A | F13-SW-102 Mains Supply CB Closed | F13SW102 MainsSupCBClose | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW102Q1OP | F13SW102Q1_OP | N/A | F13-SW-102 Mains Supply CB Opened | F13SW102 MainsSupCBOpen | N_Active | Active |  | Hardwired to DCS | - |  |  | 1 | 2025-06-05 | IO List updated in April. Variation to be raised in register
|  |  | F13SW103Q2CL | F13SW103Q2_CL | N/A | F13-SW-103 Generator Supply CB Closed | F13SW103 GenSup CB Close | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW103Q2OP | F13SW103Q2_OP | N/A | F13-SW-103 Generator Supply CB Opened | F13SW103 Gen Sup CB Open | N_Active | Active |  | Hardwired to DCS | - |  |  | 1 | 2025-06-05 | IO List updated in April. Variation to be raised in register
|  |  | F13SW103Q1CL | F13SW103Q1_CL | N/A | F13-SW-103 Mains Supply CB Closed | F13SW103 MainSupCBClose | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW103Q1OP | F13SW103Q1_OP | N/A | F13-SW-103 Mains Supply CB Opened | F13SW103 Mains SupCBOpen | N_Active | Active |  | Hardwired to DCS | - |  |  | 1 | 2025-06-05 | IO List updated in April. Variation to be raised in register
|  |  | F13SW103SD | F13SW103_SD | N/A | F13-SW-103 Surge Diverter Ok | F13SW103 Surge Div Ok | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SW114Q2CL | F13SW114Q2_CL | N/A | F13-SW-114 Generator Supply CB Closed | F13SW114 GenSup CB Close | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW114Q2OP | F13SW114Q2_OP | N/A | F13-SW-114 Generator Supply CB Opened | F13SW114 Gen Sup CB Open | N_Active | Active |  | Hardwired to DCS | - |  |  | 1 | 2025-06-05 | IO List updated in April. Variation to be raised in register
|  |  | F13SW114Q1CL | F13SW114Q1_CL | N/A | F13-SW-114 Mains Supply CB Closed | F13SW114 MainsSupCBClose | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW114Q1OP | F13SW114Q1_OP | N/A | F13-SW-114 Mains Supply CB Opened | F13SW114 Mains SupCBOpen | N_Active | Active |  | Hardwired to DCS | - |  |  | 1 | 2025-06-05 | IO List updated in April. Variation to be raised in register
|  |  | F13SW114SD | F13SW114_SD | N/A | F13-SW-114 Surge Diverter Ok | F13-SW-114 Surge Div Ok | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | F13SW120Q2CL | F13SW120Q2_CL | N/A | F13-SW-120 Generator Supply CB Closed | F13SW120 GenSup CB Close | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW120Q2OP | F13SW120Q2_OP | N/A | F13-SW-120 Generator Supply CB Opened | F13SW120 Gen Sup CB Open | N_Active | Active |  | Hardwired to DCS | - |  |  | 1 | 2025-06-05 | IO List updated in April. Variation to be raised in register
|  |  | F13SW120Q1CL | F13SW120Q1_CL | N/A | F13-SW-120 Mains Supply CB Closed | F13SW120 MainsSupCBClose | N_Active | Active |  | Hardwired to DCS | - |  |  | B
|  |  | F13SW120Q1OP | F13SW120Q1_OP | N/A | F13-SW-120 Mains Supply CB Opened | F13SW120 MainsSup CBOpen | N_Active | Active |  | Hardwired to DCS | - |  |  | 1 | 2025-06-05 | IO List updated in April. Variation to be raised in register
|  |  | F13SW120SD | F13SW120_SD | N/A | F13-SW-120 Surge Diverter Ok | F13-SW-120 Surge Div Ok | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | B
|  |  | ZSC13010 | ZAC13010 | N/A | F13-TR-002 SAG MILL 415V MCC TRANSFORMER Enclosure Door Position Switch Closed | F13TR002 415VMCC Door | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2
|  |  | F13TR002WTH | F13TR002_WTH | - | F13-TR-002 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F13TR002 Temp Hi | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-08-19 | CR-034/ MOC-240
|  |  | ZSC13020 | ZAC13020 | N/A | F13-TR-003 BALL MILL 415V MCC TRANSFORMER Enclosure Door Position Switch Closed | F13TR003 415VMCC Door | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2
|  |  | F13TR003WTH | F13TR003_WTH | - | F13-TR-003 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F13TR003 Temp Hi | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-08-19 | CR-034/ MOC-240
|  |  | ZSC13030 | ZAC13030 | N/A | F13-TR-014 RECYCLE CRUSHING 415V MCC TRANSFORMER Enclosure Door Position Switch Closed | F13TR014 415VMCC Door | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2
|  |  | F13TR014WTH | F13TR014_WTH | - | F13-TR-014 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F13TR014 Temp Hi | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-08-19 | CR-034/ MOC-240
|  |  | ZSC13068 | ZAC13068 | N/A | F13-TR-020 MILL CHILLERS 415V MCC TRANSFORMER Enclosure Door Position Switch Closed | F13TR020 415VMCC Door | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2
|  |  | F13TR020WTH | F13TR020_WTH | - | F13-TR-20 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F13TR020 Temp Hi | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 | 2025-08-19 | CR-034/ MOC-240
|  |  | XS13055 | XA13055 | 2000-F13-PID-PR-10001 | F13-WD-403 SAG Mill Feed Weightometer Alarm | F13WD403 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | WQS13055 | WS13055 | 2000-F13-PID-PR-10001 | F13-WD-403 SAG Mill Feed Weightometer Pulse Tonnes | F13WD403 Pulse Tonnes | N_Active | Active |  | Hardwired to DCS | - |  |  | 0
|  |  | XS13195 | XA13195 | 2000-F13-PID-PR-10005 | F13-WD-405 SAG Mill Feed Weightometer Alarm | F13WD405 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | B
|  |  | WQS13195 | WS13195 | 2000-F13-PID-PR-10005 | F13-WD-405 SAG Mill Feed Weightometer Pulse Tonnes | F13WD405 Pulse Tonnes | N_Active | Active |  | Hardwired to DCS | - |  |  | 0
|  |  | ZS13945 | ZI13945 | 2000-F13-PID-PR-10003 | F13-XM-421 PORTABLE MILLS INCHING DRIVE BALL MILL PLACEMENT POSITION SWITCH | F13XM421 Ball Position | Inactive | Active |  | Hardwired to DCS |  |  |  | 1 | 2025-08-19 | CR-045
|  |  | ZS13944 | ZI13944 | 2000-F13-PID-PR-10003 | F13-XM-421 PORTABLE MILLS INCHING DRIVE SAG MILL PLACEMENT POSITION SWITCH | F13XM421 SAG Position | Inactive | Active |  | Hardwired to DCS |  |  |  | 1 | 2025-08-19 | CR-045
|  |  | MSSIRENREQ | MS_SIREN_REQ | 2000-F13-PID-PR-10003 |  | F13MS401 Inch Siren | Inactive | Active |  | SoftTag | - |  | Signal from SAG Mill VSD 2000-ME001.2-M01-50001 | 1 | 2025-10-06 | CR-050
|  |  | MBSIRENREQ | MB_SIREN_REQ | 2000-F13-PID-PR-10004 |  | F13MB401 Inch Siren | Inactive | Active |  | SoftTag | - |  | Signal from Ball Mill VSD 2000-ME001.3-M01-50001 | 1 | 2025-10-06 | CR-050
|  |  | XS13760 | XI13760 | 2000-F13-PID-PR-10003 |  | F13HU413 Siren Req | Inactive | Active |  | Hardwired to DCS |  |  |  | 1 | 2025-10-06 | CR-050
|  |  | F13GE103CBTRP | 13GE103CBTRP |  | F13-GE-103 MILLS ESSENTIAL SUPPLY 415V GENERATOR CB TRIPPED | F13-GE-103 GEN CB TRP | Alarm | Normal | Alarm | Hardwired to DCS | 0
|  |  | F13GE114CBTRP | 13GE114CBTRP |  | F13-GE-114 RECYCLE CRUSHING ESSENTIAL SUPPLY 415V GENERATOR CB OPENED | F13-GE-114 GEN CB TRP | Alarm | Normal | Alarm | Hardwired to DCS | 0
|  |  | F13GE120CBTRP | 13GE120CB_TRP |  | F13-GE-120 MILL CHILLERS AND REAGENTS ESSENTIAL SUPPLY 415V GENERATOR CB OPENED | F13-GE-120 GEN CB TRP | Alarm | Normal | Alarm | Hardwired to DCS | 0
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  | 609 | 610

## 4. Digital Output
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - MILLING & CLASSIFICATION (F13) |  |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)*
2000-F13-LST-PR-10001
DIGITAL INSTRUMENTS (DO)
[19 empty] | C1 Sign Off |  | C2 Sign Off |  | C1 Comments
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | Change Date | Change Reference | OK | Date | OK | Date
|  |  |  | YY13085A | YA13085A | 2000-F13-PID-PR-10001 | F13-FN-419 Reclaim Fan Stopped Beacon A | F13FN419 Stopped Alarm | Off | On |  |  |  |  | Off = F13-FN-419 Running On = F13-FN-419 Not Running | 1 | 2025-04-10 | https://pastech-2955.atlassian.net/browse/KAN-1673 |  |  |  |  | The drive is off and therefore forcing the output to be ON but drive can't run yet
|  |  |  | YY13085B | YA13085B | 2000-F13-PID-PR-10001 | F13-FN-419 Reclaim Fan Stopped Beacon B | F13FN419 Stopped Alarm | Off | On |  |  |  |  | Off = F13-FN-419 Running On = F13-FN-419 Not Running | 0 | [6 empty] | The drive is off and therefore forcing the output to be ON but drive can't run yet
|  |  |  | YY13085C | YA13085C | 2000-F13-PID-PR-10001 | F13-FN-419 Reclaim Fan Stopped Beacon C | F13FN419 Stopped Alarm | Off | On |  |  |  |  | Off = F13-FN-419 Running On = F13-FN-419 Not Running | 0 | [6 empty] | The drive is off and therefore forcing the output to be ON but drive can't run yet
|  |  |  | YY13007 | YA13007 | 2000-F13-PID-PR-10001 | F13-FA-411 Coarse Ore Reclaim Feeder 1 Start Siren | F13FA411 Start Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds before F13-FA-411 drive is allowed to start | A | [6 empty] | drive not ready
|  |  |  | YY13017 | YA13017 | 2000-F13-PID-PR-10001 | F13-FA-412 Coarse Ore Reclaim Feeder 2 Start Siren | F13FA412 Start Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds before F13-FA-412 drive is allowed to start | A | [6 empty] | drive not ready
|  |  |  | YY13027 | YA13027 | 2000-F13-PID-PR-10001 | F13-FA-414 Emergency Feeder Start Siren | F13FA414 Start Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds before F13-FA-414 drive is allowed to start | A | [6 empty] | drive not ready
|  |  |  | YY13056A | YA13056A | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Tail End Start Siren | F13CV403 TE Start Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds before F13-CV-403 drive is allowed to start | A
|  |  |  | YY13056B | YA13056B | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Head End Start Siren | F13CV403 HE Start Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds before F13-CV-403 drive is allowed to start | A
|  |  |  | YY13056C | YA13056C | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Mid Section Start Siren | F13CV403 Mid Start Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds before F13-CV-403 drive is allowed to start | A
|  |  |  | XY13079 | XC13079 | 2000-F13-PID-PR-10001 | F13-DC-402 Reclaim Tunnel Dust Collector Controller Fault | F13DC402 Man Override | N_Active | Active |  | SoftTag |  |  | Logic: Maintain when activated. Deactivate after 10 minutes or by CRO. Include on graphic near dust collector Dwyer Dust Collector controller manual override Refer to 2000-ME012-F16-10001 | 1 | 2025-04-30 | https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-297?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC |  |  |  |  | Output received on field. Unsure of functionality
|  |  |  | YY13132 | YA13132 | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Barring Siren | F13MS401 Barring Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds continuously before as inching is commenced. Set up for both inching via the F13-HU-413 Mill Inching HPU (SAG Mill) and F13-MS-401A/B Main Motor. | 1 | 2025-06-13 | https://pastech-2955.atlassian.net/browse/KAN-1943?linkSource=email |  |  |  |  | Loop check only
|  |  |  | YY13133A | YA13133A | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Start Siren 1 | F13MS401 StartUp Siren 1 | Off | On |  |  |  |  | Siren is turned on for 10 seconds continuously before F13-MS-401A/B drive is allowed to start | A | [6 empty] | Loop check only
|  |  |  | YY13133B | YA13133B | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Start Siren 2 | F13MS401 StartUp Siren 2 | Off | On |  |  |  |  | Siren is turned on for 10 seconds continuously before F13-MS-401A/B drive is allowed to start | A | [6 empty] | Loop check only
|  |  |  | YY13145 | YA13145 | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Barring Siren | F13MB401 Barring Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds continuously before inching is commenced. Set up for both inching via the F13-HU-413 Mill Inching HPU (Ball Mill) and F13-MB-401A/B Main Motor. | 1 | 2025-06-13 | https://pastech-2955.atlassian.net/browse/KAN-1943?linkSource=email
|  |  |  | YY13146A | YA13146A | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Start Siren 1 | F13MB401 StartUp Siren 1 | Off | On |  |  |  |  | Siren is turned on for 10 seconds continuously before F13-MB-401A/B drive is allowed to start | A
|  |  |  | YY13146B | YA13146B | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Start Siren 2 | F13MB401 StartUp Siren 2 | Off | On |  |  |  |  | Siren is turned on for 10 seconds continuously before F13-MB-401A/B drive is allowed to start | A
|  |  |  | XY13230A | XC13230A | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Lift DC Relay Signal | F13BLC402 Lift DC | N_Active As per F13-SEQ-0037 | Active As per F13-SEQ-0037 |  |  |  |  | Vendor Reference: RL1_LIFT_DC RL1 Lift DC Relay Configures the DC circuit for lift polarity. | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 Removed TBC comment. No changes
|  |  |  | XY13230B | XC13230B | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Dump DC Relay Signal | F13BLC402 Dump DC | N_Active As per F13-SEQ-0037 | Active As per F13-SEQ-0037 |  |  |  |  | Vendor Reference: RL2_DUMP_DC RL2 Dump DC Relay Configures the DC circuit for Dump polarity. | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 Removed TBC comment. No changes
|  |  |  | XY13234A | XC13234A | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Lift AC Reduced Signal | F13BLC402 Lift AC Red. | N_Active As per F13-SEQ-0037 | Active As per F13-SEQ-0037 |  |  |  |  | Vendor Reference: RL3_LIFT_AC_RED RL3 Reduced Lift AC Relay Closes the Reduced power contactor on the transformer secondary. | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 Removed TBC comment. No changes
|  |  |  | XY13234B | XC13234B | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Dump AC Relay Signal | F13BLC402 Dump AC | N_Active As per F13-SEQ-0037 | Active As per F13-SEQ-0037 |  |  |  |  | Vendor Reference: RL4_DUMP_AC RL4 Dump AC Relay Closes the Dump power contactor on the transformer secondary. | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 Removed TBC comment. No changes
|  |  |  | XY13234C | XC13234C | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Lift AC Full Signal | F13BLC402 Lift AC Full | N_Active As per F13-SEQ-0037 | Active As per F13-SEQ-0037 |  |  |  |  | Vendor Reference: RL5_LIFT_AC_FUL RL5 Full Lift AC Relay Closes the Full power contactor on the transformer secondary. | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 Removed TBC comment. No changes
|  |  |  | XY13250A | XC13250A | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Standby Idle Signal | F13BLC402 Standby Idle | N_Active | Active |  |  |  |  | Vendor Reference: RL6_IDLE RL6 Standby Idle Standby Idle must be energised to enable local earth leak testing. Hoist and Trolley is in the home position and all fault conditions are healthy. Active if (else N_Active): ZI13310A.PV < F13_V_ENC_DMP + F13_V_ENC_TLR AND ZI13310A.PV > F13_V_ENC_DMP - F13_V_ENC_TLR AND ZI13229A Active AND ZI13310B.PV < F13_H_ENC_DMP + F13_H_ENC_TLR AND ZI13310B.PV > F13_H_ENC_DMP - F13_H_ENC_TLR) AND F13CR453_MXDUTY = N_Active AND F13BLC402_MXDUTY = N_Active AND XC13250C, XC13250E AND XC13250F = N_Active AND XI13206A, XI13206B AND XI13206C = N_Active | 1 | 14/05/2025 14/07/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 https://pastech-2955.atlassian.net/browse/PL-331
|  |  |  | XY13250B | XC13250B | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Power On Signal | F13BLC402 Power On | N_Active | Active |  |  |  |  | Vendor Reference: RL7_PWR RL7 Power On Energises local indication and enables release of mechanical latches Include as push button on DCS to energise (latch) | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876
|  |  |  | XY13250C | XC13250C | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Magnet Fault Signal | F13BLC402 Fault | Normal | Alarm | Alarm |  | 3 |  | Vendor Reference: RL8_MAG_FLT RL8 Magnet Fault Energises local indication of Magnet Fault Status. Alarm if: F13BLC402_MXDUTY Active OR XI13206B Active OR XS13206A Inactive | 1 | 14/05/2025 14/07/2025 19/08/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 https://pastech-2955.atlassian.net/browse/PL-331 https://pastech-2955.atlassian.net/browse/PL-331
|  |  |  | XY13250D | XC13250D | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Dump Cycle in Progress Signal | F13BLC402 Dump Cycle | N_Active As per F13-SEQ-0037 | Active As per F13-SEQ-0037 |  |  |  |  | Vendor Reference: RL9_DMP_CYC RL9 Dump Cycle in Progress Energises local indication for duration of dump and back emf discharge cycle. | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 Removed TBC comment. No changes
|  |  |  | XY13250E | XC13250E | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Trolley Overload Signal | F13CR453 Trolley Fault | Normal | Alarm | Alarm |  | 3 |  | Vendor Reference: RL10_TRO_FLT RL10 Trolley Fault Energises local indication of Trolley fault as signalled by Trolley/Hoist control panel. Alarm if: F13CR453_MXDUTY Active OR XI13206B Active OR XS13206A Inactive | 1 | 14/05/2025 14/07/2025 19/08/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 https://pastech-2955.atlassian.net/browse/PL-331 https://pastech-2955.atlassian.net/browse/PL-331
|  |  |  | XY13250F | XC13250F | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Hoist Overload Signal | F13CR453 Hoist Fault | Normal | Alarm | Alarm |  | 3 |  | Vendor Reference: RL11_HST_FLT RL11 Hoist Fault Energises local indication of Trolley fault as signalled by Trolley/Hoist control panel. Alarm if: XI13206B Active OR XS13206A Inactive | 1 | 14/05/2025 14/07/2025 19/08/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 https://pastech-2955.atlassian.net/browse/PL-331 https://pastech-2955.atlassian.net/browse/PL-331
|  |  |  | XY13251A | XC13251A | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Trolley Forward Signal | F13CR453 Trolley Fwd | N_Active | Active |  |  |  |  | Logic: Energise XC13284 for F13BLC402_T1 prior to energising XC13251A Vendor Reference: RL12_TRO_FWD RL12 Trolley Forward Energising XC13251A closes N/O contact in Trolley/Hoist control panel acting on Trolley Forward contactor. Refer to F13-CR-453_T for associated logic | 1 | 14/05/2025 28/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876
|  |  |  | XY13251B | XC13251B | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Trolley Reverse Signal | F13CR453 Trolley Rev | N_Active | Active |  |  |  |  | Logic: Energise XC13284 for F13BLC402_T1 prior to energising XC13251B Vendor Reference: RL13_TRO_REV RL13 Trolley Reverse Energising XC13251B closes N/O contact in Trolley/Hoist control panel acting on Trolley Reverse contactor. Refer to F13-CR-453_T for associated logic | 1 | 14/05/2025 28/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876
|  |  |  | XY13251C | XC13251C | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Trolley Fast Signal | F13CR453 Trolley Fast | N_Active | Active |  |  |  |  | Vendor Reference: RL14_TRO_FST RL14 Trolley Fast Energising XC13251C closes N/O contact in Trolley/Hoist control panel acting on Trolley Fast contactor. Logic: Auto: HS13140AAUT Auto AND as per Sequence F13-SEQ-0037 OR F13-SEQ-0038 OR Manual: HS13140BMAN Manual AND HS13144BFST Fast AND 'XC13251A OR XC13251B' Active | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 Removed TBC comment. No changes
|  |  |  | XY13280A | XC13280A | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Hoist Up Signal | F13CR453 Hoist Up | N_Active | Active |  |  |  |  | Vendor Reference: RL15_HST_UP RL15 Hoist Up Energising XC13280A closes N/O contact in Trolley/Hoist control panel acting on Hoist Up contactor. Refer to F13-CR-453_H for associated logic | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 Removed TBC comment. No changes
|  |  |  | XY13280B | XC13280B | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Hoist Down Signal | F13CR453 Hoist Down | N_Active | Active |  |  |  |  | Vendor Reference: RL16_HST_DWN RL16 Hoist Down Energising XC13280B closes N/O contact in Trolley/Hoist control panel acting on Hoist Down contactor. Refer to F13-CR-453_H for associated logic | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876
|  |  |  | XY13280C | XC13280C | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Hoist Fast Signal | F13CR453 Hoist Fast | N_Active | Active |  |  |  |  | Vendor Reference: RL17_HST_FST RL17 Hoist Fast Energising XC13280C closes N/O contact in Trolley/Hoist control panel acting on Hoist Fast contactor. Logic: Auto: HS13140AAUT Auto AND as per Sequence F13-SEQ-0037 OR F13-SEQ-0038 OR Manual: HS13140BMAN Manual AND HS13144BFST Fast AND 'XC13280A OR XC13280B' Active | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 Removed TBC comment. No changes
|  |  |  | XY13284 | XC13284 | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Trolley/Hoist System Start Signal | F13BLC402 System Start | N_Active | Active |  |  |  |  | Vendor Reference: RL18_SYS_SRT RL18 Trolley/Hoist System Start Energising XC13284 closes N/O contact in Trolley/Hoist control panel acting on System Start relay. Designed for momentary action with a 3 second off delay. Sounds Trolley Horn. Energising XC13284 will energise KA1 and therefore latch KM1 contactor. Logic: As per F13-SEQ-0038 OR As per F13BLC402_T1 (see Misc tab) | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 Removed TBC comment. No changes
|  |  |  | XY13311 | XC13311 | 2000-F13-PID-PR-10004 | F13-BLC-402 Ball Mill Ball Charger Bypass Signal | F13BLC402 Bypass | N_Active | Active |  |  |  |  | Include as latched push button on Ball Charger graphic. Activate/deactivate by CRO ref 2000-ME057-M02-10001 Rev C | 1 | 8/04/2025 14/07/2025 | IO Compare from email "Re: Missing IO" https://pastech-2955.atlassian.net/browse/PL-331
|  |  |  | XY13743 | XI13743 | 2000-F13-PID-PR-10003 | F13-HU-413 Portable Mills Inching Drive Hydraulic Power Unit Permissive Control | F13HU413 Inching Healthy | Disable: F13-HU-413 Interlocks and/or start permissives are unhealthy | Enable: F13-HU-413 Interlocks and start permissives are healthy |  |  |  |  | F13-HU-413 Interlocks and start permissves (refer to Drive tab) are to disable XI13743 when unhealthy, which is provided as a permission signal to the Portable HPU Inching PLC to stop and/or prevent inching of the mill. | 0
|  |  |  | YY13170 | YA13170 | 2000-F13-PID-PR-10005 | F13-CV-404 Recycle Conveyor 1 Start Siren | F13CV404 Start Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds before F13-CV-404 drive is allowed to start | A
|  |  |  | XY13183 | XC13183 | 2000-F13-PID-PR-10005 | F13-MG-403 Recycle Crusher Tramp Magnet 1 Remote Select | F13MG403 Remote Select | Remote | Local ( this probably needs to swap ) |  |  |  |  | XC13183 must be in Remote to start F13-MG-403 via Remote Start relay XC13184 | 0 | [6 empty] | loop tested only, not functionality
|  |  |  | XY13184 | XC13184 | 2000-F13-PID-PR-10005 | F13-MG-403 Recycle Crusher Tramp Magnet 1 Remote Run | F13MG403 Remote Run | N_Running | Running |  |  |  |  | XC13184 is toggled N_Running/Running by CRO from graphic OR Sequence F13-SEQ-0023/0024 This starts/stops F13-MG-403 (see Drives tab). XC13184 can only be set to RUNNING if: • Remote Select XC13183 = REMOTE AND • System Ready XI13180 = READY AND • System Fault XA13182 = NORMAL XC13184 is forced to N_RUNNING if: • Remote Select XC13183 = LOCAL OR • System Fault XA13182 = FAULT OR • F13-MG-403 Interlocks/Trips (see Drives tab) | 0 | [6 empty] | loop tested only, not funtionality
|  |  |  | YY13196A | YA13196A | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Head End Start Siren | F13CV405 HE Start Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds before F13-CV-405 drive is allowed to start | A
|  |  |  | YY13196B | YA13196B | 2000-F13-PID-PR-10005 | F13-CV-405 Recycle Conveyor 2 Tail End Start Siren | F13CV405 TE Start Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds before F13-CV-405 drive is allowed to start | A
|  |  |  | XY13213 | XC13213 | 2000-F13-PID-PR-10005 | F13-MG-404 Recycle Crusher Tramp Magnet 2 Remote Select | F13MG404 Remote Select | Remote | Local |  |  |  |  | XC13213 must be in Remote to start F13-MG-404 via Remote Start relay XC13214 | 0
|  |  |  | XY13214 | XC13214 | 2000-F13-PID-PR-10005 | F13-MG-404 Recycle Crusher Tramp Magnet 2 Remote Run | F13MG404 Remote Run | N_Running | Running |  |  |  |  | XC13214 is toggled N_Running/Running by CRO from graphic OR Sequence F13-SEQ-0023/0024 This starts/stops F13-MG-404 (see Drives tab). XC13214 can only be set to RUNNING if: • Remote Select XC13213 = REMOTE AND • System Ready XI13210 = READY AND • System Fault XA13212 = NORMAL XC13214 is forced to N_RUNNING if: • Remote Select XC13213 = LOCAL OR • System Fault XA13212 = FAULT OR • F13-MG-404 Interlocks/Trips (see Drives tab) | 0
|  |  |  | YY13224 | YA13224 | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Start Siren | F13CC401 Start Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds before F13-CC-401 drive is allowed to start | A | [6 empty] | Siren checked on actual start 15/07 MSH
|  |  |  | YY13228 | YA13228 | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Start Siren | F13CC402 Start Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds before F13-CC-402 drive is allowed to start | A
|  |  |  | YY13355 | YA13355 | 2000-F13-PID-PR-10006 | F13-CV-406 Recycle Crusher Discharge Conveyor Start Siren | F13CV406 Start Siren | Off | On |  |  |  |  | Siren is turned on for 10 seconds before F13-CV-406 drive is allowed to start | A
|  |  |  | XY13205 | XC13205 | 2000-F13-PID-PR-10005 | F13-MD-401 Recycle Crusher Metal Detector Remote Reset | F13MD401 Reset Fault | N_Active | Active: Fault Reset | [5 empty] | B
|  |  |  | MSRUN | MS_RUN | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Run Command | F13MS401 Run | Stop: Stop F13-MS-401 | Run: Run F13-MS-401 |  |  |  |  | SoftTag This tag is an output from the DCS to the SAG Mill VSD to control the SAG Mill. Refer to 2000-ME001.2-M01-50001 Used in sequences only. | A
|  |  |  | MSRESET | MS_RESET | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Trip Reset Command | F13MS401 Trip Reset | N_Active | Reset Fault |  |  |  |  | SoftTag This tag is an output from the DCS to the SAG Mill VSD to control the SAG Mill Refer to 2000-ME001.2-M01-50001 Include pushbutton on the DCS. | A
|  |  |  | MSCONVON | MS_CONV_ON | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Energise Converter Command | F13MS401 Conv On | N_Active: Open 33kV HVCB | Active: Close 33kV HVCB |  |  |  |  | SoftTag This tag is an output from the DCS to the SAG Mill VSD to control the SAG Mill Refer to 2000-ME001.2-M01-50001 Include pushbutton on the DCS. See MS_CONV_LOGIC in Misc tab for logic | 1
|  |  |  | MSLCPEN | MS_LCP_EN | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Mill Locked Charge Protection Enable Command | F13MS401 LCP Enable | Disable | Enable |  |  |  |  | SoftTag This tag is an output from the DCS to the SAG Mill VSD to control the SAG Mill Refer to 2000-ME001.2-M01-50001 Include pushbutton on the DCS. | A
|  |  |  | MSMILLEN | MS_MILL_EN | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Mill Enabled Interlock Command | F13MS401 Mill Interlock | Disable | Enable |  |  |  |  | SoftTag This tag is an output from the DCS to the SAG Mill VSD to control the SAG Mill Refer to 2000-ME001.2-M01-50001 Energised and de-energised as per the F13-MS-401A/B interlocks in the Drives tab | A
|  |  |  | MBRUN | MB_RUN | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Run Command | F13MB401 Run | Stop: Stop F13-MB-401 | Run: Run F13-MB-401 |  |  |  |  | SoftTag This tag is an output from the DCS to the Ball Mill VSD to control the Ball Mill. Refer to 2000-ME001.3-M01-50001 Used in sequences only. | A
|  |  |  | MBRESET | MB_RESET | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Trip Reset Command | F13MB401 Trip Reset | N_Active | Reset Fault |  |  |  |  | SoftTag This tag is an output from the DCS to the Ball Mill VSD to control the Ball Mill Refer to 2000-ME001.3-M01-50001 Include pushbutton on the DCS. | A
|  |  |  | MBCONVON | MB_CONV_ON | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Energise Converter Command | F13MB401 Conv On | N_Active: Open 33kV HVCB | Active: Close 33kV HVCB |  |  |  |  | SoftTag This tag is an output from the DCS to the Ball Mill VSD to control the Ball Mill Refer to 2000-ME001.3-M01-50001 Include pushbutton on the DCS. See MB_CONV_LOGIC in Misc tab for logic | 1
|  |  |  | MBLCPEN | MB_LCP_EN | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Mill Locked Charge Protection Enable Command | F13MB401 LCP Enable | Disable | Enable |  |  |  |  | SoftTag This tag is an output from the DCS to the Ball Mill VSD to control the Ball Mill Refer to 2000-ME001.3-M01-50001 Include pushbutton on the DCS. | A
|  |  |  | MBMILLEN | MB_MILL_EN | 2000-F13-PID-PR-10004 | F13-MB-401 Ball Mill Main Motor VSD Mill Enabled Interlock Command | F13MB401 Mill Interlock | Disable | Enable |  |  |  |  | SoftTag This tag is an output from the DCS to the Ball Mill VSD to control the Ball Mill Refer to 2000-ME001.3-M01-50001 Energised and de-energised as per the F13-MB-401A/B interlocks in the Drives tab | A
|  |  | x | XY13661 | XI13661 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Panel Local Mode Enabled Indicator Light | F13LU413 Panel LocMode | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: ALL Equipment AUTO OR MAN (see comment) AND HS13663TEST Inactive On if: Equipment LOCAL (see comment) OR HS13663TEST Active If any of the equipment is set to LOCAL mode, make indicator active (refer HS13662, Digital Input tab): F13-HT-433, F13-HT-434, F13-HT-435, F13-HT-436, F13-PO-427, F13-PO-428, TCV13629, F13-PO-429, F13-PO-430, F13-PO-431, F13-PO-434 OR F13-PO-435 HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13686 | XI13686 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Low Pressure Pump 1 Running Indicator Light | F13LU413 LP Pmp1 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-427 Not Running AND HS13663TEST Inactive On if: F13-PO-427 Running OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13687 | XI13687 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Low Pressure Pump 2 Running Indicator Light | F13LU413 LP Pmp2 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-428 Not Running AND HS13663TEST Inactive On if: F13-PO-428 Running OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13688 | XI13688 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Pinion Pump 1 Running Indicator Light | F13LU413 PinPmp 1 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-434 Not Running AND HS13663TEST Inactive On if: F13-PO-434 Running OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13689 | XI13689 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Pinion Pump 2 Running Indicator Light | F13LU413 PinPmp 2 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-435 Not Running AND HS13663TEST Inactive On if: F13-PO-435 Running OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13690 | XI13690 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel High Pressure Pump 1 Running Indicator Light | F13LU413 HP Pmp 1 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-429 Not Running AND HS13663TEST Inactive On if: F13-PO-429 Running OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13691 | XI13691 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel High Pressure Pump 2 Running Indicator Light | F13LU413 HP Pmp 2 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-430 Not Running AND HS13663TEST Inactive On if: F13-PO-430 Running OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13692 | XI13692 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel High Pressure Pump 3 Running Indicator Light | F13LU413 HP Pmp 3 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-431 Not Running AND HS13663TEST Inactive On if: F13-PO-431 Running OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13665 | XI13665 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Settling Reservoir Oil Level Low Indicator Light | F13LU413 Set Res Lvl L | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: LI13619 A_Lo Inactive AND HS13663TEST Inactive On if: LI13619 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13666 | XI13666 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Settling Reservoir Oil Level Low Low Indicator Light | F13LU413 Set Res Lvl LL | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: LI13619 A_LL Inactive AND HS13663TEST Inactive On if: LI13619 A_LL Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13667 | XI13667 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Settling Reservoir Temperature Low Indicator Light | F13LU413 Set Res Temp L | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: TI13615 A_Lo Inactive AND HS13663TEST Inactive On if: TI13615 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13669 | XI13669 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Condition Reservoir Oil Level Low Indicator Light | F13LU413 Cond Res Lvl L | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: LI13620 A_Lo Inactive AND HS13663TEST Inactive On if: LI13620 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13670 | XI13670 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Condition Reservoir Oil Level Low Low Indicator Light | F13LU413 Cond Res Lvl LL | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: LI13620 A_LL Inactive AND HS13663TEST Inactive On if: LI13620 A_LL Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13671 | XI13671 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Condition Reservoir Temperature High Indicator Light | F13LU413 Cond ResTemp H | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: TI13623 A_Hi Inactive AND HS13663TEST Inactive On if: TI13623 A_Hi Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13672 | XI13672 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Condition Reservoir Temperature Low Indicator Light | F13LU413 Cond ResTemp L | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: TI13623 A_Lo Inactive AND HS13663TEST Inactive On if: TI13623 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13668 | XI13668 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Reservoir Suction Compartment Heater On Indicator Light | F13LU413 Set. Res Htr On | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-HT-433 AND F13-HT-434 Not Running AND HS13663TEST Inactive On if: F13-HT-433 OR F13-HT-434 Running OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13673 | XI13673 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Reservoir Conditioned Compartment Heater On Indicator Light | F13LU413 Cond Res Htr On | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-HT-435 AND F13-HT-436 Not Running AND HS13663TEST Inactive On if: F13-HT-435 OR F13-HT-436 Running OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13674 | XI13674 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Low Pressure Lube Filter Dirty Alarm Indicator Light | F13LU413 LP Fltr Dirty | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: PDI13628 A_HH Inactive AND HS13663TEST Inactive On if: PDI13628 A_HH Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13675 | XI13675 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Low Pressure Lube Filter Bypass Indicator Light | F13LU413 LP Fltr Bypass | Off | On |  |  |  |  | Include Filter Bypass button on the DCS. CRO to manually activate the bypass indicator if F13-FI-424 and F13-FI-425 are being bypassed. When off, indicator light is not illuminated When on, indicator light is illuminated Off if: Bypass Deactivated by CRO AND HS13663TEST Inactive On if: Bypass Activated by CRO OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13676 | XI13676 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Low Pressure Lube Temperature High High Indicator Light | F13LU413 LP Lube Temp HH | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: TI13629 A_HH Inactive AND HS13663TEST Inactive On if: TI13629 A_HH Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13677 | XI13677 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Low Pressure Lube Temperature High Indicator Light | F13LU413 LP Lube Temp H | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: TI13629 A_Hi Inactive AND HS13663TEST Inactive On if: TI13629 A_Hi Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13679 | XI13679 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Feed End Bearing Flow Low Indicator Light | F13LU413 FE Brg Flow L | Off | On |  |  |  |  | No dedicated Feed End Main Bearing flow indication. This indicator will light up at the same time as XI13682. When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13640 A_Lo Inactive AND HS13663TEST Inactive On if: FI13640 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13680 | XI13680 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Feed End Bearing Oil Pressure High Indicator Light | F13LU413 FE Brg Prs H | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: PI13644 A_Hi Inactive AND PI13645 A_Hi Inactive AND PI13646 A_Hi Inactive AND PI13647 A_Hi Inactive AND HS13663TEST Inactive On if: PI13644 A_Hi Active OR PI13645 A_Hi Active OR PI13646 A_Hi Active OR PI13647 A_Hi Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13681 | XI13681 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Feed End High Pressure System Oil Pressure Low Indicator Light | F13LU413 FE HP Prs L | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: PI13644 A_Lo Inactive AND PI13645 A_Lo Inactive AND PI13646 A_Lo Inactive AND PI13647 A_Lo Inactive AND HS13663TEST Inactive On if: PI13644 A_Lo Active OR PI13645 A_Lo Active OR PI13646 A_Lo Active OR PI13647 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13682 | XI13682 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Discharge End Bearing Flow Low Indicator Light | F13LU413 Dsch Brg Flow L | Off | On |  |  |  |  | No dedicated Discharge End Main Bearing flow indication. This indicator will light up at the same time as XI13679. When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13640 A_Lo Inactive AND HS13663TEST Inactive On if: FI13640 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13683 | XI13683 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Discharge End Bearing Oil Pressure High Indicator Light | F13LU413 Dsch Brg Prs H | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: PI13648 A_Hi Inactive AND PI13649 A_Hi Inactive AND PI13650 A_Hi Inactive AND PI13651 A_Hi Inactive AND HS13663TEST Inactive On if: PI13648 A_Hi Active OR PI13649 A_Hi Active OR PI13650 A_Hi Active OR PI13651 A_Hi Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13684 | XI13684 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Discharge End Oil Pressure Low Indicator Light | F13LU413 DE HP Prs L | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: PI13648 A_Lo Inactive AND PI13649 A_Lo Inactive AND PI13650 A_Lo Inactive AND PI13651 A_Lo Inactive AND HS13663TEST Inactive On if: PI13648 A_Lo Active OR PI13649 A_Lo Active OR PI13650 A_Lo Active OR PI13651 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13685 | XI13685 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Thrust Rail Flow Low Indicator Light | F13LU413 Thr Rail Flw L | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13641 A_Lo Inactive AND HS13663TEST Inactive On if: FI13641 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13696 | XI13696 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Conditioning Circuit Flow Low Indicator Light | F13LU413 Cond. Flow L | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13630 A_Lo Inactive AND HS13663TEST Inactive On if: FI13630 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13697 | XI13697 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Conditioning Circuit Flow Low Low Indicator Light | F13LU413 Cond. Flow LL | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13630 A_LL Inactive AND HS13663TEST Inactive On if: FI13630 A_LL Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13701 | XI13701 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Pinion Bearing Discharge End Right Flow Low Indicator Light | F13LU413 PBrg FxdR FlwL | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13657 A_Lo Inactive AND HS13663TEST Inactive On if: FI13657 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13703 | XI13703 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Pinion Bearing Discharge End Left Flow Low Indicator Light | F13LU413 PBrg FxdL FlwL | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13658 A_Lo Inactive AND HS13663TEST Inactive On if: FI13658 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13700 | XI13700 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Pinion Bearing Feed End Right Flow Low Indicator Light | F13LU413 PBrg Flt R FlwL | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13659 A_Lo Inactive AND HS13663TEST Inactive On if: FI13659 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13702 | XI13702 | 2000-F13-PID-PR-10010 | F13LU413-CP SAG Mill Main Bearings Lubrication System Control Panel Pinion Bearing Feed End Left Flow Low Indicator Light | F13LU413 PBrg Flt L FlwL | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13660 A_Lo Inactive AND HS13663TEST Inactive On if: FI13660 A_Lo Active OR HS13663TEST Active HS13663 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13612 | XI13612 | 2000-F13-PID-PR-10013 | F13HU416-CP SAG Mill Brake System Local Control Panel Reservoir Level Low Warning Indicator Light | F13HU416 Res Lvl L | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: LAL13551 Inactive AND HS13736 Inactive On if: LAL13551 Active OR HS13736 Active HS13736 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13614 | XI13614 | 2000-F13-PID-PR-10013 | F13HU416-CP SAG Mill Brake System Local Control Panel Reservoir Oil Temperature High Indicator Light | F13HU416 Res Temp H | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: TAH13552 Inactive AND HS13736 Inactive On if: TAH13552 Active OR HS13736 Active HS13736 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13734 | XI13734 | 2000-F13-PID-PR-10013 | F13HU416-CP SAG Mill Brake System Local Control Panel Local Operation Indicator Light | F13HU416 Local Op | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: HS13737MODE Local Deselected AND HS13736 Inactive On if: HS13737MODE Local Selected OR HS13736 Active HS13736 Is a physical Lamp Test pushbutton | A | [6 empty] | test by turning on and off the output manually to confirm lights, and check the logic
|  |  | x | XY13735 | XI13735 | 2000-F13-PID-PR-10013 | F13HU416-CP SAG Mill Brake System Local Control Panel Brake Released Indicator Light | F13HU416 Brake Rel | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: [ZAH13545 OR ZAH13547 On (Brake Engaged)] AND HS13736 Inactive On if: [ZAH13545 AND ZAH13547 Off (Brake Released)] OR HS13736 Active HS13736 Is a physical Lamp Test pushbutton | A | [6 empty] | test by turning on and off the output manually to confirm lights, and check the logic
|  |  |  | XY13200A | XC13200A | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Start Signal | F13LU413 OCM Start | N_Active | Start: Start F13-PO-445 |  | Hardwired to PCS |  |  | Starts F13-PO-445 Latch when activated, unlatch if XC13200B = Stop If 13PO445STF.PV.1 = Active (rising-edge) AND F13-PO-445 in AUTO, activate (one-shot) F13LU413_CMD1 after 5 second delay If 13PO445STF.PV.1 = Inactive (falling-edge), activate (one-shot) F13LU413_CMD9 | 1 | 2025-03-18 | Modbus Data map reviewed by Controls. Logic reviewed
|  |  |  | XY13200B | XC13200B | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Stop Signal | F13LU413 OCM Stop | N_Active | Stop Stop F13-PO-445 |  | Hardwired to PCS |  |  | Stops F13-PO-445 Pushbutton. Unlatch XC13200A if XC13200B = Stop | 0
|  |  |  | F13LU413CMD1 | F13LU413_CMD1 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Oil Command Bit 1 (Start Test) | F13LU413 Start Test | N_Start | Start |  |  |  |  | SoftTag Logic: If 13PO445STF.PV.1 = Active (rising-edge) AND F13-PO-445 in AUTO, activate (one-shot) F13LU413_CMD1 after 5 second delay Include as pushbutton on DCS to start tests manually. Buttons can only be used if F13-PO-445 in manual. Register 21 Bit 1 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics OCM15 must be set up such that tests are initiated via the DCS (continous and automatic testing disabled) | 1 | 2025-03-18 | Modbus Data map reviewed by Controls. Changed from analogue output to digital outputs and logic updated
|  |  |  | F13LU413CMD9 | F13LU413_CMD9 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication Unit OCM Unit Oil Command Bit 9 (Stop Test) | F13LU413 Stop Test | N_Stop | Stop |  |  |  |  | SoftTag Logic: If 13PO445STF.PV.1 = Inactive (falling-edge), activate (one-shot) F13LU413_CMD9 Include as pushbutton on DCS to stop tests manually. Button can be used in all modes. Register 21 Bit 9 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics OCM15 must be set up such that tests are initiated via the DCS (continous and automatic testing disabled) | 1 | 2025-03-18 | Modbus Data map reviewed by Controls. Changed from analogue output to digital outputs and logic updated
|  |  | x | XY13848 | XI13848 | 2000-F13-PID-PR-10013 | F13LU424-CP Ball Mill Ring Gear Spray System Control Panel System Normal Indicator Light | F13LU424 Ball Spry Norm | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Refer to Misc tab for details. Normal indicator is energised if the Gear Spray Fault bit is not active. Off if: MB_SPRY_CR = Active On if: MB_SPRY_CR = Inactive | A
|  |  | x | XY13849 | XI13849 | 2000-F13-PID-PR-10013 | F13LU424-CP Ball Mill Ring Gear Spray System Control Panel Fault Indicator Light | F13LU424 Ball Spry Fault | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Refer to Misc tab for details. Fault indicator is energised if the Gear Spray Fault bits are active. Off if: MB_SPRY_CR = Inactive AND MB_SPR_NCR = Inactive On if: MB_SPRY_CR = Active OR MB_SPR_NCR = Active | A
|  |  | x | XY13850 | XI13850 | 2000-F13-PID-PR-10013 | F13LU424-CP Ball Mill Ring Gear Spray System Control Panel Cycle Running Indicator Light | F13LU424 Ball Spry Run | Off | On |  |  |  |  | Run indicator is energised when F13-PO-543 is energised (via SV13838). When off, indicator light is not illuminated When on, indicator light is illuminated Off if: SV13838 = De-energised On if: SV13838 = Energised | A
|  |  | x | XY13597 | XI13597 | 2000-F13-PID-PR-10013 | F13-LU-424 SAG Mill Ring Gear Spray System System Normal Indicator Light | F13LU424 SAG Spry Norm | Off | On |  |  |  |  | Refer to Misc tab for details. Normal indicator is energised if the Gear Spray Fault bit is not active. When off, indicator light is not illuminated When on, indicator light is illuminated Off if: MS_SPRY_CR = Active On if: MS_SPRY_CR = Inactive | A
|  |  | x | XY13598 | XI13598 | 2000-F13-PID-PR-10013 | F13-LU-424 SAG Mill Ring Gear Spray System System Fault Indicator Light | F13LU424 SAG Spry Fault | Off | On |  |  |  |  | Refer to Misc tab for details. Fault indicator is energised if the Gear Spray Fault bits are active. When off, indicator light is not illuminated When on, indicator light is illuminated Off if: MS_SPRY_CR = Inactive AND MS_SPR_NCR = Inactive On if: MS_SPRY_CR = Active OR MS_SPR_NCR = Active | A
|  |  | x | XY13599 | XI13599 | 2000-F13-PID-PR-10013 | F13-LU-424 SAG Mill Ring Gear Spray System Cycle Running Indicator Light | F13LU424 SAG Spry Run | Off | On |  |  |  |  | Run indicator is energised when F13-PO-443 is energised (via SV13588). When off, indicator light is not illuminated When on, indicator light is illuminated Off if: SV13588 = De-energised On if: SV13588 = Energised | A
|  |  | x | XY13852 | XI13852 | 2000-F13-PID-PR-10013 | F13LU416-CP Mills Seal Grease System Control Panel Ball Mill Seal Grease Fault Indicator Light | F13LU426 Seal Grse Fault | Off | On |  |  |  |  | Refer to Misc tab for details. Fault indicator is energised if the Seal Grease Fault bits are active. When off, indicator light is not illuminated When on, indicator light is illuminated Off if: MB_GRSE_CR = Inactive AND MB_GRS_NCR = Inactive On if: MB_GRSE_CR = Active OR MB_GRS_NCR = Active | A | [6 empty] | test by turning the output on/off to confirm field lights and check logic.
|  |  | x | XY13853 | XI13853 | 2000-F13-PID-PR-10013 | F13LU416-CP Mills Seal Grease System Control Panel Ball Mill Seal Grease Running Indicator Light | F13LU426 Seal Grse Run | Off | On |  |  |  |  | Run indicator is energised when F13-PO-544 is energised (via SV13856). When off, indicator light is not illuminated When on, indicator light is illuminated Off if: SV13856 = De-energised On if: SV13856 = Energised | A | [6 empty] | test by turning the output on/off to confirm field lights and check logic.
|  |  | x | XY13496 | XI13496 | 2000-F13-PID-PR-10013 | F13LU416-CP Mills Seal Grease System Control Panel Ball Mill Seal Grease System Normal Indicator Light | F13LU426 Seal Grse Norm | Off | On |  |  |  |  | Refer to Misc tab for details. Normal indicator is energised if the Seal Grease Fault bit is not active. When off, indicator light is not illuminated When on, indicator light is illuminated Off if: MB_GRSE_CR = Active On if: MB_GRSE_CR = Inactive | A | [6 empty] | test by turning the output on/off to confirm field lights and check logic.
|  |  | x | XY13601 | XI13601 | 2000-F13-PID-PR-10013 | F13LU414-CP Mills Seal Grease System Control Panel SAG Mill Seal Grease Fault Indicator Light | F13LU416 Seal Grse Fault | Off | On |  |  |  |  | Refer to Misc tab for details. Fault indicator is energised if the Seal Grease Fault bits are active. When off, indicator light is not illuminated When on, indicator light is illuminated Off if: MS_GRSE_CR = Inactive AND MS_GRS_NCR = Inactive On if: MS_GRSE_CR = Active OR MS_GRS_NCR = Active | A
|  |  | x | XY13602 | XI13602 | 2000-F13-PID-PR-10013 | F13LU414-CP Mills Seal Grease System Control Panel SAG Mill Seal Grease Cycle Running Indicator Light | F13LU416 Seal Grse Run | Off | On |  |  |  |  | Run indicator is energised when F13-PO-444 is energised (via SV13605). When off, indicator light is not illuminated When on, indicator light is illuminated Off if: SV13605 = De-energised On if: SV13605 = Energised | A
|  |  | x | XY13495 | XI13495 | 2000-F13-PID-PR-10013 | F13LU416-CP Mills Seal Grease System Control Panel SAG Mill Seal Grease System Normal Indicator Light | F13LU16 Seal Grse Norm | Off | On |  |  |  |  | Refer to Misc tab for details. Normal indicator is energised if the Seal Grease Fault bit is not active. When off, indicator light is not illuminated When on, indicator light is illuminated Off if: MS_GRSE_CR = Active On if: MS_GRSE_CR = Inactive | A
|  |  | x | XY13912 | XI13912 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Panel Local Mode Enabled Indicator Light | F13LU423 Panel LocMode | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: ALL Equipment AUTO OR MAN (see comment) AND HS13914TEST Inactive On if: Equipment LOCAL (see comment) OR HS13914TEST Inactive If any of the equipment is set to LOCAL mode, make indicator active (refer HS13915, Digital Input tab): F13-HT-529, F13-HT-530, F13-HT-531, F13-HT-532, F13-PO-527, F13-PO-528, TCV13880, F13-PO-529, F13-PO-530, F13-PO-531, F13-PO-534, F13-PO-535 HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13937 | XI13937 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Low Pressure Pump 1 Running Indicator Light | F13LU423 LP Pmp1 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-527 Not Running AND HS13914TEST Inactive On if: F13-PO-527 Running OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13940 | XI13940 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Low Pressure Pump 2 Running Indicator Light | F13LU423 LP Pmp2 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-528 Not Running AND HS13914TEST Inactive On if: F13-PO-528 Running OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13943 | XI13943 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Pinion Pump 1 Running Indicator Light | F13LU423 PinPmp 1 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-534 Not Running AND HS13914TEST Inactive On if: F13-PO-534 Running OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13946 | XI13946 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Pinion Pump 2 Running Indicator Light | F13LU423 PinPmp 2 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-535 Not Running AND HS13914TEST Inactive On if: F13-PO-535 Running OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13949 | XI13949 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel High Pressure Pump 1 Running Indicator Light | F13LU423 HP Pmp 1 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-529 Not Running AND HS13914TEST Inactive On if: F13-PO-529 Running OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13952 | XI13952 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel High Pressure Pump 2 Running Indicator Light | F13LU423 HP Pmp 2 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-530 Not Running AND HS13914TEST Inactive On if: F13-PO-530 Running OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13976 | XI13976 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel High Pressure Pump 3 Running Indicator Light | F13LU423 HP Pmp 3 Run | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-PO-531 Not Running AND HS13914TEST Inactive On if: F13-PO-531 Running OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13916 | XI13916 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Settling Reservoir Oil Level Low Indicator Light | F13LU423 Set Res Lvl Lo | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: LI13874 A_Lo Inactive AND HS13914TEST Inactive On if: LI13874 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13917 | XI13917 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Settling Reservoir Oil Level Low Low Indicator Light | F13LU423 Set Res Lvl LL | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: LI13874 A_LL Inactive AND HS13914TEST Inactive On if: LI13874 A_LL Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13918 | XI13918 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Settling Reservoir Temperature Low Indicator Light | F13LU423 Set Res Temp Lo | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: TI13866 A_Lo Inactive AND HS13914TEST Inactive On if: TI13866 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13920 | XI13920 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Condition Reservoir Oil Level Low Indicator Light | F13LU423 Cond Res Lvl Lo | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: LI13872 A_Lo Inactive AND HS13914TEST Inactive On if: LI13872 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13921 | XI13921 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Condition Reservoir Oil Level Low Low Indicator Light | F13LU423 Cond Res Lvl LL | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: LI13872 A_LL Inactive AND HS13914TEST Inactive On if: LI13872 A_LL Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13922 | XI13922 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Condition Reservoir Temperature High Indicator Light | F13LU423 Cond ResTemp Hi | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: TI13873 A_Hi Inactive AND HS13914TEST Inactive On if: TI13873 A_Hi Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13923 | XI13923 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Condition Reservoir Temperature Low Indicator Light | F13LU423 Cond ResTemp Lo | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: TI13873 A_Lo Inactive AND HS13914TEST Inactive On if: TI13873 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13919 | XI13919 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Reservoir Suction Compartment Heater On Indicator Light | F13LU423 Set Res Htr On | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-HT-529 AND F13-HT-530 Not Running AND HS13914TEST Inactive On if: F13-HT-529 OR F13-HT-530 Running OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13924 | XI13924 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Reservoir Conditioned Compartment Heater On Indicator Light | F13LU423 Cond Res Htr On | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: F13-HT-531 AND F13-HT-532 Not Running AND HS13914TEST Inactive On if: F13-HT-531 OR F13-HT-532 Running OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13926 | XI13926 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel LP Lube Filter Dirty Alarm Indicator Light | F13LU423 LP Fltr Dirty | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: PDI13879 A_HH Inactive AND HS13914TEST Inactive On if: PDI13879 A_HH Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13927 | XI13927 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel LP Lube Filter Blocked Indicator Light | F13LU423 LP Fltr Bypass | Off | On |  |  |  |  | Include Filter Bypass button on the DCS. CRO to manually activate the bypass indicator if F13-FI-426 and F13-FI-427 are being bypassed. When off, indicator light is not illuminated When on, indicator light is illuminated Off if: Bypass Deactivated by CRO AND HS13914TEST Inactive On if: Bypass Activated by CRO OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13928 | XI13928 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel LP Lube Temperature High High Indicator Light | F13LU423 LP Lube Temp HH | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: TI13880 A_HH Inactive AND HS13914TEST Inactive On if: TI13880 A_HH Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13929 | XI13929 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel LP Lube Temperature High Indicator Light | F13LU423 LP Lube Temp Hi | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: TI13880 A_Hi Inactive AND HS13914TEST Inactive On if: TI13880 A_Hi Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13930 | XI13930 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Feed End Bearing Flow Low Indicator Light | F13LU423 FE Brg Flw Lo | Off | On |  |  |  |  | No dedicated Feed End Main Bearing flow indication. This indicator will light up at the same time as XI13933. When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13891 A_Lo Inactive AND HS13914TEST Inactive On if: FI13891 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13931 | XI13931 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Feed End Bearing Oil Pressure High Indicator Light | F13LU423 FE Brg Prs Hi | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: PI13895 A_Hi Inactive AND PI13896 A_Hi Inactive AND PI13897 A_Hi Inactive AND PI13898 A_Hi Inactive AND HS13914TEST Inactive On if: PI13895 A_Hi Active OR PI13896 A_Hi Active OR PI13897 A_Hi Active OR PI13898 A_Hi Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13932 | XI13932 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Feed End High Pressure System Oil Pressure Low Indicator Light | F13LU423 FE HP Prs Lo | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: PI13895 A_Lo Inactive AND PI13896 A_Lo Inactive AND PI13897 A_Lo Inactive AND PI13898 A_Lo Inactive AND HS13914TEST Inactive On if: PI13895 A_Lo Active OR PI13896 A_Lo Active OR PI13897 A_Lo Active OR PI13898 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13933 | XI13933 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Discharge End Bearing Flow Low Indicator Light | F13LU423 DschBrg Flow Lo | Off | On |  |  |  |  | No dedicated Discharge End Main Bearing flow indication. This indicator will light up at the same time as XI13930. When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13891 A_Lo Inactive AND HS13914TEST Inactive On if: FI13891 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13934 | XI13934 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Discharge End Bearing Oil Pressure High Indicator Light | F13LU423 Dsch Brg Prs Hi | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: PI13899 A_Hi Inactive AND PI13900 A_Hi Inactive AND PI13901 A_Hi Inactive AND PI13902 A_Hi Inactive AND HS13914TEST Inactive On if: PI13899 A_Hi Active OR PI13900 A_Hi Active OR PI13901 A_Hi Active OR PI13902 A_Hi Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13935 | XI13935 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Discharge End Oil Pressure Low Indicator Light | F13LU423 DE HP Prs Lo | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: PI13899 A_Lo Inactive AND PI13900 A_Lo Inactive AND PI13901 A_Lo Inactive AND PI13902 A_Lo Inactive AND HS13914TEST Inactive On if: PI13899 A_Lo Active OR PI13900 A_Lo Active OR PI13901 A_Lo Active OR PI13902 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13936 | XI13936 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Thrust Rail Flow low Indicator Light | F13LU423 Thr Rail Flw Lo | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13892 A_Lo Inactive AND HS13914TEST Inactive On if: FI13892 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13941 | XI13941 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Conditioning Circuit Flow Low Indicator Light | F13LU423 Cond. Flow Lo | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13881 A_Lo Inactive AND HS13914TEST Inactive On if: FI13881 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13942 | XI13942 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Conditioning Circuit Flow Low Low Indicator Light | F13LU423 Cond. Flow LL | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13881 A_LL Inactive AND HS13914TEST Inactive On if: FI13881 A_LL Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13951 | XI13951 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Pinion Bearing Discharge End Left Flow Low Indicator Light | F13LU423 PBrg Dc L FlwLo | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13908 A_Lo Inactive AND HS13914TEST Inactive On if: FI13908 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | B
|  |  | x | XY13948 | XI13948 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Pinion Bearing Discharge End Right Flow Low Indicator Light | F13LU423 PBrg Dc R FlwLo | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13909 A_Lo Inactive AND HS13914TEST Inactive On if: FI13909 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | B
|  |  | x | XY13950 | XI13950 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Pinion Bearing Feed End Left Flow Low Indicator Light | F13LU423 PBrg Fd L FlwLo | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13910 A_Lo Inactive AND HS13914TEST Inactive On if: FI13910 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | B
|  |  | x | XY13947 | XI13947 | 2000-F13-PID-PR-10011 | F13LU423-CP Ball Mill Main Bearings Lubrication System Control Panel Pinion Bearing Feed End Right Flow Low Indicator Light | F13LU423 PBrg Fd R FlwLo | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: FI13911 A_Lo Inactive AND HS13914TEST Inactive On if: FI13911 A_Lo Active OR HS13914TEST Active HS13914 Is a physical Lamp Test pushbutton | B
|  |  | x | XY13742 | XI13742 | 2000-F13-PID-PR-10013 | F13HU417-CP Ball Mill Brake System Local Control Panel Reservoir Level Low Warning Indicator Light | F13HU417 Res Lvl Lo | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: LAL13802 Inactive AND HS13747TEST Inactive On if: LAL13802 Active OR HS13747TEST Active HS13747 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13744 | XI13744 | 2000-F13-PID-PR-10013 | F13HU417-CP Ball Mill Brake System Local Control Panel Reservoir Oil Temperature High Indicator Light | F13HU417 Res Temp Hi | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: TAH13803 Inactive AND HS13747TEST Inactive On if: TAH13803 Active OR HS13747TEST Active HS13747 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13745 | XI13745 | 2000-F13-PID-PR-10013 | F13HU417-CP Ball Mill Brake System Local Control Panel Local Operation Indicator Light | F13HU417 Local Op | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: HS13748MODE Local Deselected AND HS13747TEST Inactive On if: HS13748MODE Local Selected OR HS13747TEST Active HS13747 Is a physical Lamp Test pushbutton | A
|  |  | x | XY13746 | XI13746 | 2000-F13-PID-PR-10013 | F13HU417-CP Ball Mill Brake System Local Control Panel Brake Released Indicator Light | F13HU417 Brake Rel | Off | On |  |  |  |  | When off, indicator light is not illuminated When on, indicator light is illuminated Off if: [ZAH13795 OR ZAH13797 On (Brake Engaged)] AND HS13747TEST Inactive On if: [ZAH13795 AND ZAH13797 Off (Brake Released)] OR HS13747TEST Active HS13747 Is a physical Lamp Test pushbutton | B
|  |  |  | XY13201A | XC13201A | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Start Signal | F13LU423 OCM Start | N_Active | Start: Start F13-PO-446 |  | Hardwired to PCS |  |  | Starts F13-PO-446 Latch when activated, unlatch if XC13201B = Stop If 13PO446STF.PV.1 = Active (rising-edge) AND F13-PO-446 in AUTO, activate (one-shot) F13LU423_CMD1 after 5 second delay If 13PO446STF.PV.1 = Inactive (falling-edge), activate (one-shot) F13LU423_CMD9 | 1 | 2025-03-18 | Modbus Data map reviewed by Controls. Logic reviewed
|  |  |  | XY13201B | XC13201B | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Stop Signal | F13LU423 OCM Stop | N_Active | Stop Stop F13-PO-446 |  | Hardwired to PCS |  |  | Stops F13-PO-446 Pushbutton. Unlatch XC13201A if XC13201B = Stop | 0
|  |  |  | F13LU423CMD1 | F13LU423_CMD1 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Oil Command Bit 1 (Start Test) | F13LU423 Start Test | N_Start | Start |  |  |  |  | SoftTag Logic: If 13PO446STF.PV.1 = Active (rising-edge) AND F13-PO-446 in AUTO, activate (one-shot) F13LU423_CMD1 after 5 second delay Include as pushbutton on DCS to start tests manually. Button can only be used if F13-PO-446 in manual. Register 21 Bit 1 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics OCM15 must be set up such that tests are initiated via the DCS (continous and automatic testing disabled) | 1 | 2025-03-18 | Modbus Data map reviewed by Controls. Changed from analogue output to digital outputs and logic updated
|  |  |  | F13LU423CMD9 | F13LU423_CMD9 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication Unit OCM Unit Oil Command Bit 9 (Stop Test) | F13LU423 Stop Test | N_Stop | Stop |  |  |  |  | SoftTag Logic: If X13PO446STF.PV.1 = Inactive (falling-edge), activate (one-shot) F13LU423_CMD9 Include as pushbutton on DCS to stop tests manually. Button can be used in all modes. Register 21 Bit 9 Refer to 'OCM15 User Guide: Model Numbers FD330073 and FD330074' for Modbus Register Map details and graphics OCM15 must be set up such that tests are initiated via the DCS (continous and automatic testing disabled) | 1K158:Q159P159N158:H158:Q159 | 2025-03-18 | Modbus Data map reviewed by Controls. Changed from analogue output to digital outputs and logic updated
|  |  |  | XY13279I | XI13279I | 2000-F13-PID-PR-10006 | F13HU403-CP Recycle Crusher C Hydraulic Unit Control Panel Low Tramp Pressure Indicator Light | F13HU403 Low Tramp | Off | On |  |  |  |  | OFF = PI13264 > A_Lo ON = PI13264 < A_Lo | B
|  |  |  | XY13279J | XI13279J | 2000-F13-PID-PR-10006 | F13HU403-CP Recycle Crusher C Hydraulic Unit Control Panel Low Clamp Pressure Indicator Light | F13HU403 Low Clamp | Off | On |  |  |  |  | OFF = PI13263 > A_Lo ON = PI13263 < A_Lo | B
|  |  |  | XY13279K | XI13279K | 2000-F13-PID-PR-10006 | F13HU403-CP Recycle Crusher C Hydraulic Unit Control Panel Common Fault Indicator Light | F13HU403 Common Fault | Off | On |  |  |  |  | OFF = F13-PO-408 Healthy ON = F13-PO-408 Interlock is Active Refer to Drives tab, F13-PO-408 for interlocks | B
|  |  |  | XY13343I | XI13343I | 2000-F13-PID-PR-10006 | F13HU404-CP Recycle Crusher D Hydraulic Unit Control Panel Low Tramp Pressure Indicator Light | F13HU404 Low Tramp | Off | On |  |  |  |  | OFF = PI13324 > A_Lo ON = PI13324 < A_Lo | B
|  |  |  | XY13343J | XI13343J | 2000-F13-PID-PR-10006 | F13HU404-CP Recycle Crusher D Hydraulic Unit Control Panel Low Clamp Pressure Indicator Light | F13HU404 Low Clamp | Off | On |  |  |  |  | OFF = PI13323 > A_Lo ON = PI13323 < A_Lo | B
|  |  |  | XY13343K | XI13343K | 2000-F13-PID-PR-10006 | F13HU404-CP Recycle Crusher D Hydraulic Unit Control Panel Common Fault Indicator Light | F13HU404 Common Fault | Off | On |  |  |  |  | OFF = F13-PO-409 Healthy ON = F13-PO-409 Interlock is Active Refer to Drives tab, F13-PO-409 for interlocks | B
|  |  |  | HS13470 | HS13470STT | 2000-F13-PID-PR-10012 | F13-CU-402 Chiller 1 Start / Stop | F13CU402 Start / Stop | N_Active: Stop F13-CU-402 | Active: Start F13-CU-402 |  |  |  |  | On/Off Relay, DI-01 - used for unit on/off when its in remote control Ref: 2000-ME034-M01-10002 | B
|  |  |  | HS13471 | HS13471STT | 2000-F13-PID-PR-10012 | F13-CU-403 Chiller 2 Start / Stop | F13CU403 Start / Stop | N_Active: Stop F13-CU-403 | Active: Start F13-CU-403 |  |  |  |  | On/Off Relay, DI-01 - used for unit on/off when its in remote control Ref: 2000-ME034-M01-10002 | B
|  |  |  | HS13472 | HS13472STT | 2000-F13-PID-PR-10012 | F13-CU-404 Chiller 3 Start / Stop | F13CU404 Start / Stop | N_Active: Stop F13-CU-404 | Active: Start F13-CU-404 |  |  |  |  | On/Off Relay, DI-01 - used for unit on/off when its in remote control Ref: 2000-ME034-M01-10002 | B
|  |  |  | HS13473 | HS13473STT | 2000-F13-PID-PR-10012 | F13-CU-405 Chiller 4 Start / Stop | F13CU405 Start / Stop | N_Active: Stop F13-CU-405 | Active: Start F13-CU-405 |  |  |  |  | On/Off Relay, DI-01 - used for unit on/off when its in remote control Ref: 2000-ME034-M01-10002 | B
|  |  |  | SW10BT1CBCC | SW10BT1CB_CC | N/A | F00-SW-010 Bus-Tie 1 Circuit Breaker Close Command | F00SW010 BT1 CB Close | N_Active | Close | [5 empty] | 0
|  |  |  | SW10BT1CBOC | SW10BT1CB_OC | N/A | F00-SW-010 Bus-Tie 1 Circuit Breaker Open Command | F00SW010 BT1 CB Open | N_Active | Open | [5 empty] | 0
|  |  |  | SW10BT2CBCC | SW10BT2CB_CC | N/A | F00-SW-010 Bus-Tie 2 Circuit Breaker Close Command | F00SW010 BT2 CB Close | N_Active | Close | [5 empty] | 0
|  |  |  | SW10BT2CBOC | SW10BT2CB_OC | N/A | F00-SW-010 Bus-Tie 2 Circuit Breaker Open Command | F00SW010 BT2 CB Open | N_Active | Open | [5 empty] | 0
|  |  |  | XY13550A | XI13550A | 2000-F13-PID-PR-10002 | F13HU407-CP Cyclone Feed Pump Suction Valve Hydraulic Power Unit Control Panel Valve Opened Indicator Signal | F13HU407 Opened | N_Active | Active |  |  |  |  | Logic: Activate if XV13082 = open else inactive | 1 | 2025-07-02 | CR-021
|  |  |  | XY13550B | XI13550B | 2000-F13-PID-PR-10002 | F13HU407-CP Cyclone Feed Pump Suction Valve Hydraulic Power Unit Control Panel Valve Closed Indicator Signal | F13HU407 Closed | N_Active | Active |  |  |  |  | Logic: Activate if XV13082 = closed else inactive | 1 | 2025-07-02 | CR-021
|  |  |  | XY13550C | XI13550C | 2000-F13-PID-PR-10002 | F13HU407-CP Cyclone Feed Pump Suction Valve Hydraulic Power Unit Control Panel System Healthy Indicator Signal | F13HU407 Healthy | N_Active | Active |  |  |  |  | Logic: No safety or process interlocks active on F13HU407 | 1 | 2025-07-02 | CR-021
|  |  |  | XY13550D | XI13550D | 2000-F13-PID-PR-10002 | F13HU407-CP Cyclone Feed Pump Suction Valve Hydraulic Power Unit Control Panel Oil Temperature High Indicator Signal | F13HU407 Hi Temp | N_Active | Active |  |  |  |  | Logic: Activate if TI13536 >= A_Hi else inactive | 1 | 2025-07-02 | CR-021
|  |  |  | XY13550E | XI13550E | 2000-F13-PID-PR-10002 | F13HU407-CP Cyclone Feed Pump Suction Valve Hydraulic Power Unit Control Panel Oil Level Low Indicator Signal | F13HU407 Oil Lo | N_Active | Active |  |  |  |  | Logic: Activate if LI13537 <= A_Lo else inactive | 1 | 2025-07-02 | CR-021
|  |  |  | XY13550F | XI13550F | 2000-F13-PID-PR-10002 | F13HU407-CP Cyclone Feed Pump Suction Valve Hydraulic Power Unit Control Panel Local Control Enable Indicator Signal | F13HU407 Local Enabled | N_Active | Active |  |  |  |  | Logic: Activate if HS13543ALOC = local else inactive | 1 | 2025-07-02 | CR-021
|  |  |  | XY13550G | XI13550G | 2000-F13-PID-PR-10002 | F13HU407-CP Cyclone Feed Pump Suction Valve Hydraulic Power Unit Control Panel Hpu Running Indicator Signal | F13HU407 Running | N_Active | Active |  |  |  |  | Logic: Activate if F13HU407 = running else inactive | 1 | 2025-07-02 | CR-021
|  |  |  | XY13550H | XI13550H | 2000-F13-PID-PR-10002 | F13HU407-CP Cyclone Feed Pump Suction Valve Hydraulic Power Unit Control Panel Filter Blocked Indicator Signal | F13HU407 Filter Block | N_Active | Active |  |  |  |  | Logic: Activate if PAH13538 alarm or PI13535 >= A_Hi else inactive | 1 | 2025-07-02 | CR-021
|  |  |  | F13CV403ACK1 | XC13000 | 2000-F13-PID-PR-10001 | F13-CV-403 SAG MILL FEED CONVEYOR BELT RIP SWITCH RESET CONTROL SIGNAL | F13CV403 BRS Reset | N_Active | Active |  |  |  |  | Include on level 3 & 4 graphic. Ensure output is pulsed when button is pressed Variation NOFD153 | 1 | 2025-05-28 | Variation NOFD153
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 176 | 176

## 5. Totalisers
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - MILLING & CLASSIFICATION (F13)
2000-F13-LST-PR-10001
TOTALISERS
[11 empty] | Reset Period | [6 empty] | C1 Sign Off |  | C2 Sign Off |  | Comments
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | Type | P&ID | Description | Abbreviated Description (Faceplate) | Units | Shift | Day | Cont | Comments | Rev | Change Date | Change Reference | OK | Date | OK | Date
|  |  |  | WQS13055 | WQI13055 | WQI | 2000-F13-PID-PR-10001 | F13-CV-403 Weightometer Totaliser (Wet) | F13CV403 Totaliser (Wet) | t | X | X | X | WS13055 Pulse Tonnes utilised for totaliser calculation | 0
|  |  |  | WIC13121 | WQI13121 | WQI | 2000-F13-PID-PR-10001 | F13-CV-403 Weightometer Totaliser (Dry) | F13CV403 Totaliser (Dry) | t | X | X | X |  | A | [6 empty] | Tested by simulating tons per hour value on conveyor and the Totaliser functioned as per intent.
|  |  |  | WI13090 | WQI13090 | WQI | 2000-F13-PID-PR-10002 | F13-CY-401 Feed Solids Flowrate Totaliser | F13CY401 Totaliser (Dry) | t | X | X | X |  | A | [6 empty] | Tested by simulating tons per hour value on conveyor and the Totaliser functioned as per intent.
|  |  |  | WS13195 | WQI13195 | WQI | 2000-F13-PID-PR-10005 | F13-CV-405 Weightometer Totaliser (Wet) | F13CV405 Totaliser (Wet) | t | X | X | X | WS13195 Pulse Tonnes utilised for totaliser calculation | 0
|  |  |  | ZI13035 | ZQI13035 | ZQI | 2000-F13-PID-PR-10001 | F13-BLC-401 Mill Ball Indexer | F13BLC401 SAG Ball Total | # | X | X | X | Totaliser counts the number of balls that have indexed through the F13-CH-475. Count up totaliser by 1 when ZI13035 is energised (Rising-Edge Trigger). | A
|  |  |  | WI13285C | WQI13285C | WQI | 2000-F13-PID-PR-10004 | F13-BN-61A Mill Ball Transfer Totaliser | F13-BLC-402 Totaliser | kg | X | X | X | Totalise as per F13-SEQ-0037 Step 37 Controls based on ME067 Existing Ball Charging System. TBC Vendor Functional Description, 2000-ME057-M01-10001 | 1 | 2025-08-22
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 6 | 6

## 6. OnOff Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - MILLING & CLASSIFICATION (F13)
2000-F13-LST-PR-10001
OPEN-CLOSE VALVES
[14 empty] | Permissives and Trips | [12 empty] | Change Date | Change Reference | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open | Close | Bypass | Reset Required | Comments | Rev |  |  | OK | Date | OK | Date | C1 Sign Off Comments
|  |  |  | SV13061 | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Spray Water Valve 1 | F13CV403 RW Spray 1 | 11 | FC | X | X | F13-FA-411 Running | F13-FA-411 Not Running for 30 seconds | [12 empty] | B
|  |  |  | SV13062 | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Spray Water Valve 2 | F13CV403 RW Spray 2 | 11 | FC | X | X | F13-FA-412 Running | F13-FA-412 Not Running for 30 seconds | [12 empty] | B
|  |  |  | SV13063 | 2000-F13-PID-PR-10001 | F13-CV-403 SAG Mill Feed Conveyor Spray Water Valve 3 | F13CV403 RW Spray 3 | 11 | FC | X | X | F13-FA-414 Running | F13-FA-414 Not Running for 30 seconds | [12 empty] | 0
|  |  |  | XV13069 | 2000-F13-PID-PR-10001 | F13-BN-402 Emergency Feed Bin Spray Water Valve | F13BN402 RW Spray | 15 | FC | X | X | F13-FA-414 Running | F13-FA-414 Not Running for 30 seconds | [11 empty] | Electric motorised valve. IO list output is XY13069. | 1 | 6/03/2025 15/05/25 | https://pastech-2955.atlassian.net/browse/KAN-1412 Detail change, but no change required on DCS side
|  |  |  | SV13344 | 2000-F13-PID-PR-10006 | F13-CV-406 Recycle Crusher Discharge Conveyor Water Spray Solenoid 1 | F13CV406 RW Spray 1 | 11 | FC | X | X | F13-CC-401 AND F13-FV-401 Running | F13-CC-401 AND F13-FV-401 Not Running for 30 seconds | [12 empty] | B
|  |  |  | SV13345 | 2000-F13-PID-PR-10006 | F13-CV-406 Recycle Crusher Discharge Conveyor Water Spray Solenoid 2 | F13CV406 RW Spray 2 | 11 | FC | X | X | F13-CC-402 AND F13-FV-402 Running | F13-CC-402 AND F13-FV-402 Not running for 30 seconds | [12 empty] | B
|  |  |  | XV13077 | 2000-F13-PID-PR-10002 | F13-HP-401 Primary Cyclone Feed Hopper Drain Valve | F13HP401 Drain | 4 | FO | X | X | As per F13-SEQ-0010 | As per F13-SEQ-0009 | [12 empty] | A
|  |  |  | XV13081 | 2000-F13-PID-PR-10002 | F13-PP-401 Cyclone Feed Pump Suction Drain Valve | F13PP401 Suction Drain | 4 | FO | X | X | As per F13-SEQ-0010 | As per F13-SEQ-0009 | CT1 | F13-PP-401 Running | F13-PP-401 Running | 3 |  |  |  |  | X | X |  | Close suction drain valve if Cyclone Feed Pump is running | 0
|  |  |  | XV13082 | 2000-F13-PID-PR-10002 | F13-PP-401 Cyclone Feed Pump Suction Valve | F13PP401 Suction | 5 | FL | X | X | As per F13-SEQ-0009 | As per F13-SEQ-0010 | [12 empty] | 1 | 2/07/2025 2/10/2025 | CR-021 Removed OP/CP as per PAStech/FC discussion
|  |  |  | XV13074 | 2000-F13-PID-PR-10002 | F13-PP-401 Cyclone Feed Pump Process Water Addition Valve | F13HP401 PW Flush | 4 | FC | X | X |  | As per F13-SEQ-0009 | [12 empty] | A
|  |  |  | XV13083 | 2000-F13-PID-PR-10002 | F13-PP-401 Cyclone Feed Pump Suction Process Water Valve | F13PP401 PW Flush | 4 | FC | X | X |  | As per F13-SEQ-0009 | [12 empty] | A
|  |  |  | XV13084 | 2000-F13-PID-PR-10002 | F13-PP-401 Cyclone Feed Pump Discharge Drain Valve | F13PP401 Disch Drain | 4 | FO | X | X | As per F13-SEQ-0010 | As per F13-SEQ-0009 | [12 empty] | A
|  |  |  | XV13114 | 2000-F13-PID-PR-10002 | F13-FD-401 Cyclone Underflow Boil Box to Ball Mill Feed Box 1 Line 1 Valve | F13FD401 CUF to MB 1 | 3 | FL | X | X | As per F13FD401_FP1 | As per F13FD401_FP1 | CT1 | MB_NCR_ILK Active | Ball Mill Delayed Stop Active | 0 |  |  |  |  | X | X |  | Selection on F13FD401_FP1 will cause the respective valves in AUTO to actuate to position. Refer to '12. Misc' tab for details. Closed trip to bypass feed from the Ball Mill when a Delayed Stop interlock becomes active. | A
[14 empty] | CT2 | MB_CR_ILK Active | Ball Mill Instantaneous Stop Active | 0 |  |  |  |  | X | X |  | Closed trip to bypass feed from the Ball Mill when a Instantaneous Stop interlock becomes active. | A
|  |  |  | XV13115 | 2000-F13-PID-PR-10002 | F13-FD-401 Cyclone Underflow Boil Box to Ball Mill Feed Box 1 Line 2 Valve | F13FD401 CUF to MB 2 | 3 | FL | X | X | As per F13FD401_FP1 | As per F13FD401_FP1 | CT1 | MB_NCR_ILK Active | Ball Mill Delayed Stop Active | 0 |  |  |  |  | X | X |  | Selection on F13FD401_FP1 will cause the respective valves in AUTO to actuate to position. Refer to '12. Misc' tab for details. Closed trip to bypass feed from the Ball Mill when a Delayed Stop interlock becomes active. | A
[14 empty] | CT2 | MB_CR_ILK Active | Ball Mill Instantaneous Stop Active | 0 |  |  |  |  | X | X |  | Closed trip to bypass feed from the Ball Mill when a Instantaneous Stop interlock becomes active. | A
|  |  |  | XV13116 | 2000-F13-PID-PR-10002 | F13-FD-401 Cyclone Underflow Boil Box to SAG Mill Feed Box Valve | F13FD401 CUF to MS | 3 | FL | X | X | As per F13FD401_FP1 | As per F13FD401_FP1 | [12 empty] | A
|  |  |  | XV13088 | 2000-F13-PID-PR-10002 | F14-CY-411 Gravity Cyclone 1 Flushing Valve | F14CY411 Flush | 4 | FC | X | X | As per F14-SEQ-0003 | As per F14-SEQ-0003 | [11 empty] | Gravity Cyclones are flushed during the Gravity Circuit stop sequence | A
|  |  |  | XV13089 | 2000-F13-PID-PR-10002 | F14-CY-412 Gravity Cyclone 2 Flushing Valve | F14CY412 Flush | 4 | FC | X | X | As per F14-SEQ-0004 | As per F14-SEQ-0004 | [11 empty] | Gravity Cyclones are flushed during the Gravity Circuit stop sequence | A
|  |  |  | XV13094 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 1 | F13CY401 Isolation 1 | 3 | FL | X | X | If XV13094 is next in the priority system AND HS13092 = Level Control, then open XV13094 according to F13CALC10007. OR If XV13094 is next in the priority system AND HS13092 = Pressure Control, then open XV13094 according to F13CALC10011. OR IF XV13094 = DUTY and within the 6 highest priority duty valves, then open XV13094. See F13CY401_FP1 for description of priority system conditions | If XV13094 is next in the priority system AND HS13092 = Level Control, then close XV13094 according to F13CALC10007. OR If XV13094 is next in the priority system AND HS13092 = Pressure Control, then close XV13094 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13094 = STANDBY Refer F13CY401_FP1 | XV13094 Standby | 0 |  |  |  |  | X | X |  | XV13094 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13095 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 2 | F13CY401 Isolation 2 | 3 | FL | X | X | If XV13095 is next in the priority system AND HS13092 = Level Control, then open XV13095 according to F13CALC10007. OR If XV13095 is next in the priority system AND HS13092 = Pressure Control, then open XV13095 according to F13CALC10011. OR IF XV13095 = DUTY and within the 6 highest priority duty valves, then open XV13095. See F13CY401_FP1 for description of priority system conditions | If XV13095 is next in the priority system AND HS13092 = Level Control, then close XV13095 according to F13CALC10007. OR If XV13095 is next in the priority system AND HS13092 = Pressure Control, then close XV13095 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13095 = STANDBY Refer F13CY401_FP1 | XV13095 Standby | 0 |  |  |  |  | X | X |  | XV13095 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13096 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 3 | F13CY401 Isolation 3 | 3 | FL | X | X | If XV13096 is next in the priority system AND HS13092 = Level Control, then open XV13096 according to F13CALC10007. OR If XV13096 is next in the priority system AND HS13092 = Pressure Control, then open XV13096 according to F13CALC10011. OR IF XV13096 = DUTY and within the 6 highest priority duty valves, then open XV13096. See F13CY401_FP1 for description of priority system conditions | If XV13096 is next in the priority system AND HS13092 = Level Control, then close XV13096 according to F13CALC10007. OR If XV13096 is next in the priority system AND HS13092 = Pressure Control, then close XV13096 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13096 = STANDBY Refer F13CY401_FP1 | XV13096 Standby | 0 |  |  |  |  | X | X |  | XV13096 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13097 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 4 | F13CY401 Isolation 4 | 3 | FL | X | X | If XV13097 is next in the priority system AND HS13092 = Level Control, then open XV13097 according to F13CALC10007. OR If XV13097 is next in the priority system AND HS13092 = Pressure Control, then open XV13097 according to F13CALC10011. OR IF XV13097 = DUTY and within the 6 highest priority duty valves, then open XV13097. See F13CY401_FP1 for description of priority system conditions | If XV13097 is next in the priority system AND HS13092 = Level Control, then close XV13097 according to F13CALC10007. OR If XV13097 is next in the priority system AND HS13092 = Pressure Control, then close XV13097 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13097 = STANDBY Refer F13CY401_FP1 | XV13097 Standby | 0 |  |  |  |  | X | X |  | XV13097 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13098 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 5 | F13CY401 Isolation 5 | 3 | FL | X | X | If XV13098 is next in the priority system AND HS13092 = Level Control, then open XV13098 according to F13CALC10007. OR If XV13098 is next in the priority system AND HS13092 = Pressure Control, then open XV13098 according to F13CALC10011. OR IF XV13098 = DUTY and within the 6 highest priority duty valves, then open XV13098. See F13CY401_FP1 for description of priority system conditions | If XV13098 is next in the priority system AND HS13092 = Level Control, then close XV13098 according to F13CALC10007. OR If XV13098 is next in the priority system AND HS13092 = Pressure Control, then close XV13098 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13098 = STANDBY Refer F13CY401_FP1 | XV13098 Standby | 0 |  |  |  |  | X | X |  | XV13098 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13099 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 6 | F13CY401 Isolation 6 | 3 | FL | X | X | If XV13099 is next in the priority system AND HS13092 = Level Control, then open XV13099 according to F13CALC10007. OR If XV13099 is next in the priority system AND HS13092 = Pressure Control, then open XV13099 according to F13CALC10011. OR IF XV13099 = DUTY and within the 6 highest priority duty valves, then open XV13099. See F13CY401_FP1 for description of priority system conditions | If XV13099 is next in the priority system AND HS13092 = Level Control, then close XV13099 according to F13CALC10007. OR If XV13099 is next in the priority system AND HS13092 = Pressure Control, then close XV13099 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13099 = STANDBY Refer F13CY401_FP1 | XV13099 Standby | 0 |  |  |  |  | X | X |  | XV13099 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13100 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 7 | F13CY401 Isolation 7 | 3 | FL | X | X | If XV13100 is next in the priority system AND HS13092 = Level Control, then open XV13100 according to F13CALC10007. OR If XV13100 is next in the priority system AND HS13092 = Pressure Control, then open XV13100 according to F13CALC10011. OR IF XV13100 = DUTY and within the 6 highest priority duty valves, then open XV13100. See F13CY401_FP1 for description of priority system conditions | If XV13100 is next in the priority system AND HS13092 = Level Control, then close XV13100 according to F13CALC10007. OR If XV13100 is next in the priority system AND HS13092 = Pressure Control, then close XV13100 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13100 = STANDBY Refer F13CY401_FP1 | XV13100 Standby | 0 |  |  |  |  | X | X |  | XV13100 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13101 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 8 | F13CY401 Isolation 8 | 3 | FL | X | X | If XV13101 is next in the priority system AND HS13092 = Level Control, then open XV13101 according to F13CALC10007. OR If XV13101 is next in the priority system AND HS13092 = Pressure Control, then open XV13101 according to F13CALC10011. OR IF XV13101 = DUTY and within the 6 highest priority duty valves, then open XV13101. See F13CY401_FP1 for description of priority system conditions | If XV13101 is next in the priority system AND HS13092 = Level Control, then close XV13101 according to F13CALC10007. OR If XV13101 is next in the priority system AND HS13092 = Pressure Control, then close XV13101 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13101 = STANDBY Refer F13CY401_FP1 | XV13101 Standby | 0 |  |  |  |  | X | X |  | XV13101 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13102 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 9 | F13CY401 Isolation 9 | 3 | FL | X | X | If XV13102 is next in the priority system AND HS13092 = Level Control, then open XV13102 according to F13CALC10007. OR If XV13102 is next in the priority system AND HS13092 = Pressure Control, then open XV13102 according to F13CALC10011. OR IF XV13102 = DUTY and within the 6 highest priority duty valves, then open XV13102. See F13CY401_FP1 for description of priority system conditions | If XV13102 is next in the priority system AND HS13092 = Level Control, then close XV13102 according to F13CALC10007. OR If XV13102 is next in the priority system AND HS13092 = Pressure Control, then close XV13102 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13102 = STANDBY Refer F13CY401_FP1 | XV13102 Standby | 0 |  |  |  |  | X | X |  | XV13102 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13103 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 10 | F13CY401 Isolation 10 | 3 | FL | X | X | If XV13103 is next in the priority system AND HS13092 = Level Control, then open XV13103 according to F13CALC10007. OR If XV13103 is next in the priority system AND HS13092 = Pressure Control, then open XV13103 according to F13CALC10011. OR IF XV13103 = DUTY and within the 6 highest priority duty valves, then open XV13103. See F13CY401_FP1 for description of priority system conditions | If XV13103 is next in the priority system AND HS13092 = Level Control, then close XV13103 according to F13CALC10007. OR If XV13103 is next in the priority system AND HS13092 = Pressure Control, then close XV13103 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13103 = STANDBY Refer F13CY401_FP1 | XV13103 Standby | 0 |  |  |  |  | X | X |  | XV13103 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13104 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 11 | F13CY401 Isolation 11 | 3 | FL | X | X | If XV13104 is next in the priority system AND HS13092 = Level Control, then open XV13104 according to F13CALC10007. OR If XV13104 is next in the priority system AND HS13092 = Pressure Control, then open XV13104 according to F13CALC10011. OR IF XV13104 = DUTY and within the 6 highest priority duty valves, then open XV13104. See F13CY401_FP1 for description of priority system conditions | If XV13104 is next in the priority system AND HS13092 = Level Control, then close XV13104 according to F13CALC10007. OR If XV13104 is next in the priority system AND HS13092 = Pressure Control, then close XV13104 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13104 = STANDBY Refer F13CY401_FP1 | XV13104 Standby | 0 |  |  |  |  | X | X |  | XV13104 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13105 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 12 | F13CY401 Isolation 12 | 3 | FL | X | X | If XV13105 is next in the priority system AND HS13092 = Level Control, then open XV13105 according to F13CALC10007. OR If XV13105 is next in the priority system AND HS13092 = Pressure Control, then open XV13105 according to F13CALC10011. OR IF XV13105 = DUTY and within the 6 highest priority duty valves, then open XV13105. See F13CY401_FP1 for description of priority system conditions | If XV13105 is next in the priority system AND HS13092 = Level Control, then close XV13105 according to F13CALC10007. OR If XV13105 is next in the priority system AND HS13092 = Pressure Control, then close XV13105 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13105 = STANDBY Refer F13CY401_FP1 | XV13105 Standby | 0 |  |  |  |  | X | X |  | XV13105 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13106 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 13 | F13CY401 Isolation 13 | 3 | FL | X | X | If XV13106 is next in the priority system AND HS13092 = Level Control, then open XV13106 according to F13CALC10007. OR If XV13106 is next in the priority system AND HS13092 = Pressure Control, then open XV13106 according to F13CALC10011. OR IF XV13106 = DUTY and within the 6 highest priority duty valves, then open XV13106. See F13CY401_FP1 for description of priority system conditions | If XV13106 is next in the priority system AND HS13092 = Level Control, then close XV13106 according to F13CALC10007. OR If XV13106 is next in the priority system AND HS13092 = Pressure Control, then close XV13106 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13106 = STANDBY Refer F13CY401_FP1 | XV13106 Standby | 0 |  |  |  |  | X | X |  | XV13106 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13107 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 14 | F13CY401 Isolation 14 | 3 | FL | X | X | If XV13107 is next in the priority system AND HS13092 = Level Control, then open XV13107 according to F13CALC10007. OR If XV13107 is next in the priority system AND HS13092 = Pressure Control, then open XV13107 according to F13CALC10011. OR IF XV13107 = DUTY and within the 6 highest priority duty valves, then open XV13107. See F13CY401_FP1 for description of priority system conditions | If XV13107 is next in the priority system AND HS13092 = Level Control, then close XV13107 according to F13CALC10007. OR If XV13107 is next in the priority system AND HS13092 = Pressure Control, then close XV13107 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13107 = STANDBY Refer F13CY401_FP1 | XV13107 Standby | 0 |  |  |  |  | X | X |  | XV13107 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13108 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Isolation Valve 15 | F13CY401 Isolation 15 | 3 | FL | X | X | If XV13108 is next in the priority system AND HS13092 = Level Control, then open XV13108 according to F13CALC10007. OR If XV13108 is next in the priority system AND HS13092 = Pressure Control, then open XV13108 according to F13CALC10011. OR IF XV13108 = DUTY and within the 6 highest priority duty valves, then open XV13108. See F13CY401_FP1 for description of priority system conditions | If XV13108 is next in the priority system AND HS13092 = Level Control, then close XV13108 according to F13CALC10007. OR If XV13108 is next in the priority system AND HS13092 = Pressure Control, then close XV13108 according to F13CALC10011 See F13CY401_FP1 for description of priority system conditions | CT1 | XV13108 = STANDBY Refer F13CY401_FP1 | XV13108 Standby | 0 |  |  |  |  | X | X |  | XV13108 is selected as STANDBY on faceplate F13CY401_FP1 If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) Refer to HS13092 for Pressure or Level control selection Refer to F13CY401_FP1 Misc tab for auto open and close operating description. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | XV13110 | 2000-F13-PID-PR-10002 | F14-CY-411 Gravity Cyclone 1 Isolation Valve | F13CY411 Isolation | 3 | FL | X | X | As per F14-SEQ-0001 | As per F14-SEQ-0003 | CT1 | F14-SC-405 Not Running | F14-SC-405 Not Running | 0 |  |  |  |  | X | X |  | Close Gravity Cyclone 1 feed valve if Gravity Screen 1 is stopped | B
[14 empty] | CT2 | F14-SEQ-0005 Hold AND XV14031 Not Closed | F14-SEQ-0005 Hold AND XV14031 Open | 35 |  |  |  |  | X | X | X | Close Gravity Cyclone 1 feed valve if F14-SEQ-0005 is in HOLD state and XV14031 is not fully closed. On-delay timer accounts for closing duration of DN400 valve. TBC during commissioning. | B
[14 empty] | CT3 | XV13116 Opened | XV13116 Opened | 5 |  |  |  |  | X | X |  | Gravity Circuit bypassed if circuit is in SSSAG configuration (XV13116 = Opened) | B
|  |  |  | XV13111 | 2000-F13-PID-PR-10002 | F14-CY-412 Gravity Cyclone 2 Isolation Valve | F13CY412 Isolation | 3 | FL | X | X | As per F14-SEQ-0002 | As per F14-SEQ-0004 | CT1 | F14-SC-406 Not Running | F14-SC-406 Not Running | 0 |  |  |  |  | X | X |  | Close Gravity Cyclone 2 feed valve if Gravity Screen 2 is stopped | B
[14 empty] | CT2 | F14-SEQ-0006 Hold AND XV14041 Not Closed | F14-SEQ-0006 Hold AND XV14041 Open | 35 |  |  |  |  | X | X | X | Close Gravity Cyclone 2 feed valve if F14-SEQ-0006 is in HOLD state and XV14041 is not fully closed. On-delay timer accounts for closing duration of DN400 valve. TBC during commissioning. | B
[14 empty] | CT3 | XV13116 Opened | XV13116 Opened | 5 |  |  |  |  | X | X |  | Gravity Circuit bypassed if circuit is in SSSAG configuration (XV13116 = Opened) | B
|  |  |  | XV13460 | 2000-F24-PID-PR-10004 | F13-PP-401 Cyclone Feed Pump Gland Water Valve | F13PP401 Gland Water | 8 | FO | X | X | As per F13-SEQ-0009 OR F13-PP-401 Start | As per F13-SEQ-0010 | [12 empty] | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/PL-174
|  |  |  | XV13386 | 2000-F13-PID-PR-10007 | F13-GA-421 Trash Screen 1 Feed Gate Valve | F13GA421 Screen1 Fd Vlv | 3 | FL | X | X | As per F13-SEQ-0007 | As per F13-SEQ-0008 | CT1 | PWS13365A/B/C OR D Inactive | PWS13365A/B/C OR D Inactive | 0 |  |  |  |  | X | X | X | If any of the Trash Screen 1 Pull Wire Switches are activated, close the Feed Gate immediately | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1913
[14 empty] | CT2 | F13-SL-401 Not Running | F13-SL-401 Not Running | 0 |  |  |  |  | X | X |  | Bypassable | A
|  |  |  | XV13361 | 2000-F13-PID-PR-10007 | F13-SL-401 Trash Screen 1 Spray Water Valve | F13SL401 PW Spray | 7 | FC | X | X | As per F13-SEQ-0007 | As per F13-SEQ-0008 or F13-SL-401 not running for 3 minutes (one shot) | [12 empty] | A
|  |  |  | XV13387 | 2000-F13-PID-PR-10007 | F13-GA-422 Trash Screen 2 Feed Gate Valve | F13GA422 Screen2 Fd Vlv | 3 | FL | X | X | As per F13-SEQ-0007 | As per F13-SEQ-0008 | CT1 | PWS13375A/B/C OR D Inactive | PWS13375A/B/C OR D Inactive | 0 |  |  |  |  | X | X | X | If any of the Trash Screen 2 Pull Wire Switches are activated, close the Feed Gate immediately | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1913
[14 empty] | CT2 | F13-SL-402 Not Running | F13-SL-402 Not Running | 0 |  |  |  |  | X | X |  | Bypassable | A
|  |  |  | XV13371 | 2000-F13-PID-PR-10007 | F13-SL-402 Trash Screen 2 Spray Water Valve | F13SL402 PW Spray | 7 | FC | X | X | As per F13-SEQ-0007 | As per F13-SEQ-0008 or F13-SL-402 not running for 3 minutes (one shot) | [12 empty] | A
|  |  |  | XV13388 | 2000-F13-PID-PR-10007 | F13-GA-423 Trash Screen 3 Feed Gate Valve | F13GA423 Screen3 Fd Vlv | 3 | FL | X | X | As per F13-SEQ-0007 | As per F13-SEQ-0008 | CT1 | PWS13395A/B/C OR D Inactive | PWS13395A/B/C OR D Inactive | 0 |  |  |  |  | X | X | X | If any of the Trash Screen 3 Pull Wire Switches are activated, close the Feed Gate immediately | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1913
[14 empty] | CT2 | F13-SL-403 Not Running | F13-SL-403 Not Running | 0 |  |  |  |  | X | X |  | Bypassable | A
|  |  |  | XV13401 | 2000-F13-PID-PR-10008 | F13-SL-403 Trash Screen 3 Spray Water Valve | F13SL403 PW Spray | 7 | FC | X | X | As per F13-SEQ-0007 | As per F13-SEQ-0008 or F13-SL-403 not running for 3 minutes (one shot) | [12 empty] | A
|  |  |  | XV13389 | 2000-F13-PID-PR-10007 | F13-GA-424 Trash Screen 4 Feed Gate Valve | F13GA424 Screen4 Fd Vlv | 3 | FL | X | X | As per F13-SEQ-0007 | As per F13-SEQ-0008 | CT1 | PWS13405A/B/C OR D Inactive | PWS13405A/B/C OR D Inactive | 0 |  |  |  |  | X | X | X | If any of the Trash Screen 4 Pull Wire Switches are activated, close the Feed Gate immediately | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1913
[14 empty] | CT2 | F13-SL-404 Not Running | F13-SL-404 Not Running | 0 |  |  |  |  | X | X |  | Bypassable | A
|  |  |  | XV13391 | 2000-F13-PID-PR-10008 | F13-SL-404 Trash Screen 4 Spray Water Valve | F13SL404 PW Spray | 7 | FC | X | X | As per F13-SEQ-0007 | As per F13-SEQ-0008 or F13-SL-404 not running for 3 minutes (one shot) | [12 empty] | A
|  |  |  | XV13374 | 2000-F13-PID-PR-10007 | F13-SC-403 Trash Dewatering Screen Spray Water Valve | F13SC403 PW Spray | 7 | FC | X | X | As per F13-SEQ-0005 | As per F13-SEQ-0006 or F13-SC-403 not running for 3 minutes (one shot) | [12 empty] | 1 | 2025-06-19 | https://pastech-2955.atlassian.net/browse/KAN-2062
|  |  |  | SV13464 | 2000-F24-PID-PR-10004 | F13-PP-403 Trash Dewatering Screen Underflow Pump Gland Water Solenoid Valve | F13PP403 Gland Water | 11 | FO | X | X | As per F13-SEQ-0005 OR F13-PP-403 Start | As per F13-SEQ-0006 | [12 empty] | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/PL-174
|  |  |  | XV13384 | 2000-F13-PID-PR-10007 | F13-SC-403 Trash Dewatering Screen Bypass Valve | F13SC403 Bypass | 4 | FO | X | X | As per F13-SEQ-0006 | As per F13-SEQ-0005 | OT1 | F13-SC-403 Not Running | F13-SC-403 Not Running | 30 |  |  |  | X |  | X |  | Open bypass valve if the Trash Dewatering Screen is stopped | 0
|  |  |  | XV13382 | 2000-F13-PID-PR-10007 | F13-PP-403 Trash Dewatering Screen Underflow Pump Suction Valve | F13PP403 Suction | 3 | FL | X | X | As per F13-SEQ-0005 | As per F13-SEQ-0006 | CT1 | F13-PP-403 Tripped | F13-PP-403 Tripped | 3 |  |  |  |  | X | X | X | If F13-PP-403 trips (i.e., F13-PP-403 process OR critical interlock becomes true, causing the pump to stop), then close suction valve and open drain valve to drain the line. Refer to F13-PP-403 in the Drives tab for interlocking conditions. HAZOP Item 83 | 0
|  |  |  | XV13383 | 2000-F13-PID-PR-10007 | F13-PP-403 Trash Dewatering Screen Underflow Pump Drain Valve | F13PP403 Suction Drain | 3 | FL | X | X | As per F13-SEQ-0006 | As per F13-SEQ-0005 | OT1 | F13-PP-403 Tripped | F13-PP-403 Tripped | 3 |  |  |  | X |  | X | X | If F13-PP-403 trips (i.e., F13-PP-403 process OR critical interlock becomes true, causing the pump to stop), then close suction valve and open drain valve to drain the line. Refer to F13-PP-403 in the Drives tab for interlocking conditions. HAZOP Item 83 | 0
|  |  |  | XV13360 | 2000-F13-PID-PR-10008 | F13-BX-415 Trash Screens Final Collection Box Process Water Valve | F13BX415 Motive PW | 7 | FC | X | [15 empty] | A
|  |  |  | XV13220 | 2000-F13-PID-PR-10006 | F13-DG-467 Recycle Crusher Bypass Gate Valve | F13DG467 Bypass | 3 | FL | X | X | XA13202 DETECTED OR [((LI13221 > A_Hi AND LI13221 Healthy) OR (LI13222 > A_Hi AND LI13222 Healthy)) AND F13-CV-406 RUNNING] OR Both Levels Unhealthy | XA13202 NORMAL and 20 second delay off timer elapsed AND [( LI13221 < P_Hi AND LI13221 Healthy) OR (LI13222 < P_Hi AND LI13222 Healthy) ] | [11 empty] | Configure with brownfields valve template to include local control. If XV13220 is in local mode: Disregard XV13220 trips/permissives Open if HS13220AOP active Close if HS13220ACL active | 1 | 2025-07-22 | CR-031
[14 empty] | OP1 | F13-CV-406 Running | F13-CV-406 Running | 3 |  | X |  |  |  | X |  | Updated to open permissive due to template limitation. F13-CV-405 will trip if bypass is gate is OPEN AND F13-CV-406 is not running. Opened = Bypassing Closed = Not Bypassing | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
[14 empty] | OT1 | XA13204 Fault | XA13204 Fault | 3 |  |  |  | X |  | X |  | Bypass gate to open (bypass Recycle Crushers) if the Metal Detector (F13-MD-401) has a fault. | 0
|  |  |  | SV13218A | 2000-F13-PID-PR-10006 | F13-GA-411 Recycle Crusher C Isolation Gates Open Solenoid Valve | F13GA411 Gate Open | 11 | FC |  | X | HS13218AOP Active | HS13218AOP Inactive | CT3 | SV13218B Energised | SV13218B Energised | 0 |  |  |  |  | X | X |  | SV13218B and SV13218A solenoid valve cannot be energised at the same time. Refer to 2000-ME075-M01-10001 | 1 | 6/03/2025 30/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1409 https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-300?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
[14 empty] | OP1 | F13HU405_T2 Timer Elapsed | F13-HU-405 Min Run Time Elapsed | 0 |  | X |  |  |  | X |  | SV13218A cannot be energised until the F13HU405_T2 timer elapses Refer to 2000-ME075-M01-10001 | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
[14 empty] | CT1 | ZIO13218 Active | ZIO13218 Active | 3 |  |  |  |  | X | X |  | SV13218A must be deenergised if the fully open proximity switch is active. Refer to 2000-ME075-M01-10001 | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
[14 empty] | CT2 | F13HU405_T1 Timer Elapsed | Max Energise Timer Elapsed | 0 |  |  |  |  | X | X | X | SV13218A must be deenergised after the F13HU405_T1 timer elapses Refer to 2000-ME075-M01-10001 | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
|  |  |  | SV13218B | 2000-F13-PID-PR-10006 | F13-GA-411 Recycle Crusher C Isolation Gates Close Solenoid Valve | F13GA411 Gate Close | 11 | FC |  | X | HS13218BCL Active | HS13218BCL Inactive | CT3 | SV13218A Energised | SV13218A Energised | 0 |  |  |  |  | X | X |  | SV13218B and SV13218A solenoid valve cannot be energised at the same time. Refer to 2000-ME075-M01-10001 | 1 | 6/03/2025 30/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1409 https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-300?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
[14 empty] | OP1 | F13HU405_T2 Timer Elapsed | F13-HU-405 Min Run Time Elapsed | 0 |  | X |  |  |  | X |  | SV13218B cannot be energised until the F13HU405_T2 timer elapses Refer to 2000-ME075-M01-10001 | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
[14 empty] | CT1 | ZIC13218 Active | ZIC13218 Active | 3 |  |  |  |  | X | X |  | SV13218B must be deenergised if the fully closed proximity switch is active. Refer to 2000-ME075-M01-10001 | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
[14 empty] | CT2 | F13HU405_T1 Timer Elapsed | Max Energise Timer Elapsed | 0 |  |  |  |  | X | X | X | SV13218B must be deenergised after the F13HU405_T1 timer elapses Refer to 2000-ME075-M01-10001 | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
|  |  |  | SV13219A | 2000-F13-PID-PR-10006 | F13-GA-412 Recycle Crusher D Isolation Gates Open Solenoid Valve | F13GA412 Gate Open | 11 | FC |  | X | HS13219AOP Active | HS13219AOP Inactive | CT3 | SV13219B Energised | SV13219B Energised | 0 |  |  |  |  | X | X |  | SV13219B and SV13219A solenoid valve cannot be energised at the same time. Refer to 2000-ME075-M01-10001 | 1 | 6/03/2025 30/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1409 https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-300?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
[14 empty] | OP1 | F13HU405_T2 Timer Elapsed | F13-HU-405 Min Run Time Elapsed | 0 |  | X |  |  |  | X |  | SV13219A cannot be energised until the F13HU405_T2 timer elapses Refer to 2000-ME075-M01-10001 | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
[14 empty] | CT1 | ZIO13219 Active | ZIO13219 Active | 3 |  |  |  |  | X | X |  | SV13219A must be deenergised if the fully open proximity switch is active. Refer to 2000-ME075-M01-10001 | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
[14 empty] | CT2 | F13HU405_T1 Timer Elapsed | Max Energise Timer Elapsed | 0 |  |  |  |  | X | X | X | SV13219A must be deenergised after the F13HU405_T1 timer elapses Refer to 2000-ME075-M01-10001 | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
|  |  |  | SV13219B | 2000-F13-PID-PR-10006 | F13-GA-412 Recycle Crusher D Isolation Gates Close Solenoid Valve | F13GA412 Gate Close | 11 | FC |  | X | HS13219BCL Active | HS13219BCL Inactive | CT3 | SV13219A Energised | SV13219A Energised | 0 |  |  |  |  | X | X |  | SV13219B and SV13219A solenoid valve cannot be energised at the same time. Refer to 2000-ME075-M01-10001 | 1 | 6/03/2025 30/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1409 https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-300?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
[14 empty] | OP1 | F13HU405_T2 Timer Elapsed | F13-HU-405 Min Run Time Elapsed | 0 |  | X |  |  |  | X |  | SV13219B cannot be energised until the F13HU405_T2 timer elapses Refer to 2000-ME075-M01-10001 | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
[14 empty] | CT1 | ZIC13219 Active | ZIC13219 Active | 3 |  |  |  |  | X | X |  | SV13219B must be deenergised if the fully closed proximity switch is active. Refer to 2000-ME075-M01-10001 | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
[14 empty] | CT2 | F13HU405_T1 Timer Elapsed | Max Energise Timer Elapsed | 0 |  |  |  |  | X | X | X | SV13219B must be deenergised after the F13HU405_T1 timer elapses Refer to 2000-ME075-M01-10001 | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
|  |  |  | SV13185 | 2000-F13-PID-PR-10006 | F13-CC-401 Recycle Crusher C Seal Water Solenoid Valve | F13CC401 Seal Water | 11 | FO | X | X | F13-SEQ-0028 | F13-SEQ-0031 | OT1 | F13-CC-401 Running | F13-CC-401 Running | 0 |  |  |  | X |  | X |  |  | B
|  |  |  | SV13269 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Unloading 1 Solenoid Valve | F13HU403 System Pressure | 11 | FO | X | X | YS13273 Inactive AND YS13271A Inactive AND YS13272A Inactive AND YS13271B Inactive AND YS13272B Inactive AND YS13275 Inactive AND YS13276 Inactive | YS13273 Active OR YS13271A Active OR YS13272A Active OR YS13271B Active OR YS13272B Active OR YS13275 Active OR YS13276 Active | [11 empty] | Refer to YS13273 , YS13271A, YS13272A, YS13271B, YS13272B, YS13275 and YS13276 in Misc tab for details of valve control | 2
|  |  |  | SV13270 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Unloading 2 Solenoid Valve | F13HU403 High Flow | 11 | FO | X | X | YS13271B Inactive AND YS13272B Inactive | YS13271B Active OR YS13272B Active | [11 empty] | Refer to YS13271B and YS13272B in Misc tab for detail of valve control | 2
|  |  |  | SV13271 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Bowl Open Adjustment Solenoid Valve | F13HU403 Bowl Open | 11 | FC | X | X | YS13271A Active OR YS13271B Active | YS13271A Inactive AND YS13271B Inactive | [11 empty] | Refer to YS13271A and YS13271B in Misc tab for detail of valve control | B
|  |  |  | SV13272 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Bowl Close Adjustment Solenoid Valve | F13HU403 Bowl Close | 11 | FC | X | X | YS13272A Active OR YS13272B Active | YS13272A Inactive AND YS13272B Inactive | [11 empty] | Refer to YS13272A and YS13272B in Misc tab for detail of valve control | B
|  |  |  | SV13273 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Pressurize Clamping Cylinders Solenoid Valve | F13HU403 Clamp | 11 | FC | X | X | YS13273 Active | YS13273 Inactive | [11 empty] | Refer to YS13273 in Misc tab for detail of valve control | B
|  |  |  | SV13274 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Accumulator Solenoid Valve | F13HU403 Accumulator | 11 | FC | X | X | YS13271A Active OR YS13272A Active OR YS13271B Active OR YS13272B Active OR YS13274 Active | YS13271A Inactive AND YS13272A Inactive AND YS13271B Inactive AND YS13272B Inactive AND YS13274 Inactive | [11 empty] | Refer to YS13271A, YS13272A, YS13271B, YS13272B and YS13274 in Misc tab for detail of valve control | 1 | 2025-04-04 | https://pastech-2955.atlassian.net/browse/KAN-1654
|  |  |  | SV13275 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Clearing Solenoid Valve | F13HU403 Clear | 11 | FC | X | X | YS13275 Active | YS13275 Inactive | [11 empty] | Refer to YS13275 in Misc tab for detail of valve control | B
|  |  |  | SV13276 | 2000-F13-PID-PR-10006 | F13-HU-403 Recycle Crusher C Hydraulic Unit Set Tramp Release Solenoid Valve | F13HU403 Tramp | 11 | FC | X | X | YS13276 Active | YS13276 Inactive | [11 empty] | Refer to YS13276 in Misc tab for detail of valve control | B
|  |  |  | SV13292 | 2000-F13-PID-PR-10006 | F13-CC-402 Recycle Crusher D Seal Water Solenoid Valve | F13CC402 Seal Water | 11 | FO | X | X | F13-SEQ-0033 | F13-SEQ-0036 | OT1 | F13-CC-402 Running | F13-CC-402 Running | 0 |  |  |  | X |  | X |  |  | B
|  |  |  | SV13329 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Unloading 1 Solenoid Valve | F13HU404 System Pressure | 11 | FO | X | X | YS13333 Inactive AND YS13331A Inactive AND YS13334A Inactive AND YS13331B Inactive AND YS13334B Inactive AND YS13335 Inactive AND YS13336 Inactive | YS13333 Active OR YS13331A Active OR YS13334A Active OR YS13331B Active OR YS13334B Active OR YS13335 Active OR YS13336 Active | [11 empty] | Refer to YS13333, YS13331A, YS13334A, YS13331B, YS13334B, YS13335 and YS13336 in Misc tab for detail of valve control | 2
|  |  |  | SV13330 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Unloading 2 Solenoid Valve | F13HU404 High Flow | 11 | FO | X | X | YS13331B Inactive AND YS13334B Inactive | YS13331B Active OR YS13334B Active | [11 empty] | Refer to YS13331B and YS13334B in Misc tab for detail of valve control | 2
|  |  |  | SV13331 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Bowl Open Adjustment Solenoid Valve | F13HU404 Bowl Open | 11 | FC | X | X | YS13331A Active OR YS13331B Active | YS13331A Inactive AND YS13331B Inactive | [11 empty] | Refer to YS13331A and YS13331B in Misc tab for detail of valve control | B
|  |  |  | SV13332 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Bowl Close Adjustment Solenoid Valve | F13HU404 Bowl Close | 11 | FC | X | X | YS13334A Active OR YS13334B Active | YS13334A Inactive AND YS13334B Inactive | [11 empty] | Refer to YS13334A and YS13334B in Misc tab for detail of valve control | B
|  |  |  | SV13333 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Pressurize Clamping Cylinders Solenoid Valve | F13HU404 Clamp | 11 | FC | X | X | YS13333 Active | YS13333 Inactive | [11 empty] | Refer to YS13333 in Misc tab for detail of valve control | B
|  |  |  | SV13334 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Accumulator Solenoid Valve | F13HU404 Accumulator | 11 | FC | X | X | YS13331A Active OR YS13334A Active OR YS13331B Active OR YS13334B Active OR YS13334 Active | YS13331A Inactive AND YS13334A Inactive AND YS13331B Inactive AND YS13334B Inactive AND YS13334 Inactive | [11 empty] | Refer to YS13331A, YS13334A, YS13331B, YS13334B and YS13334 in Misc tab for detail of valve control | 1 | 2025-04-04 | https://pastech-2955.atlassian.net/browse/KAN-1654
|  |  |  | SV13335 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Clearing Solenoid Valve | F13HU404 Clear | 11 | FC | X | X | YS13335 Active | YS13335 Inactive | [11 empty] | Refer to YS13335 in Misc tab for detail of valve control | B
|  |  |  | SV13336 | 2000-F13-PID-PR-10006 | F13-HU-404 Recycle Crusher D Hydraulic Unit Set Tramp Release Solenoid Valve | F13HU404 Tramp | 11 | FC | X | X | YS13336 Active | YS13336 Inactive | [11 empty] | Refer to YS13336 in Misc tab for detail of valve control | B
|  |  |  | SV13591 | 2000-F13-PID-PR-10013 | F13-LU-414 SAG Mill Ring Gear Spray System Grease System Nozzle Air Supply Assembly Solenoid Valve | F13LU414 Spry Noz Air | 11 | FC | X | X | As per F13-SEQ-0020 | As per F13-SEQ-0020 | [11 empty] | Refer to HS13600 in Digital Inputs tab for detail of push button control of valves | A
|  |  |  | SV13588 | 2000-F13-PID-PR-10013 | F13-LU-414 SAG Mill Ring Gear Spray System Grease System Pump Air Supply Assembly Solenoid Valve | F13LU414 Spry Pmp Air | 11 | FC | X | X | As per F13-SEQ-0020 | As per F13-SEQ-0020 | [11 empty] | Refer to HS13600 in Digital Inputs tab for detail of push button control of valves | A
|  |  |  | SV13605 | 2000-F13-PID-PR-10013 | F13-LU-416 SAG Mill Seal Grease System SAG Mill Seal Grease Pump Air Supply Solenoid Valve | F13LU416 Seal Pmp Air | 11 | FC | X | X | As per F13-SEQ-0019 | As per F13-SEQ-0019 | [12 empty] | A
|  |  |  | SV13594 | 2000-F13-PID-PR-10013 | F13-LU-416 SAG Mill Seal Grease System Grease System Pneumatic Elevator Assembly Solenoid Valve | F13LU414 Elevator | 11 | FC |  | X | HS13604UP ACTIVE | HS13604DWN ACTIVE | [12 empty] | 1 | 2025-04-30 | https://pastech-2955.atlassian.net/browse/KAN-1681
|  |  |  | SV13557 | 2000-F13-PID-PR-10013 | F13-HU-416 Sag Mill Brake Hydraulic Power Unit Lifting Solenoid Valve | F13HU416 Brake Release | 11 | FC | X | X | MS_RL_BRK ACTIVE | MS_2S_BRK ACTIVE OR MS_EN_BRK ACTIVE | [11 empty] | Refer to Misc tab for details on auto open and close conditions | A
|  |  |  | SV13561 | 2000-F13-PID-PR-10013 | F13-HU-416 Sag Mill Brake Hydraulic Power Unit Parking Solenoid Valve | F13HU416 Brake Park | 11 | FC | X | X | MS_EN_BRK ACTIVE | MS_2S_BRK ACTIVE | [11 empty] | Refer to Misc tab for details on auto open and close conditions | A
|  |  |  | SV13562 | 2000-F13-PID-PR-10013 | F13-HU-416 Sag Mill Brake Hydraulic Power Unit 2-Stage Solenoid Valve | F13HU416 Brake 2 Stage | 11 | FO | X | X | MS_RL_BRK ACTIVE | MS_2S_BRK ACTIVE OR MS_EN_BRK ACTIVE | [11 empty] | Refer to Misc tab for details on auto open and close conditions | A
|  |  |  | SV13841 | 2000-F13-PID-PR-10013 | F13-LU-424 Ball Mill Ring Gear Spray System Nozzle Air Supply Assembly Solenoid Valve | F13LU424 Spry Noz Air | 11 | FC | X | X | As per F13-SEQ-0014 | As per F13-SEQ-0014 | [11 empty] | Refer to HS13851 in Digital Inputs tab for detail of push button control of valves | A
|  |  |  | SV13838 | 2000-F13-PID-PR-10013 | F13-LU-424 Ball Mill Ring Gear Spray System Grease System Pump Air Supply Assembly Solenoid Valve | F13LU424 Spry Pmp Air | 11 | FC | X | X | As per F13-SEQ-0014 | As per F13-SEQ-0014 | [11 empty] | Refer to HS13851 in Digital Inputs tab for detail of push button control of valves | A
|  |  |  | SV13856 | 2000-F13-PID-PR-10013 | F13-LU-426 Ball Mill Seal Grease System Ball Mill Seal Grease Pump Air Supply Solenoid Valve | F13LU426 Seal Pmp Air | 11 | FC | X | X | As per F13-SEQ-0013 | As per F13-SEQ-0013 | [12 empty] | A
|  |  |  | SV13808 | 2000-F13-PID-PR-10013 | F13-HU-417 Ball Mill Brake Hydraulic Power Unit Hydraulic Brake System Pump Discharge Solenoid Valve | F13HU417 Brake Release | 11 | FC | X | X | MB_RL_BRK ACTIVE | MB_2S_BRK ACTIVE OR MB_EN_BRK ACTIVE | [11 empty] | Refer to Misc tab for details on auto open and close conditions | A
|  |  |  | SV13812 | 2000-F13-PID-PR-10013 | F13-HU-417 Ball Mill Brake Hydraulic Power Unit Hydraulic Brake System Pump Discharge Solenoid Valve 1 | F13HU417 Brake Park | 11 | FC | X | X | MB_EN_BRK ACTIVE | MB_2S_BRK ACTIVE | [11 empty] | Refer to Misc tab for details on auto open and close conditions | A
|  |  |  | SV13813 | 2000-F13-PID-PR-10013 | F13-HU-417 Ball Mill Brake Hydraulic Power Unit Hydraulic Brake System Pump Discharge Solenoid Valve 2 | F13HU417 Brake 2 Stage | 11 | FO | X | X | MB_RL_BRK ACTIVE | MB_2S_BRK ACTIVE OR MB_EN_BRK ACTIVE | [11 empty] | Refer to Misc tab for details on auto open and close conditions | A
|  |  |  | XV13441 | 2000-F13-PID-PR-10012 | F13-CU-402 Chiller 1 Feed Valve | F13CU402 Feed | 9 | FL | X | X | As per F13-SEQ-0001 | As per F13-SEQ-0002 | [12 empty] | B
|  |  |  | XV13443 | 2000-F13-PID-PR-10012 | F13-CU-403 Chiller 2 Feed Valve | F13CU403 Feed | 9 | FL | X | X | As per F13-SEQ-0001 | As per F13-SEQ-0002 | [12 empty] | B
|  |  |  | XV13445 | 2000-F13-PID-PR-10012 | F13-CU-404 Chiller 3 Feed Valve | F13CU404 Feed | 9 | FL | X | X | As per F13-SEQ-0001 | As per F13-SEQ-0002 | [12 empty] | B
|  |  |  | XV13447 | 2000-F13-PID-PR-10012 | F13-CU-405 Chiller 4 Feed Valve | F13CU405 Feed | 9 | FL | X | X | As per F13-SEQ-0001 | As per F13-SEQ-0002 | [12 empty] | B
|  |  |  | XV13419 | 2000-F13-PID-PR-10012 | F13-TK-407 Chiller Tank Scheme Water Fill Solenoid Valve | F13TK407 Fill Valve | 9 | FL | X |  |  |  | CT1 | LI13430 > A_HH | LI13430 > A_HH | 3 |  |  |  |  | X | X |  |  | 0
|  |  |  | XV13418 | 2000-F13-PID-PR-10012 | F13-TK-409 Cooling Water Tank 2 Scheme Water Fill Solenoid Valve | F13TK409 Fill Valve | 9 | FL | X |  |  |  | CT1 | LI13426 > A_HH | LI13426 > A_HH | 3 |  |  |  |  | X | X |  |  | 0
|  |  |  | HV13238 | 2000-F13-PID-PR-10006 |  | F13LU403 Pump 1 Disch. | HV | [16 empty] | Manual hand valve with position switches. See ZIO13238 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13239 | 2000-F13-PID-PR-10006 |  | F13LU403 Pump 2 Disch. | HV | [16 empty] | Manual hand valve with position switches. See ZIO13239 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13298 | 2000-F13-PID-PR-10006 |  | F13LU404 Pump 1 Disch. | HV | [16 empty] | Manual hand valve with position switches. See ZIO13298 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13299 | 2000-F13-PID-PR-10006 |  | F13LU404 Pump 2 Disch. | HV | [16 empty] | Manual hand valve with position switches. See ZIO13299 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13422 | 2000-F13-PID-PR-10012 |  | F13PW413 Suction | HV | [16 empty] | Manual hand valve with position switches. See ZIC and ZIO13422 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13423 | 2000-F13-PID-PR-10012 |  | F13PW413 Discharge | HV | [16 empty] | Manual hand valve with position switches. See ZIC and ZIO13423 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13424 | 2000-F13-PID-PR-10012 |  | F13PW414 Suction | HV | [16 empty] | Manual hand valve with position switches. See ZIC and ZIO13424 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13425 | 2000-F13-PID-PR-10012 |  | F13PW414 Discharge | HV | [16 empty] | Manual hand valve with position switches. See ZIC and ZIO13425 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13431 | 2000-F13-PID-PR-10012 |  | F13PW415 Suction | HV | [16 empty] | Manual hand valve with position switches. See ZIC and ZIO13431 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13432 | 2000-F13-PID-PR-10012 |  | F13PW415 Discharge | HV | [16 empty] | Manual hand valve with position switches. See ZIC and ZIO13432 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13433 | 2000-F13-PID-PR-10012 |  | F13PW416 Suction | HV | [16 empty] | Manual hand valve with position switches. See ZIC and ZIO13433 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13434 | 2000-F13-PID-PR-10012 |  | F13PW416 Discharge | HV | [16 empty] | Manual hand valve with position switches. See ZIC and ZIO13434 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13442 | 2000-F13-PID-PR-10012 |  | F13CU402 Discharge | HV | [16 empty] | Manual hand valve with position switches. See ZIC and ZIO13442 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13444 | 2000-F13-PID-PR-10012 |  | F13CU403 Discharge | HV | [16 empty] | Manual hand valve with position switches. See ZIC and ZIO13444 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13446 | 2000-F13-PID-PR-10012 |  | F13CU404 Discharge | HV | [16 empty] | Manual hand valve with position switches. See ZIC and ZIO13446 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
|  |  |  | HV13448 | 2000-F13-PID-PR-10012 |  | F13CU405 Discharge | HV | [16 empty] | Manual hand valve with position switches. See ZIC and ZIO13448 Digital Input tab for position switches | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
107

## 7. Control Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - MILLING & CLASSIFICATION (F13)
2000-F13-LST-PR-10001
CONTROL VALVES
[14 empty] | Permissive and Trips | [14 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open | Close | Bypass | Reset Required | Comments | Rev | Change Date | Change Reference | OK | Date | OK | Date
|  |  |  | FCV13123 | 2000-F13-PID-PR-10003 | F13-CV-403 SAG Mill Feed Conveyor Spray Water Flow Control Valve | F13SC404 PW Spray | Detail 1 | FC | X | X | F13-SEQ-0021A | F13-SEQ-0022A | [12 empty] | B
|  |  |  | FCV13121 | 2000-F13-PID-PR-10003 | F13-BX-401 SAG Mill Feed Box Process Water Flow Control Valve | F13MS401 Water FCV | Detail 1 | FC | X | X | F13-SEQ-0021A | F13-SEQ-0022A | CT1 | F13-MS-401 = Not Running | F13-MS-401 = Not Running | 5 |  |  |  |  | X | X |  |  | B | [6 empty] | user access security is set to level 5
|  |  |  | FCV13071 | 2000-F13-PID-PR-10002 | F13-SC-401 SAG Mill Discharge Screen Process Water Flow Control Valve | F13SC401 PW Spray | Detail 1 | FC | X | X | F13-SEQ-0021A | F13-SEQ-0022A | [12 empty] | A
|  |  |  | FCV13075A | 2000-F13-PID-PR-10002 | F13-HP-401 Primary Cyclone Feed Hopper Process Water Flow Control Valve 1 | F13HP401 Water FCV 1 | Detail 1 | FC | X | X | F13-SEQ-0009 | F13-SEQ-0010 | [11 empty] | MV of FIC13075 may output to either FCV13075A or FCV13075B. Refer to FCV13075_LL in Misc tab for conditions. | 0 | [6 empty] | OOP alarm is currently configured as "reference alarm". Changed to Low priority alarm. 10s to open/close
|  |  |  | FCV13075B | 2000-F13-PID-PR-10002 | F13-HP-401 Primary Cyclone Feed Hopper Process Water Flow Control Valve 2 | F13HP401 Water FCV 2 | Detail 1 | FC | X | X | F13-SEQ-0009 | F13-SEQ-0010 | [11 empty] | MV of FIC13075 may output to either FCV13075A or FCV13075B. Refer to FCV13075_LL in Misc tab for conditions. | 0 | [6 empty] | OOP alarm is currently configured as "reference alarm". Changed to Low priority alarm. 10s to open/close
|  |  |  | FCV13143 | 2000-F13-PID-PR-10004 | F13-SC-402 Ball Mill Trommel Spray Water Valve | F13SC402 PW Spray | Detail 1 | FC | X | X | F13-SEQ-0015A | F13-SEQ-0016A | [12 empty] | A
|  |  |  | FCV13141 | 2000-F13-PID-PR-10004 | F13-BX-402 Ball Mill Feed Box Process Water Flow Control Valve | F13MB401 Water FCV | Detail 1 | FC | X | X | F13-SEQ-0015A | F13-SEQ-0016A | CT1 | F13-MB-401 = Not Running | F13-MB-401 = Not Running | 5 |  |  |  |  | X | X |  |  | B | [6 empty] | OOP alarm is currently configured as "reference alarm". Changed to Low priority alarm
|  |  |  | FCV13125 | 2000-F13-PID-PR-10009 | F13-CU-407 SAG Mill VSD Cooling System Inlet Flow Control Valve | F13CU409 Cool Wtr Spply | Detail 1 | FO | X | X | F13-SEQ-0001 OR F13-SEQ-0017 | F13-SEQ-0002 | [12 empty] | A
|  |  |  | FCV13126 | 2000-F13-PID-PR-10009 | F13-CU-408 Ball Mill VSD Cooling System Inlet Flow Control Valve | F13CU408 Cool Wtr Spply | Detail 1 | FO | X | X | F13-SEQ-0001 OR F13-SEQ-0011 | F13-SEQ-0002 | [12 empty] | A
|  |  |  | FCV13127 | 2000-F13-PID-PR-10009 | F13-CU-409 Cyclone Feed Pump Water Cooler Unit Inlet Flow Control Valve | F13CU407 Cool Wtr Spply | Detail 1 | FO | X | X | F13-SEQ-0001 OR F13-SEQ-0009 | F13-SEQ-0002 | [12 empty] | A
|  |  |  | TCV13129 | 2000-F13-PID-PR-10009 |  | F13PP401 Cool Wtr Spply | Detail 1 | FO | X | X | F13-SEQ-0001 OR F13-SEQ-0009 | F13-SEQ-0002 | [12 empty] | B
|  |  |  | TCV13410 | 2000-F13-PID-PR-10010 |  | F13MS401A Cool Wtr Feed | Detail 1 | FO | X | X | F13-SEQ-0001 OR F13-SEQ-0017 | F13-SEQ-0002 OR F13-SEQ-0022B OR F13-SEQ-0022C | [12 empty] | B | [6 empty] | OOP alarm is currently configured as "reference alarm". Changed to Low priority alarm
|  |  |  | TCV13412 | 2000-F13-PID-PR-10010 |  | F13MS401B Cool Wtr Feed | Detail 1 | FO | X | X | F13-SEQ-0001 OR F13-SEQ-0017 | F13-SEQ-0002 OR F13-SEQ-0022B OR F13-SEQ-0022C | [12 empty] | B
|  |  |  | TCV13414 | 2000-F13-PID-PR-10011 |  | F13MB401A Cool Wtr Feed | Detail 1 | FO | X | X | F13-SEQ-0001 OR F13-SEQ-0011 | F13-SEQ-0002 OR F13-SEQ-0016B OR F13-SEQ-0016C | [12 empty] | B | [6 empty] | OOP alarm is currently configured as "reference alarm". Changed to Low priority alarm
|  |  |  | TCV13416 | 2000-F13-PID-PR-10011 |  | F13MB401B Cool Wtr Feed | Detail 1 | FO | X | X | F13-SEQ-0001 OR F13-SEQ-0011 | F13-SEQ-0002 OR F13-SEQ-0016B OR F13-SEQ-0016C | [12 empty] | B
|  |  |  | TCV13629 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication System Lube Oil Heat Exchanger Cooling Water Temperature Control Valve | F13LU413 HX Cool Water | Detail 2, see comment | FO | X | X | F13-SEQ-0001 OR F13-SEQ-0017 | F13-SEQ-0002 OR F13-SEQ-0018 | [11 empty] | 2x position switches ZSO, ZSC13629 (DI tab) 1x position indicator ZI13629 (AI tab) | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407 |  |  |  |  | OOP alarm is currently configured as "reference alarm". Changed to Low priority alarm
|  |  |  | TCV13880 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Oil Heat Exchanger Cooling Water Solenoid Temperature Control Valve | F13LU423 HX Cool Water | Detail 2, see comment | FO | X | X | F13-SEQ-0001 OR F13-SEQ-0011 | F13-SEQ-0002 OR F13-SEQ-0012 | [11 empty] | 2x position switches ZSO, ZSC13880 (DI tab) 1x position indicator ZI13880 (AI tab) | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1407 |  |  |  |  | OOP alarm is currently configured as "reference alarm". Changed to Low priority alarm
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
17

## 8. PID Cont
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - MILLING & CLASSIFICATION (F13)
2000-F13-LST-PR-10001
PID Controllers
[10 empty] | Modes |  |  |  | Setpoint |  |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [8 empty] | Controlled/Manipulated Variable | [14 empty] | C1 Sign Off |  | C2 Sign Off |  | C1 Comments
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Controller Description | Abbreviated Description (Faceplate) | Normal Operating Mode | Manual | Auto | Cascade | Process Value Tag | Min | Max | Unit | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Range Min | Range Max | Lower Limit | Upper Limit | Unit | Destination Description | Destination (Output) Tag | Direct / Reverse Acting | P | I | D | Comment | Rev | Change Date | Change Reference | OK | Date | OK | Date
|  |  |  | F13CALC10002 | WIC13121 | 2000-F13-PID-PR-10001 | F13-WD-403 SAG Mill Feed Weightometer Weightometer Transmitter | F13CV403 SAG Feed Dry | Cascade | X | X | X | F13CALC10002 | 0 | 2200 | t/h | 0 | 3500 | t/h | [21 empty] | 0 | 100 | 35 | 100 | % VSD Speed | F13-FA-411, F13-FA-412 and F13-FA-414 VSD speed via F13CALC10003 | F13CALC10003 | Reverse |  |  |  | Include a deadband in the control loop to compensate for the lag between the change in Feeder speed and the measured increase in SAG Mill feed rate at the SAG Mill Feed Weightometer. Deadband TBC during commissioning. WIC13121.PV used in F13CALC10008, F13CALC10009 and F13CALC10034. See Calc tab. | 0
|  |  |  | F13CALC10039 | WIC13135 | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Mill Weight | F13MS401 Mill Weight | Automatic | X | X |  | F13CALC10039 | 830 | 1020 | t | 0 | 1500 | t | [16 empty] | 960 | 5 | 1000 | 5 |  | 0 | 3500 | 0 | 2800 | t/h | Cascade setpoint to WIC13121 if WIC13135 selected on HS13135 | WIC13121 | Reverse |  |  |  | Include a deadband in the control loop to compensate for the lag between the change in Feeder speed and the measured increase in SAG Mill weight. Deadband TBC during commissioning. Range & alarms inferred from nominal Mill operating load of 924t (2000-ME001.3-F20-50003). Range and alarm setpoints to be confirmed during commissioning. Configure output compensation. Set to 10t/h (TBC during commissioning) | 1 | 2025-10-13 | CR-052
|  |  |  | MSVOLUME | XIC13135 | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill LoadIQ Volume | F13MS401 IQ Volume | Automatic | X | X |  | MSVOLUME | 22 | 32 | % | 0 | 100 | % | [7 empty] | 22 | 300 | 32 | 300 |  |  |  | 22 | 300 | 32 | 300 |  |  |  | 0 | 3500 | 0 | 2800 | t/h | Cascade setpoint to WIC13121 if XIC13135 selected on HS13135 | WIC13121 | Reverse |  |  |  | SoftTag From LoadIQ OPC Server. Configure output compensation. Set to 10t/h (TBC during commissioning) | 1 | 2025-10-13 | CR-052
|  |  |  | F13CALC10041 | JIC13136 | 2000-F13-PID-PR-10003 | F13-MS-401 SAG Mill Main Motor VSD Total Power | F13MS401 Total Power | Automatic | X | X |  | F13CALC10041 | 0 | 20000 | kW | 0 | 25000 | kW | [21 empty] | 0 | 100 | 79.1 | 100 | % | SAG Mill (F13-MS-401 ) speed | F13-MS-401 VSD | Reverse |  |  |  | SoftTag. Modbus signal from SAG Mill VSD Refer to JI13136_LIM for controller output logic 2000-ME001.2-M01-50001 2000-F13-TQY-IC-10359. Alarms TBC during commissioning. | 1 | 2025-10-06 | CR-052 |  |  |  |  | Desktop review - MR (01/08/26)
|  |  |  | FIT13075 | FIC13075 | 2000-F13-PID-PR-10002 | F13-HP-401 Primary Cyclone Feed Hopper Process Water Flow Indicating Transmitter | F13HP401 Dilution | Cascade | X | X | X | FIT13075 | 0 | 2200 | m3/h | 0 | 3400 | m3/h | [21 empty] | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV13075A/B) position | FCV13075A AND / OR B | Reverse |  |  |  | Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. To be confirmed during commissioning. FIC13075 SV from DNIC13090A/B or LIC13076 via F13HP401_SEL. Refer to Misc tab for details. Split range as per the below: MV 0-50% = 0-100% Duty valve position MV 50-100% = 0-100% Standby valve position Refer to FCV13075_LL for selection of Duty/Standby valve in Misc tab. | 1 | 2025-03-06 | PCT alignment action register (DV to be given as % of range or in engineering units)
|  |  |  | LI13076 | LIC13076A | 2000-F13-PID-PR-10002 | F13-HP-401 Primary Cyclone Feed Hopper Level Indicating Transmitter | F13HP401 Level A | Automatic | X | X |  | LI13076 | 25 | 75 | % | 0 | 100 | % | [12 empty] | 20 | 5 | 30 | 5 | 80 | 5 | 90 | 5 |  | 0 | 3400 | 0 | 3400 | m3/h | Cascade setpoint to FIC13075 | FIC13075 | Reverse |  |  |  | Dual hopper level controller (feed water) Refer to LI13076 in Analogue Input tab for SS-DUAL detail | 1 | 2025-04-07 | Design change. Cyclone update following F28 FAT
|  |  |  | LI13076 | LIC13076B | 2000-F13-PID-PR-10002 | F13-HP-401 Primary Cyclone Feed Hopper Level Indicating Transmitter | F13HP401 Level B | Automatic | X | X |  | LI13076 | 35 | 75 | % | 0 | 100 | % | [21 empty] | 0 | 18000 | 0 | 17000 | m3/h | Cascade setpoint to FIC13090 via HS13092 | HS13092 | Direct |  |  |  | Dual hopper level controller (pump control) Refer to LI13076 in Analogue Input tab for SS-DUAL detail | 1 | 2025-04-07 | Design change. Cyclone update following F28 FAT
|  |  |  | F13CALC10006 | DNIC13090A | 2000-F13-PID-PR-10002 | F13-PP-401 Cyclone Feed Pump Discharge Density Indicating Transmitter | F13CY401 Feed Density | Automatic | X | X |  | F13CALC10006 | 50 | 70 | %w/w | 0 | 100 | %w/w |  |  |  | 5 | 5 | [15 empty] | Mask DV alarm if DNIC13090A is not selected on HS13090 | 0 | 3400 | 0 | 3400 | m3/h | Cascade setpoint to FIC13075 via F13HP401_SEL | F13HP401_SEL | Direct |  |  |  | Misc function F13HP401_SEL will initiate Density Control and utilise DNIC13090A.MV as defined in the Misc tab. Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. | 1 | 2025-03-06 | PCT alignment action register (density transmitters to align with F16,17,18 and DV to be given as % of range or in engineering units) |  |  |  |  | Desktop review - MR (01/08/26)
|  |  |  | F13CALC10004 | DNIC13090B | 2000-F13-PID-PR-10002 | F13-PP-401 Cyclone Feed Pump Discharge Density Indicating Transmitter | F13CY401 OF Density | Automatic | X | X |  | F13CALC10004 | 30 | 50 | %w/w | 0 | 100 | %w/w | [20 empty] | Mask DV alarm if DNIC13090B is not selected on HS13090 | 0 | 3400 | 0 | 3400 | m3/h | Cascade setpoint to FIC13075 via F13HP401_SEL | F13HP401_SEL | Direct |  |  |  | Misc function F13HP401_SEL will initiate Density Control and utilise DNIC13090B MV as defined in the Misc tab. Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. | 1 | 2025-03-06 | PCT alignment action register (density transmitters to align with F16,17,18 and DV to be given as % of range or in engineering units) |  |  |  |  | Desktop review - MR (01/08/26)
|  |  |  | FIT13090 | FIC13090 | 2000-F13-PID-PR-10002 | F13-PP-401 Cyclone Feed Pump Discharge Flow Indicating Transmitter | F13PP401 Flowrate | Cascade | X | X | X | FIT13090 | 0 | 17000 | m3/h | 0 | 18000 | m3/h | [14 empty] | 12160 | 300 |  |  |  |  | 1. Mask A_Lo if DNIC13090A.PV <= P_Lo 2. Mask if F13-PP-401 Not Running 3. Mask for 20 seconds (TBC) on Pump start up | 0 | 0 | 40 | 100 | % VSD Speed | Cyclone Feed Pump (F13-PP-401) VSD Speed | F13-PP-401 VSD | Reverse |  |  |  | A_Lo = Warning A_Lo estimated from adjusted theoretical settling velocity of 3.9m/s (Mechanical) Alarm setpoints and delays to be confirmed during commissioning. | 1 | 2025-03-06 | PCT alignment action register (density transmitters to align with F16,17,18)
|  |  |  | PIT13092 | PIC13092 | 2000-F13-PID-PR-10002 | F13-CY-401 Primary Cyclone Cluster Pressure Indicating Transmitter | F13CY401 Feed | Automatic | X | X |  | PIT13092 | 65 | 100 | kPag | 0 | 160 | kPag | [12 empty] | 60 | 30 | PIC13092.SV - Y | 100 | PIC13092.SV + Y | 100 | 110 | 30 | Mask A_Lo and A_LL if F13-PP-401 = Not Running | 0 | 18000 | 0 | 17000 | m3/h | Cascade setpoint to FIC13090 via HS13092 | HS13092 | Reverse |  |  |  | For Cyclone Feed Valves in AUTOMATIC mode: • FIC13090 in CASCADE, then F13CALC10007 is utilised for Cyclone Feed Valve control (see Calculation / OnOff Valves tab) • FIC13090 in MAN/AUTO, then F13CALC10011 is utilised for control of Cyclone Feed Valve control (see Calculation / OnOff Valves tab) For Cyclone Feed Valves in MANUAL mode: • A_Lo and A_Hi indicate when Cyclone Feed Valves need to be closed / opened manually by CRO. A_LL and A_HH apply in all control modes. Alarm setpoints, deadbands and delays to be confirmed during commissioning. Y = PIC13092_Deadband (Refer to F13CALC10011) | 1 | 3/04/2025 20/05/2025 26/06/2025 | Updated as per F28 logic FAT discussion https://pastech-2955.atlassian.net/browse/PL-234 (masking removed) MV Range and limits updated to align with DCS (no change on DCS, was programmed correctly)
|  |  |  | FIT13123 | FIC13123 | 2000-F13-PID-PR-10003 | F13-SC-404 SAG Mill Trommel HP Process Water Flow Indicating Transmitter | F13SC404 PW Spray | Automatic | X | X |  | FIT13123 | 100 | 200 | m3/h | 0 | 300 | m3/h | [20 empty] | 1. FCV13123 = Manual 2. Mask for 10 seconds (TBC) when changed to Auto mode | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV13123) position | FCV13123 | Reverse |  |  |  | Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. 2000-F00-CAL-PR-10001 | 1 | 2025-03-06 | PCT alignment action register (DV to be given as % of range or in engineering units)
|  |  |  | FIT13121 | FIC13121 | 2000-F13-PID-PR-10003 | F13-BX-401 SAG Mill Feed Box Process Water Flow Indicating Transmitter | F13MS401 Feed Water | Cascade | X | X | X | FIT13121 | 0 | 800 | m3/h | 0 | 1100 | m3/h | [20 empty] | 1. FCV13121 = Manual 2. Mask for 10 seconds (TBC) when changed to Auto mode | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV13121) position | FCV13121 | Reverse |  |  |  | Cascade setpoint received from either F13CALC10008 or F13CALC10009 (as defined in the Calculation tab) via HS13121 (see Misc tab). Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. 2000-F00-CAL-PR-10001 | 1 | 2025-03-06 | PCT alignment action register (DV to be given as % of range or in engineering units)
|  |  |  | FIT13143 | FIC13143 | 2000-F13-PID-PR-10004 | F13-SC-402 Ball Mill Trommel HP Process Water Flow Indicating Transmitter | F13SC402 PW Spray | Automatic | X | X |  | FIT13143 | 100 | 200 | m3/h | 0 | 320 | m3/h | [20 empty] | 1. FCV13143 = Manual 2. Mask for 10 seconds (TBC) when changed to Auto mode | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV13143) position | FCV13143 | Reverse |  |  |  | Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. 2000-F00-CAL-PR-10001 | 1 | 2025-03-06 | PCT alignment action register (DV to be given as % of range or in engineering units)
|  |  |  | FIT13141 | FIC13141 | 2000-F13-PID-PR-10004 | F13-BX-402 Ball Mill Feed Box Process Water Flow Indicating Transmitter | F13MB401 Feed Water | Automatic | X | X |  | FIT13141 | 0 | 700 | m3/h | 0 | 1100 | m3/h | [20 empty] | 1. FCV13141 = Manual 2. Mask for 10 seconds (TBC) when changed to Auto mode | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV13141) position | FCV13141 | Reverse |  |  |  | Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. 2000-F00-CAL-PR-10001 | 1 | 2025-03-06 | PCT alignment action register (DV to be given as % of range or in engineering units)
|  |  |  | LT13223 | LIC13223 | 2000-F13-PID-PR-10006 | F13-CH-461 Recycle Crusher C Feed Chute Level Transmitter | F13CH461 Level | Automatic | X | X |  | LIT13223 | 35 | 75 | % | 0 | 100 | % | [14 empty] | 30 | 5 | 80 | 5 | 90 | 5 |  | 0 | 100 | 40 | 100 | % VSD Speed | Recycle Crusher C Feeder (F13-FV-401) VSD Speed | F13-FV-401 VSD | Reverse |  |  |  | In Centum, IOP High Limit changed to 103.1% and Low Limit to -1-1% due to VEGAPULS68 limitation | A
|  |  |  | LT13227 | LIC13227 | 2000-F13-PID-PR-10006 | F13-CH-464 Recycle Crusher D Feed Chute Level Transmitter | F13CH464 Level | Automatic | X | X |  | LIT13227 | 35 | 75 | % | 0 | 100 | % | [14 empty] | 30 | 5 | 80 | 5 | 90 | 5 |  | 0 | 100 | 40 | 100 | % VSD Speed | Recycle Crusher D Feeder (F13-FV-402) VSD Speed | F13-FV-402 VSD | Reverse |  |  |  | In Centum, IOP High Limit changed to 103.1% and Low Limit to -1-1% due to VEGAPULS68 limitation | A
|  |  |  | LT13381 | LIC13381 | 2000-F13-PID-PR-10007 | F13-HP-402 Trash Dewatering Screen Underflow Hopper Level Indicating Transmitter | F13HP402 Level | Automatic | X | X |  | LIT13381 | 35 | 75 | % | 0 | 100 | % | [12 empty] | 20 | 5 | 30 | 5 | 80 | 5 | 90 | 5 |  | 0 | 100 | 40 | 100 | % VSD Speed | Trash Dewatering Screen Underflow Pump (F13-PP-403) VSD Speed | F13-PP-403 VSD | Direct |  |  |  | A_LL = Trip F13-PP-403 A_Lo = Warning A_Hi = Warning A_HH = Warning | B
|  |  |  | TIT13629 | TIC13629 | 2000-F13-PID-PR-10010 | F13-LU-413 SAG Mill Main Bearings Lubrication System Conditioned Circuit Temperature Indicating Transmitter | F13LU413 Spply Lube Temp | Automatic | X | X |  | TIT13629 | 0 | 35 | °C | 0 | 100 | °C | [16 empty] | 39 | 5 | 41 | 5 |  | 0 | 100 | 0 | 100 | % Open | Temperature Control Valve (TCV13629) position | TCV13629 | Direct |  |  |  | 2000-ME001.2-F17-50001 2000-ME001.2-D07-50002 | 1 | 2025-06-19 | https://pastech-2955.atlassian.net/browse/KAN-2061
|  |  |  | TIT13880 | TIC13880 | 2000-F13-PID-PR-10011 | F13-LU-423 Ball Mill Main Bearings Lubrication System Lube Oil Heat Exchanger Discharge Temperature Indicating Transmitter | F13LU423 Spply Lube Temp | Automatic | X | X |  | TIT13880 | 0 | 35 | °C | 0 | 100 | °C | [16 empty] | 39 | 5 | 41 | 5 |  | 0 | 100 | 0 | 100 | % Open | Temperature Control Valve (TCV13880) position | TCV13880 | Direct |  |  |  | A_Lo = Warning A_Hi = Start permissive, warning A_HH = Trip equipment 2000-ME001.3-F17-50001 | 1 | 2025-06-19 | https://pastech-2955.atlassian.net/browse/KAN-2061
|  |  |  | FIT13125 | FIC13125 | 2000-F13-PID-PR-10009 | F13-CU-407 SAG Mill VSD Cooling System | F13CU407 Cool Wtr Spply | Automatic | X | X |  | FIT13125 | 0 | 80 | m3/h | 0 | 150 | m3/h | [14 empty] | 37.5 | 5 |  |  |  |  | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MS-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV13125) position | FCV13125 | Reverse |  |  |  | 2000-F13-TQY-ME-10023 Nominal = 64m3/h Range as per instrument datasheet, max = 150 m3/h Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. A_Lo = Confirm flow for VSD start sequence F13-SEQ-0021B and SAG Mill Main Motor inching interlocks SET Controller to MANUAL and MV to 0 when MS_OP_MODE is set to NORMAL (Negative Edge, One Shot) AND after a 20 minute delay. Stop timer if controller is set to AUTO by another condition or sequence. | 1 | 6/03/2025 22/05/2025 | PCT alignment action register (DV to be given as % of range or in engineering units) https://pastech-2955.atlassian.net/browse/KAN-1809 |  |  |  |  | FCV not ready
|  |  |  | FIT13126 | FIC13126 | 2000-F13-PID-PR-10009 | F13-CU-408 Ball Mill VSD Cooling System | F13CU408 Cool Wtr Spply | Automatic | X | X |  | FIT13126 | 0 | 80 | m3/h | 0 | 150 | m3/h | [14 empty] | 37.5 | 5 |  |  |  |  | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MB-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV13126) position | FCV13126 | Reverse |  |  |  | 2000-F13-TQY-ME-10023 Nominal = 64m3/h Range as per instrument datasheet, max = 150 m3/h Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. A_Lo = Confirm flow for VSD start sequence F13-SEQ-0015B and Ball Mill Main Motor inching interlocks SET Controller to MANUAL and MV to 0 when MS_OP_MODE is set to NORMAL (Negative Edge, One Shot) AND after a 20 minute delay. Stop timer if controller is set to AUTO by another condition or sequence. | 1 | 6/03/2025 22/05/2025 | PCT alignment action register (DV to be given as % of range or in engineering units) https://pastech-2955.atlassian.net/browse/KAN-1809 |  |  |  |  | FCV not ready
|  |  |  | FIT13127 | FIC13127 | 2000-F13-PID-PR-10009 | F13-CU-409 Cyclone Feed Pump VSD Cooling System | F13CU409 Cool Wtr Spply | Automatic | X | X |  | FIT13127 | 0 | 20 | m3/h | 0 | 150 | m3/h | [14 empty] | 10 | 5 |  |  |  |  | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-PP-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV13127) position | FCV13127 | Reverse |  |  |  | Cooling Requirements Calc Rev C Nominal = 15.9m3/h A_Lo set to 70% Nom (TBC during commissioning) Range as per instrument datasheet, max = 150 m3/h A_Lo = F13-PP-401 Start Permissive Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. | 1 | 6/03/2025 22/05/2025 | PCT alignment action register (DV to be given as % of range or in engineering units) https://pastech-2955.atlassian.net/browse/KAN-1809 |  |  |  |  | FCV not ready
|  |  |  | TIT13129 | TIC13129 | 2000-F13-PID-PR-10009 |  | F13PP401 Cool Wtr Rturn | Automatic | X | X |  | TIT13129 | 10 | 36 | °C | -5 | 100 | °C | [14 empty] | 5 | 5 | 41 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open | Temperature Control Valve (TCV13129) position | TCV13129 | Direct |  |  |  | A_Hi = Warning A_Lo = Warning Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. Range and alarms estimated. Cooling Water Temperature range ideally 10-36deg C according to Cyclone Feed Pump VSD / Motor Cooling Datasheet 2000-ME063A-F14-10002. TBC during commissioning. | 1 | 6/03/2025 22/05/2025 | PCT alignment action register (DV to be given as % of range or in engineering units) https://pastech-2955.atlassian.net/browse/KAN-1809
|  |  |  | TIT13412 | TIC13412 | 2000-F13-PID-PR-10010 | F13-MS-401B SAG Mill Motor 2 Cooling Water Return Temperature | F13MS401B Cool Wtr Rturn | Automatic | X | X |  | TIT13412 | 10 | 38 | °C | -5 | 100 | °C | [14 empty] | 5 | 5 | 43 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open | Temperature Control Valve (TCV13412) position | TCV13412 | Direct |  |  |  | A_Hi = Warning A_Lo = Warning Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. Range and alarms estimated. Cooling Water Temperature range ideally 0-38 degC according to SAG and Ball Mill Datasheets (VSD / Motor). TBC during commissioning. | 1 | 2025-03-06 | PCT alignment action register (DV to be given as % of range or in engineering units) |  |  |  |  | TCV not ready
|  |  |  | TIT13410 | TIC13410 | 2000-F13-PID-PR-10010 | F13-MS-401A SAG Mill Motor 1 Cooling Water Return Temperature | F13MS401A Cool Wtr Rturn | Automatic | X | X |  | TIT13410 | 10 | 38 | °C | -5 | 100 | °C | [14 empty] | 5 | 5 | 43 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open | Temperature Control Valve (TCV13410) position | TCV13410 | Direct |  |  |  | A_Hi = Warning A_Lo = Warning Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. Range and alarms estimated. Cooling Water Temperature range ideally 0-38 degC according to SAG and Ball Mill Datasheets (VSD / Motor). TBC during commissioning. | 1 | 2025-03-06 | PCT alignment action register (DV to be given as % of range or in engineering units) |  |  |  |  | Tested the Temp transmitter only
|  |  |  | TIT13414 | TIC13414 | 2000-F13-PID-PR-10011 | F13-MB-401A Ball Mill Motor 1 Cooling Water Return Temperature | F13MB401A Cool Wtr Rturn | Automatic | X | X |  | TIT13414 | 10 | 38 | °C | -5 | 100 | °C | [14 empty] | 5 | 5 | 43 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open | Temperature Control Valve (TCV13414) position | TCV13414 | Direct |  |  |  | A_Hi = Warning A_Lo = Warning Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. Range and alarms estimated. Cooling Water Temperature range ideally 0-38 degC according to SAG and Ball Mill Datasheets (VSD / Motor). TBC during commissioning. | 1 | 2025-03-06 | PCT alignment action register (DV to be given as % of range or in engineering units) |  |  |  |  | Tested the Temp transmitter only
|  |  |  | TIT13416 | TIC13416 | 2000-F13-PID-PR-10011 | F13-MB-401B Ball Mill Motor 2 Cooling Water Return Temperature | F13MB401B Cool Wtr Rturn | Automatic | X | X |  | TIT13416 | 10 | 38 | °C | -5 | 100 | °C | [14 empty] | 5 | 5 | 43 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open | Temperature Control Valve (TCV13416) position | TCV13416 | Direct |  |  |  | A_Hi = Warning A_Lo = Warning Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. Range and alarms estimated. Cooling Water Temperature range ideally 0-38 degC according to SAG and Ball Mill Datasheets (VSD / Motor). TBC during commissioning. | 1 | 2025-03-06 | PCT alignment action register (DV to be given as % of range or in engineering units) |  |  |  |  | Tested the Temp transmitter only
|  |  |  | FIT13128 | FIC13128 | 2000-F13-PID-PR-10009 | F13CU409 Cyclone Feed Pump Motor Cooling Water Supply | F13PP401 Cool Wtr Spply | Automatic | X | X |  | FIT13128 | 0 | 76 | m3/h | 0 | 150 | m3/h | [14 empty] | 50 | 5 |  |  |  |  | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-PP-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | 0 | 100 | 0 | 100 | % Open | Temperature Control Valve (TCV13129) position | TCV13129 | Reverse |  |  |  | Cooling Requirements Calc Rev C Nominal = 60m3/h Range as per instrument datasheet, max = 150 m3/h Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. A_Lo = F13-PP-401 Start Permissive | 2 | [6 empty] | 2026-05-27 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=XUZRmk
|  |  |  | FIT13411 | FIC13411 | 2000-F13-PID-PR-10010 | F13-MS-401B SAG Mill Motor 2 Cooling Water Feed Flow Indicating Transmitter | F13MS401B Cool Wtr Feed | Automatic | X | X |  | FIT13411 | 0 | 76 | m3/h | 0 | 150 | m3/h | [14 empty] | 55 | 5 |  |  |  |  | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MS-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | 0 | 100 | 0 | 100 | % Open | Temperature Control Valve (TCV13412) position | TCV13412 | Reverse |  |  |  | 2000-F13-TQY-ME-10023 Nominal = 64m3/h Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. A_Lo = Confirm flow for VSD start sequence F13-SEQ-0021B and SAG Mill Main Motor inching interlocks | 2 | [6 empty] | 2026-05-27 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=XUZRmk
|  |  |  | FIT13409 | FIC13409 | 2000-F13-PID-PR-10010 | F13-MS-401A SAG Mill Motor 1 Cooling Water Feed Flow Indicating Transmitter | F13MS401A Cool Wtr Feed | Automatic | X | X |  | FIT13409 | 0 | 76 | m3/h | 0 | 150 | m3/h | [14 empty] | 55 | 5 |  |  |  |  | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MS-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | 0 | 100 | 0 | 100 | % Open | Temperature Control Valve (TCV13410) position | TCV13410 | Reverse |  |  |  | 2000-F13-TQY-ME-10023 Nominal = 64m3/h Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. A_Lo = Confirm flow for VSD start sequence F13-SEQ-0021B and SAG Mill Main Motor inching interlocks | 2 | [6 empty] | 2026-05-27 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=XUZRmk
|  |  |  | FIT13413 | FIC13413 | 2000-F13-PID-PR-10011 | F13-MB-401A Ball Mill Motor 1 Cooling Water Feed Flow Indicating Transmitter | F13MB401A Cool Wtr Feed | Automatic | X | X |  | FIT13413 | 0 | 76 | m3/h | 0 | 150 | m3/h | [14 empty] | 55 | 5 |  |  |  |  | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MB-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | 0 | 100 | 0 | 100 | % Open | Temperature Control Valve (TCV13414) position | TCV13414 | Reverse |  |  |  | 2000-F13-TQY-ME-10023 Nominal = 64m3/h Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. A_Lo = Confirm flow for VSD start sequence F13-SEQ-0015B and Ball Mill Main Motor inching interlocks | 2 | [6 empty] | 2026-05-27 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=XUZRmk
|  |  |  | FIT13415 | FIC13415 | 2000-F13-PID-PR-10011 | F13-MB-401B Ball Mill Motor 2 Cooling Water Feed Flow Indicating Transmitter | F13MB401B Cool Wtr Feed | Automatic | X | X |  | FIT13415 | 0 | 76 | m3/h | 0 | 150 | m3/h | [14 empty] | 55 | 5 |  |  |  |  | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MB-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | 0 | 100 | 0 | 100 | % Open | Temperature Control Valve (TCV13416) position | TCV13416 | Reverse |  |  |  | 2000-F13-TQY-ME-10023 Nominal = 64m3/h Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. A_Lo = Confirm flow for VSD start sequence F13-SEQ-0015B and Ball Mill Main Motor inching interlocks | 2 | [6 empty] | 2026-05-27 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=553&pa=1&e=XUZRmk
|  |  |  | FIT13071 | FIC13071 | 2000-F13-PID-PR-10002 | F13-SC-401 SAG Mill Discharge Screen Process Water Flow Indicating Transmitter | F13SC401 PW Spray | Automatic | X | X |  | FIT13071 | 150 | 250 | m3/h | 0 | 400 | m3/h | [20 empty] | 1. F13-SC-401 Not Running 2. Mask for 10 seconds (TBC) after start signal | 0 | 100 | 0 | 100 | % Open | Flow Control Valve (FCV13071) position | FCV13071 | Reverse |  |  |  | Include (10 second On-Delay): DV+/- alarm. Deviation setpoint (DL) configured to +/-5% of range. To be confirmed during commissioning. 2000-F00-CAL-PR-10001 | 1 | 2025-03-06 | PCT alignment action register (DV to be given as % of range or in engineering units) |  |  |  |  | Transmitter readings (not PID action) checked and good -PH 11/06/2026
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 34 | 34

## 9. Drives
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - MILLING & CLASSIFICATION (F13)
2000-F13-LST-PR-10001
DRIVE INTERLOCKS AND CONTROL
[15 empty] | Description (Unhealthy Interlocks and Healthy Start Permissives) |  |  |  | Interlocks | [8 empty] | C1 Sign Off |  | C1 Sign Off
Tag Name | P&ID | Name | Drive Type | Speed Min | Speed Max | Speed Units | SP Lower Limit | SP Upper Limit | Current Max | Manual | Auto | Start Condition (Auto Mode) | Stop Condition (Auto Mode) | # |  | Delay On | Delay Off | Start Permissive | Process | Critical | Hardwired to Drive | Bypass | Reset Required | Comments | Rev | Change Date | Change Reference | OK | Date | OK | Date | Comments
F13-FA-411 | 2000-F13-PID-PR-10001 | COARSE ORE RECLAIM FEEDER 1 | VSD | 0 | 100 | % | 40 | 100 | 494 | X | X | F13-SEQ-0025 | F13-SEQ-0026 | [11 empty] | A
[14 empty] | 1 | F13-FA-411 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FA-411 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FA-411 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FA-411 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FA-411 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FA-411 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FA-411 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | ZE13006 Active AND F13-FA-411 Running > 10 seconds | 3 |  |  |  | X |  |  |  | Wired directly to VSD |  | 2025-03-12 | [KAN-1469] Soft Tag VSD Underspeeds - Jira
[14 empty] | 9 | PWS13005A Active | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | PWS13005B Active | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 11 | YY13007 Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to F13-FA-411 start | 0
[14 empty] | 12 | TI13003A ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 13 | TI13003B ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 14 | TI13003C ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 15 | TI13003D ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 16 | TI13003E ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 17 | PS13156 Inactive | 30 |  |  | X |  |  | X |  | Gearbox Cooler Pump | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1389 https://pastech-2955.atlassian.net/browse/KAN-1388 https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 18 | TI13012 ≥ A_HH | 5 |  |  |  | X |  |  |  | Gearbox Sump Cooler Temperature | B
[14 empty] | 19 | TI13013 ≥ A_HH | 5 |  |  |  | X |  |  |  | Gearbox High Speed Bearing Temperature | B
[14 empty] | 20 | Grease Cycle Fault | 0 |  |  | X |  |  | X |  | Logic: F13LU451_T3 Elapsed (See the Misc. tab) Grease cycle switch inactive or low reservoir grease level for 24 hours. | B
[14 empty] | 21 | F13-PO-437 Not Running | 3 |  |  | X |  |  | X |  | Gearbox Oil Cooler Pump motor to be running prior to start-up of main motor drive. | 0
[14 empty] | 22 | TI13012 < P_Hi | 5 |  | X |  |  |  | X |  | Oil Temperature must be less than 70C to start Apron Feeder drive. | 0
[14 empty] | 23 | F13-CV-403 Not Running | 0 |  |  | X |  |  | X |  | SAG Mill Feed Conveyor | A
[14 empty] | 24 | F13-MS-401A/B Not Running | 0 |  |  | X |  |  | X |  | Logic: MS_RUNNING = NOT RUNNING SAG Mill Main Motor 1 and 2 Not Running | B
[14 empty] | 25 | F13-DC-401 Not Running | 1200 |  |  | X |  |  | X |  | Logic: F13-FN-402 = NOT RUNNING Alarm delay to be confirmed during commissioning. | B
[14 empty] | 26 | LI13002 ≤ A_LL | 5 |  |  | X |  |  | X |  | Coarse Ore Stockpile 2 Low Low level | B
[14 empty] | 27 | LSH13011 Inactive | 3 |  |  | X |  |  | X |  | Reclaim Feeder 1 Discharge Chute blocked | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 28 | NI17030 ≥ A_Hi AND ZSH17014 Inactive | 15 |  |  | X |  |  | X |  | Flotation Tailings Thickener Rake Torque greater than or equal to 50% True AND rake lifted to highest point is true for 15 seconds. Cut fresh feed off. Alarm delay to be confirmed during commissioning. | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 29 | F17-PO-408 Not Running | 240 |  |  | X |  |  | X |  | Flotation Tailings Thickener Rake Drive HPU Pump Not Running. Alarm delay to be confirmed during commissioning. | B
[14 empty] | 30 | NSHH30602 Active AND ZSH30603 Active | 15 |  |  | X |  |  | X |  | Concentrate Thickene torque high high is On and Rakes High is On. Bypass if instrument is faulty or for maintenance purposes. Alarm delay to be confirmed during commissioning. NB: NAHH30602 ad ZAH30603 are from existing, brownfields instrumentation. | B
[14 empty] | 31 | F30-TH-61 Not Running | 240 |  |  | X |  |  | X |  | Concentrate Thickener Rake Drive HPU Not Running. Alarm delay to be confirmed during commissioning. | B
[14 empty] | 32 | High SAG Mill Power | 5 |  |  | X |  |  | X |  | Logic: JI13136A OR JI13136B ≥ A_HH | 0
[14 empty] | 33 | High Ball Mill Power | 5 |  |  | X |  |  | X |  | Logic: JI13149A OR JI13149B ≥ A_HH | 0
[14 empty] | 34 | WI13148 ≥ A_HH | 5 |  |  | X |  |  | X |  | High Ball Mill weight | 0
[14 empty] | 35 | WIC13135 ≥ A_HH | 5 |  |  | X |  |  | X |  | High SAG Mill weight | 0
F13-LU-451 | 2000-F13-PID-PR-10001 | COARSE ORE RECLAIM FEEDER 1 AUTOLUBE GREASE SYSTEM | DOL | [5 empty] | 0.74 | X | X | F13LU451_T2 Timer In Progress | F13LU451_T2 Stopped | [10 empty] | Refer to Misc tab for timer details | A | [6 empty] | bump wrong direction 20/04/2026
[14 empty] | 1 | F13-LU-451 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-LU-451 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-LU-451 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-LU-451 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-LU-451 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-LU-451 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-LU-451 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-FA-411 Not Running & F13-LU-451 in Manual | 10 |  |  | X |  |  | X |  | Logic: F13-FA-411 Not Running and F13-LU-451 in Manual Bypass for commissioning purposes. Interlock if left in manual and feeder is not running. | B
F13-FN-422 | 2000-F13-PID-PR-10001 | COARSE ORE RECLAIM FEEDER 1 GEARBOX COOLER FAN | DOL | [5 empty] | 1.5 | X | X | TSH13994 ACTIVE for 3 seconds | TSH13994 INACTIVE for 60 seconds | [11 empty] | A
[14 empty] | 1 | F13-FN-422 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FN-422 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FN-422 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FN-422 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-422 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Manually set the switch to ON.
[14 empty] | 6 | F13-FN-422 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-422 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-PO-437 | 2000-F13-PID-PR-10001 | COARSE ORE RECLAIM FEEDER 1 GEARBOX COOLER OIL PUMP | DOL | [5 empty] | 3.25 | X | X | F13-SEQ-0025 | F13-FA-411 Not Running for 30 seconds | [10 empty] | Pump to start prior to Apron Feeder Motor. Oil pressure to be ≥ 0.7 bar and oil temperature ≤ 70C prior to apron feeder motor energising (included as Feeder drive interlock). | 1 | 2025-04-29 | RE: Recycle Crushing Punchlist Items |  |  |  |  | This hasnt been actioned? is this new? AP 30/07/2026
[14 empty] | 1 | F13-PO-437 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-437 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-437 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-437 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-437 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Manually set the switch to ON.
[14 empty] | 6 | F13-PO-437 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-437 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FA-412 | 2000-F13-PID-PR-10001 | COARSE ORE RECLAIM FEEDER 2 | VSD | 0 | 100 | % | 40 | 100 | 494 | X | X | F13-SEQ-0025 | F13-SEQ-0026 | [11 empty] | A
[14 empty] | 1 | F13-FA-412 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FA-412 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FA-412 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FA-412 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FA-412 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FA-412 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FA-412 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | ZE13016 Active AND F13-FA-412 Running > 10 seconds | 3 |  |  |  | X |  |  |  | Wired directly to VSD | 1 | 2025-03-12 | [KAN-1469] Soft Tag VSD Underspeeds - Jira
[14 empty] | 9 | PWS13015A Active | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | PWS13015B Active | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 11 | YY13017 Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to F13-FA-412 start | 0
[14 empty] | 12 | TI13004A ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 13 | TI13004B ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 14 | TI13004C ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 15 | TI13004D ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 16 | TI13004E ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 17 | PS13159 Inactive | 30 |  |  | X |  |  | X |  | Gearbox Cooler Pump | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1389 https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 18 | TI13022 ≥ A_HH | 5 |  |  |  | X |  |  |  | Gearbox Sump Cooler Temperature | B
[14 empty] | 19 | TI13023 ≥ A_HH | 5 |  |  |  | X |  |  |  | Gearbox High Speed Bearing Temperature | B
[14 empty] | 20 | Grease Cycle Fault | 0 |  |  | X |  |  | X |  | Logic: F13LU452_T3 Elapsed (See Misc. tab) Grease cycle switch inactive or low reservoir grease level for 24 hours. | B
[14 empty] | 21 | F13-PO-438 Not Running | 3 |  |  | X |  |  | X |  | Gearbox Oil Cooler Pump motor to be running prior to start-up of main motor drive. | 0
[14 empty] | 22 | TI13022 < P_Hi | 5 |  | X |  |  |  | X |  | Oil Temperature must be less than 70C to start Apron Feeder drive. | 0
[14 empty] | 23 | F13-CV-403 Not Running | 0 |  |  | X |  |  | X |  | SAG Mill Feed Conveyor | A
[14 empty] | 24 | F13-MS-401A/B Not Running | 0 |  |  | X |  |  | X |  | Logic: MS_RUNNING = NOT RUNNING SAG Mill Main Motor 1 and 2 Not Running | B
[14 empty] | 25 | F13-DC-401 Not Running | 1200 |  |  | X |  |  | X |  | Logic: F13-FN-402 = NOT RUNNING Alarm delay to be confirmed during commissioning. | B
[14 empty] | 26 | LI13002 ≤ A_LL | 5 |  |  | X |  |  | X |  | Coarse Ore Stockpile 2 Low Low level | B
[14 empty] | 27 | LSH13021 Inactive | 3 |  |  | X |  |  | X |  | Reclaim Feeder 2 Discharge Chute blocked | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 28 | NI17030 ≥ A_Hi AND ZSH17014 Inactive | 15 |  |  | X |  |  | X |  | Flotation Tailings Thickener Rake Torque greater than or equal to 50% True AND rake lifted to highest point is true for 15 seconds. Cut fresh feed off. Alarm delay to be confirmed during commissioning. | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 29 | F17-PO-408 Not Running | 240 |  |  | X |  |  | X |  | Flotation Tailings Thickener Rake Drive HPU Pump Not Running. Alarm delay to be confirmed during commissioning. | B
[14 empty] | 30 | NSHH30602 Active AND ZSH30603 Active | 15 |  |  | X |  |  | X |  | Concentrate Thickene torque high high is On and Rakes High is On. Bypass if instrument is faulty or for maintenance purposes. Alarm delay to be confirmed during commissioning. NB: NAHH30602 ad ZAH30603 are from existing, brownfields instrumentation. | B
[14 empty] | 31 | F30-TH-61 Not Running | 240 |  |  | X |  |  | X |  | Concentrate Thickener Rake Drive HPU Not Running. Alarm delay to be confirmed during commissioning. | B
[14 empty] | 32 | High SAG Mill Power | 5 |  |  | X |  |  | X |  | Logic: JI13136A OR JI13136B ≥ A_HH | 0
[14 empty] | 33 | High Ball Mill Power | 5 |  |  | X |  |  | X |  | Logic: JI13149A OR JI13149B ≥ A_HH | 0
[14 empty] | 34 | WI13148 ≥ A_HH | 5 |  |  | X |  |  | X |  | High Ball Mill weight | 0
[14 empty] | 35 | WIC13135 ≥ A_HH | 5 |  |  | X |  |  | X |  | High SAG Mill weight | 0
F13-LU-452 | 2000-F13-PID-PR-10001 | COARSE ORE RECLAIM FEEDER 2 AUTOLUBE GREASE SYSTEM | DOL | [5 empty] | 0.74 | X | X | F13LU452_T2 Timer In Progress | F13LU452_T2 Stopped | [10 empty] | Refer to Misc tab for timer details | A | [6 empty] | Bumped 20/04/2026
[14 empty] | 1 | F13-LU-452 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-LU-452 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-LU-452 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-LU-452 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-LU-452 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-LU-452 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-LU-452 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-FA-412 Not Running & F13-LU-452 in Manual | 10 |  |  | X |  |  | X |  | Logic: F13-FA-412 Not Running and F13-LU-452 in Manual Bypass for commissioning purposes. Interlock if left in manual and feeder is not running. | B
F13-FN-423 | 2000-F13-PID-PR-10001 | COARSE ORE RECLAIM FEEDER 2 GEARBOX COOLER FAN | DOL | [5 empty] | 1.5 | X | X | TSH13995 ACTIVE for 3 seconds | TSH13995 INACTIVE for 60 seconds | [11 empty] | B
[14 empty] | 1 | F13-FN-423 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FN-423 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FN-423 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FN-423 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-423 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Manually set the switch to ON.
[14 empty] | 6 | F13-FN-423 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-423 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-PO-438 | 2000-F13-PID-PR-10001 | COARSE ORE RECLAIM FEEDER 2 GEARBOX COOLER OIL PUMP | DOL | [5 empty] | 3.25 | X | X | F13-SEQ-0025 | F13-FA-412 Not Running for 30 seconds | [10 empty] | Pump to start prior to Apron Feeder Motor. Oil pressure to be ≥ 0.7 bar and oil temperature ≤ 70C prior to apron feeder motor energising (included as Feeder drive interlock). | 1 | 2025-04-29 | RE: Recycle Crushing Punchlist Items |  |  |  |  | This hasnt been actioned? is this new? AP 30/07/2026
[14 empty] | 1 | F13-PO-438 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-438 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-438 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-438 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-438 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Manually set the switch to ON.
[14 empty] | 6 | F13-PO-438 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-438 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FA-414 | 2000-F13-PID-PR-10001 | EMERGENCY FEEDER | VSD | 0 | 100 | % | 40 | 100 | 162 | X | X | F13-SEQ-0025 | F13-SEQ-0026 | [11 empty] | A
[14 empty] | 1 | F13-FA-414 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FA-414 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FA-414 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FA-414 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FA-414 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FA-414 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FA-414 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | ZE13026 Active AND F13-FA-414 Running > 10 seconds | 3 |  |  |  | X |  |  |  | Wired directly to VSD | 1 | 2025-03-12 | [KAN-1469] Soft Tag VSD Underspeeds - Jira
[14 empty] | 9 | PWS13025A Active | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | PWS13025B Active | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 11 | YY13027 Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to F13-FA-414 start | 0
[14 empty] | 12 | PS13162 Inactive | 30 |  |  | X |  |  | X |  | Gearbox Cooler Pump | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1389 https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | TI13032 ≥ A_HH | 5 |  |  |  | X |  |  |  | Gearbox Sump Cooler Temperature | B
[14 empty] | 14 | TI13033 ≥ A_HH | 5 |  |  |  | X |  |  |  | Gearbox High Speed Bearing Temperature | B
[14 empty] | 15 | Grease Cycle Fault | 0 |  |  | X |  |  | X |  | Logic: F13LU453_T3 Elapsed (See Misc. tab) Grease cycle switch inactive or low reservoir grease level for 24 hours. | B
[14 empty] | 16 | F13-PO-439 Not Running | 3 |  |  | X |  |  | X |  | Gearbox Oil Cooler Pump motor to be running prior to start-up of main motor drive. | 0
[14 empty] | 17 | TI13032 < P_Hi | 5 |  | X |  |  |  | X |  | Oil Temperature must be less than 70C to start Apron Feeder drive. | 0
[14 empty] | 18 | F13-CV-403 Not Running | 0 |  |  | X |  |  | X |  | SAG Mill Feed Conveyor | A
[14 empty] | 19 | F13-MS-401A/B Not Running | 0 |  |  | X |  |  | X |  | Logic: MS_RUNNING = NOT RUNNING SAG Mill Main Motor 1 and 2 Not Running | B
[14 empty] | 20 | LSH13031 Inactive | 3 |  |  | X |  |  | X |  | Emergency Feeder Discharge Chute blocked | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 21 | LI13036 ≤ A_LL | 5 |  |  | X |  |  | X |  | Emergency Feed Bin Low Low level | B
[14 empty] | 22 | LI13036 > A_Lo | 5 |  | X |  |  |  | X |  | Emergency Feed Bin > Low level to start | A
[14 empty] | 23 | NI17030 ≥ A_Hi AND ZSH17014 Inactive | 15 |  |  | X |  |  | X |  | Flotation Tailings Thickener Rake Torque greater than or equal to 50% True AND rake lifted to highest point is true for 15 seconds. Cut fresh feed off. Alarm delay to be confirmed during commissioning. | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 24 | F17-PO-408 Not Running | 240 |  |  | X |  |  | X |  | Flotation Tailings Thickener Rake Drive HPU Pump Not Running. Alarm delay to be confirmed during commissioning. | B
[14 empty] | 25 | NSHH30602 Active AND ZSH30603 Active | 15 |  |  | X |  |  | X |  | Concentrate Thickene torque high high is On and Rakes High is On. Bypass if instrument is faulty or for maintenance purposes. Alarm delay to be confirmed during commissioning. NB: NAHH30602 ad ZAH30603 are from existing, brownfields instrumentation. | B
[14 empty] | 26 | F30-TH-61 Not Running | 240 |  |  | X |  |  | X |  | Concentrate Thickener Rake Drive HPU Not Running. Alarm delay to be confirmed during commissioning. | B
[14 empty] | 27 | High SAG Mill Power | 5 |  |  | X |  |  | X |  | Logic: JI13136A OR JI13136B ≥ A_HH | 0
[14 empty] | 28 | High Ball Mill Power | 5 |  |  | X |  |  | X |  | Logic: JI13149A OR JI13149B ≥ A_HH | 0
[14 empty] | 29 | WI13148 ≥ A_HH | 5 |  |  | X |  |  | X |  | High Ball Mill weight | 0
[14 empty] | 30 | WIC13135 ≥ A_HH | 5 |  |  | X |  |  | X |  | High SAG Mill weight | 0
F13-LU-453 | 2000-F13-PID-PR-10001 | EMERGENCY FEEDER AUTOLUBE GREASE SYSTEM | DOL | [5 empty] | 0.74 | X | X | F13LU453_T2 Timer In Progress | F13LU453_T2 Stopped | [10 empty] | Refer to Misc tab for timer details | A
[14 empty] | 1 | F13-LU-453 Comms Failure | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | bump good 20/04/2026
[14 empty] | 2 | F13-LU-453 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-LU-453 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-LU-453 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-LU-453 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-LU-453 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-LU-453 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-FA-414 Not Running & Manual | 10 |  |  | X |  |  | X |  | Logic: F13-FA-414 Not Running and F13-LU-453 in Manual Bypass for commissioning purposes. Interlock if left in manual and feeder is not running. | B
F13-FN-424 | 2000-F13-PID-PR-10001 | EMERGENCY FEEDER GEARBOX COOLER FAN | DOL | [5 empty] | 1.5 | X | X | TSH13996 ACTIVE for 3 seconds | TSH13996 INACTIVE for 60 seconds | [11 empty] | B
[14 empty] | 1 | F13-FN-424 Comms Failure | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | NA. Signal set to ON
[14 empty] | 2 | F13-FN-424 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FN-424 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FN-424 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-424 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FN-424 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-424 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-PO-439 | 2000-F13-PID-PR-10001 | EMERGENCY FEEDER GEARBOX COOLER OIL PUMP | DOL | [5 empty] | 3.25 | X | X | F13-SEQ-0025 | F13-FA-414 Not Running for 30 seconds | [10 empty] | Pump to start prior to Apron Feeder Motor. Oil pressure to be ≥ 0.7 bar and oil temperature ≤ 70C prior to apron feeder motor energising (included as Feeder drive interlock). | 1 | 2025-04-29 | RE: Recycle Crushing Punchlist Items |  |  |  |  | This hasnt been actioned? is this new? AP 30/07/2026
[14 empty] | 1 | F13-PO-439 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-439 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-439 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-439 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-439 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-439 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0 | [6 empty] | NA. Signal set to ON
[14 empty] | 7 | F13-PO-439 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-CV-403 | 2000-F13-PID-PR-10001 | SAG MILL FEED CONVEYOR | VSD | 0 | 100 | % | 100 | 100 | 581 | X | X | F13-SEQ-0023 | F13-SEQ-0024 | [11 empty] | A
[14 empty] | 1 | F13-CV-403 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-CV-403 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-CV-403 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-CV-403 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-CV-403 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | MCC Unhealthy utilising undervoltage alarm? AP 30/07/2026
[14 empty] | 6 | F13-CV-403 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-CV-403 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | TI13991A ≥ A_HH | 5 |  |  |  | X |  |  |  |  | A
[14 empty] | 9 | TI13991B ≥ A_HH | 5 |  |  |  | X |  |  |  |  | A
[14 empty] | 10 | TI13991C ≥ A_HH | 5 |  |  |  | X |  |  |  |  | A
[14 empty] | 11 | TI13991D ≥ A_HH | 5 |  |  |  | X |  |  |  |  | A
[14 empty] | 12 | TI13991E ≥ A_HH | 5 |  |  |  | X |  |  |  |  | A
[14 empty] | 13 | BDS13053A Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 14 | BDS13053B Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 15 | BDS13053C Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 16 | BDS13053D Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 17 | BDS13053E Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 18 | BDS13053F Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 19 | BDS13053G Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 20 | BDS13053H Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 21 | PWS13050A Active | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 22 | PWS13050B Active | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 23 | PWS13050C Active | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 24 | PWS13050D Active | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 25 | PWS13050E Active | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 26 | PWS13050F Active | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 27 | PWS13050G Active | 0 |  |  |  | X | X |  | X |  | 2 | 2026-01-31 | CR-065
[14 empty] | 28 | PWS13050H Active | 0 |  |  |  | X | X |  | X |  | 2 | 2026-01-31 | CR-065
[14 empty] | 29 | VI13060A ≥ A_HH | 5 |  |  | X |  |  | X |  |  | B
[14 empty] | 30 | VI13060B ≥ A_HH | 5 |  |  | X |  |  | X |  |  | B
[14 empty] | 31 | ZS13057A Active | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 32 | ZS13057B Active | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 33 | BRS13054 Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 34 | YY13056A Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to F13-CV-403 start | 0
[14 empty] | 35 | YY13056B Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to F13-CV-403 start | 0
[14 empty] | 36 | YY13056C Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to F13-CV-403 start | 0
[14 empty] | 37 | SSL13051 Inactive AND (F13-CV-403 Running > 30 seconds) | 3 |  |  | X |  |  | X |  | Underspeed | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 38 | F13-MS-401A/B Not Running | 0 |  |  | X |  |  | X |  | Logic: MS_RUNNING = NOT RUNNING SAG Mill Main Motor 1 and 2 Not Running | B
[14 empty] | 39 | LSH13058 Inactive | 3 |  |  | X |  |  | X |  | SAG Mill Feed Conveyor Discharge Chute blocked | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 40 | F13MS401 Mill Delayed Stop | 0 |  |  |  | X |  |  |  | Logic: MS_NCR_ILK Active OR F13-SEQ-0022A Running SAG Mill Abnormal Shutdown, Mill Delayed Stop | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1877
[14 empty] | 41 | F13MS401 Mill Instantaneous Stop | 0 |  |  |  | X |  |  |  | Logic: MS_CR_ILK Active OR F13-SEQ-0022C Running SAG Mill Abnormal Shutdown, Mill Instantaneous Stop | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1877
[14 empty] | 42 | F13-PP-401 Not Running | 0 |  |  | X |  |  | X |  | Cyclone Feed Pump | 0
[14 empty] | 43 | YA24713 Alarm | 0 |  |  |  | X |  |  |  | Linear heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 12/03/2025 07/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1810
[14 empty] | 44 | YA24664 Alarm | 0 |  |  |  | X |  |  |  | Linear heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 12/03/2025 07/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1810
[14 empty] | 45 | PSL24662 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 46 | PSL24711 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 47 | F13CV403ALM3 Active | 0 |  |  | X |  |  | X |  | Belt rip monitoring controller | 1 | 6/03/2025 08/04/2025 | New instrumentation added (NSR directive) https://pastech-2955.atlassian.net/browse/KAN-1662 Variation NOFD153
[14 empty] | 48 | F13-MB-401A/B Not Running AND XV13114 OR XV13115 Open OR F13MB401 Mill Delayed Stop | 0 |  |  | X |  |  | X |  | Logic: (MB_RUNNING = NOT RUNNING OR MB_NCR_ILK Active OR F13-SEQ-0016A Running) AND (XV13114 OR XV13115 Open) Ball Mill Main Motor 1 and 2 Not Running and SABC circuit Ball Mill Abnormal Shutdown, Mill Delayed Stop | 2
F13-FN-402 | 2000-F12-PID-PR-10002 | RECLAIM TUNNEL DUST COLLECTOR FAN | DOL | [5 empty] | 59.6 59.5 | X | X | F13-SEQ-0023 | F13-SEQ-0024 | [11 empty] | A
[14 empty] | 1 | F13-FN-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FN-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FN-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FN-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FN-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | PDI13067 ≥ A_HH | 3600 |  |  |  | X |  |  |  | Reclaim Dust Pressure Diff. Trip F13-FN-402 if PDI13067 ≥ A_HH for more than 1 hour as per vendor advice. | A
[14 empty] | 9 | F13-VR-402 Not Running | 3 |  |  | X |  |  | X |  | Reclaim Dust Rotary Valve. Prevent start-up or trip F13-FN-402 if Rotary Valve is Not Running. Bypass for maintenance testing purposes. | 0
F13-VR-402 | 2000-F13-PID-PR-10001 | RECLAIM TUNNEL DUST COLLECTOR ROTARY VALVE | DOL | [5 empty] | 1.66 | X | X | F13-SEQ-0023 | F13-FN-402 Not Running AND F13-VR-402 = Running for 5 minutes | [10 empty] | Vendor advice to stop Rotary Valve 3-5 minutes after Fan stopped. | 1 | 2025-05-07 | Fixed during FAT
[14 empty] | 1 | F13-VR-402 Communcations Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | Trip | F13-VR-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-VR-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-VR-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-VR-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-VR-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-VR-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | SAL13070 Alarm AND (F13-VR-402 Running) | 30 |  |  |  | X |  |  |  | Speed monitoring via DCS (signal active per rotation). Setpoint TBC during commissioning. | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1390 https://pastech-2955.atlassian.net/browse/KAN-1569
F13-BLC-401 | 2000-F13-PID-PR-10001 | SAG MILL BALL CHARGER | DOL | [5 empty] | 9.83 | X | X | F13BLC401_T1 Elapses | F13BLC401_FT ≤= 0t | [11 empty] | A
[14 empty] | 1 | F13-BLC-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-BLC-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-BLC-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-BLC-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-BLC-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-BLC-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-BLC-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-CV-403 Not Running | 0 |  |  | X |  |  | X |  | SAG Mill Feed Conveyor | A
[14 empty] | 9 | F13-MS-401A/B Not Running | 0 |  |  | X |  |  | X |  | Logic: MS_RUNNING = NOT RUNNING SAG Mill Main Motor 1 and 2 Not Running | B
[14 empty] | 10 | LI13037 ≤ A_LL | 5 |  |  | X |  |  | X |  | SAG Mill Ball Charger Feed Bin Low Low | 0
[14 empty] | 11 | WI13055 ≤ A_Lo | 5 |  |  | X |  |  | X |  | SAG Mill Feed Conveyor Weightometer | 0
[14 empty] | 12 | ZSC13038 Active | 3 |  |  | X |  |  | X |  | SAG Ball Charger Isolation gate must be opened | 0
[14 empty] | 13 | ZSO13038 Inactive | 3 |  |  | X |  |  | X |  | SAG Ball Charger Isolation gate must be opened | 0
[14 empty] | 14 | Manual Loading Complete | 3 |  |  | X |  |  | X | X | Logic: F13-BLC-401 in Manual Mode AND F13BLC401_CTR01 =≥ F13BLC401_Parameter_4 F13CALC10001, refer to Calculation tab | 0
F13-BLC-402 | 2000-F13-PID-PR-10004 | BALL MILL BALL CHARGER MAGNET | FE | [5 empty] | 27.82 35.0 |  | X | As per F13-SEQ-0037 | As per F13-SEQ-0037 | [11 empty] | 1
[14 empty] | 1 | F13-BLC-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | 0 | [6 empty] | N/A
[14 empty] | 2 | F13-BLC-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-BLC-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0 | [6 empty] | N/A
[14 empty] | 4 | F13-BLC-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 0 | [6 empty] | N/A
[14 empty] | 5 | F13-BLC-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 0 | [6 empty] | N/A
[14 empty] | 6 | F13-BLC-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0 | [6 empty] | N/A
[14 empty] | 7 | F13-BLC-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0 | [6 empty] | N/A
[14 empty] | 8 | XS13206A Inactive | 0 |  |  |  | X |  |  |  | Emergency Stop active | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 9 | Magnet Duty Cycle Exceeded | 0 |  |  |  | X |  |  |  | Logic: F13BLC402_MXDUTY Active AND WI13285C < P_Lo F13-BLC-402 Magnet drive >= Max Duty Cycle AND WI13285C < P_Lo. WI13285C must be less than P_Lo for magnet to de-energise from max Duty Cycle | 0 | [6 empty] | MSH: 23/08Interlock verified by checking logic, was not possible to trigger during commissioning. Duty cycle timer counts down 3 seconds when magnets denergised, by the time the energises again, the timer is 0 already.
[14 empty] | 10 | Horizontal Magnet Energise Limit | 0 |  | X |  |  |  | X |  | Logic (Healthy): ZI13310A.PV < F13_H_ENC_LFT + F13_H_ENC_TLR AND ZI13310A.PV > F13_H_ENC_DMP - F13_H_ENC_TLR AND ZI13310B.PV > F13_V_ENC_DMP - F13_V_ENC_TLR F13-CR-453 Magnet cannot be energised when trolley is pass the horizontal Lift or Dump position (toward the respective Maintenance bay) or above the vertical Dump position MOC-833: Magnet allowed to lower down in dump position while energised to denergise (discharge balls) closer to surface to avoid bouncing | 1 | 15/05/2025 26/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 Call with AH |  |  |  |  | MSH: 23/08, 13BLV402CL1/2 used to calculate blocks where magnet can be energised (XC13230EN) and denergised (XC13234EN)
[14 empty] | 11 | XS13206B Inactive | 0 |  |  |  | X |  |  |  | MCCB Trip Unhealthy | 2
F13-CR-453_H | 2000-F13-PID-PR-10004 | BALL MILL CHARGER HOIST | FE | [7 empty] | X | Build as dual output drive. XC13280A drives hoist up XC13280B drives hoist down | XC13280A (Up) Inactive AND XC13280B (Down) Inactive | [11 empty] | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[12 empty] | XC13280A (Up) Active if: | [12 empty] | 0 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[12 empty] | Auto: HS13140AAUT Auto AND as per Sequence F13-SEQ-0037 OR F13-SEQ-0038 | [12 empty] | 0 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[12 empty] | Manual: HS13140BMAN Manual AND HS13203AUP Up | [12 empty] | 0 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[12 empty] | XC13280B (Down) Active if: | [12 empty] | 0 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[12 empty] | Auto: HS13140AAUT Auto AND as per Sequence F13-SEQ-0037 OR F13-SEQ-0038 | [12 empty] | 0 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[12 empty] | Manual: HS13140BMAN Manual AND HS13203BDN Down |  | 8 | XS13206A Inactive | 0 |  |  |  | X |  |  |  | Emergency Stop active | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386 |  |  |  |  | powers-off whole panel
[14 empty] | 9 | Hoist Raise & Lower Active | 5 0 |  |  |  | X |  |  |  | Logic: XC13280A Active AND XC13280B Active F13-CR-453 Hoist Up and Down relays active simultaneously | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | logic prevents both relays from energising at the same time, 0 sec delay
[14 empty] | 10 | Trolley Driving | 5 2 |  |  |  | X |  |  |  | Logic: XC13251A Active OR XC13251B Active F13-CR-453 Trolley driving forward/reverse | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | 2 seconds currently configured in FCS
[14 empty] | 11 | XI13206B Active | 3 |  |  |  | X |  |  |  | F13-CR-453 Hoist Overload MCCB Trip | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[14 empty] | 12 | F13BLC402_T2 Elapsed | 0 |  | X |  |  |  | X |  | F13-CR-453 Post-Movement Traverse Pause Timer must elapse prior to energising hoist | 0
[14 empty] | 13 | WI13285C >= A_HH AND XC13280A Active | 3 |  |  | X |  |  | X |  | F13-BLC-402 Load Cell | 0
[14 empty] | 14 | Hoist Horizontal Out of Range | 5 |  |  |  | X |  |  |  | Logic: • XC13280B Active AND • (ZI13310A.PV =/= F13_H_ENC_MNT1 ± F13_H_ENC_TLR) AND • NOT (ZI13310A.PV > F13_H_ENC_DMP - F13_H_ENC_TLR AND ZI13310A.PV < F13_H_ENC_LFT + F13_H_ENC_TLR) AND • (ZI13310A.PV =/= F13_H_ENC_MNT2 ± F13_H_ENC_TLR)) Hoist can only be lowered within specific horizontal trolley positions. Refer to 2000-ME057-M01-10001 | 1 | 15/05/2025 26/08/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 Updated to match DCS. No action required |  |  |  |  | implementation done differently but tested bounderies. Refere to 13BLC402CL1/2 for more info
[14 empty] | 15 | Hoist Vertical Out of Range | 5 |  |  |  | X |  |  |  | Logic: • XC13280B Active AND • (ZI13310B.PV > F13_V_ENC_MNT1 AND (ZI13310A.PV = F13_H_ENC_MNT1 ± F13_H_ENC_TLR)) OR (ZI13310B.PV > F13_V_ENC_LFT AND (ZI13310A.PV = F13_H_ENC_LFT ± F13_H_ENC_TLR)) OR (ZI13310B.PV > F13_V_ENC_DMP AND (ZI13310A.PV > F13_H_ENC_DMP - F13_H_ENC_TLR AND ZI13310A.PV < F13_H_ENC_LFT - F13_H_ENC_TLR)) OR (ZI13310B.PV > F13_V_ENC_MNT2 AND (ZI13310A.PV = F13_H_ENC_MNT2 ± F13_H_ENC_TLR)) Hoist can only be lowered to heights specific to the trolley's designated position. Refer to 2000-ME057-M01-10001 | 1 | 15/05/2025 26/08/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 Updated to match DCS. No action required |  |  |  |  | implementation done differently but tested bounderies. Refere to 13BLC402CL1/2 for more info
[14 empty] | 16 | Hoist Loaded Outside Limit | 5 |  |  |  | X |  |  |  | Logic: ZI13310B.PV < F13_V_ENC_DMP - F13_V_ENC_TLR AND XC13280A Active [F13-BLC-402 Magnets Energised OR WI13285C > P_Lo] | 1 | 15/05/2025 26/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 Call with Andrew H |  |  |  |  | implementation done differently but tested bounderies. Refere to 13BLC402CL1/2 for more info
F13-CR-453_T | 2000-F13-PID-PR-10004 | BALL MILL CHARGER TROLLEY | FE | [7 empty] | X | Build as dual output drive. XC13251A drives trolley forward XC13251B drives trolley in reverse | XC13251A (Fwd) Inactive AND XC13251B (Rev) Inactive | [11 empty] | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[12 empty] | XC13251A (Fwd) Active if: | [12 empty] | 0 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[12 empty] | Auto: HS13140AAUT Auto AND as per Sequence F13-SEQ-0037 OR F13-SEQ-0038 | [12 empty] | 0 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[12 empty] | Manual: HS13140BMAN Manual AND HS13189AFWD Active | [12 empty] | 0 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[12 empty] | XC13251B (Rev) Active if: | [12 empty] | 0 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[12 empty] | Auto: HS13140AAUT Auto AND as per Sequence F13-SEQ-0037 OR F13-SEQ-0038 | [12 empty] | 0 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[12 empty] | Manual: HS13140BMAN Manual AND HS13189BREV Active |  | 8 | XS13206A Inactive | 0 |  |  |  | X |  |  |  | Emergency Stop active | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 9 | Trolley Duty Cycle Exceeded | 0 |  |  |  | X |  |  |  | Logic: F13CR453_MXDUTY Active F13-CR-453 Trolley motor >= Max Duty Cycle | 0
[13 empty] | NOTE: Deenergising this drive will start F13BLC402_T2 | 10 | Trolley Energise Limits | 0 |  |  |  | X |  |  |  | Logic: F13_V_ENC_DMP + F13_V_ENC_TLR > ZI13310B.PV > F13_V_ENC_TRAV + F13_V_ENC_TLR AND ((ZI13310A.PV < F13_H_ENC_DMP - F13_H_ENC_TLR AND XC13251B Active) OR (ZI13310A.PV > F13_H_ENC_LFT + F13_H_ENC_TLR AND XC13251A Active)) OR ZI13310B.PV > F13_V_ENC_DMP + F13_V_ENC_TLR | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | implementation done differently but tested bounderies. Refere to 13BLC402CL1/2 for more info
[14 empty] | 11 | Trolley Forward & Reverse Active | 5 |  |  |  | X |  |  |  | Logic: XC13251A Active AND XC13251B Active F13-CR-453 Reverse and Forward Relays active simultaneously | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[14 empty] | 12 | Hoist Raising/Lowering | 5 |  |  |  | X |  |  |  | Logic: XC13280A OR XC13280B Active F13-CR-453 Hoist & Trolley relays active simultaneously | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[14 empty] | 13 | XI13206B Active | 3 |  |  |  | X |  |  |  | F13-CR-453 Trolley Overload MCCB Trip Active | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[14 empty] | 14 | Forward End of Travel | 3 |  |  |  | X |  |  |  | Logic: ZI13310A.PV > F13_H_ENC_MNT1 + F13_H_ENC_TLR ANDXC13251A Active F13-CR-453 Forward End of Travel Limit (Maintenance 1 bay) active | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
[14 empty] | 15 | Reverse End of Travel | 3 |  |  |  | X |  |  |  | Logic: ZI13310A.PV < F13_H_ENC_MNT2 - F13_H_ENC_TLR ANDXC13251B Active F13-CR-453 Reverse End of Travel Limit (Maintenance 2 bay) active | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876
|  | 0 | [11 empty] | 16 | Trolley Loaded Outside Limit | 0 |  |  |  | X |  |  |  | Logic: (ZI13310A.PV > F13_H_ENC_LFT + F13_H_ENC_TLR AND XC13251A Active) OR (ZI13310A.PV < F13_H_ENC_DMP - F13_H_ENC_TLR AND XC13251B Active) AND [F13-BLC-402 Magnet Energised OR WI13285C > P_Lo] | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | implementation done differently but tested bounderies. Refere to 13BLC402CL1/2 for more info
F13-FN-419 | 2000-F13-PID-PR-10001 | RECLAIM VAULT VENTILATION FAN | DOL | [5 empty] | 51.4 51.6 | X | X | F13-SEQ-0023 | F13-SEQ-0024 | [11 empty] | A
[14 empty] | 1 | F13-FN-419 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FN-419 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FN-419 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FN-419 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-419 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | N/A
[14 empty] | 6 | F13-FN-419 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-419 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-PS-402 | 2000-F13-PID-PR-10001 | COARSE ORE STOCKPILE 2 SUMP PUMP | DOL SP | [5 empty] | 51.4 51.6 | X | X | LSH13064 Active | LSH13064 Inactive for 600 seconds | [11 empty] | 0
[14 empty] | 1 | F13-PS-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PS-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PS-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PS-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PS-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PS-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PS-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-MS-401A/B Not Running | 0 |  |  | X |  |  | X |  | Logic: MS_RUNNING = NOT RUNNING SAG Mill Main Motor 1 and 2 Not Running | B
F13-PP-401 | 2000-F13-PID-PR-10002 | CYCLONE FEED PUMP | VSD | 0 | 100 | % | 40 | 100 | 946 | X | X | F13-SEQ-0009 | F13-SEQ-0010 | [11 empty] | A
[14 empty] | 1 | F13-PP-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | These are modbus signals
[14 empty] | 2 | F13-PP-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PP-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0 | [6 empty] | These are modbus signals
[14 empty] | 4 | F13-PP-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 0 | [6 empty] | These are modbus signals
[14 empty] | 5 | F13-PP-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | These are modbus signals
[14 empty] | 6 | F13-PP-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PP-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0 | [6 empty] | These are modbus signals
[14 empty] | 8 | < 6 Duty Cyclone Feed Valves | 3 |  |  | X |  |  | X |  | Less than 6 Cyclone Feed Valves Opened (XV13094 to XV13108, XV13110, XV13111) Minimum 6 Primary Cyclone Cluster Feed Valves opened | 0 | [6 empty] | Need to run a sequence to test this. Signed off on Justin De Man's witness account.
[14 empty] | 9 | Mill Stopped (SABC/SSSAG) | 250 |  |  | X |  |  | X |  | Logic: F13-MB-401 in Normal Mode AND (XV13114 OR XV13115 = Opened) AND (F13-MB-401 Tripped OR (F13SEQ0016A Running, started by MB_NCR_ILK and F13-MB-401 not running)) OR F13-MS-401 in Normal Mode AND XV13116 = Opened AND (F13-MS-401 Tripped OR (F13SEQ0022A Running, started by MS_NCR_ILK and F13-MS-401 not running)) | 2
[14 empty] | 10 | Underflow Valves Closed | 0 |  |  |  | X |  |  |  | Logic: XV13114, XV13115, XV13116 = Closed | B
[14 empty] | 11 | Cyclone UF Valve Position Conflict | 3 |  | X |  |  |  | X |  | Logic (Healthy): ''Ball Mill' Selected (F13FD401_FP1) AND - XV13114 AND XV13115 = Opened AND XV13116 = Closed OR ''SAG Mill' Selected (F13FD401_FP1) AND - XV13114 AND XV13115 = Closed AND XV13116 = Opened Cyclone Underflow discharge location 'Ball Mill' OR 'SAG Mill' is selected on faceplate F13FD401_FP1. See Misc tab. | 0
[14 empty] | 12 | XV13082 Closed | 3 |  |  | X |  |  | X |  | Cyclone Feed Pump Suction Valve | 0
[14 empty] | 13 | XV13081 Opened | 3 |  |  | X |  |  | X |  | Cyclone Feed Pump Suction Drain Valve | 0
[14 empty] | 14 | XV13084 Opened | 3 |  |  | X |  |  | X |  | Cyclone Feed Pump Discharge Drain Valve | 0
[14 empty] | 15 | PIC13092 ≥ A_HH | 30 |  |  | X |  |  | X |  | Cyclone Feed Pressure | A
[14 empty] | 16 | FI13128 > A_Lo | 30 |  | X |  |  |  | X |  | Cyclone Feed Pump Motor Cooling Water flow | B
[14 empty] | 17 | FIC13127 > A_Lo | 30 |  | X |  |  |  | X |  | Cyclone Feed Pump VSD Cooling Water flow | B
[14 empty] | 18 | TI13119 < A_Hi | 30 |  | X |  |  |  | X |  | Cyclone Feed Pump VSD Cooling Water return temperature | B
[14 empty] | 19 | FI13461 ≤ A_LL AND (F13-PP-401 Running) | 25 |  |  | X |  |  | X |  | Cyclone Feed Pump Gland Water flow | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 20 | XV13460 Auto OR Open | 3 |  | X |  |  |  | X |  | Cyclone Feed Pump Gland Water valve | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/PL-174
[14 empty] | 21 | LIC13076A ≤ A_LL | 5 |  |  | X |  |  | X |  | Logic: LIC13076A ≤ A_LL Cyclone Feed Hopper level. | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
[14 empty] | 22 | F13-FN-443 AND F13-FN-444 Running | 0 |  | X |  |  |  | X |  | Motor cooling fans are running | 2 | [7 empty] | 2026-04-28 | MOC 389
[14 empty] | 23 | 13PP401PSR = Active | 0 |  | X |  |  |  | X |  | Power station contacted prior to start. | 2
F13-FN-443 | 2000-F13-PID-PR-10002 | CYCLONE FEED PUMP MOTOR COOLING FAN 1 | DOL | [5 empty] | 26.1 | X | X | F13SEQ0009 Running | F13-PP-401 Stopped for 1200 seconds | [11 empty] | 2 | 2025-07-02 | CR-021 | [5 empty] | 2026-04-28 | MOC 389
[14 empty] | 1 | F13-FN-443 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
[14 empty] | 2 | F13-FN-443 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
[14 empty] | 3 | F13-FN-443 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
[14 empty] | 4 | F13-FN-443 E-Stop | 0 |  |  |  | X | X |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
[14 empty] | 5 | F13-FN-443 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
[14 empty] | 6 | F13-FN-443 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
[14 empty] | 7 | F13-FN-443 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
F13-FN-444 | 2000-F13-PID-PR-10002 | CYCLONE FEED PUMP MOTOR COOLING FAN 2 | DOL | [5 empty] | 26.1 | X | X | F13SEQ0009 Running | F13-PP-401 Stopped for 1200 seconds | [11 empty] | 2 | 2025-07-02 | CR-021 | [5 empty] | 2026-04-28 | MOC 389
[14 empty] | 1 | F13-FN-444 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
[14 empty] | 2 | F13-FN-444 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
[14 empty] | 3 | F13-FN-444 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
[14 empty] | 4 | F13-FN-444 E-Stop | 0 |  |  |  | X | X |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
[14 empty] | 5 | F13-FN-444 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
[14 empty] | 6 | F13-FN-444 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
[14 empty] | 7 | F13-FN-444 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2 | [7 empty] | 2026-04-28 | MOC 389
F13-HU-407 | 2000-F13-PID-PR-10002 | CYCLONE FEED PUMP SUCTION VALVE HYDRAULIC POWER UNIT | DOL | [5 empty] | 14.1 | X | X | XV13082_OP or XV13082_CL | XV13082 Opened for 5 seconds OR | [10 empty] | see Misc tab for XV13082_OP and XV13082_CL (valve open / close logic) | 1 | 2025-07-02 | CR-021
[13 empty] | XV13082 Closed for 5 seconds | 1 | F13-HU-407 Comms Failure | 0 |  |  |  | X |  |  |  |  | B
[14 empty] | 2 | F13-HU-407 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-HU-407 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-HU-407 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-HU-407 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | B
[14 empty] | 6 | F13-HU-407 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-HU-407 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | PI13535 ≥ A_HH | 5 |  |  | X |  |  | X |  | Hydraulic supply pressure | 1 | 2025-07-02 | CR-021
[14 empty] | 9 | TI13536 ≥ A_HH | 5 |  |  | X |  |  | X |  | Hydraulic reservoir temperature | 1 | 2025-07-02 | CR-021
[14 empty] | 10 | LI13537 ≤ A_LL | 5 |  |  | X |  |  | X |  | Hydraulic reservoir level | 1 | 2025-07-02 | CR-021
[14 empty] | 11 | ZSH13542 Inactive | 5 |  |  | X |  |  | X |  | Suction valve limit switch | 1 | 2025-07-02 | CR-021
F13-SC-401 | 2000-F13-PID-PR-10002 | SAG MILL DISCHARGE SCREEN | VSD | [5 empty] | 97.5 | X | X | F13-SEQ-0021A | F13-SEQ-0022A | [11 empty] | 1 | 2025-04-30 | https://pastech-2955.atlassian.net/browse/KAN-1683
[14 empty] | 1 | F13-SC-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-SC-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-SC-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-SC-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-SC-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-SC-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-SC-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LSHH13073 Inactive | 3 |  |  | X |  |  | X |  | SAG Mill Discharge Screen Oversize Chute blocked | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 9 | XS24678A Inactive | 0 |  |  |  | X |  |  |  | Fire alarm detected through FIP24678 Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-06 | Design change, fire water updates
F13-PS-404 | 2000-F13-PID-PR-10003 | MILL DISCHARGE END SUMP PUMP | DOL SP | [5 empty] | 54 160 | X | X | LI13130.PV ≥ P_Hi | LI13130.PV ≤ P_Lo | [11 empty] | A
[14 empty] | 1 | F13-PS-404 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PS-404 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PS-404 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PS-404 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PS-404 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PS-404 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PS-404 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-PP-401 Not Running | 0 |  |  | X |  |  | X |  | Cyclone Feed Pump stopped | 0
F13-PS-405 | 2000-F13-PID-PR-10003 | MILL FEED END SUMP PUMP | DOL SP | [5 empty] | 93.7 | X | X | LSH13131 Active | LSH13131 Inactive for 600 180 seconds | [11 empty] | 0
[14 empty] | 1 | F13-PS-405 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PS-405 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PS-405 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PS-405 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PS-405 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PS-405 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PS-405 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-PP-401 Not Running | 0 |  |  | X |  |  | X |  | Cyclone Feed Pump | A
F13-HU-413 | 2000-F13-PID-PR-10003 | PORTABLE MILLS INCHING DRIVE HYDRAULIC POWER UNIT | N/A | [5 empty] | 556.4822 |  | X | Inching control via F13HU413-CP is via F13HU413-CP PLC | Inching control via F13HU413-CP is via F13HU413-CP PLC | [11 empty] | 1 | 2025-05-12 | https://pastech-2955.atlassian.net/browse/KAN-1836
[14 empty] | 0 | XI13743_SEL = Inactive | 0 |  |  |  | X |  |  |  | Inactive selected on XI13743_SEL | 1 | 2025-05-12 | https://pastech-2955.atlassian.net/browse/KAN-1836 |  |  |  |  | Desktop Review
[15 empty] | PORTABLE HPU INCHING MODE ACTIVE FOR SAG MILL XI13743_SEL = 'SAG Mill' AND Any Interlock (1 to 28) | [8 empty] | Interlocks #1 to 28 are for Portable HPU Inching of the SAG Mill, F13-MS-401. Interlocks and start permissves are to disable XI13743 when unhealthy, which is provided as a permission signal to the Portable HPU Inching PLC to stop and/or prevent inching of the mill. These interlocks are only applicable when XI13743_SEL is set to 'SAG Mill'. | 2 | 2025-05-12 | https://pastech-2955.atlassian.net/browse/KAN-1836 |  |  |  |  | Desktop Review - all applicable interlocks have been greened previously.
[14 empty] | 1 | F13-PO-421 & 422 Not Running | 0 |  |  |  | X |  |  |  | Logic: • F13-PO-421 AND F13-PO-422 = Not Running | B
[14 empty] | 2 | F13-PO-427 & 428 Not Running | 0 |  |  |  | X |  |  |  | Logic: • F13-PO-427 AND F13-PO-428 = Not Running | B
[14 empty] | 3 | F13-PO-434 & 435 Not Running | 0 |  |  |  | X |  |  |  | Logic: • F13-PO-434 AND F13-PO-435 = Not Running | B
[14 empty] | 4 | F13-PO-429, 430 & 431 Not Running | 0 |  |  |  | X |  |  |  | Logic: • Less than two HP Lube Pumps running (F13-PO-429, F13-PO-430, F13-PO-431) | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1884
[14 empty] | 5 | F13-PO-427/428 Min Runtime Inactive | 0 |  |  |  | X |  |  |  | Logic: • F13MS401_T1 Not Elapsed At least one (1) F13-PO-427 OR F13-PO-428 running for ≥ F13MS401_T1 | A
[14 empty] | 6 | F13-PO-434/435 Min Runtime Inactive | 0 |  |  |  | X |  |  |  | Logic: • F13MS401_T2 Not Elapsed At least one (1) F13-PO-434 OR F13-PO-435 running for ≥ F13MS401_T2 | A
[14 empty] | 7 | F13-PO-429/430/431 Min Runtime | 0 |  |  |  | X |  |  |  | Logic: • F13MS401_T3 Not Elapsed Two (2) F13-PO-429, F13-PO-430, F13-PO-431 running for ≥ F13MS401_T3 | A
[14 empty] | 8 | Main Motor Lube Flow LL | 1 |  |  |  | X |  |  |  | Logic: • [FI13576 ≤ A_LL OR • FI13577 ≤ A_LL OR • FI13578 ≤ A_LL OR • FI13579 ≤ A_LL] Main Motor 1 Lubrication DE Flow Main Motor 1 Lubrication NDE Flow Main Motor 2 Lubrication DE Flow Main Motor 2 Lubrication NDE Flow | 2
[14 empty] | 9 | Main Motor Lube Pressure HH | 1 |  |  |  | X |  |  |  | Logic: • [PI13572 ≥ A_HH OR • PI13573 ≥ A_HH OR • PI13574 ≥ A_HH OR • PI13575 ≥ A_HH OR • PSL13572 Inactive OR • PSL13573 Inactive OR • PSL13574 Inactive OR • PSL13575 Inactive] Main Motor 1 Lubrication DE Pressure Main Motor 1 Lubrication NDE Pressure Main Motor 2 Lubrication DE Pressure Main Motor 2 Lubrication NDE Pressure | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386 |  |  |  |  | MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
[14 empty] | 10 | Main Bearings Lube Flow LL | 1 |  |  |  | X |  |  |  | Logic: • [FI13640 ≤ A_LL • FI13641 ≤ A_LL] SAG Mill Main Bearings Lubrication System Flow Divider Feed Flow SAG Mill Main Bearings Lubrication System Thrust Rail Lubrication Flow | 2
[14 empty] | 11 | Main Bearing Lube Pressure LL | 1 |  |  |  | X |  |  |  | Logic: • [PI13644 ≤ A_LL OR • PI13645 ≤ A_LL OR • PI13646 ≤ A_LL OR • PI13647 ≤ A_LL OR • PI13648 ≤ A_LL OR • PI13649 ≤ A_LL OR • PI13650 ≤ A_LL OR • PI13651 ≤ A_LL] SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure | 2
[14 empty] | 12 | Main Bearing Temperatures HH | 1 |  |  |  | X |  |  |  | Logic: • [TI13712A ≥ A_HH OR • TI13712B ≥ A_HH OR • TI13712C ≥ A_HH OR • TI13714A ≥ A_HH OR • TI13714B ≥ A_HH OR • TI13714C ≥ A_HH OR • TI13716A ≥ A_HH OR • TI13716B ≥ A_HH OR • TI13716C ≥ A_HH OR • TI13717A ≥ A_HH OR • TI13717B ≥ A_HH OR • TI13717C ≥ A_HH OR • TI13713A ≥ A_HH OR • TI13713B ≥ A_HH OR • TI13715A ≥ A_HH OR • TI13715B ≥ A_HH] SAG Mill Feed End Trunnion Bearing (Right Side) Outboard Temperature SAG Mill Feed End Trunnion Bearing (Right Side) Centre Temperature SAG Mill Feed End Trunnion Bearing (Right Side) Inboard Temperature SAG Mill Feed End Trunnion Bearing (Left Side) Outboard Temperature SAG Mill Feed End Trunnion Bearing (Left Side) Centre Temperature SAG Mill Feed End Trunnion Bearing (Left Side) Inboard Temperature SAG Mill Discharge End Trunnion Bearing (Right Side) Outboard Temperature SAG Mill Discharge End Trunnion Bearing (Right Side) Centre Temperature SAG Mill Discharge End Trunnion Bearing (Right Side) Inboard Temperature SAG Mill Discharge End Trunnion Bearing (Left Side) Outboard Temperature SAG Mill Discharge End Trunnion Bearing (Left Side) Centre Temperature SAG Mill Discharge End Trunnion Bearing (Left Side) Inboard Temperature SAG Mill Discharge End Thrust Bearing (Right Side) Outboard Temperature SAG Mill Discharge End Thrust Bearing (Right Side) Inboard Temperature SAG Mill Discharge End Thrust Bearing (Left Side) Outboard Temperature SAG Mill Discharge End Thrust Bearing (Left Side) Inboard Temperature | 2
[14 empty] | 13 | Pinion Bearing Lube Flow LL | 1 |  |  |  | X |  |  |  | Logic: • [FI13657 ≤ A_LL OR • FI13658 ≤ A_LL OR • FI13659 ≤ A_LL OR • FI13660 ≤ A_LL] SAG Mill Fixed Pinion Bearing (Right) flow SAG Mill Fixed Pinion Bearing (Left) flow SAG Mill Floating Pinion Bearing (Right) flow SAG Mill Floating Pinion Bearing (Left) flow | 2
[14 empty] | 14 | Pinion Bearing Temperatures HH | 1 |  |  |  | X |  |  |  | Logic: • [TI13704 ≥ A_HH OR • TI13705 ≥ A_HH OR • TI13706 ≥ A_HH OR • TI13707 ≥ A_HH] SAG Mill Discharge End (Fixed) Pinion Right Side Bearing Temperature SAG Mill Discharge End (Fixed) Pinion Left Side Bearing Temperature SAG Mill Feed End (Floating) Pinion Right Side Bearing Temperature SAG Mill Feed End (Floating) Pinion Left Side Bearing Temperature | 2
[14 empty] | 15 | TIC13629 ≥ A_HH Active | 1 |  |  |  | X |  |  |  | Logic: •TIC13629 ≥ A_HH SAG Mill Main Bearings Lubrication System Conditioned Circuit Temperature | 2
[14 empty] | 16 | Gear Spray System Fault | 0 |  |  |  | X |  |  |  | Logic: • F13MS401_T8 Elapsed Critical Gear Spray System Permissive for Mill Rotation Alarm | A
[14 empty] | 17 | Seal Grease System Fault | 0 |  |  |  | X |  |  |  | Logic: • F13MS401_T6 Elapsed Critical Seal Grease System Permissive for Mill Rotation Alarm | A
[14 empty] | 18 | SAG Mill Brakes Engaged | 0 |  |  |  | X |  |  |  | Logic: ZSH13545 OR ZSH13547 = Inactive (Brake Engaged) OR SV13561 = Energised OR SV13562 = Deenergised Brakes must be in released position | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386 | [6 empty] | 22/5/26: FC modification for MOC517
[14 empty] | 19 | YY13132 Healthy | 0 |  | X |  |  |  | X |  | Refer to F13MS401_INCH for siren logic. Misc tab. Logic (Healthy): • YY13132 = Healthy OR • XS13759 = Active | 1 | 3/06/2025 6/10/2025 | https://pastech-2955.atlassian.net/browse/KAN-1943 CR-050
[14 empty] | 20 | Cooling Water Flow Healthy | 1 |  | X |  |  |  | X |  | Logic (Healthy): • FI13409, FI13411 AND FIC13125 > A_Lo OR • XS13759 = Active Cooling water flow to VSD and Main Motors must be healthy | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
[14 empty] | 21 | Main Bearings Lube Flow Not Low | 1 |  | X |  |  |  | X |  | Logic (Healthy): • [FI13640 > A_Lo AND • FI13641 > A_Lo] OR • XS13759 = Active SAG Mill Main Bearings Lubrication System Flow Divider Feed Flow SAG Mill Main Bearings Lubrication System Thrust Rail Lubrication Flow | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
[14 empty] | 22 | Main Bearings Lube Pressure Not Low | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [PI13644 > A_Lo AND • PI13645 > A_Lo AND • PI13646 > A_Lo AND • PI13647 > A_Lo AND • PI13648 > A_Lo AND • PI13649 > A_Lo AND • PI13650 > A_Lo AND • PI13651 > A_Lo] OR • XS13759 = Active SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
[14 empty] | 23 | Main Bearing Temperatures Not High | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [TI13712A < A_Hi AND • TI13712B < A_Hi AND • TI13712C < A_Hi AND • TI13714A < A_Hi AND • TI13714B < A_Hi AND • TI13714C < A_Hi AND • TI13716A < A_Hi AND • TI13716B < A_Hi AND • TI13716C < A_Hi AND • TI13717A < A_Hi AND • TI13717B < A_Hi AND • TI13717C < A_Hi AND • TI13713A < A_Hi AND • TI13713B < A_Hi AND • TI13715A < A_Hi AND • TI13715B < A_Hi] OR • XS13759 = Active SAG Mill Feed End Trunnion Bearing (Right Side) Outboard Temperature SAG Mill Feed End Trunnion Bearing (Right Side) Centre Temperature SAG Mill Feed End Trunnion Bearing (Right Side) Inboard Temperature SAG Mill Feed End Trunnion Bearing (Left Side) Outboard Temperature SAG Mill Feed End Trunnion Bearing (Left Side) Centre Temperature SAG Mill Feed End Trunnion Bearing (Left Side) Inboard Temperature SAG Mill Discharge End Trunnion Bearing (Right Side) Outboard Temperature SAG Mill Discharge End Trunnion Bearing (Right Side) Centre Temperature SAG Mill Discharge End Trunnion Bearing (Right Side) Inboard Temperature SAG Mill Discharge End Trunnion Bearing (Left Side) Outboard Temperature SAG Mill Discharge End Trunnion Bearing (Left Side) Centre Temperature SAG Mill Discharge End Trunnion Bearing (Left Side) Inboard Temperature SAG Mill Discharge End Thrust Bearing (Right Side) Outboard Temperature SAG Mill Discharge End Thrust Bearing (Right Side) Inboard Temperature SAG Mill Discharge End Thrust Bearing (Left Side) Outboard Temperature SAG Mill Discharge End Thrust Bearing (Left Side) Inboard Temperature | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
[14 empty] | 24 | Pinion Bearing Lube Flow Not Low | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [FI13657 > A_Lo AND • FI13658 > A_Lo AND • FI13659 > A_Lo AND • FI13660 > A_Lo] OR • XS13759 = Active SAG Mill Fixed Pinion Bearing (Right) flow SAG Mill Fixed Pinion Bearing (Left) flow SAG Mill Floating Pinion Bearing (Right) flow SAG Mill Floating Pinion Bearing (Left) flow | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
[14 empty] | 25 | Pinion Bearing Temperatures Not High | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [TI13704 < A_Hi AND • TI13705 < A_Hi AND • TI13706 < A_Hi AND • TI13707 < A_Hi] OR • XS13759 = Active SAG Mill Discharge End (Fixed) Pinion Right Side Bearing Temperature SAG Mill Discharge End (Fixed) Pinion Left Side Bearing Temperature SAG Mill Feed End (Floating) Pinion Right Side Bearing Temperature SAG Mill Feed End (Floating) Pinion Left Side Bearing Temperature | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
[14 empty] | 26 | TIC13629 < A_Hi | 5 |  | X |  |  |  | X |  | Logic (Healthy): • TIC13629 < A_Hi OR • XS13759 = Active SAG Mill Main Bearings Lubrication System Conditioned Circuit Temperature | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
[14 empty] | 27 | Gear Spray System Alarm Inactive | 0 |  | X |  |  |  | X |  | Logic (Healthy): • F13MS401_T8 Timer stopped OR paused OR • XS13759 = Active Gear Spray System Fault Alarms must be inactive | 2 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690 |  |  |  |  | SAG & Ball Mill Grease Fault Timer Start Permissives
[14 empty] | 28 | Seal Grease System Alarm Inactive | 0 |  | X |  |  |  | X |  | Logic (Healthy): • F13MS401_T6 Timer stopped OR paused OR • XS13759 = Active Seal Grease System Fault Alarms must be inactive | 2 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690 |  |  |  |  | SAG & Ball Mill Grease Fault Timer Start Permissives
[15 empty] | PORTABLE HPU INCHING MODE ACTIVE FOR BALL MILL XI13743_SEL = 'Ball Mill' AND Any Interlock (29 to 56) | [8 empty] | Interlocks #29 to 56 are for Portable HPU Inching of the Ball Mill, F13-MB-401. Interlocks and start permissves are to disable XI13743 when unhealthy, which is provided as a permission signal to the Portable HPU Inching PLC to stop and/or prevent inching of the mill. These interlocks are only applicable when XI13743_SEL is set to 'Ball Mill'. | 2 | 2025-05-12 | https://pastech-2955.atlassian.net/browse/KAN-1836 |  |  |  |  | Desktop Review - all applicable interlocks have been greened previously.
[14 empty] | 29 | F13-PO-521 & 522 Not Running | 0 |  |  |  | X |  |  |  | Logic: • F13-PO-521 AND F13-PO-522 = Not Running | B
[14 empty] | 30 | F13-PO-527 & 528 Not Running | 0 |  |  |  | X |  |  |  | Logic: • F13-PO-527 AND F13-PO-528 = Not Running | B
[14 empty] | 31 | F13-PO-534 & 535 Not Running | 0 |  |  |  | X |  |  |  | Logic: • F13-PO-534 AND F13-PO-535 = Not Running | B
[14 empty] | 32 | F13-PO-529, 530 & 531 Not Running | 0 |  |  |  | X |  |  |  | Logic: • Less than two HP Lube Pumps running (F13-PO-529, F13-PO-530, F13-PO-531) | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1884
[14 empty] | 33 | F13-PO-527/528 Min Runtime Inactive | 0 |  |  |  | X |  |  |  | Logic: • F13MB401_T1 Not Elapsed At least one (1) F13-PO-527 OR F13-PO-528 running for ≥ F13MB401_T1 | A
[14 empty] | 34 | F13-PO-534/535 Min Runtime Inactive | 0 |  |  |  | X |  |  |  | Logic: • F13MB401_T2 Not Elapsed At least one (1) F13-PO-534 OR F13-PO-535 running for ≥ F13MB401_T2 | A
[14 empty] | 35 | F13-PO-529/530/531 Min Runtime | 0 |  |  |  | X |  |  |  | Logic: • F13MB401_T3 Not Elapsed Two (2) F13-PO-529, F13-PO-530, F13-PO-531 running for ≥ F13MB401_T3 | A
[14 empty] | 36 | Main Motor Lube Flow LL | 1 |  |  |  | X |  |  |  | Logic: • [FI13827 ≤ A_LL OR • FI13828 ≤ A_LL OR • FI13829 ≤ A_LL OR • FI13830 ≤ A_LL] Main Motor 1 Lubrication DE Flow Main Motor 1 Lubrication NDE Flow Main Motor 2 Lubrication DE Flow Main Motor 2 Lubrication NDE Flow | 2
[14 empty] | 37 | Main Motor Lube Pressure HH | 1 |  |  |  | X |  |  |  | Logic: • [PI13823 ≥ A_HH OR • PI13824 ≥ A_HH OR • PI13825 ≥ A_HH OR • PI13826 ≥ A_HH OR • PSL13823 Inactive OR • PSL13824 Inactive OR • PSL13825 Inactive OR • PSL13826 Inactive] Main Motor 1 Lubrication DE Pressure Main Motor 1 Lubrication NDE Pressure Main Motor 2 Lubrication DE Pressure Main Motor 2 Lubrication NDE Pressure | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386 |  |  |  |  | MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
[14 empty] | 38 | Main Bearings Lube Flow LL | 1 |  |  |  | X |  |  |  | Logic: • [FI13891 ≤ A_LL • FI13892 ≤ A_LL] Ball Mill Main Bearings Lubrication System Flow Divider Feed Flow Ball Mill Main Bearings Lubrication System Thrust Rail Lubrication Flow | 2
[14 empty] | 39 | Main Bearing Lube Pressure LL | 1 |  |  |  | X |  |  |  | Logic: • [PI13895 ≤ A_LL OR • PI13896 ≤ A_LL OR • PI13897 ≤ A_LL OR • PI13898 ≤ A_LL OR • PI13899 ≤ A_LL OR • PI13900 ≤ A_LL OR • PI13901 ≤ A_LL OR • PI13902 ≤ A_LL] Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure | 2
[14 empty] | 40 | Main Bearing Temperatures HH | 1 |  |  |  | X |  |  |  | Logic: • [TI13964A ≥ A_HH OR • TI13964B ≥ A_HH OR • TI13964C ≥ A_HH OR • TI13966A ≥ A_HH OR • TI13966B ≥ A_HH OR • TI13966C ≥ A_HH OR • TI13958A ≥ A_HH OR • TI13958B ≥ A_HH OR • TI13958C ≥ A_HH OR • TI13960A ≥ A_HH OR • TI13960B ≥ A_HH OR • TI13960C ≥ A_HH OR • TI13962A ≥ A_HH OR • TI13962B ≥ A_HH OR • TI13967A ≥ A_HH OR • TI13967B ≥ A_HH] Ball Mill Feed End Trunnion Bearing (Right Side) Outboard Temperature Ball Mill Feed End Trunnion Bearing (Right Side) Centre Temperature Ball Mill Feed End Trunnion Bearing (Right Side) Inboard Temperature Ball Mill Feed End Trunnion Bearing (Left Side) Outboard Temperature Ball Mill Feed End Trunnion Bearing (Left Side) Centre Temperature Ball Mill Feed End Trunnion Bearing (Left Side) Inboard Temperature Ball Mill Discharge End Trunnion Bearing (Right Side) Outboard Temperature Ball Mill Discharge End Trunnion Bearing (Right Side) Centre Temperature Ball Mill Discharge End Trunnion Bearing (Right Side) Inboard Temperature Ball Mill Discharge End Trunnion Bearing (Left Side) Outboard Temperature Ball Mill Discharge End Trunnion Bearing (Left Side) Centre Temperature Ball Mill Discharge End Trunnion Bearing (Left Side) Inboard Temperature Ball Mill Discharge End Thrust Bearing (Right Side) Outboard Temperature Ball Mill Discharge End Thrust Bearing (Right Side) Inboard Temperature Ball Mill Discharge End Thrust Bearing (Left Side) Outboard Temperature Ball Mill Discharge End Thrust Bearing (Left Side) Inboard Temperature | 2
[14 empty] | 41 | Pinion Bearing Lube Flow LL | 1 |  |  |  | X |  |  |  | Logic: • [FI13908 ≤ A_LL OR • FI13909 ≤ A_LL OR • FI13910 ≤ A_LL OR • FI13911 ≤ A_LL] Ball Mill Fixed Pinion Bearing (Right) flow Ball Mill Fixed Pinion Bearing (Left) flow Ball Mill Floating Pinion Bearing (Right) flow Ball Mill Floating Pinion Bearing (Left) flow | 2
[14 empty] | 42 | Pinion Bearing Temperatures HH | 1 |  |  |  | X |  |  |  | Logic: • [TI13957 ≥ A_HH OR • TI13956 ≥ A_HH OR • TI13955 ≥ A_HH OR • TI13954 ≥ A_HH] Ball Mill Discharge End (Fixed) Pinion Right Side Bearing Temperature Ball Mill Discharge End (Fixed) Pinion Left Side Bearing Temperature Ball Mill Feed End (Floating) Pinion Right Side Bearing Temperature Ball Mill Feed End (Floating) Pinion Left Side Bearing Temperature | 2
[14 empty] | 43 | TIC13880 ≥ A_HH Active | 1 |  |  |  | X |  |  |  | Logic: • TIC13880 ≥ A_HH Ball Mill Main Bearings Lubrication System Conditioned Circuit Temperature | 2
[14 empty] | 44 | Gear Spray System Fault | 1 |  |  |  | X |  |  |  | Logic: • F13MB401_T8 Elapsed Critical Gear Spray System Permissive for Mill Rotation | 2
[14 empty] | 45 | Seal Grease System Fault | 1 |  |  |  | X |  |  |  | Logic: • F13MB401_T6 Elapsed Critical Seal Grease System Permissive for Mill Rotation | 2
[14 empty] | 46 | Ball Mill Brakes Engaged | 0 |  |  |  | X |  |  |  | Logic: ZSH13795 OR ZSH13797 = Inactive (Brake Engaged) OR SV13813 = Deenergised Brakes must be in released position | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 47 | YY13145 Healthy | 0 |  | X |  |  |  | X |  | Refer to F13MB401_INCH for siren logic. Misc tab. Logic (Healthy): • YY13145 = Healthy OR • XS13759 = Active | 1 | 3/06/2025 6/10/2025 | https://pastech-2955.atlassian.net/browse/KAN-1943 CR-050
[14 empty] | 48 | Cooling Water Flow Healthy | 5 |  | X |  |  |  | X |  | Logic (Healthy): • FI13413, FI13415 AND FIC13126 > A_Lo OR • XS13759 = Active Cooling water flow to VSD and Main Motors must be healthy | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
[14 empty] | 49 | Main Bearings Lube Flow Not Low | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [FI13891 > A_Lo AND • FI13892 > A_Lo] OR • XS13759 = Active Ball Mill Main Bearings Lubrication System Flow Divider Feed Flow Ball Mill Main Bearings Lubrication System Thrust Rail Lubrication Flow | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
[14 empty] | 50 | Main Bearings Lube Pressure Not Low | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [PI13895 > A_Lo AND • PI13896 > A_Lo AND • PI13897 > A_Lo AND • PI13898 > A_Lo AND • PI13899 > A_Lo AND • PI13900 > A_Lo AND • PI13901 > A_Lo AND • PI13902 > A_Lo] OR • XS13759 = Active Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690 |  |  |  |  | tested only one instro, green the text until all tested
[14 empty] | 51 | Main Bearing Temperatures Not High | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [TI13964A < A_Hi AND • TI13964B < A_Hi AND • TI13964C < A_Hi AND • TI13966A < A_Hi AND • TI13966B < A_Hi AND • TI13966C < A_Hi AND • TI13958A < A_Hi AND • TI13958B < A_Hi AND • TI13958C < A_Hi AND • TI13960A < A_Hi AND • TI13960B < A_Hi AND • TI13960C < A_Hi AND • TI13962A < A_Hi AND • TI13962B < A_Hi AND • TI13967A < A_Hi AND • TI13967B < A_Hi] OR • XS13759 = Active Ball Mill Feed End Trunnion Bearing (Right Side) Outboard Temperature Ball Mill Feed End Trunnion Bearing (Right Side) Centre Temperature Ball Mill Feed End Trunnion Bearing (Right Side) Inboard Temperature Ball Mill Feed End Trunnion Bearing (Left Side) Outboard Temperature Ball Mill Feed End Trunnion Bearing (Left Side) Centre Temperature Ball Mill Feed End Trunnion Bearing (Left Side) Inboard Temperature Ball Mill Discharge End Trunnion Bearing (Right Side) Outboard Temperature Ball Mill Discharge End Trunnion Bearing (Right Side) Centre Temperature Ball Mill Discharge End Trunnion Bearing (Right Side) Inboard Temperature Ball Mill Discharge End Trunnion Bearing (Left Side) Outboard Temperature Ball Mill Discharge End Trunnion Bearing (Left Side) Centre Temperature Ball Mill Discharge End Trunnion Bearing (Left Side) Inboard Temperature Ball Mill Discharge End Thrust Bearing (Right Side) Outboard Temperature Ball Mill Discharge End Thrust Bearing (Right Side) Inboard Temperature Ball Mill Discharge End Thrust Bearing (Left Side) Outboard Temperature Ball Mill Discharge End Thrust Bearing (Left Side) Inboard Temperature | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
[14 empty] | 52 | Pinion Bearing Lube Flow Not Low | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [FI13908 > A_Lo AND • FI13909 > A_Lo AND • FI13910 > A_Lo AND • FI13911 > A_Lo] OR • XS13759 = Active Ball Mill Fixed Pinion Bearing (Right) flow Ball Mill Fixed Pinion Bearing (Left) flow Ball Mill Floating Pinion Bearing (Right) flow Ball Mill Floating Pinion Bearing (Left) flow | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
[14 empty] | 53 | Pinion Bearing Temperatures Not High | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [TI13957 < A_Hi AND • TI13956 < A_Hi AND • TI13955 < A_Hi AND • TI13954 < A_Hi] OR • XS13759 = Active Ball Mill Discharge End (Fixed) Pinion Right Side Bearing Temperature Ball Mill Discharge End (Fixed) Pinion Left Side Bearing Temperature Ball Mill Feed End (Floating) Pinion Right Side Bearing Temperature Ball Mill Feed End (Floating) Pinion Left Side Bearing Temperature | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
[14 empty] | 54 | TIC13880 < A_Hi | 5 |  | X |  |  |  | X |  | Logic (Healthy): • TIC13880 < A_Hi OR • XS13759 = Active Ball Mill Main Bearings Lubrication System Conditioned Circuit Temperature | 1 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690
[14 empty] | 55 | Gear Spray System Alarm Inactive | 0 |  | X |  |  |  | X |  | Logic (Healthy): • F13MB401_T8 Timer stopped OR paused OR • XS13759 = Active Gear Spray System Fault Alarms must be inactive | 2 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690 |  |  |  |  | SAG & Ball Mill Grease Fault Timer Start Permissives
[14 empty] | 56 | Seal Grease System Alarm Inactive | 0 |  | X |  |  |  | X |  | Logic (Healthy): • F13MB401_T6 Timer stopped OR paused OR • XS13759 = Active Seal Grease System Fault Alarms must be inactive | 2 | 2025-06-03 | https://pastech-2955.atlassian.net/browse/KAN-1690 |  |  |  |  | SAG & Ball Mill Grease Fault Timer Start Permissives
F13-MS-401A | 2000-F13-PID-PR-10010 | SAG MILL MOTOR 1 | VSD | -5 | 100 | % | 79.1 | 100 | 1707 | X | X | F13-SEQ-0021A/B | F13-SEQ-0022A/B/C | [10 empty] | Engineer-level access required to adjust Mill Speed SV. Normal operating range = 79.1% to 100% Forward inching nominal SV = 5% Reverse inching nominal SV = -5% 100% VSD Speed = 150 Motor RPM = 9.86 Mill RPM = 75.87% of Critical Speed (Cs). Refer to 2000-ME001.2-N01-50001. Normal operating range calculated from Duty Mill Speed Range (60-83% Cs). Refer to 2000-F00-DCR-PR-10001 Inching control via F13MS401-CP is directly wired to VSD Interlocks and permissives apply for both F13-MS-401A and F13-MS-401B | B
F13-MS-401B | 2000-F13-PID-PR-10010 | SAG MILL MOTOR 2 | VSD | -5 | 100 | % | 79.1 | 100 | 1707 | X | X | F13-SEQ-0021A/B | F13-SEQ-0022A/B/C | 1 | F13-MS-401A/B Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-MS-401A/B Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-MS-401A/B Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-MS-401A/B E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-MS-401A/B MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-MS-401A/B Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0 | [6 empty] | Desktop Review - Inbuilt drive template feature.
[14 empty] | 7 | F13-MS-401A/B Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[15 empty] | NORMAL MODE ACTIVE Abnormal Shutdown, Mill Delayed Stop Set MS_MILL_EN = 0 if any of these conditions are TRUE | [8 empty] | Interlocks # 8 to 17 initiate an 'Abnormal Shutdown, Mill Delayed Stop' An 'Abnormal Shutdown, Mill Delayed Stop' interlock will activate MS_NCR_ILK to trip F13-CV-403 and initiate a Sequence Stop (F13-SEQ-0022A) to stop F13-MS-401A/B. Refer to Misc tab. The condition Delay On timers here are longer than MS_NCR_ILK, such that if the conditions here become true before F13-SEQ-0022A is able to remove the MS_RUN command, the PCS will set MS_MILL_EN = 0 to force the SAG Mill to coast to stop (i.e. an instantaneous stop). These conditions can only become active if MS_OP_MODE = NORMAL (NORMAL MODE) | B
[14 empty] | 8 | F13-PP-401 Not Running | 150 |  |  |  | X |  |  | X | Cyclone Feed Pump | A
[14 empty] | 9 | F13-SC-401 Not Running | 150 |  |  |  | X |  |  | X | SAG Mill Discharge Screen | A
[14 empty] | 10 | Main Bearing Temperature Fault | 150 |  |  |  | X |  |  | X | Logic: • MS_OP_MODE = NORMAL AND • [TI13712A ≥ A_HH OR • TI13712B ≥ A_HH OR • TI13712C ≥ A_HH OR • TI13716A ≥ A_HH OR • TI13716B ≥ A_HH OR • TI13716C ≥ A_HH OR • TI13713A ≥ A_HH OR • TI13713B ≥ A_HH OR • TI13714A ≥ A_HH OR • TI13714B ≥ A_HH OR • TI13714C ≥ A_HH OR • TI13717A ≥ A_HH OR • TI13717B ≥ A_HH OR • TI13717C ≥ A_HH OR • TI13715A ≥ A_HH OR • TI13715B ≥ A_HH] (Source: 2000-ME001.2-M02-50001, "Critical Main Bearing Temperature Permissive for Mill Rotation Alarm") | B
[14 empty] | 11 | Pinion Bearing Lube Fault | 150 |  |  |  | X |  |  | X | Logic: • MS_OP_MODE = NORMAL AND • [F13-PO-434 Not Running AND F13-PO-435 Not Running OR • FI13657 ≤ A_LL OR • FI13658 ≤ A_LL OR • FI13659 ≤ A_LL OR • FI13660 ≤ A_LL] (Source: 2000-ME001.2-M02-50001, "Critical Pinion Bearing Lube System Permissive for Mill Rotation Alarm") | A
[14 empty] | 12 | Pinion Bearing Temperature Fault | 150 |  |  |  | X |  |  | X | Logic: • MS_OP_MODE = NORMAL AND • [TI13704 ≥ A_HH OR • TI13705 ≥ A_HH OR • TI13706 ≥ A_HH OR • TI13707 ≥ A_HH] (Source: 2000-ME001.2-M02-50001, "Critical Pinion Bearing Temperature Permissive for Mill Rotation Alarm") | A
[14 empty] | 13 | Pinion Bearing Flank Fault | 150 |  |  |  | X |  |  | X | Logic: • MS_OP_MODE = NORMAL AND • [TI13511 ≥ A_HH OR • TI13512 ≥ A_HH OR • TI13513 ≥ A_HH OR • TI13514 ≥ A_HH OR • TI13515 ≥ A_HH OR • TI13516 ≥ A_HH OR • TI13519 ≥ A_HH OR • TI13520 ≥ A_HH OR • TDI13511 ≥ A_HH OR • TDI13515 ≥ A_HH] (Source: 2000-ME001.2-M02-50001, "Critical Pinion Flank Temperature Permissive for Mill Rotation Alarm") | A
[14 empty] | 14 | SAG Mill Main Motor Lube Fault | 150 |  |  |  | X |  |  | X | Logic: • [MS_OP_MODE = NORMAL AND • [MS_STARTING = STARTING OR [SI13137A.PV ≤ 90RPM AND MS_RUNNING = RUNNING]]] AND • [FI13576 ≤ A_LL OR • FI13577 ≤ A_LL OR • FI13578 ≤ A_LL OR • FI13579 ≤ A_LL OR • PI13572 ≥ A_HH OR • PI13573 ≥ A_HH OR • PI13574 ≥ A_HH OR • PI13575 ≥ A_HH OR • PSL13572 Inactive OR • PSL13573 Inactive OR • PSL13574 Inactive OR • PSL13575 Inactive] OR • MS_OP_MODE = NORMAL AND • [VI13517 ≥ A_HH OR • VI13518 ≥ A_HH OR • VI13539 ≥ A_HH OR • VI13540 ≥ A_HH] (Source: 2000-ME001.2-M02-50001, "Critical SAG Mill Main Motor Lubrication Unit and Motor Alarm") | 2 | 6/03/2025 2/05/2025 27/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1790?linkSource=email https://pastech-2955.atlassian.net/browse/KAN-1934
[14 empty] | 15 | Gear Spray System Fault | 150 |  |  |  | X |  |  | X | Logic: • MS_OP_MODE = NORMAL AND • F13MS401_T8 Elapsed (See Misc. tab) (Source: 2000-ME001.2-M02-50001, "Critical Gear Spray System Permissive for Mill Rotation Alarm") | B
[14 empty] | 16 | Seal Grease System Fault | 150 |  |  |  | X |  |  | X | Logic: • MS_OP_MODE = NORMAL AND • F13MS401_T6 Elapsed (See Misc. tab) (Source: 2000-ME001.2-M02-50001, "Critical Seal Grease System Permissive for Mill Rotation Alarm") | B
[15 empty] | NORMAL MODE ACTIVE Abnormal Shutdown, Mill Instantaneous Stop Set MS_MILL_EN = 0 if any of these conditions are TRUE | [8 empty] | Interlocks #18 to 19 initiate an 'Abnormal Shutdown, Mill Instantaneous Stop' An Abnormal Shutdown, Mill Instantaneous Stop interlock will deactivate MS_MILL_EN to coast stop the mill and simultaneously activate MS_CR_ILK to initiate a Critical Stop Sequence (F13-SEQ-0022C) to engage the F13-MS-401A/B brakes (MS_2S_EN). Refer to Misc tab These conditions can only become active if MS_OP_MODE = NORMAL (NORMAL MODE) | A
[14 empty] | 17 | Main Bearing Lube System Fault | 1 |  |  |  | X |  |  | X | Logic: • MS_OP_MODE = NORMAL AND • [Less than two HP Lube Pumps running ( F13-PO-429, F13-PO-430, F13-PO-431) OR • FI13640 ≤ A_LL OR • FI13641 ≤ A_LL OR • PI13644 ≤ A_LL OR • PI13645 ≤ A_LL OR • PI13646 ≤ A_LL OR • PI13647 ≤ A_LL OR • PI13648 ≤ A_LL OR • PI13649 ≤ A_LL OR • PI13650 ≤ A_LL OR • PI13651 ≤ A_LL OR • TIC13629 ≥ A_HH] (Source: 2000-ME001.2-M02-50001, "Critical Main Bearing Lube System Permissve for Mill Rotation Alarm") | 2 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1884
[14 empty] | 18 | SAG Mill Brake Normal Fault | 0 |  |  |  | X |  |  | X | Logic: • MS_OP_MODE = NORMAL AND • [ZSH13545 Inactive (Brake Engaged) OR • ZSH13547 Inactive (Brake Engaged) OR • SV13562 Deenergised] OR • LSL13551 INACTIVE (Hydraulic Reservoir Level Low) BH 11/07/2026 MOC-703) OR (Source: 2000-ME001.2-M02-50001, "SAG Mill Brake Normal Mode Permissive for SAG Mill Motors Alarm") Note: Refer to F13-PO-432 interlocks in Drives tab | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[15 empty] | NORMAL MODE ACTIVE Start Permissives Set MS_MILL_EN = 0 if any of these conditions are FALSE | [8 empty] | Interlocks #20 to 31 are Start Permissives Conditions relevant when MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING (SAG Mill in normal mode and not running). All start permissives are true if MS_STARTING = STARTING OR MS_RUNNING = RUNNING OR MS_STOPPING = STOPPING (SAG Mill in starting, running or stopping status). Set MS_MILL_EN = 0 if any of these conditions are false to prevent start up of the SAG Mill | A
[14 empty] | 19 | YY13133A & B Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to F13-MS-401A & B start | 0
[14 empty] | 20 | Pinion Bearing Lube Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • [F13MS401_T1 Elapsed AND • F13MS401_T2 Elapsed AND • FI13657 > A_Lo AND • FI13658 > A_Lo AND • FI13659 > A_Lo AND • FI13660 > A_Lo]] (Source: 2000-ME001.2-M02-50001, "Non-Critical Pinion Bearing Lube System Permissive for Mill Rotation Alarm") | 0
[14 empty] | 21 | Pinion Bearing Temp Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • [TI13704 < A_Hi AND • TI13705 < A_Hi AND • TI13706 < A_Hi AND • TI13707 < A_Hi]] (Source: 2000-ME001.2-M02-50001, "Non-Critical Pinion Bearing Temperature Permissive for Mill Rotation Alarm") | 0
[14 empty] | 22 | Main Bearing Lube Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • [F13MS401_T3 Elapsed AND • LI13619 > A_Lo AND • LI13620 > A_Lo AND • TI13615 < A_Hi AND • TI13615 > A_Lo AND • TI13623 < A_Hi AND • TI13623 > A_Lo AND • FI13640 > A_Lo AND • FI13641 > A_Lo AND • PI13644 > A_Lo AND • PI13645 > A_Lo AND • PI13646 > A_Lo AND • PI13647 > A_Lo AND • PI13648 > A_Lo AND • PI13649 > A_Lo AND • PI13650 > A_Lo AND • PI13651 > A_Lo AND • PDSH13720 Active AND • PDSH13721 Active AND • PDSH13722 Active AND • PDSH13723 Active AND • PDSH13724 Active AND • PDSH13725 Active AND • PDSH13726 Active AND • PDSH13727 Active AND • PDSH13728 Active AND • PDSH13729 Active AND • PDSH13730 Active AND • PDSH13731 Active AND • TIC13629 < A_Hi]] (Source: 2000-ME001.2-M02-50001, "Non-Critical Main Bearing Lube System Permissve for Mill Rotation Alarm") | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386 |  |  |  |  | marking individual interlocks until all is green
[14 empty] | 23 | Main Bearing Temp Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • [TI13712A < A_Hi AND • TI13712B < A_Hi AND • TI13712C < A_Hi AND • TI13716A < A_Hi AND • TI13716B < A_Hi AND • TI13716C < A_Hi AND • TI13713A < A_Hi AND • TI13713B < A_Hi AND • TI13714A < A_Hi AND • TI13714B < A_Hi AND • TI13714C < A_Hi AND • TI13717A < A_Hi AND • TI13717B < A_Hi AND • TI13717C < A_Hi AND • TI13715A < A_Hi AND • TI13715B < A_Hi]] (Source: 2000-ME001.2-M02-50001, "Non-Critical Main Bearing Temperature Permissive for Mill Rotation Alarm") | 0
[14 empty] | 24 | Brake Common Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • LSL13551 Active AND • TSH13552 Active AND • F13-PO-432 INTERLOCKS INACTIVE AND IN AUTO AND • ZSH13546 Active AND • ZSH13548 Active] (Source: 2000-ME001.2-M02-50001, "Brake Common Permissive for SAG Mill Motor Main Drive Alarm") | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 25 | Main Motor Lube Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • [F13MS401_T4 Elapsed AND • LSL13568 Active AND • LSLL13568 Active AND • TSL13569 Inactive AND • TI13570 < A_HH AND • PDSH13565 Inactive AND • PDSHH13565 Active AND • PDSH13566 Inactive AND • PDSHH13566 Active AND • FI13576 > A_Lo AND • FI13577 > A_Lo AND • FI13578 > A_Lo AND • FI13579 > A_Lo AND • PSL13572 Active AND • PSL13573 Active AND • PSL13574 Active AND • PSL13575 Active]] (Source: 2000-ME001.2-M02-50001, "Non-Critical SAG Mill Main Motor Lubrication Unit and Motor Alarm") | 1 | 6/03/2025 05/06/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1984 |  |  |  |  | MOC-384 - Invert signal for PDSH Alarms MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
[14 empty] | 26 | Pinion Bearing Flank Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • [TI13511 < A_Hi AND • TI13512 < A_Hi AND • TI13513 < A_Hi AND • TI13514 < A_Hi AND • TI13515 < A_Hi AND • TI13516 < A_Hi AND • TI13519 < A_Hi AND • TI13520 < A_Hi AND • TDI13511 < A_Hi AND • TDI13515 < A_Hi]] (Source: 2000-ME001.2-M02-50001, "Non-Critical Pinion Flank Temperature Permissive for Mill Rotation Alarm") | 0
[14 empty] | 27 | Gear Spray System Alarm Inactive | 0 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • F13MS401_T8 Timer stopped OR paused (Gear spray grease cycles are healthy. Refer to Misc. tab)] (Source: 2000-ME001.2-M02-50001, "Non-Critical Gear Spray System Permissive for Mill Rotation Alarm") | 2 | [6 empty] | SAG & Ball Mill Grease Fault Timer Start Permissives
[14 empty] | 28 | Seal Grease System Alarm Inactive | 0 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • F13MS401_T6 Timer stopped OR paused (Seal grease cycles are healthy. Refer to Misc. tab)] (Source: 2000-ME001.2-M02-50001, "Non-Critical Seal Grease System Permissive for Mill Rotation Alarm") | 2 | [6 empty] | SAG & Ball Mill Grease Fault Timer Start Permissives
[14 empty] | 29 | Cooling Water Return Flow Not Low | 30 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • [FIC13125 > A_Lo AND • FI13409 > A_Lo AND • FI13411 > A_Lo]] SAG Mill Motor VSD Cooling Water return flowrate SAG Mill Motor 1 Cooling Water return flowrate SAG Mill Motor 2 Cooling Water return flowrate | 0
[14 empty] | 30 | Cooling Water Return Temp Not High | 30 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • [TI13117 < A_Hi AND • TIC13410 < A_Hi AND • TIC13412 < A_Hi]] SAG Mill Motor VSD Cooling Water return temperature SAG Mill Motor 1 Cooling Water return temperature SAG Mill Motor 2 Cooling Water return temperature | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1878
[14 empty] | 31 | Motor 1 Cooling Fans Running | 3 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • Minimum three (3) F13-FN-427, F13-FN-428, F13-FN-429, F13-FN-430 = RUNNING] | 1 | 2025-07-04 | CR-025
[14 empty] | 32 | Motor 2 Cooling Fans Running | 3 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • Minimum three (3) F13-FN-431, F13-FN-432, F13-FN-433, F13-FN-434 = RUNNING] | 1 | 2025-07-04 | CR-025
[14 empty] | 33 | VSD Converter On | 3 |  | X |  |  |  | X |  | Logic (Healthy): • MS_CONV_ON = Active AND • MS_33KV_STS = Closed | 1 | 2025-07-04 | CR-025
[14 empty] | 34 | 13MS401PSR = Active | 0 |  | X |  |  |  | X |  | Power station contacted prior to start. | 2
[15 empty] | INCHING MODE ACTIVE Set MS_MILL_EN = 0 if any of these conditions are TRUE for interlocks or FALSE for start permissives | [8 empty] | Interlocks #32 to 61 are Inching Mode interlocks These interlocks can only become active if MS_OP_MODE = INCHING (INCHING MODE) Set MS_MILL_EN = 0 if any of these conditions are true to prevent start up or to interlock the SAG Mill when inching the SAG Mill with the Main Motors. | A
[14 empty] | 35 | F13-PO-421 & 422 Not Running | 0 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • F13-PO-421 AND F13-PO-422 = Not Running | B
[14 empty] | 36 | F13-PO-427 & 428 Not Running | 0 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • F13-PO-427 AND F13-PO-428 = Not Running | B
[14 empty] | 37 | F13-PO-434 & 435 Not Running | 0 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • F13-PO-434 AND F13-PO-435 = Not Running | B
[14 empty] | 38 | F13-PO-429, 430 & 431 Not Running | 0 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • Less than two HP Lube Pumps running (F13-PO-429, F13-PO-430, F13-PO-431) | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1884
[14 empty] | 39 | F13-PO-427/428 Min Runtime Inactive | 0 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • F13MS401_T1 Not Elapsed At least one (1) F13-PO-427 OR F13-PO-428 running for ≥ F13MS401_T1 | A
[14 empty] | 40 | F13-PO-434/435 Min Runtime Inactive | 0 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • F13MS401_T2 Not Elapsed At least one (1) F13-PO-434 OR F13-PO-435 running for ≥ F13MS401_T2 | A
[14 empty] | 41 | F13-PO-429/430/431 Min Runtime | 0 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • F13MS401_T3 Not Elapsed Two (2) F13-PO-429, F13-PO-430, F13-PO-431 running for ≥ F13MS401_T3 | A
[14 empty] | 42 | Main Motor Lube Flow LL | 1 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • [FI13576 ≤ A_LL OR • FI13577 ≤ A_LL OR • FI13578 ≤ A_LL OR • FI13579 ≤ A_LL] Main Motor 1 Lubrication DE Flow Main Motor 1 Lubrication NDE Flow Main Motor 2 Lubrication DE Flow Main Motor 2 Lubrication NDE Flow | 2
[14 empty] | 43 | Main Motor Lube Pressure HH | 1 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • [PI13572 ≥ A_HH OR • PI13573 ≥ A_HH OR • PI13574 ≥ A_HH OR • PI13575 ≥ A_HH OR • PSL13572 Inactive OR • PSL13573 Inactive OR • PSL13574 Inactive OR • PSL13575 Inactive] Main Motor 1 Lubrication DE Pressure Main Motor 1 Lubrication NDE Pressure Main Motor 2 Lubrication DE Pressure Main Motor 2 Lubrication NDE Pressure | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 44 | Main Bearings Lube Flow LL | 1 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • [FI13640 ≤ A_LL OR • FI13641 ≤ A_LL] SAG Mill Main Bearings Lubrication System Flow Divider Feed Flow SAG Mill Main Bearings Lubrication System Thrust Rail Lubrication Flow | 2
[14 empty] | 45 | Main Bearing Lube Pressure LL | 1 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • [PI13644 ≤ A_LL OR • PI13645 ≤ A_LL OR • PI13646 ≤ A_LL OR • PI13647 ≤ A_LL OR • PI13648 ≤ A_LL OR • PI13649 ≤ A_LL OR • PI13650 ≤ A_LL OR • PI13651 ≤ A_LL] SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure | 2
[14 empty] | 46 | Main Bearing Temperatures HH | 1 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • [TI13712A ≥ A_HH OR • TI13712B ≥ A_HH OR • TI13712C ≥ A_HH OR • TI13714A ≥ A_HH OR • TI13714B ≥ A_HH OR • TI13714C ≥ A_HH OR • TI13716A ≥ A_HH OR • TI13716B ≥ A_HH OR • TI13716C ≥ A_HH OR • TI13717A ≥ A_HH OR • TI13717B ≥ A_HH OR • TI13717C ≥ A_HH OR • TI13713A ≥ A_HH OR • TI13713B ≥ A_HH OR • TI13715A ≥ A_HH OR • TI13715B ≥ A_HH] SAG Mill Feed End Trunnion Bearing (Right Side) Outboard Temperature SAG Mill Feed End Trunnion Bearing (Right Side) Centre Temperature SAG Mill Feed End Trunnion Bearing (Right Side) Inboard Temperature SAG Mill Feed End Trunnion Bearing (Left Side) Outboard Temperature SAG Mill Feed End Trunnion Bearing (Left Side) Centre Temperature SAG Mill Feed End Trunnion Bearing (Left Side) Inboard Temperature SAG Mill Discharge End Trunnion Bearing (Right Side) Outboard Temperature SAG Mill Discharge End Trunnion Bearing (Right Side) Centre Temperature SAG Mill Discharge End Trunnion Bearing (Right Side) Inboard Temperature SAG Mill Discharge End Trunnion Bearing (Left Side) Outboard Temperature SAG Mill Discharge End Trunnion Bearing (Left Side) Centre Temperature SAG Mill Discharge End Trunnion Bearing (Left Side) Inboard Temperature SAG Mill Discharge End Thrust Bearing (Right Side) Outboard Temperature SAG Mill Discharge End Thrust Bearing (Right Side) Inboard Temperature SAG Mill Discharge End Thrust Bearing (Left Side) Outboard Temperature SAG Mill Discharge End Thrust Bearing (Left Side) Inboard Temperature | 2
[14 empty] | 47 | Pinion Bearing Lube Flow LL | 1 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • [FI13657 ≤ A_LL OR • FI13658 ≤ A_LL OR • FI13659 ≤ A_LL OR • FI13660 ≤ A_LL] SAG Mill Fixed Pinion Bearing (Right) flow SAG Mill Fixed Pinion Bearing (Left) flow SAG Mill Floating Pinion Bearing (Right) flow SAG Mill Floating Pinion Bearing (Left) flow | 2
[14 empty] | 48 | Pinion Bearing Temperatures HH | 1 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • [TI13704 ≥ A_HH OR • TI13705 ≥ A_HH OR • TI13706 ≥ A_HH OR • TI13707 ≥ A_HH] SAG Mill Discharge End (Fixed) Pinion Right Side Bearing Temperature SAG Mill Discharge End (Fixed) Pinion Left Side Bearing Temperature SAG Mill Feed End (Floating) Pinion Right Side Bearing Temperature SAG Mill Feed End (Floating) Pinion Left Side Bearing Temperature | 2
[14 empty] | 49 | TIC13629 ≥ A_HH | 1 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • TIC13629 ≥ A_HH SAG Mill Main Bearings Lubrication System Conditioned Circuit Temperature | 2
[14 empty] | 50 | Gear Spray System Fault | 1 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • F13MS401_T8 Elapsed (Source: 2000-ME001.2-M02-50001, "Critical Gear Spray System Permissive for Mill Rotation Alarm") | 2
[14 empty] | 51 | Seal Grease System Fault | 1 |  |  |  | X |  |  |  | Logic: • MS_OP_MODE = INCHING AND • F13MS401_T6 Elapsed (Source: 2000-ME001.2-M02-50001, "Critical Seal Grease System Permissive for Mill Rotation Alarm") | 2
[14 empty] | 52 | SAG Mill Brakes Engaged AND Mill Running | 2 |  |  |  | X |  |  |  | Logic: (ZSH13545 OR ZSH13547 = Inactive (Brake Engaged) OR SV13561 = Deenergised OR SV13562 = Deenergised) AND 13MS401 running Brakes must be in released position | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386 | [6 empty] | 22/5/26: FC modification for MOC517
[14 empty] | 53 | YY13132 Healthy | 0 |  | X |  |  |  | X |  | Refer to F13MS401_INCH for siren logic. Misc tab. | 1 | 13/06/2025 6/10/2025 | https://pastech-2955.atlassian.net/browse/KAN-1943?linkSource=email CR-050
[14 empty] | 54 | Motor 1 Cooling Fans Running | 3 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = INCHING AND MS_RUNNING = NOT RUNNING AND • Minimum three (3) F13-FN-427, F13-FN-428, F13-FN-429, F13-FN-430 = RUNNING] | 0
[14 empty] | 55 | Motor 2 Cooling Fans Running | 3 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = INCHING AND MS_RUNNING = NOT RUNNING AND • Minimum three (3) F13-FN-431, F13-FN-432, F13-FN-433, F13-FN-434 = RUNNING] | 0
[14 empty] | 56 | Cooling Water Flow Healthy | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = INCHING AND MS_RUNNING = NOT RUNNING AND • FI13409, FI13411 AND FIC13125 > A_Lo] Cooling water flow to VSD and Main Motors must be healthy | 0
[14 empty] | 57 | Main Bearings Lube Flow Not Low | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = INCHING AND MS_RUNNING = NOT RUNNING AND • [FI13640 > A_Lo AND • FI13641 > A_Lo]] SAG Mill Main Bearings Lubrication System Flow Divider Feed Flow SAG Mill Main Bearings Lubrication System Thrust Rail Lubrication Flow | 0
[14 empty] | 58 | Main Bearings Lube Pressure Not Low | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = INCHING AND MS_RUNNING = NOT RUNNING AND • [PI13644 > A_Lo AND • PI13645 > A_Lo AND • PI13646 > A_Lo AND • PI13647 > A_Lo AND • PI13648 > A_Lo AND • PI13649 > A_Lo AND • PI13650 > A_Lo AND • PI13651 > A_Lo]] SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Feed End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure SAG Mill Main Bearings Lubrication System Discharge End Trunnion Pressure | 0
[14 empty] | 59 | Main Bearing Temperatures Not High | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = INCHING AND MS_RUNNING = NOT RUNNING AND • [TI13712A < A_Hi AND • TI13712B < A_Hi AND • TI13712C < A_Hi AND • TI13714A < A_Hi AND • TI13714B < A_Hi AND • TI13714C < A_Hi AND • TI13716A < A_Hi AND • TI13716B < A_Hi AND • TI13716C < A_Hi AND • TI13717A < A_Hi AND • TI13717B < A_Hi AND • TI13717C < A_Hi AND • TI13713A < A_Hi AND • TI13713B < A_Hi AND • TI13715A < A_Hi AND • TI13715B < A_Hi]] SAG Mill Feed End Trunnion Bearing (Right Side) Outboard Temperature SAG Mill Feed End Trunnion Bearing (Right Side) Centre Temperature SAG Mill Feed End Trunnion Bearing (Right Side) Inboard Temperature SAG Mill Feed End Trunnion Bearing (Left Side) Outboard Temperature SAG Mill Feed End Trunnion Bearing (Left Side) Centre Temperature SAG Mill Feed End Trunnion Bearing (Left Side) Inboard Temperature SAG Mill Discharge End Trunnion Bearing (Right Side) Outboard Temperature SAG Mill Discharge End Trunnion Bearing (Right Side) Centre Temperature SAG Mill Discharge End Trunnion Bearing (Right Side) Inboard Temperature SAG Mill Discharge End Trunnion Bearing (Left Side) Outboard Temperature SAG Mill Discharge End Trunnion Bearing (Left Side) Centre Temperature SAG Mill Discharge End Trunnion Bearing (Left Side) Inboard Temperature SAG Mill Discharge End Thrust Bearing (Right Side) Outboard Temperature SAG Mill Discharge End Thrust Bearing (Right Side) Inboard Temperature SAG Mill Discharge End Thrust Bearing (Left Side) Outboard Temperature SAG Mill Discharge End Thrust Bearing (Left Side) Inboard Temperature | 0
[14 empty] | 60 | Pinion Bearing Lube Flow Not Low | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = INCHING AND MS_RUNNING = NOT RUNNING AND • [FI13657 > A_Lo AND • FI13658 > A_Lo AND • FI13659 > A_Lo AND • FI13660 > A_Lo]] SAG Mill Fixed Pinion Bearing (Right) flow SAG Mill Fixed Pinion Bearing (Left) flow SAG Mill Floating Pinion Bearing (Right) flow SAG Mill Floating Pinion Bearing (Left) flow | 0
[14 empty] | 61 | Pinion Bearing Temperatures Not High | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = INCHING AND MS_RUNNING = NOT RUNNING AND • [TI13704 < A_Hi AND • TI13705 < A_Hi AND • TI13706 < A_Hi AND • TI13707 < A_Hi]] SAG Mill Discharge End (Fixed) Pinion Right Side Bearing Temperature SAG Mill Discharge End (Fixed) Pinion Left Side Bearing Temperature SAG Mill Feed End (Floating) Pinion Right Side Bearing Temperature SAG Mill Feed End (Floating) Pinion Left Side Bearing Temperature | 0
[14 empty] | 62 | TIC13629 < A_Hi | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = INCHING AND MS_RUNNING = NOT RUNNING AND • TIC13629 < A_Hi ] SAG Mill Main Bearings Lubrication System Conditioned Circuit Temperature | 0
[14 empty] | 63 | Gear Spray System Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = INCHING AND MS_RUNNING = NOT RUNNING AND • F13MS401_T8 Timer stopped OR paused] Gear Spray System Fault Alarms must be inactive | 2 | [6 empty] | SAG & Ball Mill Grease Fault Timer Start Permissives
[14 empty] | 64 | Seal Grease System Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MS_OP_MODE = INCHING AND MS_RUNNING = NOT RUNNING AND • F13MS401_T6 Timer stopped OR paused] Seal Grease System Fault Alarms must be inactive | 2 | [6 empty] | SAG & Ball Mill Grease Fault Timer Start Permissives
F13-PO-445 | 2000-F13-PID-PR-10010 | SAG MILL MAIN BEARING LUBE UNIT OIL CONDITIONING PUMP | DOL | [5 empty] | NA | X | X | F13MS401_T12 Timer Elapsed | F13MS401_T13 Timer Elapsed OR | [10 empty] | Drive is started/stopped by activating/deactivating 13PO445STF.PV.1 | 1 | 2025-03-18 | Logic reviewed with Modbus details
[13 empty] | F13LU413_STS changes from = 2 OR | [11 empty] | 1 | 2025-03-18 | Part of OCM package. Started/stopped with digital output
[13 empty] | F13MS401_OCM = Alarm | [11 empty] | 1 | 2025-03-18 | Part of OCM package. Started/stopped with digital output
[14 empty] | 7 | XS13200 Inactive | 0 |  |  |  | X |  |  |  | Common Alarm Active to trigger the drive fault | 2
[14 empty] | 8 | LI13620 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir level | A
[14 empty] | 9 | TI13623 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir temperature | A
[14 empty] | 10 | LI13620 > A_Lo | 5 |  | X |  |  |  | X |  | SAG Mill Lubrication System lube oil reservoir level | A
MOC-460
[14 empty] | 12 | YA24703 Inactive | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | PSL24701 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-427 | 2000-F13-PID-PR-10010 | SAG MILL LOW PRESSURE LUBE PUMP 1 | DOL | [5 empty] | 66.9 | X | X | F13-SEQ-0017 | F13-SEQ-0018 | [11 empty] | A
[14 empty] | 1 | F13-PO-427 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-427 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-427 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-427 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-427 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-427 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-427 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-PO-428 Running | 5 |  |  | X |  |  | X |  | F13-PO-427 and F13-PO-428 cannot run simultaneously | A
[14 empty] | 9 | LI13619 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir level | A
[14 empty] | 10 | TI13615 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir temperature | A
[14 empty] | 11 | TI13615 ≥ A_HH | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir temperature | A
[14 empty] | 12 | LI13619 > A_Lo | 5 |  | X |  |  |  | X |  | SAG Mill Lubrication System lube oil reservoir level | A
MOC-460
[14 empty] | 14 | FI13630 ≤ A_LL AND (F13-PO-427 Running > 10 seconds) | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube flowrate | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 15 | YA24703 Inactive | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 16 | PSL24701 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-428 | 2000-F13-PID-PR-10010 | SAG MILL LOW PRESSURE LUBE PUMP 2 | DOL | [5 empty] | 66.9 | X | X | F13-SEQ-0017 | F13-SEQ-0018 | [11 empty] | A
[14 empty] | 1 | F13-PO-428 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-428 Fail to Start / Stop | 0 |  |  |  | X | . |  |  |  | 0
[14 empty] | 3 | F13-PO-428 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-428 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-428 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-428 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-428 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-PO-427 Running | 5 |  |  | X |  |  | X |  | F13-PO-427 and F13-PO-428 cannot run simultaneously | A
[14 empty] | 9 | LI13619 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir level | A
[14 empty] | 10 | TI13615 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir temperature | A
[14 empty] | 11 | TI13615 ≥ A_HH | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir temperature | A
[14 empty] | 12 | LI13619 > A_Lo | 5 |  | X |  |  |  | X |  | SAG Mill Lubrication System lube oil reservoir level | A
MOC-460
[14 empty] | 14 | FI13630 ≤ A_LL AND (F13-PO-428 Running > 10 seconds) | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube flowrate | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 15 | YA24703 Inactive | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 16 | PSL24701 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-HT-43X | 2000-F13-PID-PR-10010 | SAG MILL LUBE OIL RETURN COMP. HEATER 1 & 2 | FE | [5 empty] | 27.82 | X | X | TI13615 ≤ P_Lo | TI13615 ≥ P_Hi | [10 empty] | Common motor control for F13-HT-433 & 434 | MOC-460 | 2025-05-02 | [KAN-1784] 13MS401_FP5 Not present in PCT - Jira
[14 empty] | 1 | F13-HT-43X Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-HT-43X Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-HT-43X Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | [10 empty] | 0 | [6 empty] | estop removed. No estops on heaters
[14 empty] | 5 | F13-HT-43X MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-HT-43X Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-HT-43X Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13619 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir level (settling compartment) | A
[14 empty] | 9 | TI13615 ≥ A_HH | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir temperature (settling compartment) | A
[14 empty] | 10 | HS13678BOFF Active | 0 |  |  |  | X |  |  |  | HS13678 Selector switch on F13-LU-413 CP turned to 'OFF' position | 1 | 2025-06-12 | RE: Sag Mill lube oil heater control |  |  |  |  | verified by tracing logic and signed off based on actual switched has been tested
[14 empty] | 11 | TI13615 < A_Hi | 5 |  | X |  |  |  | X |  | SAG Mill Lubrication System lube oil reservoir temperature (settling compartment) | A
F13-HT-43XX | 2000-F13-PID-PR-10010 | SAG MILL LUBE OIL CONDITIONED COMP. HEATER 3 & 4 | FE | [5 empty] | 27.82 | X | X | TI13623 ≤ P_Lo | TI13623 ≥ P_Hi | [10 empty] | Common motor control for F13-HT-435 & 436 | MOC-460 | 2025-05-02 | [KAN-1784] 13MS401_FP5 Not present in PCT - Jira
[14 empty] | 1 | F13-HT-43XX Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-HT-43XX Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-HT-43XX Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | [10 empty] | 0 | [6 empty] | estop removed. No estops on heaters
[14 empty] | 5 | F13-HT-43XX MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-HT-43XX Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-HT-43XX Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13620 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
[14 empty] | 9 | TI13623 ≥ A_HH | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
[14 empty] | 10 | HS13733BOFF Active | 0 |  |  |  | X |  |  |  | HS13733 Selector switch on F13-LU-413 CP turned to 'OFF' position | 1 | 2025-06-12 | RE: Sag Mill lube oil heater control |  |  |  |  | verified by tracing logic and signed off based on actual switched has been tested
[14 empty] | 11 | TI13623 < A_Hi | 5 |  | X |  |  |  | X |  | SAG Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
F13-PO-429 | 2000-F13-PID-PR-10010 | SAG MILL HIGH PRESSURE LUBE PUMP 1 | DOL | [5 empty] | 245 | X | X | F13-SEQ-0017 | F13-SEQ-0018 | [11 empty] | A
[14 empty] | 1 | F13-PO-429 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-429 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-429 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-429 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-429 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-429 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-429 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13620 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
[14 empty] | 9 | SSL13693 Inactive AND (F13-PO-429 Running > 10 seconds) | 10 |  |  |  | X |  |  |  | SAG Mill HP Lube Pump 1 flywheel underspeed | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 10 | F13-PO-430 AND F13-PO-431 Running | 5 |  |  |  | X |  |  |  | Maximum of 2 SAG Mill HP Lube Pumps to run simultaneously | A
[14 empty] | 11 | FI13630 ≤ A_LL | 5 |  |  | X |  |  | X |  | Lubrication System Flow | A
[14 empty] | 12 | FI13640 ≤ A_LL AND (F13-PO-429 Running > 10 seconds) | 5 |  |  | X |  |  | X |  | Lubrication System Main/Thrust Bearing Oil Flow | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 13 | FI13641 ≤ A_LL AND (F13-PO-429 Running > 10 seconds) | 5 |  |  | X |  |  | X |  | Lubrication System Thrust Bearing Oil Flow | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 14 | TI13623 ≥ A_HH | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
[14 empty] | 15 | TI13623 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
[14 empty] | 16 | FI13630 > A_Lo | 5 |  | X |  |  |  | X |  | LP SAG Mill Lubrication System | A
[14 empty] | 17 | LI13620 > A_Lo | 5 |  | X |  |  |  | X |  | SAG Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
MOC-460
[14 empty] | 15 | YA24703 Inactive | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 16 | PSL24701 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-430 | 2000-F13-PID-PR-10010 | SAG MILL HIGH PRESSURE LUBE PUMP 2 | DOL | [5 empty] | 245 | X | X | F13-SEQ-0017 | F13-SEQ-0018 | [11 empty] | A
[14 empty] | 1 | F13-PO-430 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-430 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-430 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-430 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-430 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-430 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-430 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13620 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
[14 empty] | 9 | SSL13694 Inactive AND (F13-PO-430 Running > 10 seconds) | 10 |  |  |  | X |  |  |  | SAG Mill HP Lube Pump 2 flywheel underspeed | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 10 | F13-PO-429 AND F13-PO-431 Running | 5 |  |  |  | X |  |  |  | Maximum of 2 SAG Mill HP Lube Pumps to run simultaneously | A
[14 empty] | 11 | FI13630 ≤ A_LL | 5 |  |  | X |  |  | X |  | Lubrication System Flow | A
[14 empty] | 12 | FI13640 ≤ A_LL AND (F13-PO-430 Running > 10 seconds) | 5 |  |  | X |  |  | X |  | Lubrication System Main/Thrust Bearing Oil Flow | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 13 | FI13641 ≤ A_LL AND (F13-PO-430 Running > 10 seconds) | 5 |  |  | X |  |  | X |  | Lubrication System Thrust Bearing Oil Flow | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 14 | TI13623 ≥ A_HH | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
[14 empty] | 15 | TI13623 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
[14 empty] | 16 | FI13630 > A_Lo | 5 |  | X |  |  |  | X |  | LP SAG Mill Lubrication System | A
[14 empty] | 17 | LI13620 > A_Lo | 5 |  | X |  |  |  | X |  | SAG Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
MOC-460
[14 empty] | 19 | YA24703 Inactive | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 20 | PSL24701 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-431 | 2000-F13-PID-PR-10010 | SAG MILL HIGH PRESSURE LUBE PUMP 3 | DOL | [5 empty] | 245 | X | X | F13-SEQ-0017 | F13-SEQ-0018 | [11 empty] | A
[14 empty] | 1 | F13-PO-431 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-431 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-431 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-431 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-431 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-431 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-431 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13620 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
[14 empty] | 9 | SSL13695 Inactive AND (F13-PO-431 Running > 10 seconds) | 10 |  |  |  | X |  |  |  | SAG Mill HP Lube Pump 3 flywheel underspeed | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 10 | F13-PO-429 AND F13-PO-430 Running | 5 |  |  |  | X |  |  |  | Maximum of 2 SAG Mill HP Lube Pumps to run simultaneously | A
[14 empty] | 11 | FI13630 ≤ A_LL | 5 |  |  | X |  |  | X |  | Lubrication System Flow | A
[14 empty] | 12 | FI13640 ≤ A_LL AND (F13-PO-431 Running > 10 seconds) | 5 |  |  | X |  |  | X |  | Lubrication System Main/Thrust Bearing Oil Flow | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 13 | FI13641 ≤ A_LL AND (F13-PO-431 Running > 10 seconds) | 5 |  |  | X |  |  | X |  | Lubrication System Thrust Bearing Oil Flow | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 14 | TI13623 ≥ A_HH | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
[14 empty] | 15 | TI13623 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
[14 empty] | 16 | FI13630 > A_Lo | 5 |  | X |  |  |  | X |  | LP SAG Mill Lubrication System | A
[14 empty] | 17 | LI13620 > A_Lo | 5 |  | X |  |  |  | X |  | SAG Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
MOC-460
[14 empty] | 19 | YA24703 Inactive | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 20 | PSL24701 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-432 | 2000-F13-PID-PR-10013 | SAG MILL HYDRAULIC BRAKE SYSTEM PUMP | DOL | [5 empty] | 1.62 | X | X | AUTO: PSH13555 = Inactive | AUTO: PSH13555 = Active | [10 empty] | Pressure switch includes an internal deadband to prevent the pump from cycling | A
[14 empty] | 1 | F13-PO-432 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-432 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-432 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-432 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-432 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | No field signal
[14 empty] | 6 | F13-PO-432 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-432 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LSL13551 Inactive | 3 |  |  |  | X |  |  |  | SAG Mill Brake Hydraulic Power Unit Brake Hydraulic Fluid Reservoir Level Switch | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 9 | TSH13552 Inactive | 3 |  |  |  | X |  |  |  | SAG Mill Brake Hydraulic Power Unit Brake Hydraulic Fluid Reservoir Temperature Switch | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[13 empty] | ` | 10 | HS13739 (falling edge) or HS13737 (falling edge) | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1939
F13-HT-42X | 2000-F13-PID-PR-10010 | SAG MILL MOTOR 1 & 2 ANTI-CONDENSATION HEATER | FE | [5 empty] | 39.67 | X | X | MS_RUNNING = NOT RUNNING | MS_RUNNING = RUNNING | [10 empty] | Common motor control for F13-HT-421 & 425 | 0 | [6 empty] | Load list says 39.67 A max current
[9 empty] | 40 |  |  | (F13-MS-401 Not Running) | (F13-MS-401 Running) | 1 | F13-HT-42X Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-HT-42X Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-HT-42X Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-HT-42X E-Stop | 0 |  |  |  | X | X |  |  |  | 0 | [6 empty] | no estops on heaters
[14 empty] | 5 | F13-HT-42X MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-HT-42X Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-HT-42X Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-427 | 2000-F13-PID-PR-10010 | SAG MILL MOTOR 1 - FAN 1 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0021B Running OR | [12 empty] | 1 | 2025-07-11 | CR-026
[12 empty] | MS_OP_MODE = INCHING OR |  | 1 | F13-FN-427 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[12 empty] | F13-MS-401 = Running | F13-MS-401 = Not Running AND 'MS_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-427 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[13 empty] | MS_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-427 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-427 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-427 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Always ON
[14 empty] | 6 | F13-FN-427 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-427 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-428 | 2000-F13-PID-PR-10010 | SAG MILL MOTOR 1 - FAN 2 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0021B Running OR | [12 empty] | 1 | 2025-07-11 | CR-026
[12 empty] | MS_OP_MODE = INCHING OR |  | 1 | F13-FN-428 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[12 empty] | F13-MS-401 = Running | F13-MS-401 = Not Running AND 'MS_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-428 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[13 empty] | MS_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-428 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-428 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-428 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Always ON
[14 empty] | 6 | F13-FN-428 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-428 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-429 | 2000-F13-PID-PR-10010 | SAG MILL MOTOR 1 - FAN 3 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0021B Running OR | [12 empty] | 1 | 2025-07-11 | CR-026
[12 empty] | MS_OP_MODE = INCHING OR |  | 1 | F13-FN-429 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[12 empty] | F13-MS-401 = Running | F13-MS-401 = Not Running AND 'MS_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-429 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[13 empty] | MS_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-429 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-429 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-429 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Always ON
[14 empty] | 6 | F13-FN-429 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-429 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-430 | 2000-F13-PID-PR-10010 | SAG MILL MOTOR 1 - FAN 4 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0021B Running OR | [12 empty] | 1 | 2025-07-11 | CR-026
[12 empty] | MS_OP_MODE = INCHING OR |  | 1 | F13-FN-430 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[12 empty] | F13-MS-401 = Running | F13-MS-401 = Not Running AND 'MS_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-430 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[13 empty] | MS_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-430 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-430 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-430 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Always ON
[14 empty] | 6 | F13-FN-430 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-430 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-431 | 2000-F13-PID-PR-10010 | SAG MILL MOTOR 2 - FAN 1 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0021B Running OR | [12 empty] | 1 | 2025-07-11 | CR-026 |  |  |  |  | Signed as all other lines signed and common cells greened
[12 empty] | MS_OP_MODE = INCHING OR |  | 1 | F13-FN-431 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[12 empty] | F13-MS-401 = Running | F13-MS-401 = Not Running AND 'MS_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-431 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[13 empty] | MS_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-431 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-431 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-431 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Always ON
[14 empty] | 6 | F13-FN-431 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-431 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-432 | 2000-F13-PID-PR-10010 | SAG MILL MOTOR 2 - FAN 2 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0021B Running OR | [12 empty] | 1 | 2025-07-11 | CR-026 |  |  |  |  | Signed as all other lines signed and common cells greened
[12 empty] | MS_OP_MODE = INCHING OR |  | 1 | F13-FN-432 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[12 empty] | F13-MS-401 = Running | F13-MS-401 = Not Running AND 'MS_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-432 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[13 empty] | MS_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-432 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-432 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-432 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Always ON
[14 empty] | 6 | F13-FN-432 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-432 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-433 | 2000-F13-PID-PR-10010 | SAG MILL MOTOR 2 - FAN 3 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0021B Running OR | [12 empty] | 1 | 2025-07-11 | CR-026 |  |  |  |  | Signed as all other lines signed and common cells greened
[12 empty] | MS_OP_MODE = INCHING OR |  | 1 | F13-FN-433 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[12 empty] | F13-MS-401 = Running | F13-MS-401 = Not Running AND 'MS_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-433 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2 | 2025-07-11 | CR-026
[13 empty] | MS_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-433 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-433 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-433 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Always ON
[14 empty] | 6 | F13-FN-433 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-433 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-434 | 2000-F13-PID-PR-10010 | SAG MILL MOTOR 2 - FAN 4 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0021B Running OR | [12 empty] | 1 | 2025-07-11 | CR-026 |  |  |  |  | Signed as all other lines signed and common cells greened
[12 empty] | MS_OP_MODE = INCHING |  | 1 | F13-FN-434 Comms Failure | 0 |  |  |  | X |  |  |  |  | 1 | 2025-07-11 | CR-026
[12 empty] | F13-MS-401 = Running | F13-MS-401 = Not Running AND 'MS_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-434 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 1 | 2025-07-11 | CR-026
[13 empty] | MS_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-434 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FN-434 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-434 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Always ON
[14 empty] | 6 | F13-FN-434 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-434 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-PO-421 | 2000-F13-PID-PR-10010 | SAG MILL MOTOR LUBE PUMP 1 | DOL | [5 empty] | 11.3 | X | X | F13-SEQ-0021B OR | F13-SEQ-0021B OR | [10 empty] | The motor lube pumps only need to run on mill start, stop and if motor speed < 90RPM | B | [6 empty] | Signed as all other lines signed and common cells greened
[12 empty] | F13-SEQ-0022B OR | F13-SEQ-0022B OR | 1 | F13-PO-421 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[12 empty] | MS_OP_MODE = INCHING AND DUTY SELECTED (F13MB401_FP1) OR | MS_OP_MODE = NORMAL (Negative Edge One Shot) OR | 2 | F13-PO-421 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[12 empty] | MS_STARTING = NOT STARTING AND MS_STOPPING = NOT STOPPING AND MS_RUNNING = RUNNING AND SI13137A.PV ≤ P_Lo | MS_STARTING = NOT STARTING AND MS_STOPPING = NOT STOPPING AND MS_RUNNING = RUNNING AND SI13137A.PV > P_Lo | 3 | F13-PO-421 Drive Fault | 0 |  |  |  | X |  |  |  |  | 1 | 2/05/2025 12/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1790?linkSource=email https://pastech-2955.atlassian.net/browse/KAN-1811
[14 empty] | 4 | F13-PO-421 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-421 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-421 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-421 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13571 > A_Lo | 5 |  | X |  |  |  | X |  | F13LU411 Reservoir level | 0
[14 empty] | 9 | YA24703 Inactive | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | PSL24701 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-422 | 2000-F13-PID-PR-10010 | SAG MILL MOTOR LUBE PUMP 2 | DOL | [5 empty] | 11.3 | X | X | F13-SEQ-0021B OR | F13-SEQ-0021B OR | [10 empty] | The motor lube pumps only need to run on mill start, stop and if motor speed < 90RPM | B | [6 empty] | Signed as all other lines signed and common cells greened
[12 empty] | F13-SEQ-0022B OR | F13-SEQ-0022B OR | 1 | F13-PO-422 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[12 empty] | MS_OP_MODE = INCHING AND DUTY SELECTED (F13MB401_FP1) OR | MS_OP_MODE = NORMAL (Negative Edge One Shot) OR | 2 | F13-PO-422 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[12 empty] | MS_STARTING = NOT STARTING AND MS_STOPPING = NOT STOPPING AND MS_RUNNING = RUNNING AND SI13137A.PV ≤ P_Lo | MS_STARTING = NOT STARTING AND MS_STOPPING = NOT STOPPING AND MS_RUNNING = RUNNING AND SI13137A.PV > P_Lo | 3 | F13-PO-422 Drive Fault | 0 |  |  |  | X |  |  |  |  | 1 | 2/05/2025 12/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1790?linkSource=email https://pastech-2955.atlassian.net/browse/KAN-1811
[14 empty] | 4 | F13-PO-422 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-422 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-422 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-422 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13571 > A_Lo | 5 |  | X |  |  |  | X |  | F13LU411 Reservoir level | 0
[14 empty] | 9 | YA24703 Inactive | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | PSL24701 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-FN-425 | 2000-F13-PID-PR-10010 | SAG MILL MOTOR LUBE SKID COOLER FAN | DOL | [5 empty] | 0.87 | X | X | TSH13569 Inactive | TSH13569 Active for 10 minutes | [11 empty] | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1984
[14 empty] | 1 | F13-FN-425 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FN-425 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FN-425 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FN-425 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-425 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | no field signal
[14 empty] | 6 | F13-FN-425 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-425 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | TSL13569 Active | 3 |  |  | X |  |  | X |  |  | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1984
F13-HT-408 | 2000-F13-PID-PR-10010 | SAG MILL MOTOR LUBE UNIT HEATER | FE | [5 empty] | 1.3912 | X | X | TSL13569 Active | TSL13569 Inactive for 10 minutes | [11 empty] | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1984
[14 empty] | 1 | F13-HT-408 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-HT-408 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-HT-408 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-HT-408 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-HT-408 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | no field signal
[14 empty] | 6 | F13-HT-408 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-HT-408 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | TSH13569 Inactive | 3 |  |  | X |  |  | X |  |  | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1984
F13-PO-434 | 2000-F13-PID-PR-10010 | SAG MILL PINION BEARING LUBE OIL PUMP 1 | DOL | [5 empty] | 6 | X | X | F13-SEQ-0017 | F13-SEQ-0018 | [11 empty] | A
[14 empty] | 1 | F13-PO-434 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-434 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-434 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-434 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-434 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-434 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-434 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13619 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir level | A
[14 empty] | 9 | F13-PO-435 Running | 0 |  |  |  | X |  |  |  | F13-PO-434 and F13-PO-435 cannot run simultaneously | A
[14 empty] | 10 | LI13619 > A_Lo | 5 |  | X |  |  |  | X |  | SAG Mill Lubrication System lube oil reservoir level | A
MOC-460
[14 empty] | 12 | F13-PO-427 & 428 Not Running | 0 |  |  | X |  |  | X |  | At least one (1) F13-PO-427 OR F13-PO-428 must be running for ≥ 5 seconds | B
[14 empty] | 13 | YA24703 Inactive | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 14 | PSL24701 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-435 | 2000-F13-PID-PR-10010 | SAG MILL PINION BEARING LUBE OIL PUMP 2 | DOL | [5 empty] | 6 | X | X | F13-SEQ-0017 | F13-SEQ-0018 | [11 empty] | A
[14 empty] | 1 | F13-PO-435 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-435 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-435 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-435 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-435 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-435 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-435 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13619 ≤ A_LL | 5 |  |  |  | X |  |  |  | SAG Mill Lubrication System lube oil reservoir level | A
[14 empty] | 9 | F13-PO-434 Running | 0 |  |  |  | X |  |  |  | F13-PO-434 and F13-PO-435 cannot run simultaneously | A
[14 empty] | 10 | LI13619 > A_Lo | 5 |  | X |  |  |  | X |  | SAG Mill Lubrication System lube oil reservoir level | A
MOC-460
[14 empty] | 12 | F13-PO-427 & 428 Not Running | 0 |  |  | X |  |  | X |  | At least one (1) F13-PO-427 OR F13-PO-428 must be running for ≥ 5 seconds | B | [6 empty] | verified via logic
[14 empty] | 13 | YA24703 Inactive | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 14 | PSL24701 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-MB-401A | 2000-F13-PID-PR-10011 | BALL MILL MOTOR 1 | VSD | -5 | 100 | % | 80.5 | 100 | 1707 | X | X | F13-SEQ-0015A/B | F13-SEQ-0016A/B/C | [10 empty] | Engineer-level access required to adjust Mill Speed SV in MANUAL Normal operating range = 80.5% to 100% Forward inching nominal SV = 5% Reverse inching nominal SV = -5% 100% VSD Speed = 150 Motor RPM = 10.99 Mill RPM = 74.57% of Critical Speed. Refer to 2000-ME001.2-N01-50001. Normal operating range calculated from Duty Mill Speed Range (60-78% Cs). Refer to 2000-F00-DCR-PR-10001 Interlocks and permissives apply for both F13-MB-401A and F13-MB-401B Inching control via F13MB401-CP is directly wired to VSD | B
F13-MB-401B | 2000-F13-PID-PR-10011 | BALL MILL MOTOR 2 | VSD | -5 | 100 | % | 80.5 | 100 | 1707 | X | X | F13-SEQ-0015A/B | F13-SEQ-0016A/B/C | 1 | F13-MB-401A/B Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-MB-401A/B Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-MB-401A/B Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-MB-401A/B E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-MB-401A/B MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-MB-401A/B Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-MB-401A/B Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[15 empty] | NORMAL MODE ACTIVE Abnormal Shutdown, Mill Delayed Stop Set MB_MILL_EN = 0 if any of these conditions are TRUE | [8 empty] | Interlocks # 8 to 16 initiate an 'Abnormal Shutdown, Mill Delayed Stop' An 'Abnormal Shutdown, Mill Delayed Stop' interlock will activate MB_NCR_ILK to bypass the Ball Mill via XV13114, XV13115, XV13116 auto logic (ref. F13FD401_FP1 misc tab) Closed/Open trips and initiate a Sequence Stop (F13-SEQ-0016A) to stop F13-MB-401A/B. Refer to Misc tab. If the Ball Mill is tripped, the SAG Mill will operate in Single Stage SAG. It is recommended the circuit is sequence stopped if the Ball Mill fails restart. The condition Delay On timers here are longer than MB_NCR_ILK, such that if the conditions here become true before F13-SEQ-0016A is able to remove the MB_RUN command, the PCS will set MB_MILL_EN = 0 to force the Ball Mill to coast to stop (i.e. an instantaneous stop). These conditions can only become active if MB_OP_MODE = NORMAL (NORMAL MODE) | B
[14 empty] | 8 | F13-PP-401 Not Running | 150 |  |  |  | X |  |  | X | Cyclone Feed Pump | A
[14 empty] | 9 | Main Bearing Temperature Fault | 150 |  |  | ` | X |  |  | X | Logic: • MB_OP_MODE = NORMAL AND • [TI13964A ≥ A_HH OR • TI13964B ≥ A_HH OR • TI13964C ≥ A_HH OR • TI13958A ≥ A_HH OR • TI13958B ≥ A_HH OR • TI13958C ≥ A_HH OR • TI13962A ≥ A_HH OR • TI13962B ≥ A_HH OR • TI13966A ≥ A_HH OR • TI13966B ≥ A_HH OR • TI13966C ≥ A_HH OR • TI13960A ≥ A_HH OR • TI13960B ≥ A_HH OR • TI13960C ≥ A_HH OR • TI13967A ≥ A_HH OR • TI13967B ≥ A_HH] (Source: 2000-ME001.3-M02-50001, "Critical Main Bearing Temperature Permissive for Mill Rotation Alarm") | B
[14 empty] | 10 | Pinion Bearing Lube Fault | 150 |  |  |  | X |  |  | X | Logic: • MB_OP_MODE = NORMAL AND • [F13-PO-534 Not Running AND F13-PO-535 Not Running OR • FI13908 ≤ A_LL OR • FI13909 ≤ A_LL OR • FI13910 ≤ A_LL OR • FI13911 ≤ A_LL] (Source: 2000-ME001.3-M02-50001, "Critical Pinion Bearing Lube System Permissive for Mill Rotation Alarm") | A
[14 empty] | 11 | Pinion Bearing Temperature Fault | 150 |  |  |  | X |  |  | X | Logic: • MB_OP_MODE = NORMAL AND • [TI13957 ≥ A_HH OR • TI13956 ≥ A_HH OR • TI13955 ≥ A_HH OR • TI13954 ≥ A_HH] (Source: 2000-ME001.3-M02-50001, "Critical Pinion Bearing Temperature Permissive for Mill Rotation Alarm") | A
[14 empty] | 12 | Pinion Bearing Flank Fault | 150 |  |  |  | X |  |  | X | Logic: • MB_OP_MODE = NORMAL AND • [TI13763 ≥ A_HH OR • TI13764 ≥ A_HH OR • TI13765 ≥ A_HH OR • TI13766 ≥ A_HH OR • TI13783 ≥ A_HH OR • TI13784 ≥ A_HH OR • TI13785 ≥ A_HH OR • TI13786 ≥ A_HH OR • TDI13763 ≥ A_HH OR • TDI13786 ≥ A_HH] (Source: 2000-ME001.3-M02-50001, "Critical Pinion Flank Temperature Permissive for Mill Rotation Alarm") | A
[14 empty] | 13 | Ball Mill Main Motor Lube Fault | 150 |  |  |  | X |  |  | X | Logic: • [MB_OP_MODE = NORMAL AND • [MB_STARTING = STARTING OR [SI13150A.PV ≤ 90RPM AND MB_RUNNING = RUNNING]]] AND • [FI13827 ≤ A_LL OR • FI13828 ≤ A_LL OR • FI13829 ≤ A_LL OR • FI13830 ≤ A_LL OR • PI13823 ≥ A_HH OR • PI13824 ≥ A_HH OR • PI13825 ≥ A_HH OR • PI13826 ≥ A_HH OR • PSL13823 Inactive OR • PSL13824 Inactive OR • PSL13825 Inactive OR • PSL13826 Inactive] OR • MB_OP_MODE = NORMAL AND • [VI13767 ≥ A_HH OR • VI13770 ≥ A_HH OR • VI13789 ≥ A_HH OR • VI13792 ≥ A_HH] (Source: 2000-ME001.3-M02-50001, "Critical Ball Mill Main Motor Lubrication Unit and Motor Alarm") | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386 |  |  |  |  | MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
[14 empty] | 14 | Gear Spray System Fault | 150 |  |  |  | X |  |  | X | Logic: • MB_OP_MODE = NORMAL AND • F13MB401_T8 Elapsed (Source: 2000-ME001.3-M02-50001, "Critical Gear Spray System Permissive for Mill Rotation Alarm") | A
[14 empty] | 15 | Seal Grease System Fault | 150 |  |  |  | X |  |  | X | Logic: • MB_OP_MODE = NORMAL AND • F13MB401_T6 Elapsed (Source: 2000-ME001.3-M02-50001, "Critical Seal Grease System Permissive for Mill Rotation Alarm") | A
[15 empty] | NORMAL MODE ACTIVE Abnormal Shutdown, Mill Instantaneous Stop Set MB_MILL_EN = 0 if any of these conditions are TRUE | [8 empty] | Interlocks # 17 to 18 initiate an 'Abnormal Shutdown, Mill Instantaneous Stop'. An Abnormal Shutdown, Mill Instantaneous Stop interlock will de-activate F13MB401_MILL_EN to stop the Mill and activate MB_CR_ILK to initiate a Critical Stop Sequence (F13-SEQ-0016C) to engage the F13-MB-401A/B brakes. Refer to Misc tab. If the Ball Mill is tripped, the SAG Mill will operate in Single Stage SAG. It is recommended the circuit is sequence stopped if the Ball Mill fails restart. These conditions can only become active if MB_OP_MODE = NORMAL (NORMAL MODE) | B
[14 empty] | 16 | Main Bearing Lube System Fault | 1 |  |  |  | X |  |  | X | Logic: • MB_OP_MODE = NORMAL AND • [Less than two HP Lube Pumps running (F13-PO-529, F13-PO-530, F13-PO-531) OR • FI13891 ≤ A_LL OR • FI13892 ≤ A_LL OR • PI13895 ≤ A_LL OR • PI13896 ≤ A_LL OR • PI13897 ≤ A_LL OR • PI13898 ≤ A_LL OR • PI13899 ≤ A_LL OR • PI13900 ≤ A_LL OR • PI13901 ≤ A_LL OR • PI13902 ≤ A_LL OR • TIC13880 ≥ A_HH] (Source: 2000-ME001.3-M02-50001, "Critical Main Bearing Lube System Permissve for Mill Rotation Alarm") | 2 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1884 |  |  |  |  | tested only one instro, green the text until all tested
[14 empty] | 17 | Ball Mill Brake Normal Fault | 0 |  |  |  | X |  |  | X | Logic: • MB_OP_MODE = NORMAL AND • [ZSH13795 Inactive (Brake Engaged) OR • ZSH13797 Inactive (Brake Engaged) OR • SV13813 Deenergised] OR • LSL13802 INACTIVE (Hydraulic Reservoir Level Low) (LR 14/06/2026 Source 2000-ME001.3-M02-50001 Page 770) OR • (Source: 2000-ME001.3-M02-50001, "Ball Mill Brake Normal Mode Permissive for Ball Mill Motors Alarm") Note: Refer to F13-PO-532 interlocks in Drives tab | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[15 empty] | NORMAL MODE ACTIVE Start Permissives Set MB_MILL_EN = 0 if any of these conditions are FALSE | [8 empty] | Interlocks #19 to 30 are Start Permissives Conditions relevant when MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING (Ball Mill in normal mode and not running). All start permissives are true if MB_STARTING = STARTING OR MB_RUNNING = RUNNING OR MB_STOPPING = STOPPING (Ball Mill in starting, running or stopping status). Set MB_MILL_EN = 0 if any of these conditions are false to prevent start up of the Ball Mill | A
[14 empty] | 18 | YY13146A & B Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to F13-MB-401A & B start | 0
[14 empty] | 19 | Pinion Bearing Lube Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • [F13MB401_T1 Elapsed AND • F13MB401_T2 Elapsed AND • FI13908 > A_Lo AND • FI13909 > A_Lo AND • FI13910 > A_Lo AND • FI13911 > A_Lo]] (Source: 2000-ME001.3-M02-50001, "Non-Critical Pinion Bearing Lube System Permissive for Mill Rotation Alarm") | 0 | [6 empty] | tested only one instro, green the text until all tested
[14 empty] | 20 | Pinion Bearing Temp Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • [TI13957 < A_Hi AND • TI13956 < A_Hi AND • TI13955 < A_Hi AND • TI13954 < A_Hi]] (Source: 2000-ME001.3-M02-50001, "Non-Critical Pinion Bearing Temperature Permissive for Mill Rotation Alarm") | 0
[14 empty] | 21 | Main Bearing Lube Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • [F13MB401_T3 Elapsed AND • LI13872 > A_Lo AND • LI13874 > A_Lo AND • TI13866 < A_Hi AND • TI13866 > A_Lo AND • TI13873 < A_Hi AND • TI13873 > A_Lo AND • FI13891 > A_Lo AND • FI13892 > A_Lo AND • PI13895 > A_Lo AND • PI13896 > A_Lo AND • PI13897 > A_Lo AND • PI13898 > A_Lo AND • PI13899 > A_Lo AND • PI13900 > A_Lo AND • PI13901 > A_Lo AND • PI13902 > A_Lo AND • PDSH13977 Active AND • PDSH13978 Active AND • PDSH13979 Active AND • PDSH13980 Active AND • PDSH13981 Active AND • PDSH13982 Active AND • PDSH13983 Active AND • PDSH13984 Active AND • PDSH13985 Active AND • PDSH13986 Active AND • PDSH13987 Active AND • PDSH13988 Active AND • TIC13880 < A_Hi]] (Source: 2000-ME001.3-M02-50001, "Non-Critical Main Bearing Lube System Permissve for Mill Rotation Alarm") | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 22 | Main Bearing Temp Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • [TI13964A < A_Hi AND • TI13964B < A_Hi AND • TI13964C < A_Hi AND • TI13958A < A_Hi AND • TI13958B < A_Hi AND • TI13958C < A_Hi AND • TI13962A < A_Hi AND • TI13962B < A_Hi AND • TI13966A < A_Hi AND • TI13966B < A_Hi AND • TI13966C < A_Hi AND • TI13960A < A_Hi AND • TI13960B < A_Hi AND • TI13960C < A_Hi AND • TI13967A < A_Hi AND • TI13967B < A_Hi]] (Source: 2000-ME001.3-M02-50001, "Non-Critical Main Bearing Temperature Permissive for Mill Rotation Alarm") | 0
[14 empty] | 23 | Brake Common Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • LSL13802 Active AND • TSH13803 Active AND • F13-PO-532 INTERLOCKS INACTIVE AND IN AUTO AND • ZSH13796 Active AND • ZSH13798 Active] (Source: 2000-ME001.3-M02-50001, "Brake Common Permissive for Ball Mill Motor Main Drive Alarm") | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 24 | Main Motor Lube Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • [F13MB401_T4 Elapsed AND • LSL13819 Active AND • LSLL13819 Active AND • TSL13820 Inactive AND • TI13821 < A_HH AND • PDSH13817 Inactive AND • PDSHH13817 Active AND • PDSH13816 Inactive AND • PDSHH13816 Active AND • FI13827 > A_Lo AND • FI13828 > A_Lo AND • FI13829 > A_Lo AND • FI13830 > A_Lo AND • PSL13823 Active AND • PSL13824 Active AND • PSL13825 Active AND • PSL13826 Active]] (Source: 2000-ME001.3-M02-50001, "Non-Critical Ball Mill Main Motor Lubrication Unit and Motor Alarm") | 2 | 6/03/2025 05/06/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1984 |  |  |  |  | MOC-384 - Invert signal for PDSH Alarms MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
[14 empty] | 25 | Pinion Bearing Flank Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • [TI13763 < A_Hi AND • TI13764 < A_Hi AND • TI13765 < A_Hi AND • TI13766 < A_Hi AND • TI13783 < A_Hi AND • TI13784 < A_Hi AND • TI13785 < A_Hi AND • TI13786 < A_Hi AND • TDI13763 < A_Hi AND • TDI13786 < A_Hi]] (Source: 2000-ME001.3-M02-50001, "Non-Critical Pinion Flank Temperature Permissive for Mill Rotation Alarm") | 0
[14 empty] | 26 | Gear Spray System Alarm Inactive | 0 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • F13MB401_T8 Timer stopped OR paused] (Source: 2000-ME001.3-M02-50001, "Non-Critical Gear Spray System Permissive for Mill Rotation Alarm") | 2 | [6 empty] | SAG & Ball Mill Grease Fault Timer Start Permissives
[14 empty] | 27 | Seal Grease System Alarm Inactive | 0 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • F13MB401_T6 Timer stopped OR paused] (Source: 2000-ME001.3-M02-50001, "Non-Critical Seal Grease System Permissive for Mill Rotation Alarm") | 2 | [6 empty] | SAG & Ball Mill Grease Fault Timer Start Permissives
[14 empty] | 28 | Cooling Water Return Flow Not Low | 30 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • [FIC13126 > A_Lo AND • FI13413 > A_Lo AND • FI13415 > A_Lo]] Ball Mill Motor VSD Cooling Water return flowrate Ball Mill Motor 1 Cooling Water return flowrate Ball Mill Motor 2 Cooling Water return flowrate | 1 | 2025-07-07 | FIC13413 and FIC13415 should be FI only. 'C' removed
[14 empty] | 29 | Cooling Water Return Temp Not High | 30 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • [TIC13414 < A_Hi AND • TIC13416 < A_Hi AND • TI13118 < A_Hi]] Ball Mill Motor VSD Cooling Water return temperature Ball Mill Motor 1 Cooling Water return temperature Ball Mill Motor 2 Cooling Water return temperature | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1878
[14 empty] | 30 | Motor 1 Cooling Fans Running | 3 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • Minimum three (3) F13-FN-435, F13-FN-436, F13-FN-437, F13-FN-438 = RUNNING] | 1 | 2025-07-04 | CR-025
[14 empty] | 31 | Motor 2 Cooling Fans Running | 3 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • Minimum three (3) F13-FN-439, F13-FN-440, F13-FN-441, F13-FN-442 = RUNNING] | 1 | 2025-07-04 | CR-025
[14 empty] | 32 | VSD Converter On | 3 |  | X |  |  |  | X |  | Logic (Healthy): • MB_CONV_ON = Active AND • MB_33KV_STS = Closed | 1 | 2025-07-04 | CR-025
[14 empty] | 33 | 13MB401PSR = Active | 0 |  | X |  |  |  | X |  | Power station contacted prior to start. | 2
[15 empty] | INCHING MODE ACTIVE Set MB_MILL_EN = 0 if any of these conditions are TRUE for interlocks or FALSE for start permissives | [8 empty] | Interlocks #31 to 60 are Inching Mode interlocks These interlocks can only become active if MB_OP_MODE = INCHING (INCHING MODE) Set MB_MILL_EN = 0 if any of these conditions are true to prevent start up or to interlock the Ball Mill when inching the Ball Mill with the Main Motors. | A
[14 empty] | 34 | F13-PO-521 & 522 Not Running | 0 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • F13-PO-521 AND F13-PO-522 = Not Running | B
[14 empty] | 35 | F13-PO-527 & 528 Not Running | 0 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • F13-PO-527 AND F13-PO-528 = Not Running | B
[14 empty] | 36 | F13-PO-534 & 535 Not Running | 0 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • F13-PO-534 AND F13-PO-535 = Not Running | B
[14 empty] | 37 | F13-PO-529, 530 & 531 Not Running | 0 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • Less than two HP Lube Pumps running (F13-PO-529, F13-PO-530, F13-PO-531) | 1 | 2025-05-15 | https://pastech-2955.atlassian.net/browse/KAN-1884
[14 empty] | 38 | F13-PO-527/528 Min Runtime Inactive | 0 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • F13MB401_T1 Not Elapsed At least one (1) F13-PO-527 OR F13-PO-528 running for ≥ F13MB401_T1 | A
[14 empty] | 39 | F13-PO-534/535 Min Runtime Inactive | 0 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • F13MB401_T2 Not Elapsed At least one (1) F13-PO-534 OR F13-PO-535 running for ≥ F13MB401_T2 | A
[14 empty] | 40 | F13-PO-529/530/531 Min Runtime | 0 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • F13MB401_T3 Not Elapsed Two (2) F13-PO-529, F13-PO-530, F13-PO-531 running for ≥ F13MB401_T3 | A
[14 empty] | 41 | Main Motor Lube Flow LL | 1 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • [FI13827 ≤ A_LL OR • FI13828 ≤ A_LL OR • FI13829 ≤ A_LL OR • FI13830 ≤ A_LL] Main Motor 1 Lubrication DE Flow Main Motor 1 Lubrication NDE Flow Main Motor 2 Lubrication DE Flow Main Motor 2 Lubrication NDE Flow | 2
[14 empty] | 42 | Main Motor Lube Pressure HH | 1 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • [PI13823 ≥ A_HH OR • PI13824 ≥ A_HH OR • PI13825 ≥ A_HH OR • PI13826 ≥ A_HH OR • PSL13823 Inactive OR • PSL13824 Inactive OR • PSL13825 Inactive OR • PSL13826 Inactive] Main Motor 1 Lubrication DE Pressure Main Motor 1 Lubrication NDE Pressure Main Motor 2 Lubrication DE Pressure Main Motor 2 Lubrication NDE Pressure | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386 |  |  |  |  | MOC-497 - Changed Tag Number from PSH&PAH to PSL&PAL
[14 empty] | 43 | Main Bearings Lube Flow LL | 1 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • [FI13891 ≤ A_LL • FI13892 ≤ A_LL] Ball Mill Main Bearings Lubrication System Flow Divider Feed Flow Ball Mill Main Bearings Lubrication System Thrust Rail Lubrication Flow | 2
[14 empty] | 44 | Main Bearing Lube Pressure LL | 1 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • [PI13895 ≤ A_LL OR • PI13896 ≤ A_LL OR • PI13897 ≤ A_LL OR • PI13898 ≤ A_LL OR • PI13899 ≤ A_LL OR • PI13900 ≤ A_LL OR • PI13901 ≤ A_LL OR • PI13902 ≤ A_LL] Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure | 2 | [6 empty] | green the text until all tested
[14 empty] | 45 | Main Bearing Temperatures HH | 1 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • [TI13964A ≥ A_HH OR • TI13964B ≥ A_HH OR • TI13964C ≥ A_HH OR • TI13966A ≥ A_HH OR • TI13966B ≥ A_HH OR • TI13966C ≥ A_HH OR • TI13958A ≥ A_HH OR • TI13958B ≥ A_HH OR • TI13958C ≥ A_HH OR • TI13960A ≥ A_HH OR • TI13960B ≥ A_HH OR • TI13960C ≥ A_HH OR • TI13962A ≥ A_HH OR • TI13962B ≥ A_HH OR • TI13967A ≥ A_HH OR • TI13967B ≥ A_HH] Ball Mill Feed End Trunnion Bearing (Right Side) Outboard Temperature Ball Mill Feed End Trunnion Bearing (Right Side) Centre Temperature Ball Mill Feed End Trunnion Bearing (Right Side) Inboard Temperature Ball Mill Feed End Trunnion Bearing (Left Side) Outboard Temperature Ball Mill Feed End Trunnion Bearing (Left Side) Centre Temperature Ball Mill Feed End Trunnion Bearing (Left Side) Inboard Temperature Ball Mill Discharge End Trunnion Bearing (Right Side) Outboard Temperature Ball Mill Discharge End Trunnion Bearing (Right Side) Centre Temperature Ball Mill Discharge End Trunnion Bearing (Right Side) Inboard Temperature Ball Mill Discharge End Trunnion Bearing (Left Side) Outboard Temperature Ball Mill Discharge End Trunnion Bearing (Left Side) Centre Temperature Ball Mill Discharge End Trunnion Bearing (Left Side) Inboard Temperature Ball Mill Discharge End Thrust Bearing (Right Side) Outboard Temperature Ball Mill Discharge End Thrust Bearing (Right Side) Inboard Temperature Ball Mill Discharge End Thrust Bearing (Left Side) Outboard Temperature Ball Mill Discharge End Thrust Bearing (Left Side) Inboard Temperature | 2
[14 empty] | 46 | Pinion Bearing Lube Flow LL | 1 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • [FI13908 ≤ A_LL OR • FI13909 ≤ A_LL OR • FI13910 ≤ A_LL OR • FI13911 ≤ A_LL] Ball Mill Fixed Pinion Bearing (Right) flow Ball Mill Fixed Pinion Bearing (Left) flow Ball Mill Floating Pinion Bearing (Right) flow Ball Mill Floating Pinion Bearing (Left) flow | 2
[14 empty] | 47 | Pinion Bearing Temperatures HH | 1 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • [TI13957 ≥ A_HH OR • TI13956 ≥ A_HH OR • TI13955 ≥ A_HH OR • TI13954 ≥ A_HH] Ball Mill Discharge End (Fixed) Pinion Right Side Bearing Temperature Ball Mill Discharge End (Fixed) Pinion Left Side Bearing Temperature Ball Mill Feed End (Floating) Pinion Right Side Bearing Temperature Ball Mill Feed End (Floating) Pinion Left Side Bearing Temperature | 2
[14 empty] | 48 | TIC13880 ≥ A_HH Active | 1 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING AND • TIC13880 ≥ A_HH Ball Mill Main Bearings Lubrication System Conditioned Circuit Temperature | 2
[14 empty] | 49 | Gear Spray System Fault | 1 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING • F13MB401_T8 Elapsed (Source: 2000-ME001.3-M02-50001, "Critical Gear Spray System Permissive for Mill Rotation") | 2
[14 empty] | 50 | Seal Grease System Fault | 1 |  |  |  | X |  |  |  | Logic: • MB_OP_MODE = INCHING • F13MB401_T6 Elapsed (Source: 2000-ME001.3-M02-50001, "Critical Seal Grease System Permissive for Mill Rotation") | 2
[14 empty] | 51 | Ball Mill Brakes Engaged And Mill Running | 3 |  |  |  | X |  |  |  | Logic: (ZSH13795 OR ZSH13797 = Inactive (Brake Engaged) OR SV13812 = Energised OR SV13813 = Deenergised) AND 13MB401 running Brakes must be in released position | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 52 | YY13145 Healthy | 0 |  | X |  |  |  | X |  | Refer to F13MB401_INCH for siren logic. Misc tab. | 1 | 13/06/2025 6/10/2025 | https://pastech-2955.atlassian.net/browse/KAN-1943?linkSource=email CR-050
[14 empty] | 53 | Motor 1 Cooling Fans Running | 3 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = INCHING AND MB_RUNNING = NOT RUNNING AND • Minimum three (3) F13-FN-435, F13-FN-436, F13-FN-437, F13-FN-438 = RUNNING] | 0
[14 empty] | 54 | Motor 2 Cooling Fans Running | 3 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = INCHING AND MB_RUNNING = NOT RUNNING AND • Minimum three (3) F13-FN-439, F13-FN-440, F13-FN-441, F13-FN-442 = RUNNING] | 0
[14 empty] | 55 | Cooling Water Flow Healthy | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = INCHING AND MB_RUNNING = NOT RUNNING AND • FI13413, FI13415 AND FIC13126 > A_Lo] Cooling water flow to VSD and Main Motors must be healthy | 0
[14 empty] | 56 | Main Bearings Lube Flow Not Low | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = INCHING AND MB_RUNNING = NOT RUNNING AND • [FI13891 > A_Lo AND • FI13892 > A_Lo]] Ball Mill Main Bearings Lubrication System Flow Divider Feed Flow Ball Mill Main Bearings Lubrication System Thrust Rail Lubrication Flow | 0
[14 empty] | 57 | Main Bearings Lube Pressure Not Low | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = INCHING AND MB_RUNNING = NOT RUNNING AND • [PI13895 > A_Lo AND • PI13896 > A_Lo AND • PI13897 > A_Lo AND • PI13898 > A_Lo AND • PI13899 > A_Lo AND • PI13900 > A_Lo AND • PI13901 > A_Lo AND • PI13902 > A_Lo]] Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Feed End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure Ball Mill Main Bearings Lubrication System Discharge End Trunnion Pressure | 0 | [6 empty] | green the text until all tested
[14 empty] | 58 | Main Bearing Temperatures Not High | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = INCHING AND MB_RUNNING = NOT RUNNING AND • [TI13964A < A_Hi AND • TI13964B < A_Hi AND • TI13964C < A_Hi AND • TI13966A < A_Hi AND • TI13966B < A_Hi AND • TI13966C < A_Hi AND • TI13958A < A_Hi AND • TI13958B < A_Hi AND • TI13958C < A_Hi AND • TI13960A < A_Hi AND • TI13960B < A_Hi AND • TI13960C < A_Hi AND • TI13962A < A_Hi AND • TI13962B < A_Hi AND • TI13967A < A_Hi AND • TI13967B < A_Hi]] Ball Mill Feed End Trunnion Bearing (Right Side) Outboard Temperature Ball Mill Feed End Trunnion Bearing (Right Side) Centre Temperature Ball Mill Feed End Trunnion Bearing (Right Side) Inboard Temperature Ball Mill Feed End Trunnion Bearing (Left Side) Outboard Temperature Ball Mill Feed End Trunnion Bearing (Left Side) Centre Temperature Ball Mill Feed End Trunnion Bearing (Left Side) Inboard Temperature Ball Mill Discharge End Trunnion Bearing (Right Side) Outboard Temperature Ball Mill Discharge End Trunnion Bearing (Right Side) Centre Temperature Ball Mill Discharge End Trunnion Bearing (Right Side) Inboard Temperature Ball Mill Discharge End Trunnion Bearing (Left Side) Outboard Temperature Ball Mill Discharge End Trunnion Bearing (Left Side) Centre Temperature Ball Mill Discharge End Trunnion Bearing (Left Side) Inboard Temperature Ball Mill Discharge End Thrust Bearing (Right Side) Outboard Temperature Ball Mill Discharge End Thrust Bearing (Right Side) Inboard Temperature Ball Mill Discharge End Thrust Bearing (Left Side) Outboard Temperature Ball Mill Discharge End Thrust Bearing (Left Side) Inboard Temperature | 0
[14 empty] | 59 | Pinion Bearing Lube Flow Not Low | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = INCHING AND MB_RUNNING = NOT RUNNING AND • [FI13908 > A_Lo AND • FI13909 > A_Lo AND • FI13910 > A_Lo AND • FI13911 > A_Lo]] Ball Mill Fixed Pinion Bearing (Right) flow Ball Mill Fixed Pinion Bearing (Left) flow Ball Mill Floating Pinion Bearing (Right) flow Ball Mill Floating Pinion Bearing (Left) flow | 0
[14 empty] | 60 | Pinion Bearing Temperatures Not High | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = INCHING AND MB_RUNNING = NOT RUNNING AND • [TI13957 < A_Hi AND • TI13956 < A_Hi AND • TI13955 < A_Hi AND • TI13954 < A_Hi]] Ball Mill Discharge End (Fixed) Pinion Right Side Bearing Temperature Ball Mill Discharge End (Fixed) Pinion Left Side Bearing Temperature Ball Mill Feed End (Floating) Pinion Right Side Bearing Temperature Ball Mill Feed End (Floating) Pinion Left Side Bearing Temperature | 0
[14 empty] | 61 | TIC13880 < A_Hi | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = INCHING AND MB_RUNNING = NOT RUNNING AND • TIC13880 < A_Hi] Ball Mill Main Bearings Lubrication System Conditioned Circuit Temperature | 0
[14 empty] | 62 | Gear Spray System Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = INCHING AND MB_RUNNING = NOT RUNNING AND • F13MB401_T8 Timer stopped OR paused] Gear Spray System Fault Alarms must be inactive | 2 | [6 empty] | SAG & Ball Mill Grease Fault Timer Start Permissives
[14 empty] | 63 | Seal Grease System Alarm Inactive | 5 |  | X |  |  |  | X |  | Logic (Healthy): • [MB_OP_MODE = INCHING AND MB_RUNNING = NOT RUNNING AND • F13MB401_T6 Timer stopped OR paused] Seal Grease System Fault Alarms must be inactive | 2 | [6 empty] | SAG & Ball Mill Grease Fault Timer Start Permissives
F13-PO-446 | 2000-F13-PID-PR-10011 | BALL MILL MAIN BEARING LUBE UNIT OIL CONDITIONING PUMP | DOL | [5 empty] | NA | X | X | F13MB401_T12 Timer Elapsed | F13MB401_T13 Timer Elapsed OR | [10 empty] | Drive is started/stopped by activating/deactivating 13PO446STF.PV.1 | 1 | 2025-03-18 | Logic reviewed with Modbus details
[13 empty] | F13LU423_STS changes from = 2 OR | [11 empty] | 1 | 2025-03-18 | Part of OCM package. Started/stopped with digital output
[13 empty] | F13MB401_OCM = Alarm | [11 empty] | 1 | 2025-03-18 | Part of OCM package. Started/stopped with digital output
[14 empty] | 7 | XS13201 Inactive | 0 |  |  |  | X |  |  |  | Common Alarm Active to trigger the drive fault | 2
[14 empty] | 8 | LI13872 ≤ A_LL | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir level | A
[14 empty] | 9 | TI13873 ≤ A_LL | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir temperature | A
[14 empty] | 10 | LI13872 > A_Lo | 5 |  | X |  |  |  | X |  | Ball Mill Lubrication System lube oil reservoir level | A
[14 empty] | 11 | TI13873 > A_Lo | 5 |  | X |  |  |  | X |  | Ball Mill Lubrication System lube oil reservoir temperature | A
[14 empty] | 12 | YA24708 Alarm | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 12/03/2025 07/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1810
[14 empty] | 13 | PSL24706 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-527 | 2000-F13-PID-PR-10011 | BALL MILL LOW PRESSURE LUBE PUMP 1 | DOL | [5 empty] | 66.9 | X | X | F13-SEQ-0011 | F13-SEQ-0012 | [11 empty] | A
[14 empty] | 1 | F13-PO-527 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-527 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-527 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-527 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-527 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-527 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-527 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-PO-528 Running | 0 |  |  | X |  |  | X |  | F13-PO-527 and F13-PO-528 cannot run simultaneously | A
[14 empty] | 9 | LI13874 ≤ A_LL | 5 |  |  | X |  |  | X |  | Ball Mill Lubrication System lube oil reservoir level | A
[14 empty] | 10 | TI13866 ≤ A_LL | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir temperature | A
[14 empty] | 11 | TI13866 ≥ A_HH | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir temperature | A
[14 empty] | 12 | LI13874 > A_Lo | 5 |  | X |  |  |  | X |  | Ball Mill Lubrication System lube oil reservoir level | A
MOC-460
[14 empty] | 14 | FI13881 ≤ A_LL AND (F13-PO-527 Running > 10 seconds) | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube flowrate | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 15 | YA24708 Alarm | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 12/03/2025 07/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1810
[14 empty] | 16 | PSL24706 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-528 | 2000-F13-PID-PR-10011 | BALL MILL LOW PRESSURE LUBE PUMP 2 | DOL | [5 empty] | 66.9 | X | X | F13-SEQ-0011 | F13-SEQ-0012 | [11 empty] | A
[14 empty] | 1 | F13-PO-528 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-528 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-528 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-528 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-528 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Interlock not used for this drive.
[14 empty] | 6 | F13-PO-528 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-528 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-PO-527 Running | 0 |  |  | X |  |  | X |  | F13-PO-527 and F13-PO-528 cannot run simultaneously | A
[14 empty] | 9 | LI13874 ≤ A_LL | 5 |  |  | X |  |  | X |  | Ball Mill Lubrication System lube oil reservoir level | A
[14 empty] | 10 | TI13866 ≤ A_LL | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir temperature | A
[14 empty] | 11 | TI13866 ≥ A_HH | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir temperature | A
[14 empty] | 12 | LI13874 > A_Lo | 5 |  | X |  |  |  | X |  | Ball Mill Lubrication System lube oil reservoir level | A
MOC-460
[14 empty] | 14 | FI13881 ≤ A_LL AND (F13-PO-528 Running > 10 seconds) | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube flowrate | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 15 | YA24708 Alarm | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 12/03/2025 07/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1810
[14 empty] | 16 | PSL24706 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-HT-53X | 2000-F13-PID-PR-10011 | BALL MILL LUBE OIL RETURN COMP. HEATER 1 & 2 | FE | [5 empty] | 27.82 | X | X | TI13866 ≤ P_Lo | TI13866 ≥ P_Hi | [10 empty] | Common motor control for F13-HT-529 & 530 | 1 | 2025-05-02 | [KAN-1784] 13MS401_FP5 Not present in PCT - Jira
[14 empty] | 1 | F13-HT-53X Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-HT-53X Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-HT-53X Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-HT-53X E-Stop | 0 |  |  |  | X | X |  |  |  | 0 | [6 empty] | field electrician says no estop available for this drive
[14 empty] | 5 | F13-HT-53X MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-HT-53X Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-HT-53X Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13874 ≤ A_LL | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir level (settling compartment) | A
[14 empty] | 9 | TI13866 ≥ A_HH | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir temperature (settling compartment) | 1 | 2025-06-12 | RE: Sag Mill lube oil heater control
[14 empty] | 10 | HS13925BOFF Active | 0 |  |  |  | X |  |  |  | HS13925 Selector switch on F13-LU-423 CP turned to 'OFF' position | 1 | 2025-06-12 | RE: Sag Mill lube oil heater control
[14 empty] | 11 | TI13866 < A_Hi | 5 |  | X |  |  |  | X |  | Ball Mill Lubrication System lube oil reservoir temperature (settling compartment) | A
F13-HT-53XX | 2000-F13-PID-PR-10011 | BALL MILL LUBE OIL CONDITIONED COMP. HEATER 3 & 4 | FE | [5 empty] | 27.82 | X | X | TI13873 ≤ P_Lo | TI13873 ≥ P_Hi | [10 empty] | Common motor control for F13-HT-531 & 532 | 1 | 2025-05-02 | [KAN-1784] 13MS401_FP5 Not present in PCT - Jira
[14 empty] | 1 | F13-HT-53XX Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-HT-53XX Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-HT-53XX Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-HT-53XX E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-HT-53XX MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-HT-53XX Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-HT-53XX Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13872 ≤ A_LL | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
[14 empty] | 9 | TI13873 ≥ A_HH | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | 1 | 2025-06-12 | RE: Sag Mill lube oil heater control
[14 empty] | 10 | HS13968BOFF Active | 0 |  |  |  | X |  |  |  | HS13968 Selector switch on F13-LU-423 CP turned to 'OFF' position | 1 | 2025-06-12 | RE: Sag Mill lube oil heater control
[14 empty] | 11 | TI13873 < A_Hi | 5 |  | X |  |  |  | X |  | Ball Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
F13-PO-529 | 2000-F13-PID-PR-10011 | BALL MILL HIGH PRESSURE LUBE PUMP 1 | DOL | [5 empty] | 245 | X | X | F13-SEQ-0011 | F13-SEQ-0012 | [11 empty] | A
[14 empty] | 1 | F13-PO-529 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-529 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-529 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-529 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-529 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Interlock not used on this drive
[14 empty] | 6 | F13-PO-529 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-529 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13872 ≤ A_LL | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
[14 empty] | 9 | SSL13863 Inactive AND (F13-PO-529 Running > 10 seconds) | 10 |  |  |  | X |  |  |  | Ball Mill HP Lube Pump 1 flywheel underspeed | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 10 | F13-PO-530 AND F13-PO-531 Running | 5 |  |  |  | X |  |  |  | Maximum of 2 Ball Mill HP Lube Pumps to run simultaneously | A
[14 empty] | 11 | FI13881 ≤ A_LL | 5 |  |  | X |  |  | X |  | Lubrication System Flow | A
[14 empty] | 12 | FI13891 ≤ A_LL AND (F13-PO-529 Running > 10 seconds) | 5 |  |  | X |  |  | X |  | Lubrication System Main/Thrust Bearing Oil Flow | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 13 | FI13892 ≤ A_LL AND (F13-PO-529 Running > 10 seconds) | 5 |  |  | X |  |  | X |  | Lubrication System Thrust Bearing Oil Flow | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390 |  |  |  |  | Desktop Review
[14 empty] | 14 | TI13873 ≥ A_HH | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
[14 empty] | 15 | TI13873 ≤ A_LL | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
[14 empty] | 16 | FI13881 > A_Lo | 5 |  | X |  |  |  | X |  | LP Ball Mill Lubrication System | A
[14 empty] | 17 | LI13872 > A_Lo | 5 |  | X |  |  |  | X |  | Ball Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
MOC-460
[14 empty] | 19 | YA24708 Alarm | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 12/03/2025 07/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1810
[14 empty] | 20 | PSL24706 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-530 | 2000-F13-PID-PR-10011 | BALL MILL HIGH PRESSURE LUBE PUMP 2 | DOL | [5 empty] | 245 | X | X | F13-SEQ-0011 | F13-SEQ-0012 | [11 empty] | A
[14 empty] | 1 | F13-PO-530 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-530 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-530 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-530 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-530 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Interlock not used on this drive
[14 empty] | 6 | F13-PO-530 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-530 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13872 ≤ A_LL | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
[14 empty] | 9 | SSL13864 Inactive AND (F13-PO-530 Running > 10 seconds) | 10 |  |  |  | X |  |  |  | Ball Mill HP Lube Pump 2 flywheel underspeed | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 10 | F13-PO-529 AND F13-PO-531 Running | 5 |  |  |  | X |  |  |  | Maximum of 2 Ball Mill HP Lube Pumps to run simultaneously | A
[14 empty] | 11 | FI13881 ≤ A_LL | 5 |  |  | X |  |  | X |  | Lubrication System Flow | A
[14 empty] | 12 | FI13891 ≤ A_LL AND (F13-PO-530 Running > 10 seconds) | 5 |  |  | X |  |  | X |  | Lubrication System Main/Thrust Bearing Oil Flow | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 13 | FI13892 ≤ A_LL AND (F13-PO-530 Running > 10 seconds) | 5 |  |  | X |  |  | X |  | Lubrication System Thrust Bearing Oil Flow | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390 |  |  |  |  | Desktop Review
[14 empty] | 14 | TI13873 ≥ A_HH | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
[14 empty] | 15 | TI13873 ≤ A_LL | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
[14 empty] | 16 | FI13881 > A_Lo | 5 |  | X |  |  |  | X |  | LP Ball Mill Lubrication System | A
[14 empty] | 17 | LI13872 > A_Lo | 5 |  | X |  |  |  | X |  | Ball Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
MOC-460
[14 empty] | 19 | YA24708 Alarm | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 12/03/2025 07/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1810
[14 empty] | 20 | PSL24706 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-531 | 2000-F13-PID-PR-10011 | BALL MILL HIGH PRESSURE LUBE PUMP 3 | DOL | [5 empty] | 245 | X | X | F13-SEQ-0011 | F13-SEQ-0012 | [11 empty] | A
[14 empty] | 1 | F13-PO-531 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-531 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-531 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-531 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-531 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Interlock not used on this drive
[14 empty] | 6 | F13-PO-531 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-531 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13872 ≤ A_LL | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
[14 empty] | 9 | SSL13865 Inactive AND (F13-PO-531 Running > 10 seconds) | 10 |  |  |  | X |  |  |  | Ball Mill HP Lube Pump 3 flywheel underspeed | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390 |  |  |  |  | Desktop Review
[14 empty] | 10 | F13-PO-529 AND F13-PO-530 Running | 5 |  |  |  | X |  |  |  | Maximum of 2 Ball Mill HP Lube Pumps to run simultaneously | A
[14 empty] | 11 | FI13881 ≤ A_LL | 5 |  |  | X |  |  | X |  | Lubrication System Flow | A
[14 empty] | 12 | FI13891 ≤ A_LL AND (F13-PO-531 Running > 10 seconds) | 5 |  |  | X |  |  | X |  | Lubrication System Main/Thrust Bearing Oil Flow | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 13 | FI13892 ≤ A_LL AND (F13-PO-531 Running > 10 seconds) | 5 |  |  | X |  |  | X |  | Lubrication System Thrust Bearing Oil Flow | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390 |  |  |  |  | Desktop Review
[14 empty] | 14 | TI13873 ≥ A_HH | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
[14 empty] | 15 | TI13873 ≤ A_LL | 5 |  |  |  | X |  |  |  | Ball Mill Lubrication System lube oil reservoir temperature (conditioned compartment) | A
[14 empty] | 16 | FI13881 > A_Lo | 5 |  | X |  |  |  | X |  | LP Ball Mill Lubrication System | A
[14 empty] | 17 | LI13872 > A_Lo | 5 |  | X |  |  |  | X |  | Ball Mill Lubrication System lube oil reservoir level (conditioned compartment) | A
MOC-460
[14 empty] | 19 | YA24708 Alarm | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 12/03/2025 07/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1810
[14 empty] | 20 | PSL24706 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-532 | 2000-F13-PID-PR-10013 | BALL MILL HYDRAULIC BRAKE SYSTEM PUMP | DOL | [5 empty] | 1.62 | X | X | AUTO: PSH13806 = Inactive | AUTO: PSH13806 = Active | [10 empty] | Pressure switch includes an internal deadband to prevent the pump from cycling | A
[14 empty] | 1 | F13-PO-532 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-532 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-532 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-532 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-532 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-532 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-532 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LSL13802 Inactive | 3 |  |  |  | X |  |  |  | Ball Mill Brake Hydraulic Power Unit Brake Hydraulic Fluid Reservoir Level Switch | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 9 | TSH13803 Inactive | 3 |  |  |  | X |  |  |  | Ball Mill Brake Hydraulic Power Unit Brake Hydraulic Fluid Reservoir Temperature Switch | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | HS13750 (falling edge) or HS13748 (falling edge) | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1939 |  |  |  |  | Implemented using the PSP bit rather than an Interlock as per https://pastech-2955.atlassian.net/browse/KAN-1939
F13-HT-52X | 2000-F13-PID-PR-10011 | BALL MILL MOTOR 1 & 2 ANTI-CONDENSATION HEATER | FE | [5 empty] | 39.67 | X | X | MB_RUNNING = NOT RUNNING | MB_RUNNING = RUNNING | [10 empty] | Common motor control for F13-HT-521 & 525 | 0
[12 empty] | (F13-MB-401B Not Running) | (F13-MB-401B Running) | 1 | F13-HT-52X Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-HT-52X Fail to Start / Stop | 0 |  |  |  | X |  |  | X |  | A
[14 empty] | 3 | F13-HT-52X Drive Fault | 0 |  |  |  | X |  |  | X |  | A
[14 empty] | 4 | F13-HT-52X E-Stop | 0 |  |  |  | X | X |  | X | [8 empty] | No E-Stop Signal
[14 empty] | 5 | F13-HT-52X MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | no field signal
[14 empty] | 6 | F13-HT-52X Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F13-HT-52X Drive Ready | 0 |  |  |  | X |  |  |  |  | A
F13-FN-435 | 2000-F13-PID-PR-10011 | BALL MILL MOTOR 1 - FAN 1 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0015B Running OR | [12 empty] | A
[12 empty] | MB_OP_MODE = INCHING OR |  | 1 | F13-FN-435 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2
[12 empty] | F13-MB-401 = Running | F13-MB-401 = Not Running AND 'MB_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-435 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[13 empty] | MB_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-435 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-435 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-435 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | no field signal
[14 empty] | 6 | F13-FN-435 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-435 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-436 | 2000-F13-PID-PR-10011 | BALL MILL MOTOR 1 - FAN 2 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0015B Running OR | [12 empty] | A
[12 empty] | MB_OP_MODE = INCHING OR |  | 1 | F13-FN-436 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2
[12 empty] | F13-MB-401 = Running | F13-MB-401 = Not Running AND 'MB_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-436 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[13 empty] | MB_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-436 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-436 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-436 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | no field signal
[14 empty] | 6 | F13-FN-436 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-436 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-437 | 2000-F13-PID-PR-10011 | BALL MILL MOTOR 1 - FAN 3 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0015B Running OR | [12 empty] | A
[12 empty] | MB_OP_MODE = INCHING OR |  | 1 | F13-FN-437 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2
[12 empty] | F13-MB-401 = Running | F13-MB-401 = Not Running AND 'MB_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-437 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[13 empty] | MB_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-437 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-437 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-437 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | no field signal
[14 empty] | 6 | F13-FN-437 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-437 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-438 | 2000-F13-PID-PR-10011 | BALL MILL MOTOR 1 - FAN 4 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0015B Running OR | [12 empty] | A
[12 empty] | MB_OP_MODE = INCHING OR |  | 1 | F13-FN-438 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2
[12 empty] | F13-MB-401 = Running | F13-MB-401 = Not Running AND 'MB_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-438 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[13 empty] | MB_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-438 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-438 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-438 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | no field signal
[14 empty] | 6 | F13-FN-438 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-438 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-439 | 2000-F13-PID-PR-10011 | BALL MILL MOTOR 2 - FAN 1 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0015B Running OR | [12 empty] | A
[12 empty] | MB_OP_MODE = INCHING OR |  | 1 | F13-FN-439 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2
[12 empty] | F13-MB-401 = Running | F13-MB-401 = Not Running AND 'MB_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-439 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[13 empty] | MB_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-439 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-439 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-439 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FN-439 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-439 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-440 | 2000-F13-PID-PR-10011 | BALL MILL MOTOR 2 - FAN 2 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0015B Running OR | [12 empty] | A
[12 empty] | MB_OP_MODE = INCHING OR |  | 1 | F13-FN-440 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2
[12 empty] | F13-MB-401 = Running | F13-MB-401 = Not Running AND 'MB_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-440 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[13 empty] | MB_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-440 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-440 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-440 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FN-440 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-440 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-441 | 2000-F13-PID-PR-10011 | BALL MILL MOTOR 2 - FAN 3 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0015B Running OR | [12 empty] | A
[12 empty] | MB_OP_MODE = INCHING OR |  | 1 | F13-FN-441 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2
[12 empty] | F13-MB-401 = Running | F13-MB-401 = Not Running AND 'MB_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-441 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[13 empty] | MB_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-441 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-441 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-441 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FN-441 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-441 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-442 | 2000-F13-PID-PR-10011 | BALL MILL MOTOR 2 - FAN 4 | DOL | [5 empty] | 14.6 | X | X | F13-SEQ-0015B Running OR | [12 empty] | A
[12 empty] | MB_OP_MODE = INCHING OR |  | 1 | F13-FN-442 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2
[12 empty] | F13-MB-401 = Running | F13-MB-401 = Not Running AND 'MB_OP_MODE = NORMAL for 20 minutes | 2 | F13-FN-442 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[13 empty] | MB_OP_MODE = NORMAL (Negative Edge One Shot) AND 20 minute delay NOTE: Stop timer if fan is restarted by another condition or sequence. | 3 | F13-FN-442 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F13-FN-442 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-442 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FN-442 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-442 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-PO-521 | 2000-F13-PID-PR-10011 | BALL MILL MOTOR LUBE PUMP 1 | DOL | [5 empty] | 10.4 11.3 | X | X | F13-SEQ-0015B OR | F13-SEQ-0015B OR | [10 empty] | The motor lube pumps only need to run on mill start, stop and if motor speed < 90RPM | B
[12 empty] | F13-SEQ-0016B OR | F13-SEQ-0016B OR | 1 | F13-PO-521 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[12 empty] | MB_OP_MODE = INCHING AND DUTY SELECTED (F13MB401_FP1) OR | MB_OP_MODE = NORMAL (Negative Edge One Shot) OR | 2 | F13-PO-521 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[12 empty] | MB_STARTING = NOT STARTING AND MB_STOPPING = NOT STOPPING AND MB_RUNNING = RUNNING AND SI13150A.PV ≤ P_Lo | MB_STARTING = NOT STARTING AND MB_STOPPING = NOT STOPPING AND MB_RUNNING = RUNNING AND SI13150A.PV > P_Lo | 3 | F13-PO-521 Drive Fault | 0 |  |  |  | X |  |  |  |  | 1 | 2025-05-12 | https://pastech-2955.atlassian.net/browse/KAN-1811
[14 empty] | 4 | F13-PO-521 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-521 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-521 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-521 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13822 > A_Lo | 5 |  | X |  |  |  | X |  | F13LU421 Reservoir level | 0
[14 empty] | 9 | YA24708 Alarm | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 12/03/2025 07/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1810
[14 empty] | 10 | PSL24706 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-522 | 2000-F13-PID-PR-10011 | BALL MILL MOTOR LUBE PUMP 2 | DOL | [5 empty] | 10.4 11.3 | X | X | F13-SEQ-0015B OR | F13-SEQ-0015B OR | [10 empty] | The motor lube pumps only need to run on mill start, stop and if motor speed < 90RPM | B
[12 empty] | F13-SEQ-0016B OR | F13-SEQ-0016B OR | 1 | F13-PO-522 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[12 empty] | MB_OP_MODE = INCHING AND DUTY SELECTED (F13MB401_FP1) OR | MB_OP_MODE = NORMAL (Negative Edge One Shot) OR | 2 | F13-PO-522 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[12 empty] | MB_STARTING = NOT STARTING AND MB_STOPPING = NOT STOPPING AND MB_RUNNING = RUNNING AND SI13150A.PV ≤ P_Lo | MB_STARTING = NOT STARTING AND MB_STOPPING = NOT STOPPING AND MB_RUNNING = RUNNING AND SI13150A.PV > P_Lo | 3 | F13-PO-522 Drive Fault | 0 |  |  |  | X |  |  |  |  | 1 | 2025-05-12 | https://pastech-2955.atlassian.net/browse/KAN-1811
[14 empty] | 4 | F13-PO-522 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-522 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PO-522 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-522 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13822 > A_Lo | 5 |  | X |  |  |  | X |  | F13LU421 Reservoir level | 0
[14 empty] | 9 | YA24708 Alarm | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 12/03/2025 07/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1810
[14 empty] | 10 | PSL24706 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-FN-426 | 2000-F13-PID-PR-10011 | BALL MILL MOTOR LUBE SKID COOLER FAN | DOL | [5 empty] | 0.87 | X | X | TSH13820 Inactive | TSH13820 Active for 10 minutes | [11 empty] | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1984
[14 empty] | 1 | F13-FN-426 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FN-426 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FN-426 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FN-426 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-426 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FN-426 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-426 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | TSL13820 Active | 3 |  |  | X |  |  | X |  |  | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1984
F13-HT-427 | 2000-F13-PID-PR-10011 | BALL MILL MOTOR LUBE UNIT HEATER | FE | [5 empty] | 1.3912 | X | X | TSL13820 Active | TSL13820 Inactive for 10 minutes | [11 empty] | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1984
[14 empty] | 1 | F13-HT-427 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-HT-427 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-HT-427 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-HT-427 E-Stop | 0 |  |  |  | X | X | [10 empty] | No ESTOP
[14 empty] | 5 | F13-HT-427 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-HT-427 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-HT-427 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | TSH13820 Inactive | 3 |  |  | X |  |  | X |  |  | 1 | 2025-06-04 | https://pastech-2955.atlassian.net/browse/KAN-1984
F13-PO-534 | 2000-F13-PID-PR-10011 | BALL MILL PINION BEARING LUBE OIL PUMP 1 | DOL | [5 empty] | 6 | X | X | F13-SEQ-0011 | F13-SEQ-0012 | [11 empty] | A
[14 empty] | 1 | F13-PO-534 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-534 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-534 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-534 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-534 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Interlock not used by this drive
[14 empty] | 6 | F13-PO-534 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-534 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13874 ≤ A_LL | 5 |  |  |  | X |  | X |  | Ball Mill Lubrication System lube oil reservoir level | MOC-494
[14 empty] | 9 | F13-PO-535 Running | 0 |  |  |  | X |  | X |  | F13-PO-534 and F13-PO-535 cannot run simultaneously | MOC-494
[14 empty] | 10 | LI13874 > A_Lo | 5 |  | X |  |  |  | X |  | Ball Mill Lubrication System lube oil reservoir level | A
MOC-460
[14 empty] | 12 | F13-PO-527 & 528 Not Running | 0 |  |  | X |  |  | X |  | At least one (1) F13-PO-527 OR F13-PO-528 must be running for ≥ 5 seconds | B
[14 empty] | 13 | YA24708 Alarm | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 12/03/2025 07/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1810
[14 empty] | 14 | PSL24706 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-535 | 2000-F13-PID-PR-10011 | BALL MILL PINION BEARING LUBE OIL PUMP 2 | DOL | [5 empty] | 6 | X | X | F13-SEQ-0011 | F13-SEQ-0012 | [11 empty] | A
[14 empty] | 1 | F13-PO-535 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-535 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-535 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-535 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-535 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Interlock not used by this drive
[14 empty] | 6 | F13-PO-535 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-535 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LI13874 ≤ A_LL | 5 |  |  |  | X |  | X |  | Ball Mill Lubrication System lube oil reservoir level | MOC-494
[14 empty] | 9 | F13-PO-534 Running | 0 |  |  |  | X |  | X |  | F13-PO-534 and F13-PO-535 cannot run simultaneously | MOC-494
[14 empty] | 10 | LI13874 > A_Lo | 5 |  | X |  |  |  | X |  | Ball Mill Lubrication System lube oil reservoir level | A
MOC-460
[14 empty] | 12 | F13-PO-527 & 528 Not Running | 0 |  |  | X |  |  | X |  | At least one (1) F13-PO-527 OR F13-PO-528 must be running for ≥ 5 seconds | B
[14 empty] | 13 | YA24708 Alarm | 0 |  |  |  | X |  |  |  | Infrared heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 12/03/2025 07/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1810
[14 empty] | 14 | PSL24706 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 second dampers applied to prevent trip due to themal expansion Refer to F24-LST-PR-10001 for fire water alarm system details | MOC-410 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-MG-403 | 2000-F13-PID-PR-10005 | RECYCLE CONVEYOR 1 TRAMP MAGNET | FE | [5 empty] | 16.6945 | X | X | F13-SEQ-0023 | F13-SEQ-0024 | [10 empty] | Magnet started/stopped via XC13184 | A
[14 empty] | 1 | F13-MG-403 Comms Failure | 0 |  |  |  | X | [11 empty] | Interlock not applicable to this drive
[14 empty] | 2 | F13-MG-403 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-MG-403 Drive Fault | 0 |  |  |  | X |  |  |  | Logic: XS13182 Inactive | 1 | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1887 |  |  |  |  | Electrical need to confirm how this signal is going to work before it can be signed off.
[14 empty] | 6 | F13-MG-403 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-MG-403 Drive Ready | 0 |  |  |  | X |  |  |  | Logic: XS13180 Active | 1 | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1887
F13-MG-404 | 2000-F13-PID-PR-10005 | RECYCLE CONVEYOR 2 TRAMP MAGNET | FE | [5 empty] | 45.4924 | X | X | F13-SEQ-0023 | F13-SEQ-0024 | [10 empty] | Magnet started/stopped via XC13214 | A
[14 empty] | 1 | F13-MG-404 Comms Failure | 0 |  |  |  | X | [11 empty] | Interlock not applicable to this drive
[14 empty] | 2 | F13-MG-404 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-MG-404 Drive Fault | 0 |  |  |  | X |  |  |  | Logic: XS13212 Inactive | 1 | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1887 |  |  |  |  | Electrical need to confirm how this signal is going to work before it can be signed off.
[14 empty] | 6 | F13-MG-404 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-MG-404 Drive Ready | 0 |  |  |  | X |  |  |  | Logic: XS13210 Active | 1 | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1887
F13-CV-404 | 2000-F13-PID-PR-10005 | RECYCLE CONVEYOR 1 | VSD | 0 | 100 | % | 100 | 100 | 63.7 | X | X | F13-SEQ-0023 | F13-SEQ-0024 | [11 empty] | A
[14 empty] | 1 | F13-CV-404 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-CV-404 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-CV-404 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-CV-404 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-CV-404 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-CV-404 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-CV-404 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | BDS13168A Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 9 | BDS13168B Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | PWS13165A Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 11 | PWS13165B Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 12 | BRS13169 Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | VI13172A ≥ A_HH | 5 |  |  | X |  |  | X |  |  | A
[14 empty] | 14 | VI13172B ≥ A_HH | 5 |  |  | X |  |  | X |  |  | B
[14 empty] | 15 | YY13170 Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to F13-CV-404 start | 0
[14 empty] | 16 | SSL13166 Active AND (F13-CV-404 Running > 10 seconds) | 3 |  |  | X |  |  | X |  |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 17 | F13-CV-405 Not Running | 0 |  |  | X |  |  | X |  | Recycle Conveyor 2 | A | [6 empty] | BCK 03/07/2026 - Retested after logic changes (.MV=2). Stopped without waiting for ramp down
[14 empty] | 18 | LSH13171 Inactive | 3 |  |  | X |  |  | X |  | Recycle Conveyor 1 Head Chute blocked | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-CV-405 | 2000-F13-PID-PR-10005 | RECYCLE CONVEYOR 2 | VSD | 0 | 100 | % | 100 | 100 | 128 | X | X | F13-SEQ-0023 | F13-SEQ-0024 | [11 empty] | A
[14 empty] | 1 | F13-CV-405 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-CV-405 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-CV-405 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-CV-405 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-CV-405 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-CV-405 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-CV-405 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | BDS13193A Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 9 | BDS13193B Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | BDS13193C Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 11 | BDS13193D Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 12 | BDS13193E Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | BDS13193F Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 14 | PWS13190A Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 15 | PWS13190B Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 16 | PWS13190C Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 17 | PWS13190D Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 18 | BRS13194 Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 19 | ZS13197A Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 20 | ZS13197B Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 21 | VI13199A ≥ A_HH | 5 |  |  | X |  |  | X |  |  | B
[14 empty] | 22 | VI13199B ≥ A_HH | 5 |  |  | X |  |  | X |  |  | B
[14 empty] | 23 | YY13196A & B Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to F13-CV-405 start | 0
[14 empty] | 24 | SSL13191 Inactive AND (F13-CV-405 Running > 30 seconds) | 3 |  |  | X |  |  | X |  |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 26 | LI13221 ≥ A_HH OR LI13222 ≥ A_HH | 5 |  |  | X |  |  | X |  | Recycle Crusher Feed Bin level Bypass gate is set to open when LI13221 ≥ A_Hi OR LI13222 ≥ A_Hi (provided F13-CV-406 is running) When LI13221 ≥ A_HH or LI13222 ≥ A_HH, F13-CV-405 will interlock to trip. | A
[14 empty] | 27 | F13-CV-406 N_Running & XV13220 Not Closed | 0 |  |  | X |  |  | X |  | Logic: F13-CV-406 Not Running AND XV13220 Not Closed Recycle Crusher Discharge Conveyor stopped and Bypass gate is not closed (bypassing feed bin) | B
[14 empty] | 28 | LSH13198 Inactive | 3 |  |  | X |  |  | X |  | Recycle Conveyor 2 Head Chute blocked | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 29 | YA24717 Alarm | 0 |  |  |  | X |  |  |  | Linear heat detection alarm activated Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 12/03/2025 07/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/KAN-1810
[14 empty] | 30 | PSL24715 Inactive | 3 |  |  |  | X |  |  |  | s | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-CV-406 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER DISCHARGE CONVEYOR | VSD | 0 | 100 | % | 100 | 100 | 77.6 | X | X | F13-SEQ-0023 | F13-SEQ-0024 | [11 empty] | A
[14 empty] | 1 | F13-CV-406 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-CV-406 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-CV-406 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-CV-406 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-CV-406 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-CV-406 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-CV-406 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | BDS13353A Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 9 | BDS13353B Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | PWS13350A Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386 |  |  |  |  | MOC-237 was applied on the alarm and interlock logic
[14 empty] | 11 | PWS13350B Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386 |  |  |  |  | MOC-237 was applied on the alarm and interlock logic
[14 empty] | 12 | BRS13354 Inactive | 3 |  |  | X |  |  | X | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | VI13357A ≥ A_HH | 5 |  |  | X |  |  | X |  |  | B
[14 empty] | 14 | VI13357B ≥ A_HH | 5 |  |  | X |  |  | X |  |  | B
[14 empty] | 15 | YY13355 Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to F13-CV-406 start | 0
[14 empty] | 16 | SSL13351 Active AND (F13-CV-406 Running > 10 seconds) | 3 |  |  | X |  |  | X |  |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 17 | F13-CV-403 Not Running | 0 |  |  | X |  |  | X |  | SAG Mill Feed Conveyor | A
[14 empty] | 18 | LSH13356 Inactive | 3 |  |  | X |  |  | X |  | Recycle Conveyor 2 Head Chute blocked | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-HU-405 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER ISOLATION GATES HYDRAULIC POWER UNIT | FE | [5 empty] | 7.655 9.89 | X | [14 empty] | A | [6 empty] | Start,E-stop,drive fault, comm fault PH 18/04/2026 Not sure why other things are yellow
[14 empty] | 1 | F13-HU-405 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-HU-405 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-HU-405 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-HU-405 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-HU-405 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | VV 02/06/2026 - Not applicable
[14 empty] | 6 | F13-HU-405 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-HU-405 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LSLL13216 Inactive | 3 |  |  |  | X |  |  |  | Hydraulic reservoir low low level switch | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 9 | TSHH13216 Inactive | 3 |  |  |  | X |  |  |  | Hydraulic reservoir high high temperature switch | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | Shutdown Timer Elapsed | 0 |  |  |  | X |  |  |  | Logic: F13HU405_T3 Elapsed Refer to Misc. tab | B
[14 empty] | 11 | PSL24656 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 Second dampers applied to prevent trip due to thermal expansion Refer to F24-LST-PR-10001 for the fire alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PS-403 | 2000-F13-PID-PR-10005 | RECYCLE CRUSHER AREA SUMP PUMP | DOL SP | [5 empty] | 51.4 51.6 | X | X | LSH13209 Active | LSH13209 Inactive for 600 seconds | [11 empty] | 0
[14 empty] | 1 | F13-PS-403 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PS-403 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PS-403 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PS-403 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PS-403 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | N/A
[14 empty] | 6 | F13-PS-403 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PS-403 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-CC-401 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER C | VSD | 0 | 110 | % | 80 | 110 | 716 | X | X | F13-SEQ-0028 | F13-SEQ-0031 | [10 empty] | VSD is for starting, then runs at fixed speed (2000-ME001.6-F14-50001) | B | 2025-03-14 | Upper range was incorrectly populated (should be 110 to align with upper SV limit)
[14 empty] | 1 | F13-CC-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-CC-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-CC-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-CC-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-CC-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-CC-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-CC-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | YY13224 Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to F13-CC-401 start | 0
[14 empty] | 9 | TI13255A ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 10 | TI13255B ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 11 | TI13255C ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 12 | TI13255D ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 13 | TI13255E ≥ A_HH | 5 |  |  |  | X |  |  |  |  | B
[14 empty] | 17 | VI13254A ≥ A_HH | 5 |  |  | X |  |  | X |  |  | A
[14 empty] | 18 | VI13254B ≥ A_HH | 5 |  |  | X |  |  | X |  |  | A
[14 empty] | 19 | Calibration Command Active | 0 |  |  |  | X |  |  |  | Logic: F13CC401_CAL Active Calibration command must be inactive (see Misc sheet) | A
[14 empty] | 20 | Lube Pump Min Runtime Inactive | 0 |  |  | X |  |  | X |  | Logic: F13CC401_MRT Not Elapsed Lube pump minimimum run timer must have elapsed (see Misc sheet) | A
[14 empty] | 21 | Max CSS Alarm Active | 0 |  |  |  | X |  |  |  | Logic: F13CC401_CSS ≥ A_HH Maximum CSS threshold (see F13CC401_CSS in Analogue Input sheet) | A
[14 empty] | 22 | Min CSS Alarm Active | 0 |  |  |  | X |  |  |  | Logic: F13CC401_CSS ≤ A_LL Minimum CSS threshold (see F13CC401_CSS in Analogue Input sheet) | A
[14 empty] | 23 | SI13253 ≤ A_LL AND F13-CC-401 Running | 18 |  |  |  | X |  |  |  | Low F13-CC-401 crusher counter shaft speed | 1 | 2025-04-04 | https://pastech-2955.atlassian.net/browse/KAN-1620
[14 empty] | 24 | TI13232 ≥ A_HH | 3 |  |  | X |  |  | X |  | High F13-CC-401 countershaft temperature | 0
[14 empty] | 25 | TI13243 ≥ A_HH | 3 |  |  | X |  |  | X |  | High High F13-LU-403 oil return temperature | 0
[14 empty] | 26 | TI13243 ≥ A_Hi | 60 |  |  | X |  |  | X |  | High F13-LU-403 oil return temperature On-delay differs to alarm SV as per FLS Functional Description | A
[14 empty] | 27 | LI13268 ≤ P_Lo | 5 |  |  | X |  |  | X |  | Low F13-HU-403 hyd oil level | A | [6 empty] | test via CAL
[14 empty] | 28 | LI13241 ≤ P_Lo | 5 |  |  | X |  |  | X |  | Low F13-LU-403 lube oil level | A
[14 empty] | 29 | F13CC401_CLMP Inactive | 3 |  |  | X |  |  | X |  | F13CC401_CLMP Refer to Misc. tab | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1468
[14 empty] | 30 | F13CC401_TRMP Inactive | 3 |  |  | X |  |  | X |  | F13CC401_TRMP Refer to Misc. tab | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1468
[14 empty] | 31 | System Idle Elapsed | 0 |  |  | X |  |  | X |  | Logic: F13CC401_IDL Elapsed Crusher to interlock if idled for too long during operation | 1 | 2025-03-26 | https://pastech-2955.atlassian.net/browse/KAN-1604
[14 empty] | 32 | F13-CV-406 Not Running | 0 |  |  | X |  |  | X |  | Recycle Crusher Discharge conveyor | A
[14 empty] | 33 | FI13187 ≤ A_LL | 3 |  |  |  | X |  |  |  | Low seal water flow to Recycle Crusher C | 0
[14 empty] | 34 | F13-FV-401 Not Running AND F13-CC-401 Running | 1800 |  |  | X |  |  | X |  | Feeder not running for greater than 30 minutes (adjustable, TBC during commissioning) | 1 | 2025-04-04 | https://pastech-2955.atlassian.net/browse/KAN-1619
[14 empty] | 35 | F13-CC-401 Current ≥ A_HH | 30 |  |  |  | X |  |  |  | NOTE: HAZOP Action Item 85 | A
[14 empty] | 36 | FI13244 ≤ A_LL | 3 |  |  | X |  |  | X |  | Low F13-LU-403 lube oil flow | 0
[14 empty] | 37 | PI13233 ≤ A_LL | 3 |  |  | X |  |  | X |  | Low F13-LU-403 lube oil pressure | 0
[14 empty] | 38 | PI13263 ≤ A_LL OR PI13264 ≤ A_LL | 3 |  |  | X |  |  | X |  | Low Clamp or Tramp pressure
F13-PO-401 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER C LUBRICATION PUMP 1 | DOL | [5 empty] | 22.9 | X | X | F13-SEQ-0028 | F13-SEQ-0031 | [11 empty] | A
[14 empty] | 1 | F13-PO-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Always On bit used.
[14 empty] | 6 | F13-PO-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | HV13238 Not Open | 3 |  |  | X |  |  | X |  | F13-PO-401 Discharge valve closed | 1 | 2025-05-01 | [KAN-1484] F21 Drive Interlocks (Valve Positions) - Jira
[14 empty] | 9 | TI13242 ≤ A_LL | 3 |  |  | X |  |  | X |  | Low F13-LU-403 tank temperature | 0
[14 empty] | 10 | LI13241 ≤ A_LL | 60 |  |  | X |  |  | X |  | Low F13-LU-403 lube oil level | A
[14 empty] | 11 | FI13244 ≤ A_LL AND (F13-PO-401 Running > 10 seconds) | 3 |  |  | X |  |  | X |  | Low F13-PO-401 discharge flowrate | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 12 | PSL24656 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 Second dampers applied to prevent trip due to thermal expansion Refer to F24-LST-PR-10001 for the fire alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | YA24658 Alarm | 0 |  |  |  | X |  |  |  | Infrared Heat Detector alarm activated Refer to F24-LST-PR-10001 for the fire alarm system details | 1 | 2025-03-06 | [KAN-1467] YD24658 Interlock - Jira https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-402 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER C LUBRICATION PUMP 2 | DOL | [5 empty] | 22.9 | X | X | F13-SEQ-0028 | F13-SEQ-0031 | [11 empty] | A
[14 empty] | 1 | F13-PO-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Always On bit used.
[14 empty] | 6 | F13-PO-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | HV13239 Not Open | 3 |  |  | X |  |  | X |  | F13-PO-402 Discharge valve closed | 1 | 2025-05-01 | [KAN-1484] F21 Drive Interlocks (Valve Positions) - Jira
[14 empty] | 9 | TI13242 ≤ A_LL | 3 |  |  | X |  |  | X |  | Low F13-LU-403 tank temperature | 0
[14 empty] | 10 | LI13241 ≤ A_LL | 60 |  |  | X |  |  | X |  | Low F13-LU-403 lube oil level | A
[14 empty] | 11 | FI13244 ≤ A_LL AND (F13-PO-402 Running > 10 seconds) | 3 |  |  | X |  |  | X |  | Low F13-PO-402 discharge flowrate | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 12 | PSL24656 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 Second dampers applied to prevent trip due to thermal expansion Refer to F24-LST-PR-10001 for the fire alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | YA24658 Inactive | 0 |  |  |  | X |  |  |  | Infrared Heat Detector alarm activated Refer to F24-LST-PR-10001 for the fire alarm system details | 1 | 2025-03-06 | [KAN-1467] YD24658 Interlock - Jira https://pastech-2955.atlassian.net/browse/KAN-1386
F13-HT-40X | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER C LUBRICATION HEATER 1, 2, 3 & 4 | FE | [5 empty] | 11.128 | X | X | TI13242 ≤ P_Lo | TI13242 ≥ P_Hi | [10 empty] | Common motor control for F13-HT-403, 404, 451 & 452 | 0
[14 empty] | 1 | F13-HT-40X Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-HT-40X Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0 | [6 empty] | N/A
[14 empty] | 3 | F13-HT-40X Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-HT-40X E-Stop | 0 |  |  |  | X | X |  |  |  | 0 | [6 empty] | N/A
[14 empty] | 5 | F13-HT-40X MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | N/A
[14 empty] | 6 | F13-HT-40X Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-HT-40X Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | TI13242 ≥ A_HH | 3 |  |  | X |  |  | X |  | High F13-LU-403 tank temperature | 0
[14 empty] | 9 | LI13241 ≤ A_Lo | 3 |  |  | X |  |  | X |  | Low F13-LU-403 lube oil level | 0
F13-FN-457 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER C LUBRICATION AIR COOLER 1 | DOL | [5 empty] | 15 | X | X | TI13243 ≥ P_Hi | TI13243 ≤ P_Lo | [11 empty] | A
[14 empty] | 1 | F13-FN-457 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FN-457 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FN-457 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FN-457 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-457 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | N/A
[14 empty] | 6 | F13-FN-457 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-457 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-458 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER C LUBRICATION AIR COOLER 2 | DOL | [5 empty] | 15 | X | X | TI13243 ≥ P_Hi | TI13243 ≤ P_Lo | [11 empty] | A
[14 empty] | 1 | F13-FN-458 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FN-458 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FN-458 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FN-458 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-458 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FN-458 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-458 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-PO-408 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER C HYDRAULIC PUMP | DOL | [5 empty] | 21.3 | X | X | YS13273 Active OR | (YS13273 Inactive AND | [11 empty] | A
[12 empty] | YS13271A Active OR | YS13271A Inactive AND | 1 | F13-PO-408 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[12 empty] | YS13272A Active OR | YS13272A Inactive AND | 2 | F13-PO-408 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[12 empty] | YS13271B Active OR | YS13271B Inactive AND | 3 | F13-PO-408 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[12 empty] | YS13272B Active OR | YS13272B Inactive AND | 4 | F13-PO-408 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[12 empty] | YS13275 Active OR | YS13275 Inactive AND | 5 | F13-PO-408 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Always On bit used.
[12 empty] | YS13276 Active OR | YS13276 Inactive) OR | 6 | F13-PO-408 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[12 empty] | F13CC401_HPU and HS13279ASTT Active | F13CC401_HPU and HS13279BSTP Active | 7 | F13-PO-408 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-PO-408 Running AND F13-SEQ-0029 Not Running | 300 |  |  |  | X |  |  | X | Continuous pressurisation | 1 | 6/03/2025 06/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1468 https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-308?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC |  |  |  |  | Desktop Review
[14 empty] | 9 | LI13268 ≤ A_LL | 60 |  |  | X |  |  | X |  | Low F13-HU-403 hydraulic oil level | A | [6 empty] | tested by CAL
[14 empty] | 10 | TI13267 ≥ A_HH | 5 |  |  | X |  |  | X |  | High F13-HU-403 hydraulic oil temperature | A | [6 empty] | tested by CAL
[14 empty] | 11 | PS13265 Inactive | 3 |  |  | X |  |  | X |  | Bowl fully closed | 1 | 1 | 1
[14 empty] | 12 | PS13266 Inactive | 3 |  |  | X |  |  | X |  | Bowl fully opened | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | PSL24656 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 Second dampers applied to prevent trip due to thermal expansion Refer to F24-LST-PR-10001 for the fire alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 14 | YA24658 Inactive | 0 |  |  |  | X |  |  |  | Infrared Heat Detector alarm activated Refer to F24-LST-PR-10001 for the fire alarm system details | 1 | 2025-05-06 | https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-308?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
F13-FV-401 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER C FEEDER | DVSD | 0 | 100 | % | 40 | 100 | 19.4 | X | X | LI13221 ≥ P_H AND F13-SEQ-0031 Not Running | LI13221 ≤ P_LL | [11 empty] | A
[14 empty] | 1 | F13-FV-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FV-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FV-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FV-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FV-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FV-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FV-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | Calibration Command Active | 0 |  |  |  | X |  |  |  | Logic: F13CC401_CAL Active Calibration command is active (see Misc sheet) | A
[14 empty] | 9 | Bowl Creep Alarm Active | 0 |  |  | X |  |  | X |  | Logic: F13CC401_CRP Active Bowl creep alarm (see Misc sheet) | A
[14 empty] | 10 | Crusher Min Runtime Active | 0 |  | X |  |  |  | X |  | Logic (Healthy): F13CC401_T2 Elapsed Crusher Minimum Run Time | A
[14 empty] | 11 | LIC13223 ≥ A_HH | 5 |  |  | X |  |  | X |  | High F13-CH-461 chute level | A
[14 empty] | 12 | VI13256 ≥ A_HH | 10 |  |  | X |  |  | X |  | High F13-CC-401 vibration 1 | A
[14 empty] | 13 | VI13257 ≥ A_HH | 10 |  |  | X |  |  | X |  | High F13-CC-401 vibration 2 | A
[14 empty] | 14 | VI13258 ≥ A_HH | 10 |  |  | X |  |  | X |  | High F13-CC-401 vibration 3 | A
[14 empty] | 15 | VI13259 ≥ A_HH | 10 |  |  | X |  |  | X |  | High F13-CC-401 vibration 4 | A
[14 empty] | 16 | SI13253 ≤ A_Lo AND F13-CC-401 Running | 10 |  |  |  | X |  |  |  | Low F13-CC-401 crusher counter shaft speed | 1 | 2025-04-04 | https://pastech-2955.atlassian.net/browse/KAN-1620
[14 empty] | 17 | TI13232 ≥ A_Hi | 3 |  |  | X |  |  | X |  | High F13-CC-401 countershaft temperature | 0
[14 empty] | 18 | TI13243 ≥ P_HH | 3 |  |  |  | X |  |  |  | High F13-LU-403 lube oil return temperature | 0
[14 empty] | 19 | LI13241 ≤ A_Lo | 3 |  |  | X |  |  | X |  | Low F13-LU-403 lube oil level | 0
[14 empty] | 20 | TDI13247 ≥ A_HH | 600 |  |  | X |  |  | X |  | High F13-LU-403 supply to return lube oil differential temperature | A
[14 empty] | 21 | FI13244 ≤ P_Lo | 3 |  |  | X |  |  | X |  | Low F13-LU-403 lube oil flow | 0
[14 empty] | 22 | PI13233 ≤ P_Lo | 3 |  |  | X |  |  | X |  | Low F13-LU-403 lube oil pressure | 0
[14 empty] | 23 | LI13268 ≤ A_Lo | 3 |  |  | X |  |  | X |  | Low F13-HU-403 hydraulic oil level | 0 | [6 empty] | tested by CAL
[14 empty] | 24 | PI13263 ≤ A_Lo | 180 |  |  | X |  |  | X |  | Low F13-HU-403 clamping pressure On-delay differs to alarm SV as per FLS Functional Description | A
[14 empty] | 25 | PI13263 ≤ A_LL | 5 |  |  |  | X |  |  |  | Low F13-HU-403 clamping pressure | A
[14 empty] | 26 | PI13264 ≤ A_Lo | 300 |  |  | X |  |  | X |  | Low F13-HU-403 tramping pressure On-delay differs to alarm SV as per FLS Functional Description | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1453
[14 empty] | 27 | PI13264 ≤ A_LL | 5 |  |  |  | X |  |  |  | Low F13-HU-403 tramping pressure | A
[14 empty] | 28 | TI13267 ≥ A_HH | 5 |  |  |  | X |  |  |  | High F13-HU-403 hydraulic oil temperature | A | [6 empty] | tested by CAL
[14 empty] | 29 | F13-CV-406 Not Running | 0 |  |  | X |  |  | X |  | Recycle Crusher Discharge conveyor | 0
[14 empty] | 30 | F13-CC-401 Not Running | 0 |  |  | X |  |  | X |  | Recycle Crusher C | 0
[14 empty] | 31 | LI13221 ≤ A_LL | 5 |  |  | X |  |  | X |  | Recycle Crusher Feed Bin C side | A
[14 empty] | 32 | FI13187 ≤ A_Lo | 3 |  |  | X |  |  | X |  | Low seal water flow to Recycle Crusher C | 0
[14 empty] | 33 | F13-CC-401 Current ≥ A_Hi | 30 |  |  |  | X |  |  |  | NOTE: HAZOP Action Item 85 | B
F13-CC-402 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER D | VSD | 0 | 110 | % | 80 | 110 | 716 | X | X | F13-SEQ-0033 | F13-SEQ-0036 | [10 empty] | VSD is for starting, then runs at fixed speed (2000-ME001.6-F14-50001) | B | 2025-03-14 | Upper range was incorrectly populated (should be 110 to align with upper SV limit)
[14 empty] | 1 | F13-CC-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-CC-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-CC-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-CC-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-CC-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F13-CC-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | YY13228 Healthy | 0 |  | X |  |  |  | X |  | Sound for 10 seconds prior to F13-CC-402 start | 0
[14 empty] | 9 | TI13315A ≥ A_HH | 5 |  |  |  | X |  |  |  |  | A
[14 empty] | 10 | TI13315B ≥ A_HH | 5 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-CC-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 11 | TI13315C ≥ A_HH | 5 |  |  |  | X |  |  |  |  | A
[14 empty] | 12 | TI13315D ≥ A_HH | 5 |  |  |  | X |  |  |  |  | A
[14 empty] | 13 | TI13315E ≥ A_HH | 5 |  |  |  | X |  |  |  |  | A
[14 empty] | 17 | VI13314A ≥ A_HH | 5 |  |  | X |  |  | X |  |  | A
[14 empty] | 18 | VI13314B ≥ A_HH | 5 |  |  | X |  |  | X |  |  | A
[14 empty] | 19 | Calibration Command Active | 0 |  |  |  | X |  |  |  | Logic: F13CC402_CAL Active Calibration command must be inactive (see Misc sheet) | A
[14 empty] | 20 | Lube Pump Min Runtime Inactive | 0 |  |  | X |  |  | X |  | Logic: F13CC402_MRTNot Elapsed Lube pump minimimum run timer must have elapsed (see Misc sheet) | A
[14 empty] | 21 | Max CSS Alarm Active | 0 |  |  |  | X |  |  |  | Logic: F13CC402_CSS ≥ A_HH Maximum CSS threshold (see F13CC402_CSS in Analogue Input sheet) | A
[14 empty] | 22 | Min CSS Alarm Active | 0 |  |  |  | X |  |  |  | Logic: F13CC402_CSS ≤ A_LL Minimum CSS threshold (see F13CC402_CSS in Analogue Input sheet) | A
[14 empty] | 23 | SI13313 ≤ A_LL AND F13-CC-402 Running | 18 |  |  |  | X |  |  |  | Low F13-CC-402 crusher counter shaft speed | 2 | 2025-04-04 | https://pastech-2955.atlassian.net/browse/KAN-1620 |  |  |  |  | Speed Instrument Scaled in DCS
[14 empty] | 24 | TI13282 ≥ A_HH | 3 |  |  | X |  |  | X |  | High F13-CC-402 countershaft temperature | 0
[14 empty] | 25 | TI13303 ≥ A_HH | 3 |  |  | X |  |  | X |  | High High F13-LU-404 oil return temperature | 0
[14 empty] | 26 | TI13303 ≥ A_Hi | 60 |  |  | X |  |  | X |  | High F13-LU-404 oil return temperature On-delay differs to alarm SV as per FLS Functional Description | A
[14 empty] | 27 | LI13328 ≤ P_Lo | 5 |  |  | X |  |  | X |  | Low F13-HU-404 hyd oil level | A
[14 empty] | 28 | LI13301 ≤ P_Lo | 5 |  |  | X |  |  | X |  | Low F13-LU-404 lube oil level | A
[14 empty] | 29 | F13CC402_CLMP Inactive | 3 |  |  | X |  |  | X |  | F13CC402_CLMP Refer to Misc. tab | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1468
[14 empty] | 30 | F13CC402_TRMP Inactive | 3 |  |  | X |  |  | X |  | F13CC402_TRMP Refer to Misc. tab | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1468
[14 empty] | 31 | System Idle Elapsed | 0 |  |  | X |  |  | X |  | Logic: F13CC402_IDL Elapsed Crusher to interlock if idled for too long during operation | 1 | 2025-03-26 | https://pastech-2955.atlassian.net/browse/KAN-1604
[14 empty] | 32 | F13-CV-406 Not Running | 0 |  |  | X |  |  | X |  | Recycle Crusher Discharge conveyor | A
[14 empty] | 33 | FI13294 ≤ A_LL | 3 |  |  |  | X |  |  |  | Low seal water flow to Recycle Crusher D | 0
[14 empty] | 34 | F13-FV-402 Not Running AND F13-CC-402 Running | 1800 |  |  | X |  |  | X |  | Feeder not running for greater than 30 minutes (adjustable, TBC during commissioning) | 1 | 2025-04-04 | https://pastech-2955.atlassian.net/browse/KAN-1619
[14 empty] | 35 | F13-CC-402 Current ≥ A_HH | 30 |  |  |  | X |  |  |  | NOTE: HAZOP Action Item 85 | A
[14 empty] | 36 | FI13304 ≤ A_LL | 3 |  |  | X |  |  | X |  | Low F13-LU-404 lube oil flow | 0
[14 empty] | 37 | PI13283 ≤ A_LL | 3 |  |  | X |  |  | X |  | Low F13-LU-404 lube oil pressure | 0
[14 empty] | 38 | PI13323 ≤ A_LL OR PI13324 ≤ A_LL | 3 |  |  | X |  |  | X |  | Low Clamp or Tramp pressure
F13-PO-406 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER D LUBRICATION PUMP 1 | DOL | [5 empty] | 22.9 | X | X | F13-SEQ-0033 | F13-SEQ-0036 | [11 empty] | A
[14 empty] | 1 | F13-PO-406 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-406 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-406 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-406 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-406 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Always On bit used.
[14 empty] | 6 | F13-PO-406 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-406 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | HV13298 Not Open | 3 |  |  | X |  |  | X |  | F13-PO-401 Discharge valve closed | 1 | 2025-05-01 | [KAN-1484] F21 Drive Interlocks (Valve Positions) - Jira
[14 empty] | 9 | TI13302 ≤ A_LL | 3 |  |  | X |  |  | X |  | Low F13-LU-404 tank temperature | 0
[14 empty] | 10 | LI13301 ≤ A_LL | 60 |  |  | X |  |  | X |  | Low F13-LU-404 lube oil level | A
[14 empty] | 11 | FI13304 ≤ A_LL AND (F13-PO-406 Running > 10 seconds) | 3 |  |  | X |  |  | X |  | Low Low F13-PO-406 discharge flowrate | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 12 | PSL24656 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 Second dampers applied to prevent trip due to thermal expansion Refer to F24-LST-PR-10001 for the fire alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | YA24658 Inactive | 0 |  |  |  | X |  |  |  | Infrared Heat Detector alarm activated Refer to F24-LST-PR-10001 for the fire alarm system details | 1 | 2025-03-06 | [KAN-1467] YD24658 Interlock - Jira https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PO-407 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER D LUBRICATION PUMP 2 | DOL | [5 empty] | 22.9 | X | X | F13-SEQ-0033 | F13-SEQ-0036 | [11 empty] | A
[14 empty] | 1 | F13-PO-407 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PO-407 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PO-407 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PO-407 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PO-407 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | Always On bit used.
[14 empty] | 6 | F13-PO-407 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PO-407 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | HV13299 Inactive | 3 |  |  | X |  |  | X |  | F13-PO-402 Discharge valve closed | 1 | 2025-05-01 | [KAN-1484] F21 Drive Interlocks (Valve Positions) - Jira
[14 empty] | 9 | TI13302 ≤ A_LL | 3 |  |  | X |  |  | X |  | Low F13-LU-404 tank temperature | 0
[14 empty] | 10 | LI13301 ≤ A_LL | 60 |  |  | X |  |  | X |  | Low F13-LU-404 lube oil level | A
[14 empty] | 11 | FI13304 ≤ A_LL AND (F13-PO-407 Running > 10 seconds) | 3 |  |  | X |  |  | X |  | Low Low F13-PO-407 discharge flowrate | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 12 | PSL24656 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 Second dampers applied to prevent trip due to thermal expansion Refer to F24-LST-PR-10001 for the fire alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | YA24658 Inactive | 0 |  |  |  | X |  |  |  | Infrared Heat Detector alarm activated Refer to F24-LST-PR-10001 for the fire alarm system details | 1 | 2025-03-06 | [KAN-1467] YD24658 Interlock - Jira https://pastech-2955.atlassian.net/browse/KAN-1386
F13-HT-40XX | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER D LUBRICATION HEATER 1, 2, 3 & 4 | FE | [5 empty] | 11.128 | X | X | TI13302 ≤ P_Lo | TI13302 ≥ P_Hi | [10 empty] | Common motor control for F13-HT-405, 406, 453 & 454 | 0
[14 empty] | 1 | F13-HT-40XX Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-HT-40XX Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0 | [6 empty] | N/A
[14 empty] | 3 | F13-HT-40XX Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-HT-40XX E-Stop | 0 |  |  |  | X | X |  |  |  | 0 | [6 empty] | N/A
[14 empty] | 5 | F13-HT-40XX MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | N/A
[14 empty] | 6 | F13-HT-40XX Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-HT-40XX Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | TI13302 ≥ A_HH | 3 |  |  | X |  |  | X |  | High F13-LU-404 tank temperature | 0
[14 empty] | 9 | LI13301 ≤ A_Lo | 3 |  |  | X |  |  | X |  | Low F13-LU-404 lube oil level | 0
F13-FN-459 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER D LUBRICATION AIR COOLER 1 | DOL | [5 empty] | 15 | X | X | [13 empty] | A | [6 empty] | verified by means of logic tracing and PI
[12 empty] | TI13303 ≥ P_Hi | TI13303 ≤ P_Lo | 1 | F13-FN-459 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FN-459 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FN-459 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FN-459 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-459 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FN-459 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-459 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-FN-460 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER D LUBRICATION AIR COOLER 2 | DOL | [5 empty] | 15 | X | X | [13 empty] | A
[12 empty] | TI13303 ≥ P_Hi | TI13303 ≤ P_Lo | 1 | F13-FN-460 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FN-460 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-FN-460 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-FN-460 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-FN-460 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FN-460 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-FN-460 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-PO-409 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER D HYDRAULIC PUMP | DOL | [5 empty] | 21.3 | X | X | YS13333 Active OR | (YS13333 Inactive AND | [11 empty] | A
[12 empty] | YS13331A Active OR | YS13331A Inactive AND | 1 | F13-PO-409 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[12 empty] | YS13334A Active OR | YS13334A Inactive AND | 2 | F13-PO-409 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[12 empty] | YS13331B Active OR | YS13331B Inactive AND | 3 | F13-PO-409 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[12 empty] | YS13334B Active OR | YS13334B Inactive AND | 4 | F13-PO-409 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[12 empty] | YS13335 Active OR | YS13335 Inactive AND | 5 | F13-PO-409 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[12 empty] | YS13336 Active OR | YS13336 Inactive) OR | 6 | F13-PO-409 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[12 empty] | F13CC402_HPU and HS13343ASTT Active | F13CC402_HPU and HS13343BSTP Active | 7 | F13-PO-409 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-PO-409 Running AND F13-SEQ-0034 Not Running | 300 |  |  |  | X |  |  | X | Continuous pressurisation | 1 | 6/03/2025 6/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1468 https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-308?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC |  |  |  |  | Desktop Review
[14 empty] | 9 | LI13328 ≤ A_LL | 60 |  |  | X |  |  | X |  | Low F13-HU-404 hydraulic oil level | A | [6 empty] | tested via CAL
[14 empty] | 10 | TI13327 ≥ A_HH | 5 |  |  | X |  |  | X |  | High F13-HU-404 hydraulic oil temperature | A | [6 empty] | tested via CAL
[14 empty] | 11 | PS13325 Inactive | 3 |  |  | X |  |  | X |  | Bowl fully closed | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1389 |  |  |  |  | Housekeeping - PIL removed.
[14 empty] | 12 | PS13326 Inactive | 3 |  |  | X |  |  | X |  | Bowl fully opened | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1389 |  |  |  |  | Housekeeping - PIL removed.
[14 empty] | 13 | PSL24656 Inactive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated 3 Second dampers applied to prevent trip due to thermal expansion Refer to F24-LST-PR-10001 for the fire alarm system details | 1 | 2025-03-12 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 14 | YA24658 Inactive | 0 |  |  |  | X |  |  |  | Infrared Heat Detector alarm activated Refer to F24-LST-PR-10001 for the fire alarm system details | 1 | 2025-05-06 | https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-308?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
F13-FV-402 | 2000-F13-PID-PR-10006 | RECYCLE CRUSHER D FEEDER | DVSD | 0 | 100 | % | 40 | 100 | 19.4 | X | X | LI13222 ≥ P_HH AND F13-SEQ-0036 Not Running | LI13222 ≤ P_Lo | [11 empty] | 1 | 2025-05-08 | https://pastech-2955.atlassian.net/browse/PL-315?focusedCommentId=11683&page=com.atlassian.jira.plugin.system.issuetabpanels%253Acomment-tabpanel%23comment-11683
[14 empty] | 1 | F13-FV-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-FV-402 Fail to Start / Stop | 0 |  |  |  | X |  |  | X |  | A
[14 empty] | 3 | F13-FV-402 Drive Fault | 0 |  |  |  | X |  |  | X |  | A
[14 empty] | 4 | F13-FV-402 E-Stop | 0 |  |  |  | X | X |  | X |  | A
[14 empty] | 5 | F13-FV-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-FV-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F13-FV-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 8 | Calibration Command Active | 0 |  |  |  | X |  |  |  | Logic: F13CC402_CAL Active Calibration command is active (see Misc sheet) | A
[14 empty] | 9 | Bowl Creep Alarm Active | 0 |  |  | X |  |  | X |  | Logic: F13CC402_CRP Active Bowl creep alarm (see Misc sheet) | A
[14 empty] | 10 | Crusher Min Runtime Active | 0 |  | X |  |  |  | X |  | Logic (Healthy): F13CC402_T2 Elapsed Crusher Minimum Run Time | A
[14 empty] | 11 | LIC13227 ≥ A_HH | 5 |  |  | X |  |  | X |  | High F13-CH-464 chute level | A
[14 empty] | 12 | VI13316 ≥ A_HH | 10 |  |  | X |  |  | X |  | High F13-CC-402 vibration 1 | A
[14 empty] | 13 | VI13317 ≥ A_HH | 10 |  |  | X |  |  | X |  | High F13-CC-402 vibration 2 | A
[14 empty] | 14 | VI13318 ≥ A_HH | 10 |  |  | X |  |  | X |  | High F13-CC-402 vibration 3 | A
[14 empty] | 15 | VI13319 ≥ A_HH | 10 |  |  | X |  |  | X |  | High F13-CC-402 vibration 4 | A
[14 empty] | 17 | SI13313 ≤ A_Lo AND F13-CC-402 Running | 10 |  |  |  | X |  |  |  | Low F13-CC-402 crusher counter shaft speed | 2 | 2025-04-04 | https://pastech-2955.atlassian.net/browse/KAN-1620
[14 empty] | 18 | TI13282 ≥ A_Hi | 3 |  |  | X |  |  | X |  | High F13-CC-402 countershaft temperature | 0
[14 empty] | 19 | TI13303 ≥ P_HH | 3 |  |  |  | X |  |  |  | High F13-LU-404 lube oil return temperature | 0
[14 empty] | 20 | LI13301 ≤ A_Lo | 3 |  |  | X |  |  | X |  | Low F13-LU-404 lube oil level | 0
[14 empty] | 21 | TDI13307 ≥ A_HH | 600 |  |  | X |  |  | X |  | High F13-LU-404 supply to return lube oil differential temperature | A
[14 empty] | 22 | FI13304 ≤ P_Lo | 3 |  |  | X |  |  | X |  | Low F13-LU-404 lube oil flow | 0
[14 empty] | 23 | PI13283 ≤ P_Lo | 3 |  |  | X |  |  | X |  | Low F13-LU-404 lube oil pressure | 0
[14 empty] | 24 | LI13328 ≤ A_Lo | 3 |  |  | X |  |  | X |  | Low F13-HU-404 hydraulic oil level | 0
[14 empty] | 25 | PI13323 ≤ A_Lo | 180 |  |  | X |  |  | X |  | Low F13-HU-404 clamping pressure On-delay differs to alarm SV as per FLS Functional Description | A
[14 empty] | 26 | PI13323 ≤ A_LL | 5 |  |  |  | X |  |  |  | Low F13-HU-404 clamping pressure | A
[14 empty] | 27 | PI13324 ≤ A_Lo | 300 |  |  | X |  |  | X |  | Low F13-HU-404 tramping pressure On-delay differs to alarm SV as per FLS Functional Description | A
[14 empty] | 28 | PI13324 ≤ A_LL | 5 |  |  |  | X |  |  |  | Low F13-HU-404 tramping pressure | A
[14 empty] | 29 | TI13327 ≥ A_HH | 5 |  |  |  | X |  |  |  | High F13-HU-404 hydraulic oil temperature | A | [6 empty] | tested via cal
[14 empty] | 30 | F13-CV-406 Not Running | 0 |  |  | X |  |  | X |  | Recycle Crusher Discharge conveyor | 0
[14 empty] | 31 | F13-CC-402 Not Running | 0 |  |  | X |  |  | X |  | Recycle Crusher D | 0
[14 empty] | 32 | LI13222 ≤ A_LL | 5 |  |  | X |  |  | X |  | Recycle Crusher Feed Bin D side | A
[14 empty] | 33 | FI13294 ≤ A_Lo | 3 |  |  | X |  |  | X |  | Low seal water flow to Recycle Crusher D | 0
[14 empty] | 34 | F13-CC-402 Current ≥ A_Hi | 30 |  |  |  | X |  |  |  | NOTE: HAZOP Action Item 85 | B
F13-PS-409 | 2000-F13-PID-PR-10007 | TRASH SCREEN AREA SUMP PUMP | DOL SP | [5 empty] | 51.4 51.6 | X | X | LSH13385 Active | LSH13385 Inactive for 600 seconds | [11 empty] | 0
[14 empty] | 1 | F13-PS-409 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PS-409 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PS-409 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PS-409 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PS-409 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PS-409 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PS-409 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F13-SC-403 | 2000-F13-PID-PR-10007 | TRASH DEWATERING SCREEN | DDOL | [5 empty] | 19.4 | X | X | F13-SEQ-0005 | F13-SEQ-0006 | [11 empty] | A
[14 empty] | 1 | F13-SC-403 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-SC-403 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-SC-403 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-SC-403 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-SC-403 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-SC-403 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-SC-403 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | XS24679A Inactive | 0 |  |  |  | X |  |  |  | Fire alarm detected through FIP24679 Refer to F24-LST-PR-10001 for fire water alarm system details | 1 | 2025-03-06 | Design change, fire water updates
F13-PP-403 | 2000-F13-PID-PR-10007 | TRASH DEWATERING SCREEN UNDERFLOW PUMP | VSD | 0 | 100 | % | 80 | 100 | 183 | X | X | F13-SEQ-0005 | F13-SEQ-0006 | [11 empty] | 2 | [6 empty] | JDM 23/07: Increased ML to achieve min flow to distribution box
[14 empty] | 1 | F13-PP-403 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PP-403 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PP-403 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PP-403 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PP-403 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PP-403 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PP-403 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LIC13381 ≤ A_LL | 5 |  |  | X |  |  | X |  | Low F13-HP-402 level | 1 | 2025-05-07 | https://pastech-2955.atlassian.net/browse/KAN-1806
[14 empty] | 9 | FSL13465 Inactive AND (F13-PP-403 Running) | 30 |  |  | X |  |  | X |  | Low Gland Water Flow Switch | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | SV13464 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland Water Valve in auto or open | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/PL-174
[14 empty] | 11 | XV13382 Closed | 3 |  |  | X |  |  | X |  | F13-PP-403 Suction Valve closed | 0
[14 empty] | 12 | XV13383 Opened | 3 |  |  | X |  |  | X |  | F13-PP-403 Suction Drain Valve opened | 0
F13-SL-401 | 2000-F13-PID-PR-10007 | TRASH SCREEN 1 | DOL | [5 empty] | 21.3 | X | X | F13-SEQ-0007 | F13-SEQ-0008 | [11 empty] | A
[14 empty] | 1 | F13-SL-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-SL-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-SL-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-SL-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-SL-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  | Not Applicable - JM 31/05/2026 | A
[14 empty] | 6 | F13-SL-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-SL-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | SAL13366 Alarm AND (F13-SL-401 Running) | 30 |  |  | X |  |  | X | X | Speed monitoring via DCS (signal active per rotation). To interlock at zero speed as per Delkor FD. Setpoint TBC during commissioning. | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 9 | BDS13367C Inactive | 3 |  |  | X |  |  | X |  |  | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | BDS13367D Inactive | 3 |  |  | X |  |  | X |  |  | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 11 | PWS13365A Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 12 | PWS13365B Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | PWS13365C Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 14 | PWS13365D Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 15 | PSL13368 Inactive | 15 |  |  | X |  |  | X |  | Process Water sprays to Trash Screen | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 16 | PSL13370 Inactive | 15 |  |  | X |  |  | X |  | Process Water sprays to Trash Screen | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 17 | PSL13369 Inactive | 300 |  |  | X |  |  | X |  | Instrument Air to Trash Screen | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-SL-402 | 2000-F13-PID-PR-10007 | TRASH SCREEN 2 | DOL | [5 empty] | 21.3 | X | X | F13-SEQ-0007 | F13-SEQ-0008 | [11 empty] | A
[14 empty] | 1 | F13-SL-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-SL-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-SL-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-SL-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-SL-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  | Not Applicable - JM 31/05/2026 | A
[14 empty] | 6 | F13-SL-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-SL-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | SAL13376 Alarm AND (F13-SL-402 Running) | 30 |  |  | X |  |  | X | X | Speed monitoring via DCS (signal active per rotation). To interlock at zero speed as per Delkor FD. Setpoint TBC during commissioning. | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 9 | BDS13377C Inactive | 3 |  |  | X |  |  | X |  |  | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | BDS13377D Inactive | 3 |  |  | X |  |  | X |  |  | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 11 | PWS13375A Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 12 | PWS13375B Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | PWS13375C Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 14 | PWS13375D Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 15 | PSL13378 Inactive | 15 |  |  | X |  |  | X |  | Process Water sprays to Trash Screen | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 16 | PSL13380 Inactive | 15 |  |  | X |  |  | X |  | Process Water sprays to Trash Screen | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 17 | PSL13379 Inactive | 300 |  |  | X |  |  | X |  | Instrument Air to Trash Screen | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-SL-403 | 2000-F13-PID-PR-10008 | TRASH SCREEN 3 | DOL | [5 empty] | 21.3 | X | X | F13-SEQ-0007 | F13-SEQ-0008 | [11 empty] | A
[14 empty] | 1 | F13-SL-403 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-SL-403 Fail to Start / Stop | 0 |  |  |  | X |  |  |  | Not Applicable - JM 31/05/2026 | 0
[14 empty] | 3 | F13-SL-403 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-SL-403 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-SL-404 MCC Unhealthy | 0 |  |  |  | X |  |  |  | Not Applicable - JM 31/05/2026 | A
[14 empty] | 6 | F13-SL-403 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-SL-403 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | SAL13396 Alarm AND( F13-SL-403 Running) | 30 |  |  | X |  |  | X | X | Speed monitoring via DCS (signal active per rotation). To interlock at zero speed as per Delkor FD. Setpoint TBC during commissioning. | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 9 | BDS13397C Inactive | 3 |  |  | X |  |  | X |  |  | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | BDS13397D Inactive | 3 |  |  | X |  |  | X |  |  | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 11 | PWS13395A Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 12 | PWS13395B Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | PWS13395C Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 14 | PWS13395D Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 15 | PSL13398 Inactive | 15 |  |  | X |  |  | X |  | Process Water sprays to Trash Screen | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 16 | PSL13400 Inactive | 15 |  |  | X |  |  | X |  | Process Water sprays to Trash Screen | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 17 | PSL13399 Inactive | 300 |  |  | X |  |  | X |  | Instrument Air to Trash Screen | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-SL-404 | 2000-F13-PID-PR-10008 | TRASH SCREEN 4 | DOL | [5 empty] | 21.3 | X | X | F13-SEQ-0007 | F13-SEQ-0008 | [11 empty] | A
[14 empty] | 1 | F13-SL-404 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-SL-404 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-SL-404 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-SL-404 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-SL-404 MCC Unhealthy | 0 |  |  |  | X |  |  |  | Not Applicable - JM 31/05/2026 | A
[14 empty] | 6 | F13-SL-404 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-SL-404 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | SAL13406 Alarm AND (F13-SL-404 Running) | 30 |  |  | X |  |  | X | X | Speed monitoring via DCS (signal active per rotation). To interlock at zero speed as per Delkor FD. Setpoint TBC during commissioning. | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1390
[14 empty] | 9 | BDS13407C Inactive | 3 |  |  | X |  |  | X |  |  | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 10 | BDS13407D Inactive | 3 |  |  | X |  |  | X |  |  | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 11 | PWS13405A Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 12 | PWS13405B Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | PWS13405C Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 14 | PWS13405D Inactive | 0 |  |  |  | X | X |  | X |  | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 15 | PSL13394 Inactive | 15 |  |  | X |  |  | X |  | Process Water sprays to Trash Screen | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 16 | PSL13408 Inactive | 15 |  |  | X |  |  | X |  | Process Water sprays to Trash Screen | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 17 | PSL13404 Inactive | 300 |  |  | X |  |  | X |  | Instrument Air to Trash Screen | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-CU-402 | 2000-F13-PID-PR-10012 | CHILLER 1 | FE | [5 empty] | 632.0246 | X | X | F13-SEQ-0001 | F13-SEQ-0002 | [11 empty] | A
[14 empty] | 1 | F13-CU-402 Comms Failure | 0 |  |  |  | X |  |  |  | looks at PV.BAD of ready signal. AP - 30/07/2026 | A
[14 empty] | 2 | F13-CU-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-CU-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F13-CU-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-CU-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-CU-402 In Duty Mode | 0 |  | X |  |  |  | X |  | See F13CU400_FP1 Misc tab | 1 | 2025-05-02 | https://pastech-2955.atlassian.net/browse/KAN-1787
[14 empty] | 9 | HV13442 Open | 3 |  | X |  |  |  | X |  | Chiller discharge valve must be in fully open position to start | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 10 | HV13442 Closed | 3 |  |  | X |  |  | X |  |  | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 11 | XV13441 Closed | 3 |  |  | X |  |  | X |  | Chiller suction valve must be opened | 0
[14 empty] | 12 | F13-PW-416 AND F13-PW-415 Not Running | 5 |  |  |  | X |  |  |  | A Chiller Recirculaton Pump must be running | 2
F13-CU-403 | 2000-F13-PID-PR-10012 | CHILLER 2 | FE | [5 empty] | 632.0246 | X | X | F13-SEQ-0001 | F13-SEQ-0002 | [11 empty] | A
[14 empty] | 1 | F13-CU-403 Comms Failure | 0 |  |  |  | X |  |  |  | looks at PV.BAD of ready signal. AP - 30/07/2026 | A
[14 empty] | 2 | F13-CU-403 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-CU-403 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F13-CU-403 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-CU-403 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-CU-403 In Duty Mode | 0 |  | X |  |  |  | X |  | See F13CU400_FP1 Misc tab | 1 | 2025-05-02 | https://pastech-2955.atlassian.net/browse/KAN-1787
[14 empty] | 9 | HV13444 Open | 3 |  | X |  |  |  | X |  | Chiller discharge valve must be in fully open position to start | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 10 | HV13444 Closed | 3 |  |  | X |  |  | X |  |  | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 11 | XV13441 Closed | 3 |  |  | X |  |  | X |  | Chiller suction valve must be opened | 0
[14 empty] | 12 | F13-PW-416 AND F13-PW-415 Not Running | 5 |  |  |  | X |  |  |  | A Chiller Recirculaton Pump must be running | 2
F13-CU-404 | 2000-F13-PID-PR-10012 | CHILLER 3 | FE | [5 empty] | 632.0246 | X | X | F13-SEQ-0001 | F13-SEQ-0002 | [11 empty] | A
[14 empty] | 1 | F13-CU-404 Comms Failure | 0 |  |  |  | X |  |  |  | looks at PV.BAD of ready signal. AP - 30/07/2026 | A
[14 empty] | 2 | F13-CU-404 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-CU-404 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F13-CU-404 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-CU-404 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F13-CU-404 In Duty Mode | 0 |  | X |  |  |  | X |  | See F13CU400_FP1 Misc tab | 1 | 2025-05-02 | https://pastech-2955.atlassian.net/browse/KAN-1787
[14 empty] | 9 | HV13446 Open | 3 |  | X |  |  |  | X |  | Chiller discharge valve must be in fully open position to start | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 10 | HV13446 Closed | 3 |  |  | X |  |  | X |  |  | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 11 | XV13441 Closed | 3 |  |  | X |  |  | X |  | Chiller suction valve must be opened | 0
[14 empty] | 12 | F13-PW-416 AND F13-PW-415 Not Running | 5 |  |  |  | X |  |  |  | A Chiller Recirculaton Pump must be running | 2
F13-CU-405 | 2000-F13-PID-PR-10012 | CHILLER 4 | FE | [5 empty] | 632.0246 | X | X | F13-SEQ-0001 | F13-SEQ-0002 | [11 empty] | A
[14 empty] | 1 | F13-CU-405 Comms Failure | 0 |  |  |  | X |  |  |  | looks at PV.BAD of ready signal. AP - 30/07/2026 | A
[14 empty] | 2 | F13-CU-405 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-CU-405 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 6 | F13-CU-405 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-CU-405 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | XV13441 Closed | 3 |  |  | X |  |  | X |  | Chiller suction valve must be opened | 0
[14 empty] | 9 | HV13448 Open | 3 |  | X |  |  |  | X |  | Chiller discharge valve must be in fully open position to start | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 10 | HV13448 Closed | 3 |  |  | X |  |  | X |  |  | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 11 | XV13441 Closed | 3 |  |  | X |  |  | X |  | Chiller suction valve must be opened | 0
[14 empty] | 12 | F13-PW-416 AND F13-PW-415 Not Running | 5 |  |  |  | X |  |  |  | A Chiller Recirculaton Pump must be running | 2
F13-PW-413 | 2000-F13-PID-PR-10012 | COOLING WATER PUMP 1 | DOL | [5 empty] | 300 | X | X | F13-SEQ-0001 | F13-SEQ-0002 | [11 empty] | A
[14 empty] | 1 | F13-PW-413 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PW-413 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PW-413 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PW-413 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PW-413 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | N/A 10/06/2026 - Always on bit - 30/07/2026
[14 empty] | 6 | F13-PW-413 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PW-413 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | HV13422 Closed | 3 |  |  | X |  |  | X |  | F13-PW-413 Suction Valve must not be in closed position | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 9 | HV13422 Open | 3 |  | X |  |  |  | X |  | F13-PW-413 Suction Valve must be in open position to start pump | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 10 | HV13423 Closed | 3 |  |  | X |  |  | X |  | F13-PW-413 Discharge Valve must not be in closed position | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 11 | HV13423 Open | 3 |  | X |  |  |  | X |  | F13-PW-413 Discharge Valve must be in open position to start pump | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 12 | LI13426 ≤ A_LL | 5 |  |  | X |  |  | X |  | Cooling Water Tanks level low | B
[14 empty] | 13 | FSLL13436 Inactive AND (F13-PW-413 Running) | 30 |  |  | X |  |  | X |  | Common discharge flow switch low low | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PW-414 | 2000-F13-PID-PR-10012 | COOLING WATER PUMP 2 | DOL | [5 empty] | 300 | X | X | F13-SEQ-0001 | F13-SEQ-0002 | [11 empty] | A
[14 empty] | 1 | F13-PW-414 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PW-414 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PW-414 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PW-414 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PW-414 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A | [6 empty] | N/A 10/06/2026 - Always on bit - 30/07/2026
[14 empty] | 6 | F13-PW-414 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PW-414 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | HV13424 Closed | 3 |  |  | X |  |  | X |  | F13-PW-414 Suction Valve must not be in closed position | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 9 | HV13424 Open | 3 |  | X |  |  |  | X |  | F13-PW-414 Suction Valve must be in open position to start pump | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 10 | HV13425 Closed | 3 |  |  | X |  |  | X |  | F13-PW-414 Discharge Valve must not be in closed position | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 11 | HV13425 Open | 3 |  | X |  |  |  | X |  | F13-PW-414 Discharge Valve must be in open position to start pump | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 12 | LI13426 ≤ A_LL | 5 |  |  | X |  |  | X |  | Cooling Water Tanks level low | B
[14 empty] | 13 | FSLL13436 Inactive AND (F13-PW-414 Running) | 30 |  |  | X |  |  | X |  | Common discharge flow switch low low | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
F13-PW-415 | 2000-F13-PID-PR-10012 | CHILLER RECIRCULATING WATER PUMP 1 | DOL | [5 empty] | 76.6 | X | X | F13-SEQ-0001 | F13-SEQ-0002 | [11 empty] | A
[14 empty] | 1 | F13-PW-415 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PW-415 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PW-415 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PW-415 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PW-415 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PW-415 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PW-415 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | HV13431 Closed | 3 |  |  | X |  |  | X |  | F13-PW-415 Suction Valve must not be in closed position | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 9 | HV13431 Open | 3 |  | X |  |  |  | X |  | F13-PW-415 Suction Valve must be in open position to start pump | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 10 | HV13432 Closed | 3 |  |  | X |  |  | X |  | F13-PW-415 Discharge Valve must not be in closed position | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 11 | HV13432 Open | 3 |  | X |  |  |  | X |  | F13-PW-415 Discharge Valve must be in open position to start pump | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 12 | FSLL13435 Inactive AND (F13-PW-415 Running) | 30 |  |  | X |  |  | X |  | Common discharge flow switch low low | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | Chiller Valves Unhealthy | 3 |  |  | X |  |  | X |  | Logic: XV13441 Closed OR ZSC13442 Active AND XV13443 Closed OR ZSC13444 Active AND XV13445 Closed OR ZSC13446 Active AND XV13447 Closed OR ZSC13448 Active Minimum of 1 set of Chiller suction and discharge valves must be opened to prevent deadhead | 0
[14 empty] | 14 | LI13430 ≤ A_LL | 5 |  |  | X |  |  | X |  | Chiller Tank (F13-TK-407) level low | B
F13-PW-416 | 2000-F13-PID-PR-10012 | CHILLER RECIRCULATING WATER PUMP 2 | DOL | [5 empty] | 76.6 | X | X | F13-SEQ-0001 | F13-SEQ-0002 | [11 empty] | A
[14 empty] | 1 | F13-PW-416 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F13-PW-416 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F13-PW-416 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F13-PW-416 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F13-PW-416 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F13-PW-416 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 7 | F13-PW-416 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | HV13433 Closed | 3 |  |  | X |  |  | X |  | F13-PW-416 Suction Valve must not be in closed position | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 9 | HV13433 Open | 3 |  | X |  |  |  | X |  | F13-PW-416 Suction Valve must be in open position to start pump | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 10 | HV13434 Closed | 3 |  |  | X |  |  | X |  | F13-PW-416 Discharge Valve must not be in closed position | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 11 | HV13434 Open | 3 |  | X |  |  |  | X |  | F13-PW-416 Discharge Valve must be in open position to start pump | 1 | 2025-05-01 | https://pastech-2955.atlassian.net/browse/KAN-1484
[14 empty] | 12 | FSLL13435 Inactive AND (F13-PW-416 Running) | 30 |  |  | X |  |  | X |  | Common discharge flow switch low low | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
[14 empty] | 13 | Chiller Valves Unhealthy | 3 |  |  | X |  |  | X |  | Logic: XV13441 Closed OR ZSC13442 Active AND XV13443 Closed OR ZSC13444 Active AND XV13445 Closed OR ZSC13446 Active AND XV13447 Closed OR ZSC13448 Active Minimum of 1 set of Chiller suction and discharge valves must be opened to prevent deadhead | 0
[14 empty] | 14 | LI13430 ≤ A_LL | 5 |  |  | X |  |  | X |  | Chiller Tank (F13-TK-407) level low | B
F13-FN-451 | - | SAG MILL LUBE ROOM FAN (INDUCTION) | DOL | [6 empty] | X | [14 empty] | 1 | 2025-06-17 | CR-016 IC013 Change Register |  |  |  |  | FLC not verified DCS set as 3.4A running current was 2.7A
[14 empty] | 1 | F13-FN-451 Comms Failure | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 2 | F13-FN-451 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 3 | F13-FN-451 Drive Fault | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 4 | F13-FN-451 E-Stop | 0 |  |  |  | X | X |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 5 | F13-FN-451 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 6 | F13-FN-451 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register |  |  |  |  | Desktop Review - Inbuilt drive template feature.
[14 empty] | 7 | F13-FN-451 Drive Ready | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
F13-FN-452 | - | SAG MILL LUBE ROOM FAN (EXTRACTION) | VSD | 0 | 100 | % | 40 | 100 |  | X | [14 empty] | 1 | 2025-06-17 | CR-016 IC013 Change Register |  |  |  |  | FLC not verified DCS set as 4.3A 100% running current was 2.4A
[14 empty] | 1 | F13-FN-452 Comms Failure | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 2 | F13-FN-452 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 3 | F13-FN-452 Drive Fault | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 4 | F13-FN-452 E-Stop | 0 |  |  |  | X | X |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 5 | F13-FN-452 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 6 | F13-FN-452 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 7 | F13-FN-452 Drive Ready | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
F13-FN-453 | - | BALL MILL LUBE ROOM FAN (INDUCTION) | DOL | [6 empty] | X | [14 empty] | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 1 | F13-FN-453 Comms Failure | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 2 | F13-FN-453 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 3 | F13-FN-453 Drive Fault | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[10 empty] | 1 |  |  |  | 4 | F13-FN-453 E-Stop | 0 |  |  |  | X | X |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 5 | F13-FN-453 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 6 | F13-FN-453 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 7 | F13-FN-453 Drive Ready | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
F13-FN-454 | - | BALL MILL LUBE ROOM FAN (EXTRACTION) | VSD | 0 | 100 | % | 40 | 100 |  | X | [14 empty] | 1 | 2025-06-17 | CR-016 IC013 Change Register |  |  |  |  | FLC not verified
[14 empty] | 1 | F13-FN-454 Comms Failure | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 2 | F13-FN-454 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 3 | F13-FN-454 Drive Fault | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 4 | F13-FN-454 E-Stop | 0 |  |  |  | X | X |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 5 | F13-FN-454 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 6 | F13-FN-454 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
[14 empty] | 7 | F13-FN-454 Drive Ready | 0 |  |  |  | X |  |  |  |  | 1 | 2025-06-17 | CR-016 IC013 Change Register
F13-HT-420 | - | CYCLONE FEED PUMP MOTOR SPACE HEATER | DOL | [5 empty] | 4.96 | X |  | F13-PP-401 NOT RUNNING | F13-PP-401 RUNNING | [10 empty] | Drive missed initially - PAStech PL-155 | 1
[14 empty] | 1 | F13-HT-420 Comms Failure | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 2 | F13-HT-420 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 3 | F13-HT-420 Drive Fault | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 4 | F13-HT-420 E-Stop | 0 |  |  |  | X | X | [10 empty] | No e-Stop
[14 empty] | 5 | F13-HT-420 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 1 | [6 empty] | Always on bit
[14 empty] | 6 | F13-HT-420 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 1 | [6 empty] | Out of service needs to be added to faceplate
[14 empty] | 7 | F13-HT-420 Drive Ready | 0 |  |  |  | X |  |  |  |  | 1
119

## 10. Sequence
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - MILLING & CLASSIFICATION (F13)
2000-F13-LST-PR-10001
SEQUENCES
Seq No. | Seq Description | Step | Action | Tag / Item | Description | Next Step Delay (s) | Step Advance Condition | Comments | Rev | Equipment Permissives | Recovery Seq. No if Step Faults
PLEASE REFER TO SEQUENCE FLOWCHART DOCUMENT (2000-F13-LST-PR-10002)
0

## 11. Calculation
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - MILLING & CLASSIFICATION (F13)
2000-F13-LST-PR-10001
CALCULATIONS
|  |  | Unit | Inputs |  |  |  | Operator Input | Calc. Value | Manual Input | [7 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Description (Software Tag Only) |  | # | Tag | Unit | Description |  |  | Nom | Min | Max | Calculation | Comments | Rev | Change Date | Change Reference | OK | Date | OK | Date
F13CALC10001 | 2000-F13-PID-PR-10001 | F13BLC401 Ball Index |  | 1 | F13BLC401_Parameter_1 | kg/t | F13MS401 Ball/Feed Ratio | X |  | 0.4 | 0 | 1 | Tonnage required for 1x Mill Ball: 'F13BLC401_Parameter_2 / F13BLC401_Parameter_1 = F13BLC401_Parameter_5 Minus F13BLC401_Parameter_5 from Totaliser for each Mill Ball successfully indexed: Minus F13BLC401_Parameter_5 from F13BLC401_FT totaliser value every time ZI13035 = True for one shot (Rising-Edge Trigger). Calculate balls required based off Totaliser value (for indication purposes): ( F13BLC401_Parameter_1 * F13BLC401_FT ) / F13BLC401_Parameter_2 = F13BLC401_Parameter_3 Calculate instantaneous mill ball addition rate: ( F13BLC401_C1 * F13BLC401_Parameter_2 / 1000 ) / (F13BLC401_T2.PV / 60) = WI13035.PV In addition to the above, if F13-BLC-401 indexer is in MANUAL mode: 1. CRO enters the weight of balls required F13BLC401_Parameter_6. 2. F13BLC401_Parameter_6 / F13BLC401_Parameter_2 = F13BLC401_Parameter_4 3. F13-BLC-401 indexer is started manually by the CRO. 4. If F13BLC401_C1 >= F13BLC401_Parameter_4, F13-BLC-401 is interlocked (see Drives) If F13-BLC-401 = Not Running (falling-edge) Set F13BLC401_Parameter_6 to 0 (one shot) | F13BLC401_FT, F13BLC401_C1, F13BLC401_T1 and F13BLC401_T2 are defined in the Misc tab. Engineer-level access only. | 1 | 2025-05-02 | https://pastech-2955.atlassian.net/browse/PL-302
|  |  |  | 2 | F13BLC401_Parameter_2 | kg | F13BLC401 Ball Wt 125mm | X |  | 8.04 | 0 | 20 |  | Engineer-level access only.
|  |  |  | 3 | F13BLC401_Parameter_3 | # | F13BLC401 Balls Req. Aut |  | X |  |  |  |  | F13-BLC-401 AUTO: The F13-BLC-401 indexer starts when F13BLC401_T1 elapses. The F13-BLC-401 indexer stops when F13BLC401_FT <= 0. See Drives tab
|  |  |  | 4 | F13BLC401_Parameter_4 | # | F13BLC401 Balls Req Man |  | X
|  |  |  | 5 | F13BLC401_Parameter_5 | t | F13MS401 Feed/Ball |  | X
|  |  |  | 6 | F13BLC401_Parameter_6 | kg | F13BLC401 Balls Req Man | X |  | 100 | - | - |  | Assumed F13BLC401_T2 is in minutes. Please convert calculations accordingly. Engineer-level access only.
|  |  |  | 6 | F13BLC401_T2 | minutes | F13BLC401 IndexerRuntime | [6 empty] | Indexer Runtime. See Misc tab.
|  |  |  | 7 | F13BLC401_FT | t | F13MS401 Feed Totaliser | [6 empty] | Totalise WI13090.PV to F13BLC401_FT. See Misc tab.
|  |  |  | 8 | F13BLC401_C1 | # | F13BLC401 Balls Indexed |  | X |  |  |  |  | Counter conditions in Misc tab.
|  |  |  | 9 | WI13035.PV | t/h | F13BLC401 Ball Tonnage |  | X |  |  |  |  | WI13035.PV used in F13CALC10002.
F13CALC10002 | 2000-F13-PID-PR-10001 | F13CV403 Dry Tonnes |  | 1 | WI13055.PV | t/h | F13CV403 SAG Feed Wet | [5 empty] | (WI13055.PV * (1-(FreshOre_Parameter_1/100))) - WI13035.PV = WIC13121.PV | F13-CV-403 wet tonnes, minus ore moisture and ball addition tonnage | 1 | 2025-05-01 | Fixed copy paste error
|  |  |  | 2 | FreshOre_Parameter_1 | % | Fresh Ore & Sprays | X |  | 5 | 0 | 10 |  | Engineer-level access only.
|  |  |  | 3 | WIC13121.PV | t/h | F13CV403 SAG Feed Dry |  | X | 180 |  |  |  | WI13035.PV calculated in F13CALC10001
|  |  |  | 4 | WI13035.PV | t/h | F13BLC401 Ball Tonnage | [6 empty] | A delay is required on WI13035.PV to account for the distance between the SAG Mill Ball Charger and WE13055 weightometer element (TBC during commissioning).
F13CALC10003 | 2000-F13-PID-PR-10001 | F13FA411/412/414 Ratio |  | 1 | WIC13121.MV | % | WIC13121 PID Output | [5 empty] | WIC13121 to have split, direct acting outputs to Feeder F13-FA-411, F13-FA-412 and F13-FA-414 VSD speeds. CRO can input a ratio value for each Feeder, which adjusts the respective Feeder speed relative to WIC13121.MV output. E.g., if the output of WIC13121.MV is calling for a 50% Feeder VSD speed and the ratio is set to 0.8, the final Feeder VSD speed is 40% (50% * 0.8). | Duty Feeders are selected on Faceplate: F13FA400_FP1 (see Misc tab). | 1
|  |  |  | 2 | F13FA411_Parameter_1 | - | F13FA411 VSD Speed Ratio | X |  | 0.5 | 0 | 1 |  | WIC13121 Output to standby Feeders are ignored. |  | 2025-05-01 | Updated to align with DCS programming. No action
|  |  |  | 3 | F13FA412_Parameter_1 | - | F13FA412 VSD Speed Ratio | X |  | 0.5 | 0 | 1 |  |  |  | 2025-05-01 | Updated to align with DCS programming. No action
|  |  |  | 4 | F13FA414_Parameter_1 | - | F13FA414 VSD Speed Ratio | X |  | 0 | 0 | 1 |  |  |  | 2025-05-01 | Updated to align with DCS programming. No action
F13CALC10004 | 2000-F13-PID-PR-10002 | F13CY401 O/flow Density |  | 1 | WI13121B.PV | t/h | F16 Fresh Feed Solids | [5 empty] | IF OVERFLOW (PSA) IS SELECTED ON HS13090 DO THIS CALCULATION: 1. Calculate Solids % Concentration of slurry at the Flotation PSA (F16-AN-402): ((XI16172.PV - F13CY401_Parameter_2) / (F13CY401_Parameter_1 - F13CY401_Parameter_2)) * (F13CY401_Parameter_1 / XI16172.PV) = F16AN402_Parameter_2 2. Calculate total slurry flowrate from Trash Screens Final Collection Box (F13-BX-415): WI13121B.PV / F16AN402_Parameter_2 = F16SA401_Parameter_1 3. Calculate total water added to slurry at Trash Screens, Trash Dewatering Screen and Final Collection Box (in tph): (FI13363.PV + FI13373.PV + FI13403.PV + FI13393.PV + FI13359.PV + F13SC403_Parameter_1) * F13CY401_Parameter_2 = F16SA401_Parameter_2 4. Calculate Cyclone (F13-CY-401) overflow density: WI13121B.PV / (F16SA401_Parameter_1 - F16SA401_Parameter_2) = DNIC13090B.PV IF OVERFLOW (CALC) IS SELECTED ON HS13090 DO THIS CALCULATION: DNIC13090B.PV = WI13121B.PV / (WI13121B.PV + (WI13121B.PV - DNIC13090B.SV * WI13121B.PV) / DNIC13090B.SV) WATER_REQ = (WI13121B.PV - DNIC13090B.SV * WI13121B.PV) / DNIC13090B.SV / F13CY401_Parameter_2 DNIC13090B.MV = WATER_REQ - (FIC13071.PV + FIC13121.PV + FIC13143 .PV + FIC13141 .PV + FIC13123.PV + FI13363.PV + FI13373.PV + FI13403.PV + FI13393.PV + FI13359.PV + F13SC403_Parameter_1 + F16SA401_Parameter_2) | Calculated in F13CALC10034 | 1 | 2025-03-06 | PCT alignment action register (density transmitters to align with F16,17,18)
|  |  |  | 2 | FI13363.PV | m3/h | F13SL401 Spray Water
|  |  |  | 3 | FI13373.PV | m3/h | F13SL402 Spray Water
|  |  |  | 4 | FI13403.PV | m3/h | F13SL403 Spray Water
|  |  |  | 5 | FI13393.PV | m3/h | F13SL404 Spray Water
|  |  |  | 6 | FI13359.PV | m3/h | F13BX415 Motive Water
|  |  |  | 7 | F13SC403_Parameter_1 | m3/h | F13SC403 Spray Water | X |  | 15 | 0 | 20 |  | Assumed WI13121B will equal Cyclone OF solids (dry) at steady state Engineer-level access only. No flowmeter for F13SC403_Parameter_1. Operator input estimate.
|  |  |  | 8 | F13CY401_Parameter_1 | SG | F13CY401 Solids SG | X |  | 2.89 | 2.5 | 3.3 |  | Engineer-level access only.
|  |  |  | 9 | F13CY401_Parameter_2 | SG | F13CY401 Solution SG | X |  | 1.07 | 0.8 | 1.2 |  | F13SC403_Parameter_1 = 0 if XV13374 is closed Engineer-level access only.
|  |  |  | 10 | XI16172.PV | SG | F16AN402 Slurry SG | [6 empty] | Flotation Feed Slurry SG as measured by the Particle Size Analyser
|  |  | CPV1 | 11 | F16AN402_Parameter_2 | % solids | F16AN402 Slurry % Solids |  | X
|  |  | CPV2 | 12 | F16SA401_Parameter_1 | t/h | Rougher Feed Slurry |  | X
|  |  | CPV3 | 13 | F16SA401_Parameter_2 | t/h | Trash Screen Water Addition |  | X
|  |  | CPV | 14 | DNIC13090B.PV | % solids | F13CY401 OF % Solids |  | X | [6 empty] | 2025-03-06 | PCT alignment action register (density transmitters to align with F16,17,18)
|  |  |  | 15 | WATER_REQ | m3/h | Total Water Required
|  |  |  | 16 | DNIC13090B.SV | % solids | F13CY401 OF % Solids
|  |  |  | 17 | FIC13071.PV | m3/h | F13SC401 PW Spray
|  |  |  | 18 | FIC13121.PV | m3/h | F13MS401 Feed Water
|  |  |  | 19 | FIC13143 .PV | m3/h | F13SC402 PW Spray
|  |  |  | 20 | FIC13141 .PV | m3/h | F13MB401 Feed Water
|  |  |  | 21 | FIC13123.PV | m3/h | F13SC404 PW Spray
F13CALC10006 | 2000-F13-PID-PR-10002 | F13CY401 Dry Tonnes |  | 1 | DI13090.PV | t/m3 | F13CY401 Feed Density SG | [5 empty] | 100* ((DI13090.PV - F13CY401_Parameter_2) / (F13CY401_Parameter_1 - F13CY401_Parameter_2)) * (F13CY401_Parameter_1 / DI13090.PV) = DNIC13090A.PV ( DI13090.PV * FI13090.PV ) * ( DNIC13090A.PV / 100 ) = WI13090.PV | Use F13CY401_Parameter_1 and F13CY401_Parameter_2 value from F13CALC10004 | 1 | 2025-03-06 | PCT alignment action register (density transmitters to align with F16,17,18)
|  |  |  | 2 | DNIC13090A.PV | % solids | F13CY401 Feed Density |  | X | [6 empty] | 2025-03-06 | PCT alignment action register (density transmitters to align with F16,17,18)
|  |  |  | 3 | FIC13090.PV | m3/h | F13CY401 Feed Flowrate
|  |  |  | 4 | WI13090.PV | t/h | F13CY401 Dry Tonnes |  | X
F13CALC10007 | 2000-F13-PID-PR-10002 | F13PP401 Pressure Ctrl | [10 empty] | VALVE OPEN/CLOSE CONDITIONS: If (LIC13076B.PV >= LIC13076B.SV + LIC13076B_Deadband AND F13-PP-401 = RUNNING) for LIC13076B_OnDelay seconds: Open 1x CYCLONE FEED VALVE If (LIC13076B.PV <= LIC13076B.SV - LIC13076B_Deadband and F13-PP-401 = RUNNING) for LIC13076B_OnDelay seconds: Close 1x CYCLONE FEED VALVE |  | 1 | 7/04/2025 19/06/2025 | Cyclones design change following F28 FAT. https://pastech-2955.atlassian.net/browse/KAN-2064
|  |  |  | 1 | LIC13076B.PV | % | F13HP401 Level PV | [6 empty] | Operating with HS13092 = Pressure Control |  | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | 2 | LIC13076B.SV | % | F13HP401 Level SV | [6 empty] | Refer to F13CY401_FP1 for Cyclone Feed Valve open/close priority system Engineer-level access only. |  | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | 3 | LIC13076B_Deadband | % | F13HP401 Deadband Range | X |  | 5 | 0 | 20 |  | Deadbands to be determined during commissioning to ensure valves do not frequently cycle open/close |  | 2025-04-07 | Cyclones design change following F28 FAT.
|  |  |  | 4 | LIC13076B_OnDelay | s | LIC13076B Deadband Timer | X |  | 60 | 0 | 300 |  | Include an x second (TBC during commissioning) delay timer must elapse between the opening and/or closing of Cyclone Feed Valves Engineer-level access only. |  | 2025-04-07 | Cyclones design change following F28 FAT.
F13CALC10011 | 2000-F13-PID-PR-10002 | F13PP401 Level Control |  | 1 | PIC13092.PV | kPa | F13CY401 Pressure PV | [5 empty] | VALVE OPEN/CLOSE CONDITIONS: If (PIC13092.PV >= PIC13092.SV + PIC13092_Deadband AND F13-PP-401 = RUNNING) for PIC13092_OnDelay seconds: Open 1x CYCLONE FEED VALVE If (PIC13092.PV <= PIC13092.SV - PIC13092_Deadband AND F13-PP-401 = RUNNING) for PIC13092_OnDelay seconds: Close 1x CYCLONE FEED VALVE | Operating with HS13092 = Level Control | 1 | 7/04/2025 19/05/2025 19/06/2025 | Cyclones design change following F28 FAT. PCT alignment kPag to kPa https://pastech-2955.atlassian.net/browse/KAN-2064
|  |  |  | 2 | PIC13092.SV | kPa | F13CY401 Pressure SV | [6 empty] | Refer to F13CY401_FP1 for Cyclone Feed Valve open/close priority system Engineer-level access only. |  | 7/04/2025 19/05/2025 | Cyclones design change following F28 FAT. PCT alignment kPag to kPa
|  |  |  | 3 | PIC13092_Deadband (Y) | kPa | F13CY401 Deadband (Y) | X |  | 5 | 0 | 20 |  |  |  | 7/04/2025 19/05/2025 | Cyclones design change following F28 FAT. PCT alignment kPag to kPa
|  |  |  | 4 | PIC13092_OnDelay | s | PIC13092 Deadband Timer | X |  | 60 | 0 | 300 |  | Deadbands to be determined during commissioning to ensure valves do not frequently cycle open/close Include an x second (TBC during commissioning) delay timer must elapse between the opening and/or closing of Cyclone Feed Valves Engineer-level access only. |  | 2025-04-07 | Cyclones design change following F28 FAT.
F13CALC10008 | 2000-F13-PID-PR-10003 | F13MS401 Fd Water Ratio |  | 1 | F13MS401_Parameter_1 | m3/t | F13MS401 Water/FeedRatio | X |  | 0.3 | 0 | 1 | F13MS401_Parameter_1 * (WIC13121.PV) = FIC13121.SV | Engineer-level access only. | 0
|  |  |  | 2 | WIC13121.PV | t/h | F13CV403 SAG Feed Dry
|  |  |  | 3 | FIC13121.SV | m3/h | F13MS401 Feed Water |  | X |  |  |  |  | HS13121 set to select SAG Mill Feed Water to Solids ratio control. See Misc. tab
F13CALC10009 | 2000-F13-PID-PR-10003 | F13MS401 Fd Water Dnsity |  | 1 | WI13055.PV | t/h | F13CV403 SAG Feed Wet | [5 empty] | 1. Calculate Moisture Feed Rate from Ore & Pebbles to SAG Mill: (WI13055.PV - WIC13121) + (WI13195.PV * ( Pebbles_Parameter_1 / 100) ) = F13MS401_Parameter_2 2. Calculate Solid Feed Rate of Ore & Pebbles to SAG Mill: WIC13121.PV + (WI13195.PV * ( 1 - ( Pebbles_Parameter_1 / 100 ))) = F13MS401_Parameter_3 3. Calculate water required to achieve F13MS401_Parameter_4 % solids setpoint (entered by CRO) and input to Feed Water controller: ((F13MS401_Parameter_3 / (F13MS401_Parameter_4 / 100)) - F13MS401_Parameter_3 - F13MS401_Parameter_2) / F13MS401_Parameter_5 = FIC13121.SV |  | 0
|  |  |  | 2 | WIC13121.PV | t/h | F13CV403 SAG Feed Dry
|  |  |  | 3 | WI13195.PV | t/h | F13CV405 RC Feed Wet
|  |  |  | 4 | Pebbles_Parameter_1 | % moisture | F13CV406 Pebbles | X |  | 13 | 0 | 20 |  | Engineer-level access only.
|  |  |  | 5 | F13MS401_Parameter_2 | t/h | SAG Moisture Feed Rate |  | X
|  |  |  | 6 | F13MS401_Parameter_3 | t/h | SAG Solid Feed Rate |  | X
|  |  |  | 7 | F13MS401_Parameter_4 | % solids | F13MS401 D/C % Solids | X |  | 75 | 0 | 100 |  | Engineer-level access only.
|  |  |  | 8 | F13MS401_Parameter_5 | SG | F13MS401 Solution SG | X |  | 1.07 | 0.8 | 1.2 |  | Engineer-level access only.
|  |  |  | 9 | FIC13121.SV | m3/h | F13MS401 Feed Water |  | X |  |  |  |  | HS13121 Faceplate to select SAG Mill Discharge Density control
F13CALC10010 | 2000-F13-PID-PR-10006 | F13LU403 Lube Oil dT 1 |  | 1 | TI13247.PV | °C | F13LU403 Lube Oil Supply | [5 empty] | abs(TI13243.PV - TI13247.PV) = TDI13247.PV | Calculate differential temperature on supply and return oil temperature indicators. | 0
|  |  |  | 2 | TI13243.PV | °C | F13LU403 Lube Oil Return | [6 empty] | Calculate as absolute value
|  |  |  | 3 | TDI13247.PV | °C | F13LU403 Lube Oil dT 1 |  | X
F13CALC10012 | 2000-F13-PID-PR-10006 | F13LU403 Lube Filter dP |  | 1 | PI13237.PV | kPa | F13LU403 Fltr Upstream | [5 empty] | abs(PI13237.PV - PI13236.PV) = PDI13237.PV | Calculate differential pressure across filter. | 0
|  |  |  | 2 | PI13236.PV | kPa | F13LU403 Fltr Downstream | [6 empty] | Calculate as absolute value
|  |  |  | 3 | PDI13237.PV | kPa | F13LU403 Lube Filter dP |  | X
F13CALC10013 | 2000-F13-PID-PR-10006 | F13LU404 Lube Oil dT 1 |  | 1 | TI13307.PV | °C | F13LU404 Lube Oil Supply | [5 empty] | abs(TI13303.PV - TI13307.PV) = TDI13307.PV | Calculate differential temperature on supply and return oil temperature indicators. | 0
|  |  |  | 2 | TI13303.PV | °C | F13LU404 Lube Oil Return | [6 empty] | Calculate as absolute value
|  |  |  | 3 | TDI13307.PV | °C | F13LU404 Lube Oil dT 1 |  | X
F13CALC10015 | 2000-F13-PID-PR-10006 | F13LU404 Lube Filter dP |  | 1 | PI13296.PV | kPa | F13LU404 Fltr Upstream | [5 empty] | abs(PI13297.PV - PI13296.PV) = PDI13296.PV | Calculate differential pressure across filter. | 0
|  |  |  | 2 | PI13297.PV | kPa | F13LU404 Fltr Downstream | [6 empty] | Calculate as absolute value
|  |  |  | 3 | PDI13296.PV | kPa | F13LU404 Lube Filter dP |  | X
F13CALC10016 | 2000-F13-PID-PR-10010 | F13MS401A Pin. Gear dT |  | 1 | TI13511.PV | °C | F13MS401 Pin. Flank R 1 | [5 empty] | abs(TI13514.PV - TI13511.PV) = TDI13511.PV | Calculate the difference between outermost (feed and discharge end) pinion gear flank temperatures. | 0
|  |  |  | 2 | TI13514.PV | °C | F13MS401 Pin. Flank R 4 | [6 empty] | Calculate as absolute value
|  |  |  | 3 | TDI13511.PV | °C | F13MS401 Pin. Gear R dT |  | X
F13CALC10017 | 2000-F13-PID-PR-10010 | F13MS401B Pin. Gear dT |  | 1 | TI13515.PV | °C | F13MS401 Pin. Flank L 1 | [5 empty] | abs(TI13520.PV - TI13515.PV) = TDI13515.PV | Calculate the difference between outermost (feed and discharge end) pinion gear flank temperatures. | 0 | [6 empty] | TI13515 field instrument has an issue and currently in IOP-
|  |  |  | 2 | TI13520.PV | °C | F13MS401 Pin. Flank L 4 | [6 empty] | Calculate as absolute value | [7 empty] | Tested using CAL mode
|  |  |  | 3 | TDI13515.PV | °C | F13MS401 Pin. Gear L dT |  | X
F13CALC10018 | 2000-F13-PID-PR-10010 | F13MS401 Fd TrnBrgR dT |  | 1 | TI13712A.PV | °C | F13MS401 Feed Trn R OB | [5 empty] | abs(Max(TI13712A.PV, TI13712B.PV, TI13712C.PV) - Min(TI13712A.PV, TI13712B.PV, TI13712C.PV)) = TDI13712.PV | Calculate the difference between the highest and lowest temperature of the three signals. | 0
|  |  |  | 2 | TI13712B.PV | °C | F13MS401 Feed Trn R Ctr | [6 empty] | Calculate as absolute value
|  |  |  | 3 | TI13712C.PV | °C | F13MS401 Feed Trn R IB
|  |  |  | 4 | TDI13712.PV | °C | F13MS401 Fd TrnBrgR dT |  | X
F13CALC10019 | 2000-F13-PID-PR-10010 | F13MS401 Dsch TrnBrgR dT |  | 1 | TI13716A.PV | °C | F13MS401 Dsch Trn R OB | [5 empty] | abs(Max(TI13716A.PV, TI13716B.PV, TI13716C.PV) - Min(TI13716A.PV, TI13716B.PV, TI13716C.PV)) = TDI13716.PV | Calculate the difference between the highest and lowest temperature of the three signals. | 0
|  |  |  | 2 | TI13716B.PV | °C | F13MS401 Dsch Trn R Ctr | [6 empty] | Calculate as absolute value
|  |  |  | 3 | TI13716C.PV | °C | F13MS401 Dsch Trn R IB
|  |  |  | 4 | TDI13716.PV | °C | F13MS401 Dsch TrnBrgR dT |  | X
F13CALC10020 | 2000-F13-PID-PR-10010 | F13MS401 Fd TrnBrgL dT |  | 1 | TI13714A.PV | °C | F13MS401 Feed Trn L OB | [5 empty] | abs(Max(TI13714A.PV, TI13714B.PV, TI13714C.PV) - Min(TI13714A.PV, TI13714B.PV, TI13714C.PV)) = TDI13714.PV | Calculate the difference between the highest and lowest temperature of the three signals. | 0
|  |  |  | 2 | TI13714B.PV | °C | F13MS401 Feed Trn L Ctr | [6 empty] | Calculate as absolute value
|  |  |  | 3 | TI13714C.PV | °C | F13MS401 Feed Trn L IB
|  |  |  | 4 | TDI13714.PV | °C | F13MS401 Fd TrnBrgL dT |  | X
F13CALC10021 | 2000-F13-PID-PR-10010 | F13MS401 Dsch TrnBrgL dT |  | 1 | TI13717A.PV | °C | F13MS401 Dsch Trn L OB | [5 empty] | abs(Max(TI13717A.PV, TI13717B.PV, TI13717C.PV) - Min(TI13717A.PV, TI13717B.PV, TI13717C.PV)) = TDI13717.PV | Calculate the difference between the highest and lowest temperature of the three signals. | 0
|  |  |  | 2 | TI13717B.PV | °C | F13MS401 Dsch Trn L Ctr | [6 empty] | Calculate as absolute value
|  |  |  | 3 | TI13717C.PV | °C | F13MS401 Dsch Trn L IB | [14 empty] | TI13717C field instrument has an issue and currently in IOP+
|  |  |  | 4 | TDI13717.PV | °C | F13MS401 Dsch TrnBrgL dT |  | X
F13CALC10022 | 2000-F13-PID-PR-10011 | F13MB401A Pin. Gear dT |  | 1 | TI13763.PV | °C | F13MB401 Pin. Flank R 1 | [5 empty] | abs(TI13766.PV - TI13763.PV) = TDI13763.PV | Calculate the difference between outermost (feed and discharge end) pinion gear flank temperatures. | 0
|  |  |  | 2 | TI13766.PV | °C | F13MB401 Pin. Flank R 4 | [6 empty] | Calculate as absolute value
|  |  |  | 3 | TDI13763.PV | °C | F13MB401 Pin. Gear R dT |  | X
F13CALC10023 | 2000-F13-PID-PR-10011 | F13MB401B Pin. Gear dT |  | 1 | TI13783.PV | °C | F13MB401 Pin. Flank L 1 | [5 empty] | abs(TI13786.PV - TI13783.PV) = TDI13786.PV | Calculate the difference between outermost (feed and discharge end) pinion gear flank temperatures. | 0
|  |  |  | 2 | TI13786.PV | °C | F13MB401 Pin. Flank L 4 | [6 empty] | Calculate as absolute value
|  |  |  | 3 | TDI13786.PV | °C | F13MB401 Pin. Gear L dT |  | X
F13CALC10024 | 2000-F13-PID-PR-10011 | F13MB401 Fd TrnBrgR dT |  | 1 | TI13964A.PV | °C | F13MB401 Feed Trn R OB | [5 empty] | abs(Max(TI13964A.PV, TI13964B.PV, TI13964C.PV) - Min(TI13964A.PV, TI13964B.PV, TI13964C.PV)) = TDI13964.PV | Calculate the difference between the highest and lowest temperature of the three signals. | 0
|  |  |  | 2 | TI13964B.PV | °C | F13MB401 Feed Trn R Ctr | [6 empty] | Calculate as absolute value
|  |  |  | 3 | TI13964C.PV | °C | F13MB401 Feed Trn R IB
|  |  |  | 4 | TDI13964.PV | °C | F13MB401 Fd TrnBrgR dT |  | X
F13CALC10025 | 2000-F13-PID-PR-10011 | F13MB401 Dsch TrnBrgR dT |  | 1 | TI13958A.PV | °C | F13MB401 Dsch Trn R OB | [5 empty] | abs(Max(TI13958A.PV, TI13958B.PV, TI13958C.PV) - Min(TI13958A.PV, TI13958B.PV, TI13958C.PV)) = TDI13958.PV | Calculate the difference between the highest and lowest temperature of the three signals. | 0
|  |  |  | 2 | TI13958B.PV | °C | F13MB401 Dsch Trn R Ctr | [6 empty] | Calculate as absolute value
|  |  |  | 3 | TI13958C.PV | °C | F13MB401 Dsch Trn R IB
|  |  |  | 4 | TDI13958.PV | °C | F13MB401 Dsch TrnBrgR dT |  | X
F13CALC10026 | 2000-F13-PID-PR-10011 | F13MB401 Fd TrnBrgL dT |  | 1 | TI13966A.PV | °C | F13MB401 Feed Trn L OB | [5 empty] | abs(Max(TI13966A.PV, TI13966B.PV, TI13966C.PV) - Min(TI13966A.PV, TI13966B.PV, TI13966C.PV)) = TDI13966.PV | Calculate the difference between the highest and lowest temperature of the three signals. | 0
|  |  |  | 2 | TI13966B.PV | °C | F13MB401 Feed Trn L Ctr | [6 empty] | Calculate as absolute value
|  |  |  | 3 | TI13966C.PV | °C | F13MB401 Feed Trn L IB
|  |  |  | 4 | TDI13966.PV | °C | F13MB401 Fd TrnBrgL dT |  | X
F13CALC10027 | 2000-F13-PID-PR-10011 | F13MB401 Dsch TrnBrgL dT |  | 1 | TI13960A.PV | °C | F13MB401 Dsch Trn L OB | [5 empty] | abs(Max(TI13960A.PV, TI13960B.PV, TI13960C.PV) - Min(TI13960A.PV, TI13960B.PV, TI13960C.PV)) = TDI13960.PV | Calculate the difference between the highest and lowest temperature of the three signals. | 0
|  |  |  | 2 | TI13960B.PV | °C | F13MB401 Dsch Trn L Ctr | [6 empty] | Calculate as absolute value
|  |  |  | 3 | TI13960C.PV | °C | F13MB401 Dsch Trn L IB
|  |  |  | 4 | TDI13960.PV | °C | F13MB401 Dsch TrnBrgL dT |  | X
F13CALC10028 | 2000-F13-PID-PR-10006 | F13HU403 Hyd. Filter dP |  | 1 | PI13261.PV | kPa | F13HU403 Pump Disch. | [5 empty] | abs(PI13261.PV - PI13262.PV) = PDI13261.PV | Calculate differential pressure across filter. | 0
|  |  |  | 2 | PI13262.PV | kPa | F13HU403 System Pressure | [6 empty] | Calculate as absolute value
|  |  |  | 3 | PDI13261.PV | kPa | F13HU403 Hyd. Filter dP |  | X
F13CALC10029 | 2000-F13-PID-PR-10006 | F13HU404 Hyd. Filter dP |  | 1 | PI13321.PV | kPa | F13HU404 Pump Disch. | [5 empty] | abs(PI13321.PV - PI13322.PV) = PDI13321.PV | Calculate differential pressure across filter. | 0
|  |  |  | 2 | PI13322.PV | kPa | F13HU404 System Pressure | [6 empty] | Calculate as absolute value
|  |  |  | 3 | PDI13321.PV | kPa | F13HU404 Hyd. Filter dP |  | X
F13CALC10030 | 2000-F13-PID-PR-10006 | F13CC401 Actual CSS |  | 1 | F13CC401_RAT | mm | F13CC401 Tooth Ratio | X |  | 0.23 | - | - | IF F13CC401_CUP = True (Rising Edge Trigger), THEN Add F13CC401_RAT to F13CC401_CSS.PV 'IF F13CC401_CDN = True (Rising Edge Trigger), THEN Subtract F13CC401_RAT from F13CC401_CSS.PV | See '12. Misc tab' for SoftTag details See F13-SEQ-0029 for auto CSS calibration sequence. Engineer-level access only. | 0
|  |  |  | 2 | F13CC401_CSS.PV | mm | F13CC401 Crusher CSS |  | X
|  |  |  | 3 | F13CC401_CSS.SV | mm | F13CC401 Crusher CSS | X |  | 12 | F13CC401_MIN | F13CC401_MAX |  | Engineer level access entered setpoint. See F13CC401_MIN, F13CC401_MAX in Misc tab for details. This is used in F13-SEQ-0029 CSS Calibration Sequence. Engineer-level access only.
F13CALC10032 | 2000-F13-PID-PR-10006 | F13CC402 Actual CSS |  | 1 | F13CC401_RAT | mm | F13CC402 Tooth Ratio | X |  | 0.23 | - | - | IF F13CC402_CUP = True (Rising Edge Trigger), THEN Add F13CC402_RAT to F13CC402_CSS.PV 'IF F13CC402_CDN = True (Rising Edge Trigger), THEN Subtract F13CC402_RAT from F13CC402_CSS.PV | See '12. Misc tab' for SoftTag details. See F13-SEQ-0029 for auto CSS calibration sequence. Engineer-level access only. | 0
|  |  |  | 2 | F13CC402_CSS.PV | mm | F13CC402 Crusher CSS |  | X
|  |  |  | 3 | F13CC402_CSS.SV | mm | F13CC402 Crusher CSS | X |  | 12 | F13CC402_MIN | F13CC402_MAX |  | Engineer level access entered setpoint. See F13CC402_MIN, F13CC402_MAX in Misc tab for details. This is used in F13-SEQ-0034 CSS Calibration Sequence. Engineer-level access only.
F13CALC10034 | 2000-F16-PID-PR-10001 | F16 Fresh Feed Solids |  | 1 | WIC13121.PV | t/h | F13CV403 MS Feed Dry | [5 empty] | WIC13121.PV + MI19627A.PV + MI19627B = WIC13121B.PV |  | 2 | 2026-02-25 | MOC-121
|  |  |  | 2 | MI19627A.PV | t/h | F19PP61A Dry Tonnes | [6 empty] | Confirm MI19627A and B are SOLIDS only throughput calculations (brownfields) | [7 empty] | MI19627A/B.CPV are brownfields calculation on FCS0202
|  |  |  | 3 | MI19627B.PV | t/h | F19PP61B Dry Tonnes
|  |  |  | 4 | WI13121B.PV | t/h | F16 Fresh Feed Solids |  | X
F13CALC10035 | 2000-F13-PID-PR-10003 | F13MS401 Disch Brg Rxn |  | 1 | PI13648.PV | kPa | F13LU413 Dsch Trn Brg 1 | [5 empty] | (((PI13651.PV - 300) * 1050 * 900 * 0.73 * cos(54°) ) / 1000000) + '(((PI13650.PV - 300) * 1050 * 900 * 0.73 * cos(16°) ) / 1000000) + '(((PI13649.PV - 300) * 1050 * 900 * 0.73 * cos(16°) ) / 1000000) + '(((PI13648.PV - 300) * 1050 * 900 * 0.73 * cos(54°) ) / 1000000) = MS_DSCH_RXN MS_DSCH_RXN / 9.81 = MS_DSCH_WT | 1050 mm and 900 mm are the outer dimensions of the lift pads. | 1 | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 2 | PI13649.PV | kPa | F13LU413 Dsch Trn Brg 2 | [6 empty] | 54˚ and 16˚ are the angles of the pads with respect to the center of the bearing. |  | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 3 | PI13650.PV | kPa | F13LU413 Dsch Trn Brg 3 | [6 empty] | 0.73 represents the pad Average Pressure to Pocket Pressure coefficient, given by the fluid film analysis (typically around 0.69-0.73) |  | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 4 | PI13651.PV | kPa | F13LU413 Dsch Trn Brg 4 | [6 empty] | The pressure drop from the pressure transmitter to recess can swing depending on the pressure transmitter location in the lube lines. If the pressure transmitter is right next to the bearing housing it is typically 300 kPa. |  | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 5 | MS_DSCH_RXN | kN | F13MS401 DschTrunBrg Rxn |  | X
|  |  |  | 6 | MS_DSCH_WT | t | F13MS401 DschTrunBrg Wt |  | X |  |  |  |  | Please refer to 2000-ME001.2-M02-50001, section 3F.
F13CALC10036 | 2000-F13-PID-PR-10003 | F13MS401 Feed Brg Rxn |  | 1 | PI13644.PV | kPa | F13LU413 Feed Trn Brg 1 | [5 empty] | (((PI13647.PV - 300) * 1050 * 900 * 0.73 * cos(54°) ) / 1000000) + '(((PI13646.PV - 300) * 1050 * 900 * 0.73 * cos(16°) ) / 1000000) + '(((PI13645.PV - 300) * 1050 * 900 * 0.73 * cos(16°) ) / 1000000) + '(((PI13644.PV - 300) * 1050 * 900 * 0.73 * cos(54°) ) / 1000000) = MS_FD_RXN MS_FD_RXN / 9.81 = MS_FD_WT | 1050 mm and 900 mm are the outer dimensions of the lift pads. | 1 | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 2 | PI13645.PV | kPa | F13LU413 Feed Trn Brg 2 | [6 empty] | 54˚ and 16˚ are the angles of the pads with respect to the center of the bearing. |  | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 3 | PI13646.PV | kPa | F13LU413 Feed Trn Brg 3 | [6 empty] | 0.73 represents the pad Average Pressure to Pocket Pressure coefficient, given by the fluid film analysis (typically around 0.69-0.73) |  | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 4 | PI13647.PV | kPa | F13LU413 Feed Trn Brg 4 | [6 empty] | The pressure drop from the pressure transmitter to recess can swing depending on the pressure transmitter location in the lube lines. If the pressure transmitter is right next to the bearing housing it is typically 300 kPa. |  | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 5 | MS_FD_RXN | kN | F13MS401 FeedTrunBrg Rxn |  | X
|  |  |  | 6 | MS_FD_WT | t | F13MS401 FeedTrunBrg Wt |  | X |  |  |  |  | Please refer to 2000-ME001.2-M02-50001, section 3F.
F13CALC10037 | 2000-F13-PID-PR-10004 | F13MB401 Disch Brg Rxn |  | 1 | PI13899.PV | kPa | F13LU423 Dsch Trn Brg 1 | [5 empty] | (((PI13902.PV - 300) * 1050 * 900 * 0.73 * cos(54°) ) / 1000000) + '(((PI13901.PV - 300) * 1050 * 900 * 0.73 * cos(16°) ) / 1000000) + '(((PI13900.PV - 300) * 1050 * 900 * 0.73 * cos(16°) ) / 1000000) + '(((PI13899.PV - 300) * 1050 * 900 * 0.73 * cos(54°) ) / 1000000) = MB_DSCH_RXN MB_DSCH_RXN / 9.81 = MB_DSCH_WT | 1050 mm and 900 mm are the outer dimensions of the lift pads. | 1 | 19/05/2025 19/05/2025 | PCT alignment (kPag to kPa) https://pastech-2955.atlassian.net/browse/KAN-1903
|  |  |  | 2 | PI13900.PV | kPa | F13LU423 Dsch Trn Brg 2 | [6 empty] | 54˚ and 16˚ are the angles of the pads with respect to the center of the bearing. |  | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 3 | PI13901.PV | kPa | F13LU423 Dsch Trn Brg 3 | [6 empty] | 0.73 represents the pad Average Pressure to Pocket Pressure coefficient, given by the fluid film analysis (typically around 0.69-0.73) |  | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 4 | PI13902.PV | kPa | F13LU423 Dsch Trn Brg 4 | [6 empty] | The pressure drop from the pressure transmitter to recess can swing depending on the pressure transmitter location in the lube lines. If the pressure transmitter is right next to the bearing housing it is typically 300 kPa. |  | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 5 | MB_DSCH_RXN | kN | F13MB401 DschTrunBrg Rxn |  | X
|  |  |  | 6 | MB_DSCH_WT | t | F13MB401 DschTrunBrg Wt |  | X |  |  |  |  | Please refer to 2000-ME001.3-M02-50001, section 3F.
F13CALC10038 | 2000-F13-PID-PR-10004 | F13MB401 Feed Brg Rxn |  | 1 | PI13895.PV | kPa | F13LU423 Feed Trn Brg 1 | [5 empty] | (((PI13898.PV - 300) * 1050 * 900 * 0.73 * cos(54°) ) / 1000000) + '(((PI13897.PV - 300) * 1050 * 900 * 0.73 * cos(16°) ) / 1000000) + '(((PI13896.PV - 300) * 1050 * 900 * 0.73 * cos(16°) ) / 1000000) + '(((PI13895.PV - 300) * 1050 * 900 * 0.73 * cos(54°) ) / 1000000) = MB_FD_RXN MB_FD_RXN / 9.81 = MB_FD_WT | 1050 mm and 900 mm are the outer dimensions of the lift pads. | 1 | 19/05/2025 19/05/2025 | PCT alignment (kPag to kPa) https://pastech-2955.atlassian.net/browse/KAN-1903
|  |  |  | 2 | PI13896.PV | kPa | F13LU423 Feed Trn Brg 2 | [6 empty] | 54˚ and 16˚ are the angles of the pads with respect to the center of the bearing. |  | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 3 | PI13897.PV | kPa | F13LU423 Feed Trn Brg 3 | [6 empty] | 0.73 represents the pad Average Pressure to Pocket Pressure coefficient, given by the fluid film analysis (typically around 0.69-0.73) |  | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 4 | PI13898.PV | kPa | F13LU423 Feed Trn Brg 4 | [6 empty] | The pressure drop from the pressure transmitter to recess can swing depending on the pressure transmitter location in the lube lines. If the pressure transmitter is right next to the bearing housing it is typically 300 kPa. |  | 2025-05-19 | PCT alignment (kPag to kPa)
|  |  |  | 5 | MB_FD_RXN | kN | F13MB401 FeedTrunBrg Rxn |  | X | [6 empty] | 2025-07-01 | MB_DSCH was reading FD
|  |  |  | 6 | MB_FD_WT | t | F13MB401 FeedTrunBrg Wt |  | X |  |  |  |  | Please refer to 2000-ME001.3-M02-50001, section 3F.
F13CALC10039 | 2000-F13-PID-PR-10003 | F13MS401 Mill Weight |  | 1 | MS_FD_RXN | kN | F13MS401 FeedTrunBrg Rxn |  | X |  |  |  | (((MS_FD_RXN + MS_DSCH_RXN) / 9.81) - MS_DEADWEIGHT) * MS_CORR_FCTR = WIC13135.PV |  | 0
|  |  |  | 2 | MS_DSCH_RXN | kN | F13MS401 DschTrunBrg Rxn |  | X
|  |  |  | 3 | WIC13135.PV | t | F13MS401 Mill Weight |  | X
[5 empty] | MS_CORR_FCTR |  | F13MS401 Mill Weight Correction Factor |  |  | 1.633 | 1.5 | 1.75 |  | Engineer level access
|  |  |  | 4 | MS_DEADWEIGHT | t | F13MS401 Deadweight | X |  | 1539 | 1450 | 2000 |  | Estimated total weight of mill uncharged (i.e., component and liner weights). TBC during commissioning. Engineer-level access only.
F13CALC10040 | 2000-F13-PID-PR-10004 | F13MB401 Mill Weight |  | 1 | MB_FD_RXN | kN | F13MB401 FeedTrunBrg Rxn |  | X |  |  |  | ((MB_FD_RXN + MB_DSCH_RXN) / 9.81) - MB_DEADWEIGHT = WI13148.PV |  | 0
|  |  |  | 2 | MB_DSCH_RXN | kN | F13MB401 DschTrunBrg Rxn |  | X
|  |  |  | 3 | WI13148.PV | t | F13MB401 Mill Weight |  | X
|  |  |  | 4 | MB_DEADWEIGHT | t | F13MB401 Deadweight | X |  | 1286 | 1150 | 2000 |  | Estimated total weight of mill uncharged (i.e., component and liner weights). TBC during commissioning. 2000-ME001.3-F20-50003. Engineer-level access only.
F13CALC10041 | 2000-F13-PID-PR-10010 | F13MS401 Total Power |  | 1 | JI13136A.PV | kW | F13MS401 Master Power | [5 empty] | JI13136A.PV + JI13136B.PV = JIC13136.PV |  | 0 | 2025-10-30 | CR-052
|  |  |  | 2 | JI13136B.PV | kW | F13MS401 Slave Power
|  |  |  | 3 | JIC13136.PV | kW | F13MS401 Total Power |  | X
F13CALC10042 | 2000-F13-PID-PR-10011 | F13MB401 Total Power |  | 1 | JI13149A.PV | kW | F13MB401 Master Power | [5 empty] | JI13149A.PV + JI13149B.PV = JI13149.PV |  | 0 | 2025-10-30 | CR-052
|  |  |  | 2 | JI13149B.PV | kW | F13MB401 Slave Power
|  |  |  | 3 | JI13149.PV | kW | F13MB401 Total Power |  | X
F13CALC10043 | 2000-F13-PID-PR-10010 | F13MS401 Total Torque |  | 1 | MS_MSTR_T | kNm | F13MS401 Master Torque | [5 empty] | MS_MSTR_T + MS_SLVE_T = MS_TORQUE |  | 1 | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1903
|  |  |  | 2 | MS_SLVE_T | kNm | F13MS401 Slave Torque | [8 empty] | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1903
|  |  |  | 3 | MS_TORQUE | kNm | F13MS401 Total Torque |  | X | [6 empty] | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1903
F13CALC10044 | 2000-F13-PID-PR-10011 | F13MB401 Total Torque |  | 1 | MB_MSTR_T | kNm | F13MB401 Master Torque | [5 empty] | MB_MSTR_T + MB_SLVE_T = MB_TORQUE |  | 1 | 6/03/2025 19/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1411 https://pastech-2955.atlassian.net/browse/KAN-1903
|  |  |  | 2 | MB_SLVE_T | kNm | F13MB401 Slave Torque | [8 empty] | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1903
|  |  |  | 3 | MB_TORQUE | kNm | F13MB401 Total Torque |  | X | [6 empty] | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1903
F13CALC10045 | 2000-F13-PID-PR-10010 | F13MS401 Total Current |  | 1 | MS_MSTR_I | Amps | F13MS401 Master Current | [5 empty] | MS_MSTR_I + MS_SLVE_I = MS_CURRENT |  | 1 | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1903
|  |  |  | 2 | MS_SLVE_I | Amps | F13MS401 Slave Current | [8 empty] | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1903
|  |  |  | 3 | MS_CURRENT | Amps | F13MS401 Total Current |  | X | [6 empty] | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1903
F13CALC10046 | 2000-F13-PID-PR-10011 | F13MB401 Total Current |  | 1 | MB_MSTR_I | Amps | F13MB401 Master Current | [5 empty] | MB_MSTR_I + MB_SLVE_I = MB_CURRENT |  | 1 | 6/03/2025 19/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1411 https://pastech-2955.atlassian.net/browse/KAN-1903
|  |  |  | 2 | MB_SLVE_I | Amps | F13MB401 Slave Current | [8 empty] | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1903
|  |  |  | 3 | MB_CURRENT | Amps | F13MB401 Total Current |  | X | [6 empty] | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1903
F13CALC10047 | 2000-F13-PID-PR-10004 | F13CR453 Duty Cycle | % | 1 | F13CR453_Parameter_1 | % | F13-CR-453 Dty Cycle Req. | X |  | 40 | 0 | 100 | if F13-CR-453_T = Running, Increment counter by 1 every second if F13-CR-453_T = Stopped, Decrement counter by (F13CR453_Parameter_1/100) / (1 - F13CR453_Parameter_1/100) every second If counter >= (F13CR453_Parameter_1/100 * F13CR453_Parameter_2): Activate F13CR453_MXDUTY If counter <= 0 Deactivate F13CR453_MXDUTY Counter cannot be < 0 |  | 1 | 14/05/2025 27/05/2025 24/06/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC close out Functional description comments returned As per discussion with BH | [5 empty] | #DIV/0! | s off time
|  |  |  | 2 | F13CR453_Parameter_2 | Seconds | F13-CR-453 Duty Cycle Period | X |  | 3600 | 0 | 7200
|  |  |  | 3 | F13CR453_Parameter_3 | Seconds | F13-CR-453 Off Duty |  | X
F13CALC10048 | 2000-F13-PID-PR-10004 | F13BLC402 Duty Cycle | % | 1 | F13BLC402_Parameter_1 | % | F13-BLC-402 Dty Cycle Req. | X |  | 75 | 0 | 100 | if F13-BLC-402 = Running, Increment counter by 1 every second if F13-BLC-402 = Stopped, Decrement counter by (F13BLC402_Parameter_1/100) / (1 - F13BLC402_Parameter_1/100) every second If counter >= (F13BLC402_Parameter_1/100 * F13BLC402_Parameter_2): Activate F13BLC402_MXDUTY If counter <= 0 Deactivate F13BLC402_MXDUTY Counter cannot be < 0 | 3 | 1 | 14/05/2025 27/05/2025 24/06/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC close out Functional description comments returned As per discussion with BH
|  |  |  | 2 | F13BLC402_Parameter_2 | Seconds | F13-BLC-402 Duty Cycle Period | X |  | 1200 | 0 | 7200 |  | 900 |  | On for | [6 empty] | #DIV/0! | s off time
|  |  |  | 3 | F13BLC402_Parameter_3 | Seconds | F13-BLC-402 Off Duty |  | X | [6 empty] | Off for
F13CALC10049 | 2000-F13-PID-PR-10004 | F13BLC402 Charge Cycle |  | 1 | F13BLC402_Parameter_5 | kg/t | F13MB402 Ball/Feed Ratio | X |  | 0.2 | 0 | 1 | F13BLC402_MEM - WI13285C.PV = F13BLC402_Parameter_8 F13BLC402_Parameter_8 / F13BLC402_Parameter_5 = F13BLC402_Parameter_6 WHEN CALLED TO ON STEP 37 OF F13SEQ0037 (One Shot): • Minus F13BLC402_Parameter_6 from F13BLC402_FT totaliser AND • Add F13BLC402_Parameter_8 to WQI13285C totaliser Calculate kg of balls required based off Totaliser value (for indication purposes): F13BLC402_Parameter_5 * F13BLC402_FT = F13BLC402_Parameter_7 | Controls based on ME067 Existing Ball Charging System. TBC Vendor Functional Description, 2000-ME057-M01-10001 Engineer-level access only. | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC close out. Corrected step number
|  |  |  | 2 | F13BLC402_Parameter_6 | t | F13MB401 Feed/Ball |  | X
|  |  |  | 3 | F13BLC402_Parameter_7 | kg | F13BLC402 Balls Req. |  | X |  |  |  |  | Calculations for F13BLC402_FT and WQI13285C must only occur for 1 shot and when called for in STEP 37 of F13SEQ0037 only.
|  |  |  | 4 | F13BLC402_Parameter_8 | kg | F13BLC402 Balls Unloaded |  | X
|  |  |  | 5 | F13BLC402_MEM | kg | F13BLC402 Stored Value | [6 empty] | Refer to Misc tab for stored value details
|  |  |  | 6 | WI13285C.PV | kg | F13BLC402 Load Cell
|  |  |  | 7 | F13BLC402_FT | t | F13MS401 FeedTotaliser2 |  | X |  |  |  |  | Refer to Misc tab for totaliser details
45

## 12. Misc
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - MILLING & CLASSIFICATION (F13)
2000-F13-LST-PR-10001
MISC. INSTRUMENTS AND CONTROLLERS
[13 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Description | Normal State | Alarm State | Hardwired (y/n) | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | Change Date | Change Reference | OK | Date | OK | Date
HS13090 | 2000-F13-PID-PR-10002 | F13CY401 Density Sel. | Operator Selection |  | N |  |  |  | Selector for the Density Controller to be used for Cascade Control of FIC13075. Faceplate Selection: • Cycloned Feed Density (DNIC13090A) OR • Cyclone Overflow Density (PSA) (DNIC13090B) OR • Cyclone Overflow Density (CALC) (DNIC13090B) | 1 | 2025-03-06 | PCT alignment action register (density transmitters to align with F16,17,18) |  |  |  |  | Misc Logic Functionality checked only. Valves/Instrument not yet loop checked FC 18/6/26 : wait to test with valving
HS13121 | 2000-F13-PID-PR-10003 | F13MS401 SAG Water Sel. | Operator Selection |  | N |  |  |  | Selector for choosing which Calculation block (F13CALC10008 / F13CALC10009) is used for the Cascade Control of FIC13121. Faceplate Selection: • Water to Solids Ratio (F13CALC10008) OR • SAG Mill Discharge % Solids (F13CALC10009) OR • MANTA Density (DIC13121) | 1 | [6 empty] | Misc Logic Functionality checked only. Valves/Instrument not yet checked for WI13035 27/07/2026 Logic added by MANTA
FCV13075_LL | 2000-F13-PID-PR-10002 | FCV13075 Control | Operator Selection |  | N |  |  |  | Set duty and standby valves for FIC13075 split range control of FCV13075A and FCV13075B. Selected valve will be in DUTY mode. Valves in AUTO will actuate as per split range, see FIC13075 PID control tab. Faceplate Selection: FCV13075A OR FCV13075B | 0 | [6 empty] | Misc Logic Functionality checked only. Valves/Instrument has been loop checked.
F13FA400_FP1 | 2000-F13-PID-PR-10001 | F13FA400 Duty Feeders | Operator Selection |  | N |  |  |  | Selected Reclaim Feeders will be in DUTY mode. Deselected Reclaim Feeders will be in STANDBY mode. For use in F13-SEQ-0025 Faceplate Selection: • Reclaim Feeder 1 (F13-FA-411) • Reclaim Feeder 2 (F13-FA-412) • Emergency Feeder (F13-FA-414) | A | [6 empty] | Misc Logic Functionality checked only. Selector button configured using tagnames 13FA411DU/412DU/414DU. Changed to 2 point access
F13CC400_FP1 | 2000-F13-PID-PR-10006 | F13CC400 Duty R.Crushers | Operator Selection |  | N |  |  |  | Selected Recycle Crushers will be in DUTY mode. Deselected Recycle Crushers will be in STANDBY mode. For use in F13-SEQ-0003 Faceplate Selection: • Recycle Crusher C (F13-CC-401) • Recycle Crusher D (F13-CC-402) | A | [6 empty] | Misc Logic: Functionality checked only.
F13FD401_FP1 | 2000-F13-PID-PR-10002 | F13FD401 Discharge Loc. | Operator Selection |  | N |  |  |  | Cyclone Underflow Feed Box (F13-FD-401) discharge location selector faceplate. Selection on faceplate will cause the respective valves to change to AUTO and to actuate to position. CRO to select destination Faceplate Selection: • SAG Mill (Single Stage SAG) OR - Open XV13116 THEN ON CONFIRMATION OF OPEN FEEDBACK, - Close XV13114 AND XV13115 • Ball Mill (Typical SABC) - Open XV13114 AND XV13115 THEN ON CONFIRMATION OF OPEN FEEDBACK, - Close XV13116 One shot to SAG Mill (Single Stage SAG) if: - XV13114 OR XV13115 = Open and - MB_OP_MODE = Normal and - MB_CR_ILK = Active OR MB_NCR_ILK = Active | 2 | [6 empty] | Misc Logic Functionality checked only. Valves/Instrument not yet loop checked FC 18/6/26 : wait to test with valving VV 01/07/2026; Misc Logic Functionality checked
F13PP401_ILK | 2000-F13-PID-PR-10002 | F13PP401 Ball Mill Interlock | Logic |  | N |  |  |  | If (MB_OP_MODE = Normal and (XV13114 OR XV13115 Open) and MB_RUNNING = active) and MB_CR_ILK = Active OR MB_NCR_ILK = Active): SET F13HP401_FP1 TO LEVEL AND SET HS13092 TO LEVEL AND SET FIC13075 TO CAS AND SET LIC13076A TO AUT AND SET FIC13090 TO CAS AND SET LIC13076B TO AUT AND F13PP401 SPEED AND FCV13075A AND B TO CAS | 2 | [6 empty] | desktop review
F13FD401_ALM | 2000-F13-PID-PR-10002 | F13FD401 SingleStageSAG | Normal | Alarm | N |  | 3 |  | Alarm to advise CRO that the Cyclone Underflow Feed Box (F13-FD-401) discharge valves are not in their normal operating positions. Alarm every 1 hour after reset if condition is still true. Activate alarm if: XV13116 = OPENED OR XV13114 = CLOSED OR XV13115 = CLOSED | 1 | 2025-06-04 | Reset every hour comment removed as per Teams discussion |  |  |  |  | Misc Logic Functionality checked only. Valves/Instrument not yet loop checked VV 26/06/26; Valve/Instrument has been loop tested
F13SL400_FP1 | 2000-F13-PID-PR-10007 '2000-F13-PID-PR-10008 | F13SL400 Trash Screen | Operator Selection |  | N |  |  |  | Selected Trash Screens will be in DUTY mode. Deselected Trash Screens will be in STANDBY mode. Up to 4 options can be selected. For use in F13-SEQ-0007 Faceplate Selection: • Trash Screen 1 (F13-SL-401) • Trash Screen 2 (F13-SL-402) • Trash Screen 3 (F13-SL-403) • Trash Screen 4 (F13-SL-404) | A | [6 empty] | Misc Logic Functionality checked only. Selector button configured using tagnames 13SL401DU/402DU/403DU/404DU. Graphic faceplate needed to be changed to 2 step access.
F13PW415_FP1 | 2000-F13-PID-PR-10012 | F13PW415 & 416 Duty | Operator Selection |  | N |  |  |  | Selected Chiller Recirculation Water Pumps will be in DUTY mode. Deselected Chiller Recirculation Water Pumps will be in STANDBY mode. For use in F13-SEQ-0001 Faceplate Selections: • Chiller Recirculation Water Pump 1 (F13-PW-415) OR • Chiller Recirculation Water Pump 2 (F13-PW-416) F13-PW-415 can only be selected for DUTY if ZIO13431 = Opened AND ZIO13432 = Opened i.e., HV13431 & HV13432 = Opened F13-PW-416 can only be selected for DUTY if ZIO13433 = Opened AND ZIO13434 = Opened i.e., HV13433 & HV13434 = Opened | 1 | 2025-06-05 | https://pastech-2955.atlassian.net/browse/KAN-1993 |  |  |  |  | Logic Functionality checked only 13PW415_FP1 is catered by NSR duty standby drive faceplate selection for 13PW415/416
F13PW413_FP1 | 2000-F13-PID-PR-10012 | F13PW413 & 414 Duty | Operator Selection |  | N |  |  |  | Selected Cooling Water Pumps will be in DUTY mode. Deselected Cooling Water Pumps will be in STANDBY mode. For use in F13-SEQ-0001 Faceplate Selections: • Cooling Water Pump 1 (F13-PW-413) OR • Cooling Water Pump 2 (F13-PW-414) F13-PW-413 can only be selected for DUTY if ZIO13422 = Opened AND ZIO13423 = Opened i.e., HV13422 & HV13423 = Opened F13-PW-414 can only be selected for DUTY if ZIO13424 = Opened AND ZIO13425 = Opened i.e., HV13424 & HV13425 = Opened | 1 | 2025-06-05 | https://pastech-2955.atlassian.net/browse/KAN-1993 |  |  |  |  | Logic Functionality checked only 13PW413_FP1 is catered by NSR duty standby drive faceplate selection for 13PW413/414
F13HP401_FP1 | 2000-F13-PID-PR-10002 | FIC13075 Controllers | Operator Selection |  | N |  |  |  | Only 1 option on this Faceplate can be selected. Cascade Set Value selector logic for FIC13075. FIC13075 must be in CASCADE. As default, Density & Level is selected and will operate as per F13HP401_SEL to provide Density Control (DNIC13090A/B) during normal operation, or Hopper Level Protection (LIC13076A) when hopper level is low. 'Density' will enable Density Control (DNIC13090A/B) only. 'Level' will enable Level Control (LIC13076A) only. Faceplate Selections: • Density OR • Level OR • Density & Level | 1 | 6/03/2025 07/04/2025 | PCT alignment action register (density transmitters to align with F16,17,18) Cyclones design change following F28 FAT. |  |  |  |  | Selector Logic Functionality Checked only. Default by definition meaning operator selecting DENS>LVL function.
F13HP401_SEL | 2000-F13-PID-PR-10002 | F13HP401 Selector Func | Conditional Selector |  | N |  |  |  | ACTIVATE Density Control (DNIC13090A/B via HS13090 provides CSV to FIC13075) IF: 'Density' Selected on F13HP401_FP1 OR LIC13076A.PV > A_Lo for 320 seconds (TBC) AND 'Density & Level' selected on F13HP401_FP1 ACTIVATE Level Control (LIC13076A provides CSV to FIC13075) IF: 'Level' Selected on F13HP401_FP1 OR LIC13076A.PV < A_Lo AND 'Density & Level' selected on F13HP401_FP1 FIC13075 must be in CASCADE control F13HP401_FP1 Faceplate to select 'Density', 'Level', 'Density & Level' controllers. | 1 | 6/03/2025 07/04/2025 | PCT alignment action register (density transmitters to align with F16,17,18) Cyclones design change following F28 FAT. |  |  |  |  | Logic Functionality checked only Actual selection To be tested with 13HP401_FP1 / HS13090
HS13092 | 2000-F13-PID-PR-10002 | F13PP401 Control Method | Operator Selection |  | N |  |  |  | Selector for the Pressure or Level control of FIC13090 and the Cyclone Feed Valves Selection: • Level Control (LIC13076B Cascade SV to FIC13090) • Pressure Control (PIC13090 Cascade SV to FIC13090) If the Cyclone Feed Pump is in pressure control, valves open/close based on a hopper level deadband (F13CALC10007) If the Cyclone Feed Pump is in level control, valves open/close based on a pressure deadband (F13CALC10011) | 1 | 2025-04-07 | Cyclones design change following F28 FAT. |  |  |  |  | Selector Logic Functionality Checked only. Switching to the correct corresponding control method was also verified during loop tuning attempt.
F13CU400_FP1 | 2000-F13-PID-PR-10012 | F13CU400 Chillers | Operator Selection |  | N |  |  |  | Selected Chillers will be in DUTY mode Deselected Chillers will be in STANDBY mode Faceplate Selections: • Chiller 1 • Chiller 2 • Chiller 3 • Chiller 4 F13-CU-402 can only be selected for DUTY if ZIO13442 = Opened AND ZIC13442 = Inactive i.e., HV13442 = Opened F13-CU-403 can only be selected for DUTY if ZIO13444 = OpenedAND ZIC13444 = Inactive i.e., HV13444 = Opened F13-CU-404 can only be selected for DUTY if ZIO13446 = Opened AND ZIC13446 = Inactive i.e., HV13446 = Opened F13-CU-405 can only be selected for DUTY if ZIO13448 = Opened AND ZIC13448 = Inactive i.e., HV13448 = Opened | 1 | 2025-06-05 | https://pastech-2955.atlassian.net/browse/KAN-1993 |  |  |  |  | Logic Functionality checked only Graphic faceplate has been changed to 2 step access.
F13FN419_OFF | 2000-F13-PID-PR-10001 | F13FN419 Stopped | Normal | Alarm | N |  | 0 |  | If F13-FN-419 = Stopped: F13FN419_OFF = Alarm Else F13FN419_OFF = Normal | 1 | 2025-04-10 | https://pastech-2955.atlassian.net/browse/KAN-1673 |  |  |  |  | Logic Functionality checked only VV 27/06/2026; Checked with 13FN419 Stopped status
F13CY401_FP1 | 2000-F13-PID-PR-10002 | F13CY401 Cyclones | Operator Selection |  | N |  |  |  | Up to 15 duty Cyclone Feed Valves can be selected. A minimum of 6 DUTY cyclones must be selected for the Cyclone Feed Pump to start. For Cyclone Feed Valves in AUTOMATIC Mode and • HS13092 = Pressure Control, then F13CALC10007 is utilised for Cyclone Feed Valve control (see Calculation / OnOff Valves tab) • HS13092 = Level Control, then F13CALC10011 is utilised for Cyclone Feed Valve control (see Calculation / OnOff Valves tab) For Cyclone Feed Valves in MANUAL Mode: • A_Lo and A_Hi indicate when Cyclone Feed Valves need to be opened / closed manually by CRO (see PID Cont tab) Selected Cyclones will be in DUTY mode. If a Cyclone Feed Valve is changed to DUTY, set it to AUTO mode (one shot). DUTY Cyclone Feed Valves that are in AUTO are called to open or close as described above, in accordance with the priority system described below. DUTY Cyclone Feed Valves that are in MANUAL are manually opened or closed by the CRO. Deselected Cyclones will be in STANDBY mode. STANDBY Cyclone Feed Valves are forced to Close Trip (as per OnOff Valves tab). Cyclone Feed Valve Priority System: Incorporate a CRO entered priority system, ranging from '1' (highest priority) to '15' (lowest priority), for auto open and close operation of DUTY selected Cyclone Feed Valves that are in AUTO. This hierarchy will dictate the sequence in which Cyclone Feed Valves automatically open or close as per F13CALC10007 Calculations tab (if HS13092 = Pressure Control) or F13CALC10011 Calculations tab (if HS13092 = Level Control). • The top 6 highest priority DUTY Cyclone Feed Valves are opened in AUTO mode (see OnOff Valves tab). • The remaining DUTY Cyclone Feed Valves auto open in ascending order of priority as Cyclone feed pressure increases. • Cyclone Feed Valves will auto close in descending order of prior↓ity as Cyclone feed pressure decreases. • STANDBY selected or Cyclone Feed Valves in MANUAL mode will not auto open and close and are to be disregarded from the priority system. • STANDBY feed valves are close tripped (see OnOff Valves tab). • If a Cyclone Feed Valve fails to open / close, the next priority DUTY and AUTO Cyclone Feed Valve will open / close. The failed Cyclone Feed Valve will be forced into STANDBY MODE. If a Gravity Cyclone 1 OR 2 Feed Valve is opened, the next available lowest priority opened Cyclone Feed Valve will close simultaneously. If a Gravity Cyclone 1 OR 2 Feed Valve is closed, the next available highest priority closed Cyclone Feed Valve will open simultaeneously. NOTE: It's up to the CRO to ensure that the priorities assigned to the DUTY selected Cyclone Feed Valves achieve an even distribution of operating Cyclones across the entire Cyclone cluster and that the priorities are assigned to align with the cyclone maintenance strategy. Faceplate Selections (include a graphic which allows the CRO to assign a unique value from 1 to 15 to each Cyclone Feed Valve): • XV13094 • XV13095 • XV13096 • XV13097 • XV13098 • XV13099 • XV13100 • XV13101 • XV13102 • XV13103 • XV13104 • XV13105 • XV13106 • XV13107 • XV13108 | 1 | 2025-04-07 | Cyclones design change following F28 FAT. |  |  |  |  | Logic Functionality Tested. Required Simulating Gravity Cyclone Feed Valves and 13PP401 to test as these assets were not available during tests. Tested quick successive changes in valve feedback and command. (Simulate Faulted Valves.)
F13CY401_RUN | 2000-F13-PID-PR-10002 | F13CY401 Cyclone Runtime | Runtime Totaliser |  | N |  |  |  | Include a Runtime Totaliser for each of the below Primary Cyclone and Gravity Cyclone Feed Valves. Include functionality to RESET the Runtime Totaliser for individual valves. Sum Runtime Totaliser for the respective valve when XV13### = OPENED AND F13-PP-401 = RUNNING. Valves Include: • XV13094 • XV13095 • XV13096 • XV13097 • XV13098 • XV13099 • XV13100 • XV13101 • XV13102 • XV13103 • XV13104 • XV13105 • XV13106 • XV13107 • XV13108 • XV13110 • XV13111 | A
F13CY401A_RPG | 2000-F13-PID-PR-10002 | F13CY401A Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401A_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401B_RPG | 2000-F13-PID-PR-10002 | F13CY401B Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401B_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401C_RPG | 2000-F13-PID-PR-10002 | F13CY401C Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401C_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401D_RPG | 2000-F13-PID-PR-10002 | F13CY401D Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401D_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401E_RPG | 2000-F13-PID-PR-10002 | F13CY401E Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401E_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401F_RPG | 2000-F13-PID-PR-10002 | F13CY401F Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401F_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401G_RPG | 2000-F13-PID-PR-10002 | F13CY401G Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401G_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401H_RPG | 2000-F13-PID-PR-10002 | F13CY401H Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401H_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401J_RPG | 2000-F13-PID-PR-10002 | F13CY401J Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401J_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401K_RPG | 2000-F13-PID-PR-10002 | F13CY401K Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401K_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401M_RPG | 2000-F13-PID-PR-10002 | F13CY401M Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401M_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401N_RPG | 2000-F13-PID-PR-10002 | F13CY401N Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401N_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401P_RPG | 2000-F13-PID-PR-10002 | F13CY401P Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401P_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401Q_RPG | 2000-F13-PID-PR-10002 | F13CY401Q Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401Q_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY401R_RPG | 2000-F13-PID-PR-10002 | F13CY401R Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401R_AMN = 1 OR 2 for the alarm on-delay timer | 0
F13CY411_RPG | 2000-F13-PID-PR-10002 | F13CY411 Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY411_AMN = 1 OR 2 for the alarm on-delay timer | 0 | [6 empty] | Marked as FUTURE, not build in PCT | VG 8/8/26: As found, the tagname has been changed from 13CY401S_RPG to 13CY411_RPG
F13CY412_RPG | 2000-F13-PID-PR-10002 | F13CY412 Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY412_AMN = 1 OR 2 for the alarm on-delay timer | 0 | [6 empty] | Marked as FUTURE, not build in PCT | VG 8/8/26: As found, the tagname has been changed from 13CY401T_RPG to 13CY412_RPG
F13CY401U_RPG | 2000-F13-PID-PR-10002 | F13CY401U Roping Alarm | Normal | Alarm | N |  | 10 |  | Alarm if F13CY401U_AMN = 1 OR 2 for the alarm on-delay timer | 0 | [6 empty] | Not used in the graphic only in the background
F13CY401_AMN | 2000-F13-PID-PR-10002 | F13CY401 Status Text | Graphic |  | N |  |  |  | Display the following status text on the F13CY401 cluster graphic for each corresponding F13CY401i_AMN (where i = A, B, C, D, E, F, G, H, J, K, M, N, P, Q, R) and F14CY411_AMN, F14CY412_AMN instead of the integer. Tags defined in Analogue Input tab. For each F13CY401i_AMN and F14CY411_AMN, F14CY412_AMN If 0, display "OFF" If 1, display "ROPING" If 2, display "ROPING TRANSITION" If 3, display "SEMI ROPING" If 4, display "SPLASH" else, display "ERROR" | 1 | 2025-06-25 | PL317
F13HU405_T1 | 2000-F13-PID-PR-10006 |  | Timer PT = 2 Minutes | Timer Elapsed | N |  | 0 |  | Open/close solenoid valves cannot be active for > 2 consecutive minutes. Start on-delay timer if any of the below solenoid valves are energised, else stop timer: • SV13218A Energised OR • SV13218B Energised OR • SV13219A Energised OR • SV13219B Energised If F13HU405_T1 timer elapses: • SV13218A, SV13218B, SV13219A and SV13219B are forced to deenergise and an alarm is triggered. Reset required. Refer to solenoid valves in OnOff Valves tab | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
F13HU405_T2 | 2000-F13-PID-PR-10006 |  | Timer PT = 3 Seconds |  | N |  |  |  | Timer to allow motor to get to full speed whilst unloaded. Start on-delay timer when F13-HU-405 = RUNNING, else stop timer. If F13HU405_T2 timer elapses: • SV13218A, SV13218B, SV13219A and SV13219B OP2 Permissive = Healthy Refer to solenoid valves in OnOff Valves tab | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
F13HU405_T3 | 2000-F13-PID-PR-10006 |  | Timer PT = 10 Minutes | Timer Elapsed | N |  | 0 |  | Timer to shutdown F13-HU-405 if it's running without any operator actions. Start on-delay timer when: • F13-HU-405 Energised AND • SV13218A Deenergised AND • SV13218B Deenergised AND • SV13219A Deenergised AND • SV13219B Deenergised If F13HU405_T3 timer elapses: • F13-HU-405 is interlocked and alarm is triggered. Reset required. Refer to Drives tab | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1409
F13BLC401_T1 | 2000-F13-PID-PR-10001 |  | Timer PT = 60 Minutes |  | N |  |  |  | Timer with 60 minute PRESET TIME (PT). The F13-BLC-401 Indexer STARTS every 60 minutes the SAG Mill Main Motors and SAG Mill Feed Conveyor are RUNNING. After the timer elapses, it is to reset to 0 and restarted if the SAG Mill and Feed Conveyor are still running. START / CONTINUE (if paused): MS_RUNNING = RUNNING AND F13-CV-403 = RUNNING PAUSE: MS_RUNNING = NOT RUNNING OR F13-CV-403 = NOT RUNNING When F13BLC401_T1 elapses: ENERGISE F13-BLC-401 indexer (if in AUTO) AND RESET timer to 0 NOTE: The F13-BLC-401 indexer starts when F13BLC401_T1 elapses. The F13-BLC-401 indexer stops when F13BLC401_FT <= 0. See Drives tab and F13CALC10001. | 0 | [6 empty] | desktop review
F13BLC401_T2 | 2000-F13-PID-PR-10001 | F13BLC401 Run Time | Timer PT = N/A |  | N |  |  |  | F13BLC401_T2 is to measure the duration that F13-BLC-401 is running for the purpose of negating mill balls from the SAG Mill Fresh Feed calculation WIC13121. START: F13-BLC-401 Indexer = RUNNING. STOP (and reset to 0): F13-BLC-401 Indexer = NOT RUNNING. Assumed the output here is in minutes. Please convert calculations accordingly (refer to F13CALC10001). Refer to F13CALC10001 | 0 | [6 empty] | desktop review can see it has incremented. Also can see clear start conditions.
F13BLC401_FT | 2000-F13-PID-PR-10001 | F13MS401 FeedTotaliser1 | Totaliser |  | N |  |  |  | SAG Mill Fresh Feed (Dry) Totaliser Totaliser Input PV = WIC13121.PV Totaliser is used to calculate how many Mill Balls are required based on SAG Mill tonnage. Totaliser value is negated as Mill Balls are successfully indexed onto the SAG Mill Feed Conveyor. The F13-BLC-401 indexer starts when F13BLC401_T1 elapses. The F13-BLC-401 indexer interlocks to stop when F13BLC401_FT <= 0. See Drives tab and F13CALC10001. Refer to F13CALC10001 | 0
F13BLC401_C1 | 2000-F13-PID-PR-10001 | F13BLC401 Balls Indexed | Counter |  | N |  |  |  | If F13-BLC-401 indexer is RUNNING, count for one shot (Rising-Edge Trigger) each time ZI13035 = Active If F13-BLC-401 indexer is NOT RUNNING, reset counter to zero. Refer to F13CALC10001 | 0
F13LU451_T1 | 2000-F13-PID-PR-10001 | F13FA411 GreaseCycleTime | Timer PT = 4680 Seconds |  | N |  |  |  | Source: 2000-ME004-M01-10002 Timer is started (or resumed if paused) by the following conditions: - F13-FA-411 Running AND F13LU451_T2 Stopped Timer is paused if: - F13-FA-411 Not Running When F13LU451_T1 elapses: - Stop and reset F13LU451_T1 and - Start F13LU451_T2 Timer Settings: DEFAULT SETTING: 4680 SECONDS. ENGINEER CONFIGURABLE RANGE: 3000 - 6000 SECONDS. | A
F13LU451_T2 | 2000-F13-PID-PR-10001 | F13FA411 Greasing Timer | Timer PT = 120 Seconds |  | N |  |  |  | Source: 2000-ME004-M01-10002 Timer is started when F13LU451_T1 elapses. F13-LU-451 starts greasing when F13LU451_T2 is in progress (refer to Drives tab, F13-LU-451) When timer elapses, F13LU451_T2 will stop (and reset to 0) and F13LU451_T1 will restart provided F13-FA-411 is still running. If F13-FA-411 stops during the grease cycle, F13LU451_T2 will elapse and turn off. Timer Settings: DEFAULT SETTING: 120 SECONDS. ENGINEER CONFIGURABLE RANGE: 10 - 600 SECONDS. | B | [6 empty] | desktop review
F13LU451_T3 | 2000-F13-PID-PR-10001 | F13FA411 24Hr Fault Time | Timer PT = 86400 Seconds | Alarm (13LU451_T3A) at 57600 Seconds | N |  |  |  | Source: 2000-ME004-M01-10002 Timer is started if: - XS13008 does not pulse / activate whilst F13-FA-411 is running OR - LAL13009 Alarm Stop and reset timer when - XS13008 does pulse / activate whilst F13-FA-411 is running AND - LAL13009 Inactive Pause timer if: - F13-FA-411 = Stopped If timer elapses, F13-FA-411 interlocks (see Drives tab). Show beside relevant Feeder graphic Timer Settings: DEFAULT SETTING: 86400 SECONDS ENGINEER CONFIGURABLE RANGE: 3600 - 86400 SECONDS. | 1 | 6/03/2025 29/04/2025 30/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1470 RE: Recycle Crushing Punchlist Items https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-295?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC |  |  |  |  | desktop review
F13LU452_T1 | 2000-F13-PID-PR-10001 | F13FA412 GreaseCycleTime | Timer PT = 4680 Seconds |  | N |  |  |  | Source: 2000-ME004-M01-10002 Timer is started (or resumed if paused) by the following conditions: - F13-FA-412 Running AND F13LU452_T2 Stopped Timer is paused if: - F13-FA-412 Not Running When F13LU452_T1 elapses: - Stop and reset F13LU452_T1 and - Start F13LU452_T2 Timer Settings: DEFAULT SETTING: 4680 SECONDS. ENGINEER CONFIGURABLE RANGE: 3000 - 6000 SECONDS. | A
F13LU452_T2 | 2000-F13-PID-PR-10001 | F13FA412 Greasing Timer | Timer PT = 120 Seconds |  | N |  |  |  | Source: 2000-ME004-M01-10002 Timer is started when F13LU452_T1 elapses. F13-LU-452 starts greasing when F13LU452_T2 is in progress (refer to Drives tab, F13-LU-452) When timer elapses, F13LU452_T2 will stop (and reset to 0) and F13LU452_T1 will restart provided F13-FA-412 is still running. If F13-FA-412 stops during the grease cycle, F13LU452_T2 will elapse and turn off. Timer Settings: DEFAULT SETTING: 120 SECONDS. ENGINEER CONFIGURABLE RANGE: 10 - 600 SECONDS. | B | [6 empty] | desktop review
F13LU452_T3 | 2000-F13-PID-PR-10001 | F13FA412 24Hr Fault Time | Timer PT = 86400 Seconds | Alarm (13LU452_T3A) at 57600 Seconds | N |  | 0 |  | Source: 2000-ME004-M01-10002 Timer is started if: - XS13018 does not pulse / activate whilst F13-FA-412 is running OR - LAL13019 Active Stop and reset timer when: - XS13018 does pulse / activate whilst F13-FA-412 is running AND - LAL13019 Inactive Pause timer if: - F13-FA-412 = Stopped If timer elapses, F13-FA-412 interlocks (see Drives tab). Show beside relevant Feeder graphic Timer Settings: DEFAULT SETTING: 86400 SECONDS ENGINEER CONFIGURABLE RANGE: 3600 - 86400 SECONDS. | 1 | 6/03/2025 29/04/2025 30/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1470 RE: Recycle Crushing Punchlist Items https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-295?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
F13LU453_T1 | 2000-F13-PID-PR-10001 | F13FA414 GreaseCycleTime | Timer PT = 4680 Seconds |  | N |  |  |  | Source: 2000-ME004-M01-10003 Timer is started (or resumed if paused) by the following conditions: - F13-FA-414 Running AND F13LU453_T2 Stopped Timer is paused if: - F13-FA-414 Not Running When F13LU453_T1 elapses: - Stop and reset F13LU453_T1 and - Start F13LU453_T2 Timer Settings: DEFAULT SETTING: 4680 SECONDS. ENGINEER CONFIGURABLE RANGE: 3000 - 6000 SECONDS. | A | [6 empty] | desktop review
F13LU453_T2 | 2000-F13-PID-PR-10001 | F13FA414 Greasing Timer | Timer PT = 120 Seconds |  | N |  |  |  | Source: 2000-ME004-M01-10003 Timer is started when F13LU453_T1 elapses. F13-LU-453 starts greasing when F13LU453_T2 is in progress (refer to Drives tab, F13-LU-453) When timer elapses, F13LU453_T2 will stop (and reset to 0) and F13LU453_T1 will restart provided F13-FA-414 is still running. If F13-FA-414 stops during the grease cycle, F13LU453_T2 will elapse and turn off. Timer Settings: DEFAULT SETTING: 120 SECONDS. ENGINEER CONFIGURABLE RANGE: 10 - 600 SECONDS. | B | [6 empty] | desktop review
F13LU453_T3 | 2000-F13-PID-PR-10001 | F13FA414 24Hr Fault Time | Timer PT = 86400 Seconds | Alarm (13LU453_T3A) at 57600 Seconds | N |  | 0 |  | Source: 2000-ME004-M01-10003 Timer is started if: - XS13028 does not pulse / activate whilst F13-FA-414 is running OR - LAL13029 Active Stop and reset timer when: - XS13028 does pulse / activate whilst F13-FA-414 is running AND - LAL13029 Inactive Pause timer if: - F13-FA-414 = Stopped If timer elapses, F13-FA-414 interlocks (see Drives tab). Show beside relevant Feeder graphic Timer Settings: DEFAULT SETTING: 86400 SECONDS ENGINEER CONFIGURABLE RANGE: 3600 - 86400 SECONDS. | 1 | 6/03/2025 29/04/2025 30/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1470 RE: Recycle Crushing Punchlist Items https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-295?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
F13CC401_CLMP | 2000-F13-PID-PR-10006 | F13CC401 Clamp | Button |  | N |  |  |  | Enabling F13CC401_CLMP will auto activate/deactivate event switch YS13273 (Clamping) via process switchpoints. See Misc tab for details (YS13273). Interlock for F13-CC-401. Actions: • Activating F13CC401_CLMP will set the F13-HU-403 equipment and valves to AUTO, including: F13-PO-408, SV13269, SV13270, SV13271, SV13272, SV13273, SV13274, SV13275, SV13276. • De-activating F13CC401_CLMP AND F13CC401_TRMP, F13CC401_HPU AND F13CC401_CLR will set the F13-HU-403 equipment and valves to MANUAL, and stop / de-energise them (one shot), including: F13-PO-408, SV13269, SV13270, SV13271, SV13272, SV13273, SV13274, SV13275, SV13276. • Activating F13CC401_CLMP enables process switchpoints on YS13273. See Misc tab for details of process switchpoints (YS13273) F13CC401_HPU must be de-activated to activate F13CC401_CLMP. Ensure button cannot be disabled if F13-CC-401 is running. Enable/Disable button: • AUTO CLAMP PRESSURISE See 2000-ME001.6-M02-50001 for details | 1 | 6/03/2025 28/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1468 https://pastech-2955.atlassian.net/browse/KAN-1709
F13CC401_TRMP | 2000-F13-PID-PR-10006 | F13CC401 Tramp | Button |  | N |  |  |  | Enabling F13CC401_TRMP will auto activate/deactivate event switch YS13276 (Tramping) via process switchpoints. See Misc tab for details (YS13276). Interlock for F13-CC-401. Actions: • Activating F13CC401_TRMP will set the F13-HU-403 equipment and valves to AUTO, including: F13-PO-408, SV13269, SV13270, SV13271, SV13272, SV13273, SV13274, SV13275, SV13276. De-activating F13CC401_CLMP AND F13CC401_TRMP, F13CC401_HPU AND F13CC401_CLR will set the F13-HU-403 equipment and valves to MANUAL, and stop / de-energise them (one shot), including: F13-PO-408, SV13269, SV13270, SV13271, SV13272, SV13273, SV13274, SV13275, SV13276. Activating F13CC401_TRMP enables process switchpoints on YS13276 See Misc tab for details of process switchpoints (YS13276). F13CC401_HPU must be de-activated to activate F13CC401_TRMP. Ensure button cannot be disabled if F13-CC-401 is running. Enable/Disable button: • AUTO TRAMP PRESSURISE See 2000-ME001.6-M02-50001 for details | 1 | 6/03/2025 28/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1468 https://pastech-2955.atlassian.net/browse/KAN-1709
F13CC401_CLR | 2000-F13-PID-PR-10006 | F13CC401 Clearing | Button |  | N |  |  |  | Push button on DCS Push button only available if F13CC401_TRMP, F13CC401_CLMP and F13CC401_HPU inactive If activated, activate YS13275 De-activating F13CC401_CLMP AND F13CC401_TRMP, F13CC401_HPU AND F13CC401_CLR will set the F13-HU-403 equipment and valves to MANUAL, and stop / de-energise them (one shot), including: F13-PO-408, SV13269, SV13270, SV13271, SV13272, SV13273, SV13274, SV13275, SV13276. | 1 | 2025-04-28 | https://pastech-2955.atlassian.net/browse/KAN-1709
F13CC401_FP2 | 2000-F13-PID-PR-10006 | F13LU403 Duty Lube Pump | Operator Selection |  | N |  |  |  | Selected Lube Pumps will be in DUTY mode. Deselected Lube Pumps will be in STANDBY mode. For use in F13-SEQ-0028 Faceplate Selection: • F13-PO-401 OR • F13-PO-402 See 2000-ME001.6-M02-50001 for details | B | [6 empty] | Logic Functionality checked only To revisit once Pumps are loop/bump tested. 13CC401_FP2 is catered by NSR duty standby faceplate selection for 13PO401/402 VV; 25/07/2026 - 13PO401/402 pumps confirmed ran.
F13CC401_MRT | 2000-F13-PID-PR-10006 | F13CC401 Lube Min Time | Timer PT = 120 Seconds |  | N |  |  |  | FLS Ref: LUBE_MRT_TM Minimum time the Lubrication Unit must run before F13-CC-401 is allowed to start (see Drives tab). Start 120 second timer when duty F13-PO-401 OR F13-PO-402 = RUNNING. Stop and reset timer when F13-PO-401 AND F13-PO-402 = NOT RUNNING. See 2000-ME001.6-M02-50001 for details | B
F13CC401_T2 | 2000-F13-PID-PR-10006 | F13CC401 Drive Min Time | Timer PT = 120 Seconds |  | N |  |  |  | F13-FV-401 Start Permissive. Refer Drives tab. This is the minimum time the Crusher drive must run (to ensure proper crusher bushing lubrication) before feed can be introduced. Start 120 second delay on timer when F13-CC-401 = RUNNING. Stop and reset timer when F13-CC-401 = NOT RUNNING. See 2000-ME001.6-M02-50001 for details | B
F13CC401_T3 | 2000-F13-PID-PR-10006 | F13CC401 Stop Delay | Timer PT = 120 Seconds |  | N |  |  |  | Lube pump to run on for two minutes after crusher has stopped. Used in F13-SEQ-0031. Start 120 second timer when F13-CC-401 = NOT RUNNING. Stop and reset timer when F13-CC-401 = RUNNING. See 2000-ME001.6-M02-50001 for details | B
F13CC401_IDL | 2000-F13-PID-PR-10006 | F13CC401 Idling | Timer PT = 1200 Seconds |  | N |  |  |  | FLS Ref: CR_Idle_OK Start timer: F13CC401 Power (kW) PV from VSD < F13CC401 Power (kW) Set Value (F13CC401_PWR) AND F13-CC-401 = RUNNING Else, stop and reset time See 2000-ME001.6-M02-50001 for details | 1 | 2025-03-26 | https://pastech-2955.atlassian.net/browse/KAN-1604
F13CC401_PWR | 2000-F13-PID-PR-10006 | F13CC401 Idle Power | Setpoint |  | N |  |  |  | FLS Ref: CR_Idle_OK For use in F13CC401_IDL. Entered by operator in kW. Nominal: 94kW Range: 0 - 200kW Engineer level access required for changes. Nominal based on 25% load, 2000-ME001.6-F14-50001 Rev E. TBC during commissioning. See 2000-ME001.6-M02-50001 for details | 1 | 2025-03-26 | https://pastech-2955.atlassian.net/browse/KAN-1604
F13CC401_CAL | 2000-F13-PID-PR-10006 | F13CC401 Calib. Cmd | Inactive |  | N |  |  |  | FLS Ref: CALIB_CMD Activated and de-activated as part of F13-SEQ-0034 See 2000-ME001.6-M02-50001 for details | 1 | 2025-05-01 | Updated to align with programming. No action
F13CC401_RAT | 2000-F13-PID-PR-10006 | F13CC401 Tooth Ratio | Setpoint |  | N |  |  |  | DEFAULT SETTING: 0.23 mm ENGINEER CONFIGURABLE RANGE: 0 - 1 mm Used for F13CALC10030 and F13CC401_CRP See 2000-ME001.6-M02-50001 for details | 0
F13CC401_CRP | 2000-F13-PID-PR-10006 | F13CC401 Bowl Creep | Inactive | Active | N |  | 3 | Mask alarm and interlocks when: F13CC401_CAL = Active OR PI13263 < A_LL | FLS Ref: BCRP_OK Alarm to activate when: - F13CC401_CSS.PV > F13CC401_CSS.SV + (2 * F13CC401_RAT) OR - F13CC401_CSS.PV < F13CC401_CSS.SV - (2 * F13CC401_RAT) Deactivate when: - F13CC401_CSS.PV within +/- (2 * F13CC401_RAT) Refer to F13CALC10030 See 2000-ME001.6-M02-50001 for details | 1 | 2025-04-07 | https://pastech-2955.atlassian.net/browse/KAN-1652
F13CC401_DUP | 2000-F13-PID-PR-10006 | F13CC401 Count Dir. Up | Inactive |  | N |  |  |  | CNTDIRUP Bowl raising or lowering direction is determined using two limit switches. If F13CC401_DUP and F13CC401_CUP energise, then F13CC401_CSS will increase by F13CC401_RAT (See F13CALC10030). i.e., the CSS has increased. Activate when: - ZA13252A = Active AND ZA13252B = Inactive SV13271 = Open Deactivate when: - ZA13252A = Inactive AND ZA13252B = Inactive SV13271 = Closed Refer to F13CALC10030 See 2000-ME001.6-M02-50001 for details | 0
F13CC401_DDN | 2000-F13-PID-PR-10006 | F13CC401 Count Dir. Down | Inactive |  | N |  |  |  | CNTDIRDOWN Bowl raising or lowering direction is determined using two limit switches. If F13CC401_DDN and F13CC401_CDN energise, then F13CC401_CSS will decrease by F13CC401_RAT (See F13CALC10030). i.e., the CSS has decreased. Activate when: - ZA13252A = Inactive AND ZA13252B = Active SV13272 = Open Deactivate when: - ZA13252A = Inactive AND ZA13252B = Inactive SV13272 = Closed Refer to F13CALC10030 See 2000-ME001.6-M02-50001 for details | 0
F13CC401_CUPA | 2000-F13-PID-PR-10006 | F13CC401 Count Up | Inactive |  | N |  |  |  | CNTUP Bowl raising or lowering direction is determined using two limit switches. If F13CC401_DUP and F13CC401_CUP energise, then F13CC401_CSS will increase by F13CC401_RAT (See F13CALC10030). i.e., the CSS has increased. F13CC401_CUP = Active for one shot (Rising-Edge Trigger) if: • F13CC401_DUP = Active AND ZA13252A = Active Refer to F13CALC10030 See 2000-ME001.6-M02-50001 for details | 0
F13CC401_CUPB | 2000-F13-PID-PR-10006 | F13CC401 Count Up | Inactive |  | N |  |  |  | CNTUP Bowl raising or lowering direction is determined using two limit switches. If F13CC401_DUP and F13CC401_CUP energise, then F13CC401_CSS will increase by F13CC401_RAT (See F13CALC10030). i.e., the CSS has increased. F13CC401_CUP = Active for one shot (Rising-Edge Trigger) if: • F13CC401_DUP = Active AND ZA13252B = Active Refer to F13CALC10030 See 2000-ME001.6-M02-50001 for details | 0
F13CC401_CDNA | 2000-F13-PID-PR-10006 | F13CC401 Count Down | Inactive |  | N |  |  |  | CNTDOWN Bowl raising or lowering direction is determined using two limit switches. If F13CC401_DDN and F13CC401_CDN energise, then F13CC401_CSS will decrease by F13CC401_RAT (See F13CALC10030). i.e., the CSS has decreased. F13CC401_CDN = Active for one shot (Rising-Edge Trigger) if: • F13CC401_DDN = Active AND ZA13252A = Active Refer to F13CALC10030 See 2000-ME001.6-M02-50001 for details | 0
F13CC401_CDNB | 2000-F13-PID-PR-10006 | F13CC401 Count Down | Inactive |  | N |  |  |  | CNTDOWN Bowl raising or lowering direction is determined using two limit switches. If F13CC401_DDN and F13CC401_CDN energise, then F13CC401_CSS will decrease by F13CC401_RAT (See F13CALC10030). i.e., the CSS has decreased. F13CC401_CDN = Active for one shot (Rising-Edge Trigger) if: • F13CC401_DDN = Active AND ZA13252B = Active Refer to F13CALC10030 See 2000-ME001.6-M02-50001 for details | 0
F13CC401_MAX | 2000-F13-PID-PR-10006 | F13CC401 Max CSS | Setpoint |  | N |  |  |  | FLS Ref: CSS_MAX The max allowable CSS setpoint. Engineer access only. DEFAULT SETTING: 20 mm ENGINEER CONFIGURABLE RANGE: 0 - 40 mm F13CC401_MAX must be > F13CC401_MIN Used in F13CC401_CSS alarms and interlocks. See F13CC401_CSS in Analogue Input tab. See 2000-ME001.6-M02-50001 for details | 1 | 2025-04-07 | https://pastech-2955.atlassian.net/browse/KAN-1656
F13CC401_MIN | 2000-F13-PID-PR-10006 | F13CC401 Min CSS | Setpoint |  | N |  |  |  | FLS Ref: CSS_MIN The minimum allowable CSS. Engineer access only. DEFAULT SETTING: 6.5 mm ENGINEER CONFIGURABLE RANGE: 0 - 13 mm F13CC401_MAX must be > F13CC401_MIN Used in F13CC401_CSS alarms and interlocks. See F13CC401_CSS in Analogue Input tab. See 2000-ME001.6-M02-50001 for details | 1 | 2025-04-07 | https://pastech-2955.atlassian.net/browse/KAN-1656
F13CC401_WR | 2000-F13-PID-PR-10006 | F13CC401 Wear Rates | Graphic |  | N |  |  |  | Record and log F13CC401_CSS.PV during CSS Calibration Sequence F13-SEQ-0029 Step 7. This information is used to estimate mantle wear. See F13-SEQ-0029 Step 7B: • The first recorded 'mantle contact' value of a newly installed mantle is forced to equal 0, and is given a unique mantle identifier #. See F13-SEQ-0029 Step 7A: • Subsequent recorded 'mantle contact' values for the existing mantle equals F13CC401_CSS.PV when the mantle is in contact with the bowl, and retains the latest unique mantle identifier #. Include wear rates in a table (or similar) with each calibration sequence as a line item. Include Unique Mantle #, Calibration Time Stamp, Recorded 'Mantle Contact' Value and the Cumulative of 'Mantle Contact' values for the current Unique Mantle #. Ensure all past and present values can be accessed for analysis. See 2000-ME001.6-M02-50001 for details | B
HS13279ASTT_OP | 2000-F13-PID-PR-10006 | F13CC401-CP Start | Op Guide | [5 empty] | HS13279ASTT is used to request local control via an Op guide: "Field local request button pressed. Enable F13CC401_HPU to hand over control." | 1 | 2025-04-09 | https://pastech-2955.atlassian.net/browse/KAN-1658
F13CC401_HPU | 2000-F13-PID-PR-10006 | F13HU403 Activate LCP | Inactive |  | N |  |  |  | If F13CC401_HPU = Active, F13-HU-403 pump and valves will operate according to the control panel button / switch descriptions, refer HS13279B, HS13279C, HS13279D, HS13279E, HS13279F, HS13279G, HS13279H in the Digital Input tab. To enable F13CC401_HPU, F13-CC-401 = Not Running AND F13-SEQ-0028 AND F13-SEQ-0029 Not Running Logic: If F13CC401_HPU = Active: • Set F13-PO-408, SV13269, SV13270, SV13271, SV13272, SV13273, SV13274, SV13275, SV13276 forced to AUT AND • DE-ACTIVATE F13CC401_CLMP AND F13CC401_TRMP. Deactivate/unlatch F13CC401_HPU if: • HS13279BSTP = Active OR • Deactivated by CRO Process Interlocks must apply (hence MANUAL mode), however; DCS can stop F13-PO-408 and de-energise solenoid valves ONLY. LCS start / stop conditions apply as per the control panel button / switch descriptions. See 2000-ME001.6-M02-50001 for details | 1 | 6/03/2025 4/4/2025 | https://pastech-2955.atlassian.net/browse/KAN-1468 https://pastech-2955.atlassian.net/browse/KAN-1654
YS13273 | 2000-F13-PID-PR-10006 | F13CC401 Press Clamp Cyl | Inactive |  | N |  |  |  | If F13CC401_CLMP is Active THEN auto activate/deactivate as per the below: • Activate YS13273 when PI13263 <= P_Lo • Deactivate YS13273 when PI13263 >= P_Hi When YS13273 = Active, set the following: • F13-PO-408 = Running AND • SV13269 = Closed AND • SV13273 = Open If YS13273 = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13273, YS13271A, YS13272A, YS13271B, YS13272B, YS13275, YS13276 or YS13274 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1468
YS13271A | 2000-F13-PID-PR-10006 | F13CC401 Open Bowl Slow | Inactive |  | N |  |  |  | YS13271A Activated by: • Sequence F13-SEQ-0029 (via YS13271ASEQ = Active) OR • F13CC401_HPU AND HS13279COP AND HS13279FSLOW ACTIVE Deactivated by: • Sequence F13-SEQ-0029 (via YS13271ASEQ = Inactive) OR • (F13CC401_HPU OR HS13279COP OR HS13279FSLOW INACTIVE) AND YS13271ASEQ INACTIVE OR • PS13266 Open for 2 seconds When YS13271A = Active, set the following: • F13-PO-408 = Running AND • SV13269 = Closed AND • SV13271 = Open AND • SV13274 = Open If YS13271A = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13273, YS13271A, YS13272A, YS13271B, YS13272B, YS13275, YS13276 or YS13274 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). YS13271ASEQ: If F13-SEQ-0029 sequence pauses or stops deactivate YS13271ASEQ | 2 | 6/03/2025 4/4/2025 | https://pastech-2955.atlassian.net/browse/KAN-1468 https://pastech-2955.atlassian.net/browse/KAN-1654
YS13272A | 2000-F13-PID-PR-10006 | F13CC401 Close Bowl Slow | Inactive |  | N |  |  |  | YS13272A Activated by: • Sequence F13-SEQ-0029 (via YS13272ASEQ = Active) OR • F13CC401_HPU AND HS13279DCL AND HS13279FSLOW ACTIVE Deactivated by: • Sequence F13-SEQ-0029 (via YS13272ASEQ = Inactive) OR • (F13CC401_HPU OR HS13279DCL OR HS13279FSLOW INACTIVE) AND YS13272ASEQ INACTIVE OR • PS13265 Closed for 2 seconds When YS13272A = Active, set the following: • F13-PO-408 = Running AND • SV13269 = Closed AND • SV13272 = Open AND • SV13274 = Open If YS13272A = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13273, YS13271A, YS13272A, YS13271B, YS13272B, YS13275, YS13276 or YS13274 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). YS13272ASEQ: If F13-SEQ-0029 sequence pauses or stops deactivate YS13272ASEQ | 2 | 6/03/2025 4/4/2025 | https://pastech-2955.atlassian.net/browse/KAN-1468 https://pastech-2955.atlassian.net/browse/KAN-1654
YS13271B | 2000-F13-PID-PR-10006 | F13CC401 Open Bowl Fast | Inactive |  | N |  |  |  | YS13271B Activated by: • F13CC401_HPU AND HS13279COP AND HS13279EFAST ACTIVE Deactivated by: • F13CC401_HPU OR HS13279COP OR HS13279EFAST INACTIVE OR • PS13266 Opened for 2 seconds When YS13271B = Active, set the following: • F13-PO-408 = Running AND • SV13269 = Closed AND • SV13270 = Closed AND • SV13271 = Open AND • SV13274 = Open If YS13271B = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13273, YS13271A, YS13272A, YS13271B, YS13272B, YS13275, YS13276 or YS13274 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1389
YS13272B | 2000-F13-PID-PR-10006 | F13CC401 Close Bowl Fast | Inactive |  | N |  |  |  | YS13272B Activated by: • F13CC401_HPU AND HS13279DCL AND HS13279EFAST ACTIVE Deactivated by: • F13CC401_HPU OR HS13279DCL OR HS13279EFAST INACTIVE OR • PS13265 Closed for 2 seconds When YS13272B = Active, set the following: • F13-PO-408 = Running AND • SV13269 = Closed AND • SV13270 = Closed AND • SV13272 = Open AND • SV13274 = Open If YS13272B = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13273, YS13271A, YS13272A, YS13271B, YS13272B, YS13275, YS13276 or YS13274 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1389
YS13275 | 2000-F13-PID-PR-10006 | F13CC401 Clearing | Inactive |  | N |  |  |  | YS13275 Activated by: • CRO via a pushbutton on the DCS (ref F13CC401_CLR) OR • F13CC401_HPU AND HS13279HCLR ACTIVE ELSE deactivate. When YS13275 = Active, set the following: • F13-PO-408 = Running AND • SV13269 = Closed AND • SV13275 = Open If YS13275 = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13273, YS13271A, YS13272A, YS13271B, YS13272B, YS13275, YS13276 or YS13274 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). | 2 | 2025-04-28 | https://pastech-2955.atlassian.net/browse/KAN-1709
YS13276 | 2000-F13-PID-PR-10006 | F13CC401 Set Tramp Rel. | Inactive |  | N |  |  |  | If F13CC401_TRMP is Active OR [F13CC401_HPU AND HS13279GTRP ACTIVE] THEN auto activate/deactivate as per the below: • Activate YS13276 when PI13264 < P_Lo • Deactivate YS13276 when PI13264 > P_Hi When YS13276 = Active, set the following: • F13-PO-408 = Running AND • SV13269 = Closed AND • SV13276 = Open If YS13276 = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13273, YS13271A, YS13272A, YS13271B, YS13272B, YS13275, YS13276 or YS13274 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1468
YS13274 | 2000-F13-PID-PR-10006 | F13CC401 Depressurise | Inactive |  | N |  |  |  | When YS13274 = Active, set the following: • SV13274 = Open If F13-SEQ-0029 sequence pauses or stops, deactivate YS13274 If YS13274 = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13273, YS13271A, YS13272A, YS13271B, YS13272B, YS13275, YS13276 or YS13274 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). | 2 | 2025-04-04 | https://pastech-2955.atlassian.net/browse/KAN-1654
F13CC402_CLMP | 2000-F13-PID-PR-10006 | F13CC402 Clamp | Button |  | N |  |  |  | Enabling F13CC402_CLMP will auto activate/deactivate event switch YS13333 (Clamping) via process switchpoints. See Misc tab for details (YS13333). Interlock for F13-CC-402. Actions: • Activating F13CC402_CLMP will set the F13-HU-404 equipment and valves to AUTO, including: F13-PO-409, SV13329, SV13330, SV13331, SV13332, SV13333, SV13334, SV13335, SV13336. • De-activating F13CC402_CLMP AND F13CC402_TRMP, F13CC402_HPU AND F13CC402_CLR will set the F13-HU-404 equipment and valves to MANUAL, and stop / de-energise them (one shot), including: F13-PO-409, SV13329, SV13330, SV13331, SV13332, SV13333, SV13334, SV13335, SV13336. • Activating F13CC402_CLMP enables process switchpoints on YS13333 See Misc tab for details of process switchpoints (YS13333) F13CC402_HPU must be de-activated to activate F13CC402_CLMP. Ensure button cannot be disabled if F13-CC-402 is running. Enable/Disable button: • AUTO CLAMP PRESSURISE See 2000-ME001.6-M02-50001 for details | 1 | 6/03/2025 28/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1468 https://pastech-2955.atlassian.net/browse/KAN-1709
F13CC402_TRMP | 2000-F13-PID-PR-10006 | F13CC402 Tramp | Button |  | N |  |  |  | Enabling F13CC402_TRMP will auto activate/deactivate event switch YS13336 (Tramping) via process switchpoints. See Misc tab for details (YS13336). Interlock for F13-CC-402. Actions: • Activating F13CC402_TRMP will set the F13-HU-404 equipment and valves to AUTO, including: F13-PO-409, SV13329, SV13330, SV13331, SV13332, SV13333, SV13334, SV13335, SV13336. • De-activating F13CC402_CLMP AND F13CC402_TRMP, F13CC402_HPU AND F13CC402_CLR will set the F13-HU-404 equipment and valves to MANUAL, and stop / de-energise them (one shot), including: F13-PO-409, SV13329, SV13330, SV13331, SV13332, SV13333, SV13334, SV13335, SV13336. Activating F13CC402_TRMP enables process switchpoints on YS13336 See Misc tab for details of process switchpoints (YS13336). F13CC402_HPU must be de-activated to activate F13CC402_TRMP. Ensure button cannot be disabled if F13-CC-402 is running. Enable/Disable button: • AUTO TRAMP PRESSURISE See 2000-ME001.6-M02-50001 for details | 1 | 6/03/2025 28/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1468 https://pastech-2955.atlassian.net/browse/KAN-1709
F13CC402_CLR | 2000-F13-PID-PR-10006 | F13CC402 Clearing | Button |  | N |  |  |  | Push button on DCS Push button only available if F13CC402_TRMP, F13CC402_CLMP and F13CC402_HPU inactive If activated, activate YS13335 De-activating F13CC402_CLMP AND F13CC402_TRMP, F13CC402_HPU AND F13CC402_CLR will set the F13-HU-404 equipment and valves to MANUAL, and stop / de-energise them (one shot), including: F13-PO-409, SV13329, SV13330, SV13331, SV13332, SV13333, SV13334, SV13335, SV13336. | 1 | 2025-04-28 | https://pastech-2955.atlassian.net/browse/KAN-1709
F13CC402_FP2 | 2000-F13-PID-PR-10006 | F13LU404 Duty Lube Pump | Operator Selection |  | N |  |  |  | Selected Lube Pumps will be in DUTY mode. Deselected Lube Pumps will be in STANDBY mode. For use in F13-SEQ-0033 Faceplate Selection: • F13-PO-406 OR • F13-PO-407 See 2000-ME001.6-M02-50001 for details | B | [6 empty] | Selector Logic Functionality Checked only. It switches the DUTY pump on both the logic side and the Facpelate. Thus, the duty/standby functionality itself is functioning.
F13CC402_MRT | 2000-F13-PID-PR-10006 | F13CC402 Lube Min Time | Timer PT = 120 Seconds |  | N |  |  |  | FLS Ref: LUBE_MRT_TM Minimum time the Lubrication Unit must run before F13-CC-402 is allowed to start (see Drives tab). Start 120 second delay on timer when duty F13-PO-406 OR F13-PO-407 = RUNNING. Stop and reset timer when F13-PO-406 AND F13-PO-407 = NOT RUNNING. See 2000-ME001.6-M02-50001 for details | B
F13CC402_T2 | 2000-F13-PID-PR-10006 | F13CC402 Drive Min Time | Timer PT = 120 Seconds |  | N |  |  |  | F13-FV-402 Start Permissive. Refer Drives tab. This is the minimum time the Crusher drive must run (to ensure proper crusher bushing lubrication) before feed can be introduced. Start 120 second delay on timer when F13-CC-402 = RUNNING. Stop and reset timer when F13-CC-402 = NOT RUNNING. See 2000-ME001.6-M02-50001 for details | B
F13CC402_T3 | 2000-F13-PID-PR-10006 | F13CC402 Stop Timer | Timer PT = 120 Seconds |  | N |  |  |  | Lube pump to run on for two minutes after crusher has stopped. Used in F13-SEQ-0036 Start 120 second timer when F13-CC-402 = NOT RUNNING. Stop and reset timer when F13-CC-402 = RUNNING. See 2000-ME001.6-M02-50001 for details | B
F13CC402_IDL | 2000-F13-PID-PR-10006 | F13CC402 Idling | Timer PT = 1200 Seconds |  | N |  |  |  | FLS Ref: CR_Idle_OK Start timer: F13CC402 Power (kW) PV from VSD < F13CC402 Power (kW) Set Value (F13CC402_PWR) AND F13-CC-402 = RUNNING Else, stop and reset time See 2000-ME001.6-M02-50001 for details | 1 | 2025-03-26 | https://pastech-2955.atlassian.net/browse/KAN-1604
F13CC402_PWR | 2000-F13-PID-PR-10006 | F13CC402 Idle Power | Setpoint |  | N |  |  |  | FLS Ref: CR_Idle_OK For use in F13CC402_IDL. Entered by operator in kW. Nominal: 94kW Range: 0 - 200kW Engineer level access required for changes. Nominal based on 25% load, 2000-ME001.6-F14-50001 Rev E. TBC during commissioning. See 2000-ME001.6-M02-50001 for details | 1 | 2025-03-26 | https://pastech-2955.atlassian.net/browse/KAN-1604
F13CC402_CAL | 2000-F13-PID-PR-10006 | F13CC402 Calib. Cmd | Inactive |  | N |  |  |  | FLS Ref: CALIB_CMD Activated and de-activated as part of F13-SEQ-0029 See 2000-ME001.6-M02-50001 for details | 1 | 2025-05-01 | Updated to align with programming. No action
F13CC402_RAT | 2000-F13-PID-PR-10006 | F13CC402 Tooth Ratio | Setpoint = 0.23mm |  | N |  |  |  | DEFAULT SETTING: 0.23 mm ENGINEER CONFIGURABLE RANGE: 0 - 1 mm Used for F13CALC10030 and F13CC402_CRP See 2000-ME001.6-M02-50001 for details | 0
F13CC402_CRP | 2000-F13-PID-PR-10006 | F13CC402 Bowl Creep | Inactive | Active | N |  | 3 | Mask alarm and interlocks when: F13CC402_CAL = Active OR PI13323 < A_LL | FLS Ref: BCRP_OK Alarm to activate when: - F13CC402_CSS.PV > F13CC402_CSS.SV + (2 * F13CC402_RAT) OR - F13CC402_CSS.PV < F13CC402_CSS.SV - (2 * F13CC402_RAT) Deactivate when: - F13CC402_CSS.PV within +/- (2 * F13CC402_RAT) Refer to F13CALC10032 See 2000-ME001.6-M02-50001 for details | 1 | 2025-04-07 | https://pastech-2955.atlassian.net/browse/KAN-1652
F13CC402_DUP | 2000-F13-PID-PR-10006 | F13CC402 Count Dir. Up | Inactive |  | N |  |  |  | CNTDIRUP Bowl raising or lowering direction is determined using two limit switches. If F13CC402_DUP and F13CC402_CUP energise, then F13CC402_CSS will increase by F13CC402_RAT (See F13CALC10032). i.e., the CSS has increased. Activate when: - ZA13312A = Active AND ZA13312B = Inactive SV13331 = OPEN Deactivate when: - ZA13312A = Inactive AND ZA13312B = Inactive SV13331 = CLOSED Refer to F13CALC10032 See 2000-ME001.6-M02-50001 for details | 0
F13CC402_DDN | 2000-F13-PID-PR-10006 | F13CC402 Count Dir. Down | Inactive |  | N |  |  |  | CNTDIRDOWN Bowl raising or lowering direction is determined using two limit switches. If F13CC402_DDN and F13CC402_CDN energise, then F13CC402_CSS will decrease by F13CC402_RAT (See F13CALC10032). i.e., the CSS has decreased. Activate when: - ZA13312A = Inactive AND ZA13312B = Active SV13332 = OPEN Deactivate when: - ZA13312A = Inactive AND ZA13312B = Inactive SV13332 = CLOSED Refer to F13CALC10032 See 2000-ME001.6-M02-50001 for details | 0
F13CC402_CUPA | 2000-F13-PID-PR-10006 | F13CC402 Count Up | Inactive |  | N |  |  |  | CNTUP Bowl raising or lowering direction is determined using two limit switches. If F13CC402_DUP and F13CC402_CUP energise, then F13CC402_CSS will increase by F13CC402_RAT (See F13CALC10032). i.e., the CSS has increased. F13CC402_CUP = Active for one shot (Rising-Edge Trigger) if: • F13CC402_DUP = Active AND ZA13312A = Active Refer to F13CALC10032 See 2000-ME001.6-M02-50001 for details | 0
F13CC402_CUPB | 2000-F13-PID-PR-10006 | F13CC402 Count Up | Inactive |  | N |  |  |  | CNTUP Bowl raising or lowering direction is determined using two limit switches. If F13CC402_DUP and F13CC402_CUP energise, then F13CC402_CSS will increase by F13CC402_RAT (See F13CALC10032). i.e., the CSS has increased. F13CC402_CUP = Active for one shot (Rising-Edge Trigger) if: • F13CC402_DUP = Active AND ZA13312B = Active Refer to F13CALC10032 See 2000-ME001.6-M02-50001 for details
F13CC402_CDNA | 2000-F13-PID-PR-10006 | F13CC402 Count Down | Inactive |  | N |  |  |  | CNTDOWN Bowl raising or lowering direction is determined using two limit switches. If F13CC402_DDN and F13CC402_CDN energise, then F13CC402_CSS will decrease by F13CC402_RAT (See F13CALC10032). i.e., the CSS has decreased. F13CC402_CDN = Active for one shot (Rising-Edge Trigger) if: • F13CC402_DDN = Active AND ZA13312A = Active Refer to F13CALC10032 See 2000-ME001.6-M02-50001 for details | 0
F13CC402_CDNB | 2000-F13-PID-PR-10006 | F13CC402 Count Down | Inactive |  | N |  |  |  | CNTDOWN Bowl raising or lowering direction is determined using two limit switches. If F13CC402_DDN and F13CC402_CDN energise, then F13CC402_CSS will decrease by F13CC402_RAT (See F13CALC10032). i.e., the CSS has decreased. F13CC402_CDN = Active for one shot (Rising-Edge Trigger) if: • F13CC402_DDN = Active AND ZA13312B = Active Refer to F13CALC10032 See 2000-ME001.6-M02-50001 for details
F13CC402_MAX | 2000-F13-PID-PR-10006 | F13CC402 Max CSS | Setpoint |  | N |  |  |  | FLS Ref: CSS_MAX The max allowable CSS setpoint. Engineer access only.. DEFAULT SETTING: 20 mm ENGINEER CONFIGURABLE RANGE: 0 - 40 mm F13CC402_MAX must be > F13CC401_MIN Used in F13CC402_CSS alarms and interlocks. See F13CC402_CSS in Analogue Input tab. See 2000-ME001.6-M02-50001 for details | 1 | 2025-04-07 | https://pastech-2955.atlassian.net/browse/KAN-1656
F13CC402_MIN | 2000-F13-PID-PR-10006 | F13CC402 Min CSS | Setpoint |  | N |  |  |  | FLS Ref: CSS_MIN The minimum allowable CSS. Engineer access only. DEFAULT SETTING: 6.5 mm ENGINEER CONFIGURABLE RANGE: 0 - 13 mm F13CC402_MAX must be > F13CC401_MIN Used in F13CC402_CSS alarms and interlocks. See F13CC402_CSS in Analogue Input tab. See 2000-ME001.6-M02-50001 for details | 1 | 2025-04-07 | https://pastech-2955.atlassian.net/browse/KAN-1656
F13CC402_WR | 2000-F13-PID-PR-10006 | F13CC402 Wear Rates | Graphic |  | N |  |  |  | Record and log F13CC402_CSS.PV during CSS Calibration Sequence F13-SEQ-0034 Step 7. This information is used to estimate mantle wear. See F13-SEQ-0034 Step 7B: • The first recorded 'mantle contact' value of a newly installed mantle is forced to equal 0, and is given a unique mantle identifier #. See F13-SEQ-0034 Step 7A: • Subsequent recorded 'mantle contact' values for the existing mantle equals F13CC402_CSS.PV when the mantle is in contact with the bowl, and retains the latest unique mantle identifier #. Include wear rates in a table (or similar) with each calibration sequence as a line item. Include Unique Mantle #, Calibration Time Stamp, Recorded 'Mantle Contact' Value and the Cumulative of 'Mantle Contact' values for the current Unique Mantle #. Ensure all past and present values can be accessed for analysis. See 2000-ME001.6-M02-50001 for details | B
HS13343ASTT_OP | 2000-F13-PID-PR-10006 | F13CC402-CP Start | Op Guide | [5 empty] | HS13343ASTT is used to request local control via an Op guide: "Field local request button pressed. Enable F13CC402_HPU to hand over control." | 1 | 2025-04-09 | https://pastech-2955.atlassian.net/browse/KAN-1658
F13CC402_HPU | 2000-F13-PID-PR-10006 | F13HU404 Activate LCP | Inactive |  | N |  |  |  | If F13CC402_HPU = Active, F13-HU-404 pump and valves will operate according to the control panel button / switch descriptions, refer HS13343B, HS13343C, HS13343D, HS13343E, HS13343F, HS13343G, HS13343H in the Digital Input tab. To enable F13CC402_HPU, F13-CC-402 = Not Running AND F13-SEQ-0033 AND F13-SEQ-0034 Not Running Logic: If F13CC402_HPU = Active: • Set F13-PO-409, SV13329, SV13330, SV13331, SV13332, SV13333, SV13334, SV13335, SV13336 forced to AUT AND • DE-ACTIVATE F13CC402_CLMP AND F13CC402_TRMP. Deactivate/unlatch F13CC402_HPU if: • HS13343BSTP = Active OR • Deactived by CRO Process Interlocks must apply (hence MANUAL mode), however; DCS can stop F13-PO-409 and de-energise solenoid valves ONLY. LCS start / stop conditions apply as per the control panel button / switch descriptions. See 2000-ME001.6-M02-50001 for details | 1 | 6/03/2025 4/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1389 https://pastech-2955.atlassian.net/browse/KAN-1654
YS13333 | 2000-F13-PID-PR-10006 | F13CC402 Press Clamp Cyl | Inactive |  | N |  |  |  | if F13CC402_CLMP is ACTIVE THEN auto activate/deactivate as per the below: Activate YS13333 when PI13323 < P_Lo Deactivate YS13333 when PI13323 > P_Hi When YS13333 = Active, set the following: • F13-PO-409 = Running AND • SV13329 = Closed AND • SV13333 = Open If YS13333 = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13333, YS13331A, YS13334A, YS13331B, YS13334B, YS13335, YS13336 or YS13334 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1468
YS13331A | 2000-F13-PID-PR-10006 | F13CC402 Open Bowl Slow | Inactive |  | N |  |  |  | YS13331A Activated by: • Sequence F13-SEQ-0034 (via YS13331ASEQ = Active) OR • F13CC402_HPU AND HS13343COP AND HS13343FSLOW ACTIVE Deactivated by: • Sequence F13-SEQ-0034 (via YS13331ASEQ = Inactive) OR • (F13CC402_HPU OR HS13343COP OR HS13343FSLOW INACTIVE) AND YS13331ASEQ INACTIVE OR • PS13326 Opened for 2 seconds When YS13331A = Active, set the following: • F13-PO-409 = Running AND • SV13329 = Closed AND • SV13331 = Open AND • SV13334 = Open If YS13331A = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13333, YS13331A, YS13334A, YS13331B, YS13334B, YS13335, YS13336 or YS13334 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). YS13331ASEQ: If F13-SEQ-0034 sequence pauses or stops deactivate YS13331ASEQ | 2 | 6/03/2025 4/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1389 https://pastech-2955.atlassian.net/browse/KAN-1654
YS13334A | 2000-F13-PID-PR-10006 | F13CC402 Close Bowl Slow | Inactive |  | N |  |  |  | YS13334A Activated by: • Sequence F13-SEQ-0034 (via YS13334ASEQ = Active) OR • F13CC402_HPU AND HS13343DCL AND HS13343FSLOW ACTIVE Deactivated by: • Sequence F13-SEQ-0034 (via YS13334ASEQ = Inactive) OR • (F13CC402_HPU OR HS13343DCL OR HS13343FSLOW INACTIVE) AND YS13334ASEQ INACTIVE OR • PS13325 Closed for 2 seconds When YS13334A = Active, set the following: • F13-PO-409 = Running AND • SV13329 = Closed AND • SV13332 = Open AND • SV13334 = Open If YS13334A = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13333, YS13331A, YS13334A, YS13331B, YS13334B, YS13335, YS13336 or YS13334 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). YS13334ASEQ: If F13-SEQ-0034 sequence pauses or stops deactivate YS13334ASEQ | 2 | 6/03/2025 4/04/2025 | https://pastech-2955.atlassian.net/browse/KAN-1389 https://pastech-2955.atlassian.net/browse/KAN-1654
YS13331B | 2000-F13-PID-PR-10006 | F13CC402 Open Bowl Fast | Inactive |  | N |  |  |  | YS13331B Activated by: • F13CC402_HPU AND HS13343COP AND HS13343EFAST ACTIVE Deactivated by: • F13CC402_HPU OR HS13343COP OR HS13343EFAST INACTIVE OR • PS13326 Opened for 2 seconds When YS13331B = Active, set the following: • F13-PO-409 = Running AND • SV13329 = Closed AND • SV13330 = Closed AND • SV13331 = Open AND • SV13334 = Open If YS13331B = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13333, YS13331A, YS13334A, YS13331B, YS13334B, YS13335, YS13336 or YS13334 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1389
YS13334B | 2000-F13-PID-PR-10006 | F13CC402 Close Bowl Fast | Inactive |  | N |  |  |  | YS13334B Activated by: • F13CC402_HPU AND HS13343DCL AND HS13343EFAST ACTIVE Deactivated by: • F13CC402_HPU OR HS13343DCL OR HS13343EFAST INACTIVE OR • PS13325 Closed for 2 seconds When YS13334B = Active, set the following: • F13-PO-409 = Running AND • SV13329 = Closed AND • SV13330 = Closed AND • SV13332 = Open AND • SV13334 = Open If YS13334B = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13333, YS13331A, YS13334A, YS13331B, YS13334B, YS13335, YS13336 or YS13334 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1389
YS13335 | 2000-F13-PID-PR-10006 | F13CC402 Clearing | Inactive |  | N |  |  |  | YS13335 Activated by: • CRO via a pushbutton on the DCS (ref F13CC402_CLR) OR • F13CC402_HPU AND HS13343HCLR ACTIVE ELSE deactivate. When YS13335 = Active, set the following: • F13-PO-409 = Running AND • SV13329 = Closed AND • SV13335 = Open If YS13335 = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13333, YS13331A, YS13334A, YS13331B, YS13334B, YS13335 , YS13336 or YS13334 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). | 2 | 2025-04-28 | https://pastech-2955.atlassian.net/browse/KAN-1709
YS13336 | 2000-F13-PID-PR-10006 | F13CC402 Set Tramp Rel. | Inactive |  | N |  |  |  | If F13CC402_TRMP is Active OR [F13CC402_HPU AND HS13343GTRP ACTIVE] THEN auto activate/deactivate as per the below: • Activate YS13336 when PI13324 < P_Lo • Deactivate YS13336 when PI13324 > P_Hi When YS13336 = Active, set the following: • F13-PO-409 = Running AND • SV13329 = Closed AND • SV13336 = Open If YS13336 = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13333, YS13331A, YS13334A, YS13331B, YS13334B, YS13335 , YS13336 or YS13334 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). | 2 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1468
YS13334 | 2000-F13-PID-PR-10006 | F13CC402 Depressurise | Inactive |  | N |  |  |  | When YS13334 = Active, set the following: • SV13334 = Open If F13-SEQ-0034 sequence pauses or stops deactivate YS13334 If YS13334 = Inactive, the effected valves and pumps will deenergise/stop. However, if any of the following tags - YS13333, YS13331A, YS13334A, YS13331B, YS13334B, YS13335, YS13336 or YS13334 - are active and share common valves/pumps, those valves/pumps will remain energised until all relevant tags are inactive (see OnOff Valves and Drive tab for details). | 2 | 2025-04-04 | https://pastech-2955.atlassian.net/browse/KAN-1654
F13MS401_FP1 | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 Motor Lbe Pump | Operator Selection |  | N |  |  |  | CRO to select Duty SAG Mill Motor Lube Pump 1 OR 2. For use in F13-SEQ-0021B & 0022B. Faceplate Selection: • SAG Mill Motor Lube Pump 1 (F13-PO-421) OR • SAG Mill Motor Lube Pump 2 (F13-PO-422) | A | [6 empty] | Duty Pump selection is catered by NSR faceplate which triggers 13PO421DU/13PO422DU for sequence use.
F13MS401_FP2 | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 HP Lube Pump | Operator Selection |  | N |  |  |  | CRO to select Duty SAG Mill HP Lubrication Pump 1, 2 AND/OR 3. 2 Options must be selected. For use in F13-SEQ-0017. Faceplate Selection: • SAG Mill HP Lube Pump 1 (F13-PO-429) • SAG Mill HP Lube Pump 2 (F13-PO-430) • SAG Mill HP Lube Pump 3 (F13-PO-431) | A | [6 empty] | 2 step authentication access implemented
F13MS401_FP3 | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 LP Lube Pump | Operator Selection |  | N |  |  |  | CRO to select Duty SAG Mill LP Lubrication Pump 1 OR 2. For use in F13-SEQ-0017. Faceplate Selection: • SAG Mill LP Lube Pump 1 (F13-PO-427) OR • SAG Mill LP Lube Pump 2 (F13-PO-428) | A | [6 empty] | Duty Pump selection is catered by NSR faceplate which triggers 13PO427DU/13PO428DU for sequence use.
F13MS401_FP4 | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 PinBrg Lbe Pump | Operator Selection |  | N |  |  |  | CRO to select Duty SAG Mill Pinion Bearing Lube Oil Pump 1 OR 2. For use in F13-SEQ-0017. Faceplate Selection: • SAG Mill Pinion Bearing Lube Oil Pump 1 (F13-PO-434) OR • SAG Mill Pinion Bearing Lube Oil Pump 2 (F13-PO-435) | A | [6 empty] | Duty Pump selection is catered by NSR faceplate which triggers 13PO434DU/13PO435DU for sequence use.
MS_SPRY_CR | 2000-F13-PID-PR-10013 | F13MS401 Gear Spry Cr | Normal | Alarm | N |  | 0 |  | Critical Gear Spray System Permissive for Mill Rotation Alarm Alarm when: • F13MS401_T8 Elapsed Normal when: • F13MS401_T8 Not Elapsed OR Stopped | 1 | 2025-06-04 | Copy paste error. On-delay fixed on DCS side - AH
MS_GRSE_CR | 2000-F13-PID-PR-10013 | F13MS401 Seal Grse Cr | Normal | Alarm | N |  | 0 |  | Critical Seal Grease System Permissive for Mill Rotation Alarm Alarm when: • F13MS401_T6 Elapsed Normal when: • F13MS401_T6 Not Elapsed OR Stopped | 1 | 2025-06-04 | Copy paste error. On-delay fixed on DCS side - AH
MS_BRKFLT1 | 2000-F13-PID-PR-10013 | F13MS401 Brake NormFault | Normal | Alarm | N |  | 5 |  | Logic: • MS_OP_MODE = NORMAL AND • [ZSH13545 Inactive (Brake Engaged) OR • ZSH13547 Inactive (Brake Engaged) OR • SV13562 Deenergised] OR • LSL13551 INACTIVE (Hydraulic Reservoir Level Low) BH 11/07/2026 MOC-703) OR (Source: 2000-ME001.2-M02-50001, "SAG Mill Brake Normal Mode Permissive for SAG Mill Motors Alarm") Note: Refer to F13-PO-432 interlocks in Drives tab | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
MS_BRKFLT2 | 2000-F13-PID-PR-10013 | F13MS401 Brake ComAlarm | Normal |  | N |  |  |  | Logic (Healthy): • [MS_OP_MODE = NORMAL AND MS_RUNNING = NOT RUNNING AND • LSL13551 Active AND • TSH13552 Active AND • F13-PO-432 INTERLOCKS INACTIVE AND IN AUTO AND • ZSH13546 Active AND • ZSH13548 Active] (Source: 2000-ME001.2-M02-50001, "Brake Common Permissive for SAG Mill Motor Main Drive Alarm") | 1 | 6/03/2025 10/7/25 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/PL-336
MS_SPR_NCR | 2000-F13-PID-PR-10013 | F13MS401 Gear Spry NCr | Normal | Alarm | N |  | 0 |  | Gear Spray Failed Cycle Alarm Alarm when: • F13MS401_T8.PV > 0 seconds (i.e., timer has started) Normal when: • F13MS401_T8.PV = 0 seconds (i.e., timer has stopped and reset) | B
MS_GRS_NCR | 2000-F13-PID-PR-10013 | F13MS401 Seal Grse NCr | Normal | Alarm | N |  | 0 |  | Seal Grease Failed Cycle Alarm Alarm when: • F13MS401_T6 > 0 seconds (i.e., timer has started) Normal when: • F13MS401_T6 = 0 seconds (i.e., timer has stopped and reset) | B
F13MS401FEED | 2000-F13-PID-PR-10003 | F13MS401 No Feed Alarm | Timer PT = 20 Minutes | Timer Elapsed | N |  | 0 |  | IF MS_RUNNING = RUNNING AND WI13055.PV < 2 t/h (TBC during commissioning) for 'PT' minutes, alarm and show pop-up prompt. Stop and reset timer if MS_RUNNING = NOT RUNNING OR WI13055.PV > 2 t/h (TBC during commissioning) ALARM and PROMPT CRO "WARNING: SAG Mill running for 'PT' minutes without feed." < CLOSE > CRO to close prompt and manually action shutdown of Area F13 if required. | 1 | [6 empty] | TBC on WI13055 setpoint
MS_2S_BRK | 2000-F13-PID-PR-10013 | F13MS401 2-Stage Brake | Inactive |  | N |  |  |  | Two-Stage Braking for the SAG Mill IF HS13737MODE = Automatic THEN: • MS_2S_BRK is activated as per F13-SEQ-0022C OR manually by the CRO if MS_RUNNING = NOT RUNNING (include button on DCS) See 14. Cause & Effects tab for initiating conditions When MS_2S_BRK is ACTIVE: 1. Set SV13561, SV13562, SV13557 AND F13-PO-432 to AUTO 2. De-energise SV13561, SV13562 and SV13557 ONLY 1 CAN BE ACTIVE AT ANY TIME: MS_2S_BRK, MS_EN_BRK, MS_RL_BRK. The active tag is to latch, and unlatch when another tag becomes active. | 2 | 2026-02-28 | CR-026
MS_EN_BRK | 2000-F13-PID-PR-10013 | F13MS401 Parking Brake | Inactive |  | N |  |  |  | Parking Brake for the SAG Mill IF HS13737MODE = Local AND HS13738BRK = Engage, THEN activate MS_EN_BRK See 14. Cause & Effects tab for initiating conditions IF MS_EN_BRK = ACTIVE then: Immediately energise SV13561, and de-energise SV13562 and SV13557 AND Set F13-PO-432 to AUTO ONLY 1 CAN BE ACTIVE AT ANY TIME: MS_2S_BRK, MS_EN_BRK, MS_RL_BRK. The active tag is to latch, and unlatch when another tag becomes active. | 2 | 2026-02-28 | CR-026
MS_RL_BRK | 2000-F13-PID-PR-10013 | F13MS401 Release Brake | Inactive |  | N |  |  |  | Common Release Brake for the SAG Mill IF HS13737MODE = Automatic THEN MS_RL_BRK is activated as per F13-SEQ-0021A OR manually by the CRO (include button on DCS) OR IF HS13737MODE = Local AND HS13738BRK = Release, THEN activate MS_RL_BRK OR IF HS13737MODE Rising Edge Trigger (Local to Auto), THEN activate MS_RL_BRK See 14. Cause & Effects tab for initiating conditions IF MS_RL_BRK = ACTIVE then: Immediately energise SV13557 and SV13562, and de-energise SV13561 AND Set F13-PO-432 to AUTO. ONLY 1 CAN BE ACTIVE AT ANY TIME: MS_2S_BRK, MS_EN_BRK, MS_RL_BRK. The active tag is to latch, and unlatch when another tag becomes active. | 2 | 2025-06-30 | https://pastech-2955.atlassian.net/browse/PL-338
MS_NCR_ILK | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 Delayed Intlk | Normal | Alarm | N |  | 10 |  | Abormal Shutdown, Mill Delayed Stop Activation of MS_NCR_ILK will trip the SAG Mill Feed Conveyor F13-CV-403 (see Drives tab) to stop feed, and initiate F13-SEQ-0022A to sequence stop F13-MS-401A/B. Prompt CRO: "13MS401 Delayed Stop interlck active. Delayed Stop sequence initiating" < Close > MS_NCR_ILK is activated when: • MS_RUNNING = RUNNING AND • F13-MS-401A/B Delayed Stop Interlock = ACTIVE (refer to Drives tab) Disregard Drive tab condition on-delay timer and utilise 10 second on-delay on all conditions here (see Drives tab for further explanation). Motor lube timers extended to 15 sec to allow lube pumps to start. | 1 | 9/05/2025 19/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1807 https://pastech-2955.atlassian.net/browse/KAN-1877
MS_CR_ILK | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 Instant Intlk | Normal | Alarm | N |  | 1 |  | Abormal Shutdown, Mill Instantaneous Stop Activation of MS_CR_ILK will trip the SAG Mill Feed Conveyor F13-CV-403 (see Drives tab) to stop feed, and initiate F13-SEQ-0022C to sequence stop engages the F13-MS-401A/B brake (MS_2S_BRK). Prompt CRO: "13MS401 Instant Stop interlck active. Instant Stop sequence initiating" < Close > MS_CR_ILK is activated when: • MS_ESTOP = E-STOP ACTIVE OR • [MS_RUNNING = RUNNING AND • F13-MS-401A/B Instantaneous Stop Interlock = ACTIVE (refer to Drives tab)] Disregard Drive tab condition on-delay timer and utilise 1 second on-delay on all conditions here (exception, 0 second delay on MS_ESTOP). | 2 | 9/05/2025 19/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1807 https://pastech-2955.atlassian.net/browse/KAN-1877
F13MS401_T1 | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 LP Lube Delay | Timer PT = 5 Minutes |  | N |  |  |  | Minimum time the SAG Mill Low Pressure Lubrication Pump (1 off) must run before starting the SAG Mill Main Motor or inching the mill. Used in MS_PBL_NCR & MS_MBL_NCR and Drive Interlocks If timer has not elapsed, then the SAG Mill can not be started START: F13-PO-427 OR F13-PO-428 = RUNNING STOP (reset to 0): F13-PO-427 AND F13-PO-428 = NOT RUNNING Healthy Signal: • 1x LP Lube Pump (F13-PO-427 OR F13-PO-428) RUNNING for >= F13MS401_T1 PRESET TIME | 1 | 2025-06-30 | https://pastech-2955.atlassian.net/browse/KAN-1882 Removed deleted tags. No impact to logic
F13MS401_T2 | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 PinBrgLbe Delay | Timer PT = 5 Minutes |  | N |  |  |  | Minimum time the SAG Mill Pinion Bearing Lubrication Pump (1 off) must run before starting the SAG Mill Main Motor or inching the mill. Used in MS_PBL_NCR & MS_MBL_NCR and Drive Interlocks If timer has not elapsed, then the SAG Mill can not be started START: F13-PO-434 OR F13-PO-435 = RUNNING STOP (reset to 0): F13-PO-434 AND F13-PO-435 = NOT RUNNING Healthy Signal: • 1x Pinion Bearing Lube Pump (F13-PO-434 OR F13-PO-435) RUNNING for >= F13MS401_T2 PRESET TIME | 1 | 2025-06-30 | https://pastech-2955.atlassian.net/browse/KAN-1882 Removed deleted tags. No impact to logic
F13MS401_T3 | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 HP Lube Delay | Timer PT = 5 Minutes |  | N |  |  |  | Minimum time the SAG Mill HP Lubrication Pumps (2 off) must run before starting the SAG Mill Main Motor or inching the mill. Used in MS_MBL_NCR and Drive Interlocks If timer has not elapsed, then the SAG Mill can not be started START: (2 or more pumps) F13-PO-429, F13-PO-430 AND/OR F13-PO-431 = RUNNING STOP (reset to 0): (2 or more pumps) F13-PO-429, F13-PO-430 AND F13-PO-431 = NOT RUNNING Healthy Signal: • 2x HP Lube Pumps (F13-PO-429 AND/OR F13-PO-430 AND/OR F13-PO-431) RUNNING for >= F13MS401_T3 PRESET TIME | 1 | 2025-06-30 | https://pastech-2955.atlassian.net/browse/KAN-1882 Removed deleted tags. No impact to logic
F13MS401_T4 | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 Motor Lbe Delay | Timer PT = 10 Seconds |  | N |  |  |  | Minimum time the SAG Mill Motor Lubrication Pump (1 off) must run before starting the SAG Mill Main Motor. Used in MS_ML_NCR and Drive Interlocks If timer has not elapsed, then the SAG Mill can not be started START: F13-PO-421 OR F13-PO-422 = RUNNING STOP (reset to 0): F13-PO-421 AND F13-PO-422 = NOT RUNNING Healthy Signal: • 1x SAG Mill Motor Lube Pump (F13-PO-421 OR F13-PO-422) RUNNING for >= F13MS401_T4 PRESET TIME | 1 | 2025-06-30 | https://pastech-2955.atlassian.net/browse/KAN-1882 Removed deleted tags. No impact to logic
F13MS401_T5 | 2000-F13-PID-PR-10013 | F13MS401 Seal Grse Freq. | Timer PT = 6 Hours |  | N |  |  |  | Utilise a timer to initiate F13-SEQ-0019 every 6 hours that the SAG Mill Motors are running and F13-SEQ-0019 is not running. START or CONTINUE timer when the SAG Mill Main Motors are running and F13-SEQ-0019 is not running. PAUSE timer if the SAG Mill Main Motors are stopped. When timer elapses, the timer is STOPPED and a Rising-Edge Trigger will initiate F13-SEQ-0019. If the SAG Mill is still running after F13-SEQ-0019 is stopped / completed, the timer will START again (and reset to 0). START (and reset to 0) / CONTINUE (if paused): MS_RUNNING = RUNNING AND F13-SEQ-0019 = NOT RUNNING STOP: Timer Elapses PAUSE: MS_RUNNING = NOT RUNNING When F13MS401_T5 reaches PRESET TIME: Initiate F13-SEQ-0019 with Rising Edge Trigger | B
F13MS401_T6 | 2000-F13-PID-PR-10013 | F13MS401 Seal Grse Fail | Timer PT = 370 Minutes |  | N |  |  |  | If F13MS401_T6 elapses before F13MS401_C1 is able to do a successful seal grease dose (i.e. reach it's count setpoint), a critical alarm MS_GRSE_CR will activate. START: As per F13-SEQ-0019 STOP (and reset to 0): As per F13-SEQ-0019 OR F13MS401_C1 = Count Setpoint (4) CONTINUE: MS_RUNNING = RUNNING PAUSE: MS_RUNNING = NOT RUNNING If F13MS401_T6 has elapsed: Activate MS_GRSE_CR ACTIVATE MS_GRS_NCR IF F13MS401_T6.PV > 0 seconds | B
F13MS401_T7 | 2000-F13-PID-PR-10013 | F13MS401 Gear Spry Freq. | Timer PT = 15 Minutes |  | N |  |  |  | Utilise a timer to initiate F13-SEQ-0020 every 15 minutes that the SAG Mill Motors are running and F13-SEQ-0020 is not running. START or CONTINUE timer when the SAG Mill Main Motors are running and F13-SEQ-0020 is not running. PAUSE timer if the SAG Mill Main Motors are stopped. When timer elapses, the timer is STOPPED and a Rising-Edge Trigger will initiate F13-SEQ-0020. If the SAG Mill is still running after F13-SEQ-0020 is stopped / completed, the timer will START again (and reset to 0). START (and reset to 0) / CONTINUE (if paused): MS_RUNNING = RUNNING AND F13-SEQ-0020 = NOT RUNNING STOP: Timer Elapses PAUSE: MS_RUNNING = NOT RUNNING When F13MS401_T7 reaches PRESET TIME: Initiate F13-SEQ-0020 with Rising Edge Trigger | B
F13MS401_T8 | 2000-F13-PID-PR-10013 | F13MS401 Gear Spry Fail | Timer PT = 30 Minutes |  | N |  |  |  | If F13MS401_T8 elapses before F13MS401_C2 is able to do a successful gear spray dose (i.e. reach it's count setpoint), a critical alarm MS_SPRY_CR will activate. Timer is set for 2 failed cycles. START: As per F13-SEQ-0020 STOP (and reset to 0): As per F13-SEQ-0020 OR F13MS401_C2 = Count Setpoint (22) CONTINUE: MS_RUNNING = RUNNING PAUSE: MS_RUNNING = NOT RUNNING If F13MS401_T8 has elapsed: Activate MS_SPRY_CR ACTIVATE MS_SPR_NCR IF F13MS401_T8.PV > 0 seconds | A
F13MS401_T10 | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 Lube Off MRT | Timer PT = 5 Minutes |  | N |  |  |  | Minimum time the LP Lube and Pinion Bearing Lube Pumps must run after stopping the SAG Mill Main Motor or Inching Drive. Sequence permissive for F13-SEQ-0018. START (and reset to 0): MS_RUNNING = NOT RUNNING STOP: Timer elapsed | B | [6 empty] | not available in checkmate
F13MS401_T12 | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13PO445 Test Interval | Timer PT = 60 Minutes |  | N |  |  |  | Timer utilised to start the SAG Mill Main Bearing Lube Unit Oil Conditioning Pump. The Pump starting will initiate a test in all modes (see F13LU413_CMD1 in Digital Output tab). START (and reset to 0): F13-PO-445 in AUTO AND F13LU413_STS.PV ≠ 2 (OCM not in 'Testing' status) STOP: F13-PO-445 in MANUAL OR F13LU413_STS.PV = 2 (OCM in 'Testing' status) Timer elapses: Set XC13200A = Start to start F13-PO-445 Nominally set to 60 minutes Engineer-level access for changes OCM15 must be set up such that tests are initiated via the DCS (continous and automatic testing disabled) | 1 | 18/03/2025 30/06/2025 | Modbus Data map reviewed by Controls. Logic reviewed Added _STS =2 in stop condition as discussed. No change to logic required |  |  |  |  | Logic tested. 13PO445 hasn’t been run yet as per Drives PCT.
F13MS401_T13 | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13PO445 Test Duration | Timer PT = 5 Minutes |  | N |  |  |  | Timer to start when the SAG Mill Main Bearing Lube Unit Oil Conditioning Monitoring is testing. START (and reset to 0): F13-PO-445 in AUTO AND RUNNING AND F13LU413_STS.PV = 2 (OCM in 'Testing' status) STOP: F13-PO-445 in MANUAL OR F13LU413_STS.PV ≠ 2 (OCM not in 'Testing' status) Timer elapses: Activate XC13200B = Stop to stop F13-PO-445. Nominally set to 5 minutes Engineer-level access for changes OCM15 must be set up such that tests are initiated via the DCS (continous and automatic testing disabled) | 1 | 18/03/2025 30/06/2025 | Modbus Data map reviewed by Controls. Logic reviewed Added _STS =/= 2 in stop condition as discussed. No change to logic required |  |  |  |  | Logic tested. 13PO445 hasn’t been run yet as per Drives PCT.
F13MS401_OCM | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13PO445 Test Fail | Normal | Alarm | N |  | 60 | Mask if F13-PO-445 = Manual mode | Activate alarm if: F13-PO-445 = Running (XC13200A = Start) AND 13LU413_STS.PV ≠ 2 (OCM not in 'Testing' status) | 0 | [6 empty] | Logic tested. 13PO445 hasn’t been run yet as per Drives PCT.
F13MS401_C1 | 2000-F13-PID-PR-10013 | F13MS401 Seal Grse Count | Counter SV = 4 Counts |  | N |  |  |  | Utilise counter to count up via Rising-Edge Trigger for every KS13611 = Active. KS13611 activates each time F13-PO-444 pulses, and is used to confirm seal grease flow. A successful grease cycle is complete when the counter setpoint is reached. COUNT UP: Rising-Edge Trigger for every KS13611 = Active RESET: As per F13-SEQ-0019 If F13MS401_C1 reaches Count Setpoint (4): As per F13-SEQ-0019 | A | [6 empty] | Checked count and CTUP, reset is part of seq wasn't checked
F13MS401_C2 | 2000-F13-PID-PR-10013 | F13MS401 Gear Spry Count | Counter SV = 22 Counts |  | N |  |  |  | Utilise counter to count up via Rising-Edge Trigger for every KS13596 = Active. KS13596 activates each time F13-PO-443 pulses, and is used to confirm seal grease flow. A successful grease cycle is complete when the counter setpoint is reached. COUNT UP: Rising-Edge Trigger for every KS13596 = Active RESET: As per F13-SEQ-0020 If F13MS401_C2 reaches Count Setpoint (22): As per F13-SEQ-0020 | A
XI13743_SEL | 2000-F13-PID-PR-10003 | F13HU413 Mill Selector | Logic |  | N |  |  |  | ZI13944 and ZI13945 are position switches to indicate the install location of the inching drive (SAG or Ball Mill respectively). 3 selector: - ZI13944 Active AND ZI13945 Inactive = SAG Mill - ZI13945 Active AND ZI13944 Inactive = Ball Mill - (ZI13944 AND ZI13945 Inactive) OR (ZI13944 AND ZI13945 Active) = Inactive Note, see Drive tab F13-HU-413: If SAG Mill, activate SAG Mill related interlocks for F13-HU-413 If Ball Mill, activate Ball Mill related interlocks for F13-HU-413 If Inactive, interlock F13-HU-413 | 1 | 9/05/2025 20/08/2025 | https://pastech-2955.atlassian.net/browse/KAN-1690 CR-045
F13XM421_ANS | 2000-F13-PID-PR-10003 | F13XM421 Install Error | Normal | Alarm | N |  | 20 |  | ZI13944 AND ZI13945 Active then alarm | 1 | 2025-08-20 | CR-045 |  |  |  |  | Desktop Review
F13MB401_FP1 | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 Motor Lbe Pump | Operator Selection |  | N |  |  |  | CRO to select Duty Ball Mill Motor Lube Pump 1 OR 2. For use in F13-SEQ-0015B & 0016B Faceplate Selection: • Ball Mill Motor Lube Pump 1 (F13-PO-521) OR • Ball Mill Motor Lube Pump 2 (F13-PO-522) | A
F13MB401_FP2 | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 HP Lube Pump | Operator Selection |  | N |  |  |  | CRO to select Duty Ball Mill HP Lubrication Pump 1, 2 AND/OR 3. 2 Options must be selected. For use in F13-SEQ-0011. Faceplate Selection: • Ball Mill HP Lube Pump 1 (F13-PO-529) • Ball Mill HP Lube Pump 2 (F13-PO-530) • Ball Mill HP Lube Pump 3 (F13-PO-531) | A
F13MB401_FP3 | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 LP Lube Pump | Operator Selection |  | N |  |  |  | CRO to select Duty Ball Mill LP Lubrication Pump 1 OR 2. For use in F13-SEQ-0011. Faceplate Selection: • Ball Mill LP Lube Pump 1 (F13-PO-527) OR • Ball Mill LP Lube Pump 2 (F13-PO-528) | A
F13MB401_FP4 | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 PinBrg Lbe Pump | Operator Selection |  | N |  |  |  | CRO to select Duty Ball Mill Pinion Bearing Lube Oil Pump 1 OR 2. For use in F13-SEQ-0011. Faceplate Selection: • Ball Mill Pinion Bearing Lube Oil Pump 1 (F13-PO-534) OR • Ball Mill Pinion Bearing Lube Oil Pump 2 (F13-PO-535) | A
MB_SPRY_CR | 2000-F13-PID-PR-10013 | F13MB401 Gear Spry Cr | Normal | Alarm | N |  | 0 |  | Critical Gear Spray System Permissive for Mill Rotation Alarm Alarm when: • F13MB401_T8 Elapsed Normal when: • F13MB401_T8 Not Elapsed OR Stopped | 1 | 2025-06-04 | Copy paste error. On-delay fixed on DCS side - AH
MB_GRSE_CR | 2000-F13-PID-PR-10013 | F13MB401 Seal Grse Cr | Normal | Alarm | N |  | 0 |  | Critical Seal Grease System Permissive for Mill Rotation Alarm Alarm when: • F13MB401_T6 Elapsed Normal when: • F13MB401_T6 Not Elapsed OR Stopped | 1 | 2025-06-04 | Copy paste error. On-delay fixed on DCS side - AH
MB_BRKFLT1 | 2000-F13-PID-PR-10013 | F13MS401 Brake NormFault | Normal | Alarm | N |  | 5 |  | Logic: • MB_OP_MODE = NORMAL AND • [ZSH13795 Inactive (Brake Engaged) OR • ZSH13797 Inactive (Brake Engaged) OR • SV13813 Deenergised] OR • LSL13802 INACTIVE (Hydraulic Reservoir Level Low) (LR 14/06/2026 Source 2000-ME001.3-M02-50001 Page 770) OR • (Source: 2000-ME001.3-M02-50001, "Ball Mill Brake Normal Mode Permissive for Ball Mill Motors Alarm") Note: Refer to F13-PO-532 interlocks in Drives tab | 1 | 2025-03-06 | https://pastech-2955.atlassian.net/browse/KAN-1386
MB_BRKFLT2 | 2000-F13-PID-PR-10013 | F13MS401 Brake ComAlarm | Normal |  | N |  |  |  | Logic (Healthy): • [MB_OP_MODE = NORMAL AND MB_RUNNING = NOT RUNNING AND • LSL13802 Active AND • TSH13803 Active AND • F13-PO-532 INTERLOCKS INACTIVE AND IN AUTO AND • ZSH13796 Active AND • ZSH13798 Active] (Source: 2000-ME001.3-M02-50001, "Brake Common Permissive for Ball Mill Motor Main Drive Alarm") | 1 | 6/03/2025 10/7/25 | https://pastech-2955.atlassian.net/browse/KAN-1386 https://pastech-2955.atlassian.net/browse/PL-336
MB_SPR_NCR | 2000-F13-PID-PR-10013 | F13MB401 Gear Spry NCr | Normal | Alarm | N |  | 0 |  | Gear Spray Failed Cycle Alarm Alarm when: • F13MB401_T8.PV > 0 seconds (i.e., timer has started) Normal when: • F13MB401_T8.PV = 0 seconds (i.e., timer has stopped and reset) | B
MB_GRS_NCR | 2000-F13-PID-PR-10013 | F13MB401 Seal Grse NCr | Normal | Alarm | N |  | 0 |  | Seal Grease Failed Cycle Alarm Alarm when: • F13MB401_T6 > 0 seconds (i.e., timer has started) Normal when: • F13MB401_T6 = 0 seconds (i.e., timer has stopped and reset) | B
MB_2S_BRK | 2000-F13-PID-PR-10013 | F13MB401 2-Stage Brake | Inactive |  | N |  |  |  | Two-Stage Braking for Ball Mill IF HS13748MODE = Automatic THEN: • MB_2S_BRK is activated as per F13-SEQ-0016C OR manually by the CRO if MB_RUNNING = NOT RUNNING (include button on DCS) See 14. Cause & Effects tab for initiating conditions When MB_2S_BRK is ACTIVE: 1. Set SV13812, SV13813, SV13808 AND F13-PO-532 to AUTO 2. De-energise SV13812, SV13813 and SV13808 ONLY 1 CAN BE ACTIVE AT ANY TIME: MB_2S_BRK, MB_EN_BRK, MB_RL_BRK. The active tag is to latch, and unlatch when another tag becomes active. | 2 | 30/06/2025 28/02/2026 | https://pastech-2955.atlassian.net/browse/PL-338 CR-026
MB_EN_BRK | 2000-F13-PID-PR-10013 | F13MB401 Parking Brake | Inactive |  | N |  |  |  | Parking Brake for Ball Mill IF HS13748MODE = Local AND HS13749BRK = Engage, THEN activate MB_EN_BRK See 14. Cause & Effects tab for initiating conditions IF MB_EN_BRK = ACTIVE then: Immediately energise SV13812, and de-energise SV13813 and SV13808 AND Set F13-PO-532 to AUTO. ONLY 1 CAN BE ACTIVE AT ANY TIME: MB_2S_BRK, MB_EN_BRK, MB_RL_BRK. The active tag is to latch, and unlatch when another tag becomes active. | 2 | 2026-02-28 | CR-026
MB_RL_BRK | 2000-F13-PID-PR-10013 | F13MB401 Release Brake | Inactive |  | N |  |  |  | Common Release Brake for Ball Mill IF HS13748MODE = Automatic THEN MB_RL_BRK is activated as per F13-SEQ-0015A OR manually by the CRO (include button on DCS) OR IF HS13748MODE = Local AND HS13749BRK = Release, THEN activate MB_RL_BRK OR IF HS13748MODE Rising Edge Trigger (Local to Auto), THEN activate MB_RL_BRK See 14. Cause & Effects tab for initiating conditions IF MB_RL_BRK = ACTIVE then: Immediately energise SV13808 and SV13813, and de-energise SV13812 AND Set F13-PO-532 to AUTO. ONLY 1 CAN BE ACTIVE AT ANY TIME: MB_2S_BRK, MB_EN_BRK, MB_RL_BRK. The active tag is to latch, and unlatch when another tag becomes active. | 1 | 2025-06-30 | https://pastech-2955.atlassian.net/browse/PL-338
MB_NCR_ILK | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 Delayed Intlk | Normal | Alarm | N |  | 10 |  | Abormal Shutdown, Mill Delayed Stop Activation of MB_NCR_ILK will bypass the Ball Mill (via XV13114, XV13115, XV13116, refer to F13FD401_FP1) Closed/Open trips - see OnOff Valves tab), and initiate F13-SEQ-0016A to sequence stop F13-MB-401A/B. If the Ball Mill is tripped, the SAG Mill will operate in Single Stage SAG. It is recommended the circuit is sequence stopped if the Ball Mill fails restart. Prompt CRO: "13MB401 Delayed Stop interlck active. Delayed Stop sequence initiating" < Close > MB_NCR_ILK is activated when: • MB_RUNNING = RUNNING AND • F13-MB-401A/B Delayed Stop Interlock = ACTIVE (refer to Drives tab) Disregard Drive tab condition on-delay timer and utilise 10 second on-delay on all conditions here (see Drives tab for further explanation). Motor lube timers extended to 15 sec to allow lube pumps to start. | 1 | 9/05/2025 19/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1807 https://pastech-2955.atlassian.net/browse/KAN-1877
MB_CR_ILK | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 Instant Intlk | Normal | Alarm | N |  | 1 |  | Abormal Shutdown, Mill Instantaneous Stop Activation of MB_CR_ILK will bypass the Ball Mill (via XV13114, XV13115, XV13116 , refer to F13FD401_FP1) Closed/Open trips - see OnOff Valves tab), and initiate F13-SEQ-0016C to and engages the Ball Mill brakes (MB_2S_BRK). If the Ball Mill is tripped, the SAG Mill will operate in Single Stage SAG. It is recommended the circuit is sequence stopped if the Ball Mill fails restart. Prompt CRO: "13MB401 Instant Stop interlck active. Instant Stop sequence initiating" < Close > MB_CR_ILK is activated when: • MB_ESTOP = E-STOP ACTIVE OR • [MB_RUNNING = RUNNING AND • F13-MB-401A/B Instantaneous Stop Interlock = ACTIVE (refer to Drives tab)] Disregard Drive tab condition on-delay timer and utilise 1 second on-delay on all conditions here (exception, 0 second delay on MB_ESTOP). | 1 | 9/05/2025 19/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1807 https://pastech-2955.atlassian.net/browse/KAN-1877
F13MB401_T1 | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 LP Lube Delay | Timer PT = 5 Minutes |  | N |  |  |  | Minimum time the Ball Mill Low Pressure Lubrication Pump (1 off) must run before starting the Ball Mill Main Motor or inching the mill. Used in Drive Interlocks If timer has not elapsed, then the Ball Mill can not be started START: F13-PO-527 OR F13-PO-528 = RUNNING STOP (reset to 0): F13-PO-527 AND F13-PO-528 = NOT RUNNING Healthy Signal: • 1x LP Lube Pump (F13-PO-527 OR F13-PO-528) RUNNING for >= F13MB401_T1 PRESET TIME | 1 | 2025-06-30 | https://pastech-2955.atlassian.net/browse/KAN-1882 Removed deleted tags. No impact to logic
F13MB401_T2 | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 PinBrgLbe Delay | Timer PT = 5 Minutes |  | N |  |  |  | Minimum time the Ball Mill Pinion Bearing Lubrication Pump (1 off) must run before starting the Ball Mill Main Motor or inching the mill. Used in Drive Interlocks If timer has not elapsed, then the Ball Mill can not be started START: F13-PO-534 OR F13-PO-535 = RUNNING STOP (reset to 0): F13-PO-534 AND F13-PO-535 = NOT RUNNING Healthy Signal: • 1x Pinion Bearing Lube Pump (F13-PO-534 OR F13-PO-535) RUNNING for >= F13MB401_T2 PRESET TIME | 1 | 2025-06-30 | https://pastech-2955.atlassian.net/browse/KAN-1882 Removed deleted tags. No impact to logic
F13MB401_T3 | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 HP Lube Delay | Timer PT = 5 Minutes |  | N |  |  |  | Minimum time the Ball Mill HP Lubrication Pumps (2 off) must run before starting the Ball Mill Main Motor or inching the mill. Used in Drive Interlocks If timer has not elapsed, then the Ball Mill can not be started START: (2 or more pumps) F13-PO-529, F13-PO-530 AND/OR F13-PO-531 = RUNNING STOP (reset to 0): (2 or more pumps) F13-PO-529, F13-PO-530 AND/OR F13-PO-531 = NOT RUNNING Healthy Signal: • 2x HP Lube Pumps (F13-PO-529 AND/OR F13-PO-530 AND/OR F13-PO-531) RUNNING for >= F13MB401_T3 PRESET TIME | 1 | 2025-06-30 | https://pastech-2955.atlassian.net/browse/KAN-1882 Removed deleted tags. No impact to logic
F13MB401_T4 | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 Motor Lbe Delay | Timer PT = 10 Seconds |  | N |  |  |  | Minimum time the Ball Mill Motor Lubrication Pump (1 off) must run before starting the Ball Mill Main Motor. Used in MB_ML_NCR and Drive Interlocks If timer has not elapsed, then the Ball Mill can not be started START: F13-PO-521 OR F13-PO-522 = RUNNING STOP (reset to 0): F13-PO-521 AND F13-PO-522 = NOT RUNNING Healthy Signal: • 1x Ball Mill Motor Lube Pump (F13-PO-521 OR F13-PO-522) RUNNING for >= F13MB401_T4 PRESET TIME | 1 | 2025-06-30 | https://pastech-2955.atlassian.net/browse/KAN-1882 Removed deleted tags. No impact to logic
F13MB401_T5 | 2000-F13-PID-PR-10013 | F13MB401 Seal Grse Freq. | Timer PT = 6 Hours |  | N |  |  |  | Utilise a timer to initiate F13-SEQ-0013 every 6 hours that the Ball Mill Motors are running and F13-SEQ-0013 is not running. START or CONTINUE timer when the Ball Mill Main Motors are running and F13-SEQ-0013 is not running. PAUSE timer if the Ball Mill Main Motors are stopped. When the timer elapses, the timer is STOPPED and a Rising-Edge Trigger will initiate F13-SEQ-0013. If the Ball Mill is still running after F13-SEQ-0013 is stopped / completed, the timer will START again (and reset to 0). START (and reset to 0) / CONTINUE (if paused): MB_RUNNING = RUNNING AND F13-SEQ-0013 = NOT RUNNING STOP: Timer Elapses PAUSE: MB_RUNNING = NOT RUNNING When F13MB401_T5 reaches PRESET TIME: Initiate F13-SEQ-0013 with Rising Edge Trigger | B
F13MB401_T6 | 2000-F13-PID-PR-10013 | F13MB401 Seal Grse Fail | Timer PT = 370 Minutes |  | N |  |  |  | If F13MB401_T6 elapses before F13MB401_C1 is able to do a successful seal grease dose (i.e. reach it's count setpoint), a critical alarm MB_GRSE_CR will activate. START: As per F13-SEQ-0013 STOP (and reset to 0): As per F13-SEQ-0013 OR F13MB401_C1 = Count Setpoint (4) CONTINUE: MB_RUNNING = RUNNING PAUSE: MB_RUNNING = NOT RUNNING If F13MB401_T6 has elapsed: Activate MB_GRSE_CR ACTIVATE MB_GRS_NCR IF F13MB401_T6.PV > 0 seconds | B
F13MB401_T7 | 2000-F13-PID-PR-10013 | F13MB401 Gear Spry Freq. | Timer PT = 15 Minutes |  | N |  |  |  | Utilise a timer to initiate F13-SEQ-0014 every 15 minutes that the Ball Mill Motors are running and F13-SEQ-0014 is not running. START or CONTINUE timer when the Ball Mill Main Motors are running and F13-SEQ-0014 is not running. PAUSE timer if the Ball Mill Main Motors are stopped. When timer elapses, the timer is STOPPED and a Rising-Edge Trigger will initiate F13-SEQ-0014. If the Ball Mill is still running after F13-SEQ-0014 is stopped / completed, the timer will START again (and reset to 0). START (and reset to 0) / CONTINUE (if paused): MB_RUNNING = RUNNING AND F13-SEQ-0014 = NOT RUNNING STOP: Timer Elapses PAUSE: MB_RUNNING = NOT RUNNING When F13MB401_T7 reaches PRESET TIME: Initiate F13-SEQ-0014 with Rising Edge Trigger | B |  | Needs Ball Mill Running to test/sign off.
F13MB401_T8 | 2000-F13-PID-PR-10013 | F13MB401 Gear Spry Fail | Timer PT = 30 Minutes |  | N |  |  |  | If F13MB401_T8 elapses before F13MB401_C2 is able to do a successful gear srpay dose (i.e. reach it's count setpoint), a critical alarm MB_SPRY_CR will activate. Timer is set for 2 failed cycles. START: As per F13-SEQ-0014 STOP (and reset to 0): As per F13-SEQ-0014 OR F13MB401_C2 = Count Setpoint (22) CONTINUE: MB_RUNNING = RUNNING PAUSE: MB_RUNNING = NOT RUNNING If F13MB401_T8 has elapsed: Activate MB_SPRY_CR ACTIVATE MB_SPR_NCR IF F13MB401_T8.PV > 0 seconds | A
F13MB401_T10 | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 Lube Off MRT | Timer PT = 5 Minutes |  | N |  |  |  | Minimum time the LP Lube and Pinion Bearing Lube Pumps must run after stopping the Ball Mill Main Motor or Inching Drive. Sequence permissive for F13-SEQ-0012. START (and reset to 0): MB_RUNNING = NOT RUNNING STOP: Timer elapsed | B
F13MB401_T12 | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13PO446 Test Interval | Timer PT = 60 Minutes |  | N |  |  |  | Timer utilised to start the Ball Mill Main Bearing Lube Unit Oil Conditioning Pump. The Pump starting will initiate a test in all modes (see F13LU423_CMD1 in Digital Output tab). START (and reset to 0) / RESUME: F13-PO-446 in AUTO AND F13LU423_STS.PV ≠ 2 (OCM not in 'Testing' status) STOP: F13-PO-446 in MANUAL OR F13LU423_STS.PV = 2 (OCM in 'Testing' status) Timer elapses: Set XC13201A = Start to start F13-PO-446. Nominally set to 60 minutes Engineer-level access for changes OCM15 must be set up such that tests are initiated via the DCS (continous and automatic testing disabled) | 1 | 18/03/2025 30/06/2025 | Modbus Data map reviewed by Controls. Logic reviewed Added _STS =2 in stop condition as discussed. No change to logic required
F13MB401_T13 | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13PO446 Test Duration | Timer PT = 5 Minutes |  | N |  |  |  | Timer to start when the Ball Mill Main Bearing Lube Unit Oil Conditioning Monitoring is testing. START (and reset to 0) / RESUME: F13-PO-446 in AUTO AND RUNNING AND F13LU423_STS.PV = 2 (OCM in 'Testing' status) STOP: F13-PO-446 in MANUAL OR F13LU423_STS.PV ≠ 2 (OCM in 'Testing' status) Timer elapses: Activate XC13201B = Stop to stop F13-PO-446. Nominally set to 5 minutes Engineer-level access for changes OCM15 must be set up such that tests are initiated via the DCS (continous and automatic testing disabled) | 1 | 18/03/2025 30/06/2025 | Modbus Data map reviewed by Controls. Logic reviewed Added _STS =/= 2 in stop condition as discussed. No change to logic required
F13MB401_OCM | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13PO446 Test Fail | Normal | Alarm | N |  | 60 | Mask if F13-PO-446 = Manual mode | Activate alarm if: F13-PO-446 = Running (XC13201A = Start) AND 13LU423_STS.PV ≠ 2 (OCM not in 'Testing' status) | 0
F13MB401_C1 | 2000-F13-PID-PR-10013 | F13MB401 Seal Grse Count | Counter SV = 4 Counts |  | N |  |  |  | Utilise counter to count up via Rising-Edge Trigger for every KS13862 = Active. KS13862 activates each time F13-PO-544 pulses, and is used to confirm seal grease flow. A successful grease cycle is complete when the counter setpoint is reached. COUNT UP: Rising-Edge Trigger for every KS13862 = Active RESET: As per F13-SEQ-0013 If F13MB401_C1 reaches Count Setpoint (4): As per F13-SEQ-0013 | A
F13MB401_C2 | 2000-F13-PID-PR-10013 | F13MB401 Gear Spry Count | Counter SV = 22 Counts |  | N |  |  |  | Utilise counter to count up via Rising-Edge Trigger for every KS13847 = Active. KS13847 activates each time F13-PO-543 pulses, and is used to confirm seal grease flow. A successful grease cycle is complete when the counter setpoint is reached. COUNT UP: Rising-Edge Trigger for every KS13847 = Active RESET: As per F13-SEQ-0014 If F13MB401_C2 reaches Count Setpoint (22): As per F13-SEQ-0014 | A
F13BLC402_SEQ_EN | 2000-F13-PID-PR-10004 | F13BLC402 Seq Auto En | Active |  | N |  |  |  | Memory bit is used as a condition to enable auto looping of F13-SEQ-0037. Activate and latch if: • HS13140AAUT Auto AND 'BLC_REM_STRT = Active OR HS13179ASTT = Start' Deactivate/unlatch if: • CRO activates BLC_REM_STOP on DCS OR • Field Operator presses HS13179BSTP on LCP OR • HS13140BMAN = Manual OR • F13BLC402_HOME = Alarm Controls based on ME067 Existing Ball Charging System. TBC Vendor Functional Description, 2000-ME057-M01-10001 | 0
F13BLC402_SEQSTT | 2000-F13-PID-PR-10004 | F13BLC Seq Auto En | Active |  | N |  |  |  | Memory bit is used as a condition to enable auto looping of F13-SEQ-0037. Activate and latch if F13BLC402_FT >= F13BLC402_STT Deactivate/unlatch if F13BLC402_FT <= 0 Controls based on ME067 Existing Ball Charging System. TBC Vendor Functional Description, 2000-ME057-M01-10001 | 0
F13BLC402_STT | 2000-F13-PID-PR-10004 | F13BLC402 StartFrequency | Setpoint |  | N |  |  |  | CRO entered start frequency setpoint (in tonnes). Used in conditions for enabling F13BLC402_SEQSTT. If F13BLC402_FT >= F13BLC402_STT, F13BLC402_SEQSTT is activated. DEFAULT SETTING: 5000 t ENGINEER CONFIGURABLE RANGE: 2000 - 20000 t | 0
F13BLC402_FT | 2000-F13-PID-PR-10004 | F13MS401 FeedTotaliser2 | Totaliser |  | N |  |  |  | SAG Mill Fresh Feed (Dry) Totaliser Totaliser Input PV = WIC13121.PV Used in conditions for enabling F13BLC402_SEQSTT. Totaliser value is negated as Mill Balls are successfully transferred to the Ball Mill via Sequence F13SEQ0037 Refer to F13CALC10049 AND F13SEQ0037 | 0
F13BLC402_MEM | 2000-F13-PID-PR-10004 | F13BLC402 Stored Weight | Memory |  | N |  |  |  | Store the value of WI13285C.PV on STEP 26 of F13-SEQ-0037. Overwrite existing value if required. Reset to 0 on STEP 38 of F13-SEQ-0037. Refer to F13CALC10049 AND F13SEQ0037 | 1
BLC_REM_STRT | 2000-F13-PID-PR-10004 | F13BLC402 Rem AutoStart | Inactive |  | N |  |  |  | Pushbutton on the DCS to start auto ball loading. See F13BLC402_SEQ_EN. Activates F13BLC402_SEQ_EN (Misc tab). Controls based on ME067 Existing Ball Charging System. TBC Vendor Functional Description, 2000-ME057-M01-10001 | 0
BLC_REM_STOP | 2000-F13-PID-PR-10004 | F13BLC402 Rem AutoStop | Inactive |  | N |  |  |  | Pushbutton on the DCS to stop auto ball loading. See F13BLC402_SEQ_EN. Deactivates and unlatches F13BLC402_SEQ_EN (Misc tab). Controls based on ME067 Existing Ball Charging System. TBC Vendor Functional Description, 2000-ME057-M01-10001 | 0
F13BLC402_HOME | 2000-F13-PID-PR-10004 | F13BLC402 Homing Alarm | Inactive | Homing Request Alarm | N |  | 10 |  | A homing request alarm is initiated on the DCS when: • The system power on relay (XC13250B) is inactive in auto mode (HS13140AAUT) OR • The F13-SEQ-0037 is stopped in auto mode (HS13140AAUT) and standby idle (XC13250A) is inactive OR • There is a mismatch between the bunker limit (ZI13229B) and horizontal encoder (ZI13310A) i.e., when ZI13229B is active, ZI13310A should be within range Activate F13BLC402_HOME if (else Inactive): • XC13250B Inactive AND HS13140AAUT Active OR • F13-SEQ-0037 Not Running AND HS13140AAUT Active AND XC13250A Inactive OR • ZI13229A Active AND ZI13310B.PV =/= F13_H_ENC_DMP ± F13_H_ENC_TLR for 3 seconds OR • ZI13229A Inactive AND ZI13310B.PV = F13_H_ENC_DMP ± F13_H_ENC_TLR for 3 seconds | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876
F13CR453_MXDUTY | 2000-F13-PID-PR-10004 | F13CR453 Max Duty | Inactive | Alarm | N |  | 0 |  | REFER TO F13CALC10047 This will interlock F13-CR-453 Trolley Forward motor (refer to Drives tab). | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876
F13BLC402_MXDUTY | 2000-F13-PID-PR-10004 | F13BLC402 Max Duty | Inactive | Alarm | N |  | 0 |  | REFER TO F13CALC10048 This will interlock F13-BLC-402 drive (refer to Drives tab). | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876
F13BLC402_LOAD | 2000-F13-PID-PR-10004 | F13BLC402 Load Warning | Timer PT = 10 5 Minutes | Timer Elapsed | N |  | 0 |  | Activate a warning if WI13285C is > P_Lo for more than PT minutes (TBC during commissioning) This is to ensure the CRO can investigate the long loading duration before the Magnet duty cycle is complete. P_Lo value to be confirmed during commissioning | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC removed only |  |  |  |  | time changed to 5 (300 sec), magnet time during normal loading is 270-280 sec
F13_V_ENC_TLR | 2000-F13-PID-PR-10004 | F13CR453 HoistTolernce | Setpoint |  | N |  | - |  | Hoist vertical encoder position tolerance. Used in Hoist Drive interlocks (see Drives tab) Nominal: 5mm Lower Limit: 0mm Upper Limit: 100mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC removed only |  |  |  |  | set to 100 during commissioning given drag caused by seq steps & transition lags
F13_H_ENC_TLR | 2000-F13-PID-PR-10004 | F13CR453 TrolleyTolernce | Setpoint |  | N |  | - |  | Trolley horizontal encoder position tolerance. Used in Hoist Drive interlocks (see Drives tab) Nominal: 20mm Lower Limit: 0mm Upper Limit: 100mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC removed only |  |  |  |  | set to 100 during commissioning given drag caused by seq steps & transition lags
F13_H_ENC_LFT | 2000-F13-PID-PR-10004 | F13CR453 Lift Pos. | Setpoint |  | N |  | - |  | F13-BN-404 Absolute Position ZI13229B Should be active at this trolley position Used in F13-SEQ-0037 and Hoist Drive interlocks (see Drives tab) Nominal: 5000 mm Lower Limit: 4900 mm Upper Limit: 5100 mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876
F13_H_ENC_LFTX | 2000-F13-PID-PR-10004 | F13CR453 Bkr. X Dist | Setpoint |  | N |  | - |  | F13-BN-404 X Distance Distance before F13-BN-404 Absolute Position that trolley normal travel relay de-energises in F13-SEQ-0037. Used in F13-SEQ-0037 Nominal: 60mm Lower Limit: 0mm Upper Limit: 1000mm Setpoint TBC during commissioning. Set F13_H_ENC_LFTX such that the Trolley stops at the ZI13229B limit switch position when Trolley Forward (XC13251A) is de-energised in F13-SEQ-0037. Include in graphic which allows the adjustment of the above Nominal setpoint. Requires Engineer login to change value | 1 | 14/05/2025 27/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC close out Functional description comments returned |  |  |  |  | exists in logic in conjuction with checking actual limit switch to top was implmeneted with tolernace as it was more accurate
F13_H_ENC_LFTY | 2000-F13-PID-PR-10004 | F13CR453 Bkr. Y Dist | Setpoint |  | N |  | - |  | F13-BN-404 Y Distance Distance after F13-BN-404 Abosolute Position that trolley fast travel relay energises in F13-SEQ-0037. Used in F13-SEQ-0037 Nominal: 80mm Lower Limit: 0mm Upper Limit: 1000mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value | 1 | 14/05/2025 27/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC close out Functional description comments returned
F13_H_ENC_LFTZ | 2000-F13-PID-PR-10004 | F13CR453 Bkr. Z Dist | Setpoint |  | N |  | - |  | F13-BN-404 Z Distance Distance before F13-BN-404 Absolute Position that trolley fast travel relay de-energises in F13-SEQ-0037. Used in F13-SEQ-0037 Nominal: 245mm Lower Limit: 0mm Upper Limit: 1000mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value | 1 | 14/05/2025 27/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC close out Functional description comments returned |  |  |  |  | set to 840 during commissioning
F13_H_ENC_DMP | 2000-F13-PID-PR-10004 | F13CR453 Chute Pos. | Setpoint |  | N |  | - |  | F13-CH-442 Absolute Position ZI13229A Should be active at this trolley position Used in F13-SEQ-0037 and Hoist Drive interlocks (see Drives tab) Nominal: 2250 mm Lower Limit: 2150 mm Upper Limit: 2350 mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | set to 2215 during commissioning
F13_H_ENC_DMPX | 2000-F13-PID-PR-10004 | F13CR453 Chute X Dist | Setpoint |  | N |  | - |  | F13-CH-442 - X Distance Distance before F13-CH-442 Absolute Position that trolley normal travel relay de-energises in F13-SEQ-0037. Used in F13-SEQ-0037 Nominal: 60mm Lower Limit: 0mm Upper Limit: 1000mm Setpoint TBC during commissioning. Set F13_H_ENC_DMPX such that the Trolley stops at the ZI13229A limit switch position when Trolley Reverse (XC13251B) is de-energised in F13-SEQ-0037. Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value | 1 | 14/05/2025 27/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC close out Functional description comments returned |  |  |  |  | exists in logic in conjuction with checking actual limit switch to top was implmeneted with tolernace as it was more accurate
F13_H_ENC_DMPY | 2000-F13-PID-PR-10004 | F13CR453 Chute Y Dist | Setpoint |  | N |  | - |  | F13-CH-442 - Y Distance Distance after F13-CH-442 Absolute Position that trolley fast travel relay energises in F13-SEQ-0037. Used in F13-SEQ-0037 Nominal: 80mm Lower Limit: 0mm Upper Limit: 1000mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value | 1 | 14/05/2025 27/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC close out Functional description comments returned
F13_H_ENC_DMPZ | 2000-F13-PID-PR-10004 | F13CR453 Chute Z Dist | Setpoint |  | N |  | - |  | F13-CH-442 - Z Distance Distance before F13-CH-442 Absolute Position that trolley fast travel relay de-energises in F13-SEQ-0037. Used in F13-SEQ-0037 Nominal: 245mm Lower Limit: 0mm Upper Limit: 1000mm Include in graphic which allows the adjustment of the above Nominal setpoint Requires Engineer login to change value | 1 | 14/05/2025 27/05/2025 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC close out Functional description comments returned |  |  |  |  | set to 800 during commissing
F13_H_ENC_MNT1 | 2000-F13-PID-PR-10004 | F13CR453 Maint. Pos. | Setpoint |  | N |  | - |  | Maintenance 1 Absolute Position ZI13226A Should be active at this trolley position Used in Hoist Drive interlocks (see Drives tab) Nominal: 7900 mm Lower Limit: 7800 mm Upper Limit: 8000 mm Include in graphic which allows the adjustment of the above Nominal setpoint at DCS . Requires Engineer login to change value | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | set to 7994 durining commissioning
F13_H_ENC_MNT2 | 2000-F13-PID-PR-10004 | F13CR453 Maint. Pos. | Setpoint |  | N |  | - |  | Maintenance 2 Absolute Position ZI13226B Should be active at this trolley position Used in Hoist Drive interlocks (see Drives tab) Nominal: 0 mm Lower Limit: 0 mm Upper Limit: 100 mm Include in graphic which allows the adjustment of the above Nominal setpoint at DCS . Requires Engineer login to change value | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876
F13_V_ENC_TRAV | 2000-F13-PID-PR-10004 | F13CR453 Hoist Trav. Pos | Setpoint |  | N |  | - |  | Hoist Traverse Absolute Position Used in F13-SEQ-0037 & Hoist Drive interlocks (see Drives tab) Nominal: 0 mm Lower Limit: 0 mm Upper Limit: 100 mm Include in graphic which allows the adjustment of the above Nominal setpoint at DCS . Requires Engineer login to change value | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | reading -5 in field, even after "teaching" the encoder (tought when all the way down)
F13_V_ENC_DMP | 2000-F13-PID-PR-10004 | F13CR453 Hoist Dump Pos | Setpoint |  | N |  | - |  | Hoist Dump Absolute Position Used in F13-SEQ-0037 & Hoist Drive interlocks (see Drives tab) Nominal: 375 mm Lower Limit: 275 mm Upper Limit: 475 mm Include in graphic which allows the adjustment of the above Nominal setpoint DCS . Requires Engineer login to change value | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876
F13_V_ENC_MNT2 | 2000-F13-PID-PR-10004 | F13CR453 Hoist Mnt 2 Pos | Setpoint |  | N |  | - |  | Hoist Maintenance 2 Position Used in Hoist Drive interlocks (see Drives tab) Nominal: 2488 mm Lower Limit: 2388 mm Upper Limit: 2588 mm Include in graphic which allows the adjustment of the above Nominal setpoint at DCS . Requires Engineer login to change value | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | set to 2535 during commisisning
F13_V_ENC_CHT | 2000-F13-PID-PR-10004 | F13CR453 Hoist Chute Pos | Setpoint |  | N |  | - |  | Hoist Chute Absolute Position Used in F13-SEQ-0037 & Hoist Drive interlocks (see Drives tab) Nominal: 20498 mm Lower Limit: 20398 mm Upper Limit: 20598 mm Include in graphic which allows the adjustment of the above Nominal setpoint DCS . Requires Engineer login to change value | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | set to 20598 durining commisining to allow max fast down travel
F13_V_ENC_LFT | 2000-F13-PID-PR-10004 | F13CR453 Hoist Lift Pos | Setpoint |  | N |  | - |  | Hoist Lift Position Used in F13-SEQ-0037 & Hoist Drive interlocks (see Drives tab) Nominal: 22475 mm Lower Limit: 22375 mm Upper Limit: 22575 22975mm Include in graphic which allows the adjustment of the above Nominal setpoint at DCS . Requires Engineer login to change value | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | SH set to 22975 and actual setpoint to 22875 to allow magnet for a closer approach when feeder is low
F13_V_ENC_MNT1 | 2000-F13-PID-PR-10004 | F13CR453 Hoist Mnt 1 Pos | Setpoint |  | N |  | - |  | Hoist Maintenance 1 Position Used in Hoist Drive interlocks (see Drives tab) Nominal: 23200 mm Lower Limit: 23100 mm Upper Limit: 23300 mm Include in graphic which allows the adjustment of the above Nominal setpoint from the DCS Distance to be confirmed during commissioning. Requires Engineer login to adjust timer | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 |  |  |  |  | set to 23290 durining commisining
F13BLC402_T1 | 2000-F13-PID-PR-10004 | F13CR453 PreMovePause | Timer PT = 5 seconds |  | N |  | - |  | Trolley Pre-movement Pause. Timer to allow for horn energisation before driving the trolley, see XC13251A/B in Digital Output tab for details Timer to begin when a Trolley FWD (XC13251A) or REV (XC13251B) start command is called. Trolley will energise after the Pre-movement Pause timer has elapsed (see Drives tab) Energise XC13284 whilst timing up Nominal: 5s Lower Limit:0s Upper Limit:60s Include in graphic which allows the adjustment of the above Nominal setpoint from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC removed only
F13BLC402_T2 | 2000-F13-PID-PR-10004 | F13CR453 PostMovePause | Timer PT = 1 2 seconds |  | N |  | - |  | Trolley Post-movement Pause Timer to begin when the Trolley FWD (XC13251A) or REV (XC13251B) relay de-energises. This is to allow for any horizontal sway to stop prior to lowering the hoist (interlock on Hoist included in Drives tab). Nominal: 1s Lower Limit:0s Upper Limit:60s Include in graphic which allows the adjustment of the above Nominal setpoint from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC removed only |  |  |  |  | found at 2 sec in FCS, commissioning with that
F13BLC402_T3 | 2000-F13-PID-PR-10004 | F13CR453 EndCyclePause | Timer PT = 1 seconds |  | N |  | - |  | End of Cycle Pause For use in F13-SEQ-0037 Nominal: 1s Lower Limit:0s Upper Limit:600s Include in graphic which allows the adjustment of the above Nominal setpoint from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC removed only
F13BLC402_KT1 | 2000-F13-PID-PR-10004 | F13BLC402 LiftRiseTime | Timer PT = 6 seconds |  | N |  | - |  | Lift Current Rise Timer For use in F13-SEQ-0037 Nominal: 6s Lower Limit:0s Upper Limit:10s Include in graphic which allows the adjustment of the above Nominal setpoint from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC removed only
F13BLC402_KT2 | 2000-F13-PID-PR-10004 | F13BLC402 SwtchRiseTme | Timer PT = 4 seconds |  | N |  | - |  | Switch Current Rise Timer For use in F13-SEQ-0037 Nominal: 4s Lower Limit:0s Upper Limit:10s Include in graphic which allows the adjustment of the above Nominal setpoint from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC removed only |  |  |  |  | delaycycle(2) was introduced between AC Reduced and AC full relay energisation, as separate steps lead to balls falling (not quick enough)
F13BLC402_KT3 | 2000-F13-PID-PR-10004 | F13BLC402 LiftBackEMF | Timer PT = 7 seconds |  | N |  | - |  | Lift Back EMF Timer For use in F13-SEQ-0037 Nominal: 7s Lower Limit:0s Upper Limit:10s Include in graphic which allows the adjustment of the above Nominal setpoint from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC removed only
F13BLC402_KT4 | 2000-F13-PID-PR-10004 | F13BLC402 DumpRiseTme | Timer PT = 3 seconds |  | N |  | - |  | Dump Current Rise Timer For use in F13-SEQ-0037 Nominal: 3s Lower Limit:0s Upper Limit:10s Include in graphic which allows the adjustment of the above Nominal setpoint from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC removed only
F13BLC402_KT5 | 2000-F13-PID-PR-10004 | F13BLC402 DumpBackEMF | Timer PT = 3 seconds |  | N |  | - |  | Dump Back EMF Timer For use in F13-SEQ-0037 Nominal: 3s Lower Limit:0s Upper Limit:10s Include in graphic which allows the adjustment of the above Nominal setpoint from the DCS Timer to be confirmed during commissioning. Requires Engineer login to adjust timer | 1 | 2025-05-14 | https://pastech-2955.atlassian.net/browse/KAN-1876 TBC removed only
XV13082_OP | 2000-F13-PID-PR-10002 | XV13082 Open | Logic |  | N |  |  |  | If XV13082 open is requested: - Start F13HU407 - After F13HU407 running 10 seconds, energise SVO13082 to open XV13082 If ZSO13082 = active then deenergise SVO13082 Refer to 2000-PP007-M01-10001 | 1 | 2025-07-02 | CR-021
XV13082_CL | 2000-F13-PID-PR-10002 | XV13082 Close | Logic |  | N |  |  |  | If XV13082 close is requested: - Start F13HU407 - After F13HU407 running 10 seconds, energise SVC13082 to close XV13082 If ZSC13082 = active then deenergise SVC13082 Refer to 2000-PP007-M01-10001 | 1 | 2025-07-02 | CR-021
HS13543_LOGIC | 2000-F13-PID-PR-10002 | HS13543 Local/Remote | Logic |  | N |  |  |  | If HS13543ALOC = active, force XV13082 = AUT if HS13543BREM rising edge, one shot XV13082 = MAN If HS13543ALOC = active and HS13544AOP = active then open XV13082 If HS13543ALOC = active and HS13544ACL = active then close XV13082 | 2 | 2025-07-02 | CR-021 |  |  |  |  | VV 0707/2026; ALOC is treated as AUT condition in DCS for valve to open via local panel, and XV mode to Manual when operated in DCS
MS_CONV_LOGIC | 2000-F13-PID-PR-10003 | F13MS401 Conv On Logic | Logic |  | N |  |  |  | Include MS_CONV_ON and MS_33KV_STS as a breaker on relevant SLD graphic. MS_CONV_ON opens and closes breaker, MS_33KV_STS provides breaker position feedback. MS_CONV_ON can only be activated by HV operator (from relevant SLD graphic) or sequence (F13-SEQ-0021B) if: F13-PW-413 or F13-PW-414 = running, and FSLL13436 = active for >= 10 seconds. MS_CONV_ON is deactivated if: Manually by HV operator (on relevant SLD graphic) or (MS_CONV_RDY = not ready and MS_CONV_ON is off) or F13-PW-413 and F13-PW-414 = stopped and MS_CONV_ON active for 320 seconds or FSLL13436 is inactive and MS_CONV_ON active for 320 seconds Pulse MS_CONV_ON off if the HV breaker 00SW10B12 is open for 10 seconds | 2 | 4/07/2025 6/05/2026 | CR-025 https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=430&pa=1&e=JnwMgk |  |  |  |  | 17/05/2026: During the uncoupled run with Toshiba, the MS_CONV_ON, bit has been operated directly from the logic instead of the faceplate due to the MS_CONV_RDY Modbus Signal isnt channging. To be addressed by Toshiba 4/6/2026 - test the interlocks by simulating a converter on and turning off the cooling water pump. Have not test sequence trigger to start.
MB_CONV_LOGIC | 2000-F13-PID-PR-10004 | F13MB401 Conv On Logic | Logic |  | N |  |  |  | Include MB_CONV_ON and MB_33KV_STS as a breaker on relevant SLD graphic. MB_CONV_ON opens and closes breaker, MB_33KV_STS provides breaker position feedback. MB_CONV_ON can only be activated by HV operator (from relevant SLD graphic) or sequence (F13-SEQ-0015B) if: F13-PW-413 or F13-PW-414 = running, and FSLL13436 = active for >= 10 seconds. MB_CONV_ON is deactivated if: Manually by HV operator (on relevant SLD graphic) or (MB_CONV_RDY = not ready and MB_CONV_ON is off) or F13-PW-413 and F13-PW-414 = stopped and MB_CONV_ON active for 320 seconds or FSLL13436 is inactive and MB_CONV_ON active for 320 seconds Pulse MB_CONV_ON off if the HV breaker 00SW10B03 is open for 10 seconds | 2 | 4/07/2025 6/05/2026 | CR-025 https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=430&pa=1&e=JnwMgk |  |  |  |  | 17/05/2026: During the uncoupled run with Toshiba, the MS_CONV_ON, bit has been operated directly from the logic instead of the faceplate due to the MS_CONV_RDY Modbus Signal isnt channging. To be addressed by Toshiba 4/6/2026 - test the interlocks by simulating a converter on and turning off the cooling water pump. Have not test sequence trigger to start.
13PP401_CONV_LOGIC | 2000-F13-PID-PR-10004 | F13PP401 Conv On Logic | Logic |  | N |  |  |  | Include 13PP401_CONV and 00SW10B07 as a breaker on relevant SLD graphic. 13PP401_CONV opens and closes breaker, 00SW10B07 provides breaker position feedback. 13PP401_CONV can only be activated by HV operator (from relevant SLD graphic) or sequence (F13-SEQ-0009) if: F13-PW-413 or F13-PW-414 = running, and FSLL13436 = active for >= 10 seconds. 13PP401_CONV is deactivated if: Manually by HV operator (on relevant SLD graphic) or (13PP401CRDY = not ready and 13PP401_CONV is off) or F13-PW-413 and F13-PW-414 = stopped and 13PP401_CONV active for 320 seconds or FSLL13436 is inactive and 13PP401_CONV active for 320 seconds Pulse 13PP401_CONV off if the HV breaker 00SW10B07 is open for 10 seconds | 2 | 2026-05-29 | Advice from Toshiba vendor (Yardi) to add this into the system, similar to the mill converters. |  |  |  |  | Newly added converter on signal for cyclone feed pump. 4/6/2026 - test the interlocks by simulating a converter on and turning off the cooling water pump. Have not test sequence trigger to start.
F13MS401_INCH | 2000-F13-PID-PR-10003 | F13MS401 Inching Siren | Logic |  | N |  |  |  | Logic to activate the SAG Mill (F13-MS-401) inching siren when the mill is requested to inch from H13-HU-413 or F13MS401-CP. if (XI13743_SEL = SAG Mill and XS13760 = active) or MS_SIREN_REQ = active: activate siren YY13132 else YY13132 inactive | 1 | 2025-10-06 | CR-050
F13MB401_INCH | 2000-F13-PID-PR-10004 | F13MB401 Inching Siren | Logic |  | N |  |  |  | Logic to activate the Ball Mill (F13-MB-401) inching siren when the mill is requested to inch from H13-HU-413 or F13MB401-CP. if (XI13743_SEL = Ball Mill and XS13760 = active) or MB_SIREN_REQ = active: activate siren YY13145 else YY13145 inactive | 1 | 2025-10-06 | CR-050
JIC13136_LIM | 2000-F13-PID-PR-10003 | JIC13136 Limiter | Normal | Alarm | N |  | See Comments |  | if JIC13136 in auto and MS_INTENSITY >= 'i' for 'j' seconds: alarm JIC13136_LIM if JIC13136_LIM alarm set JIC13136 MH to JIC13136.PV - 'k' (instantaneous) else set JIC13136 MH to 100% include JIC13136_LIM alarm off-delay of 'l' seconds include functionality to enable/disable above logic from graphic i,j,k,l are adjustable by metallurgist from graphic initial conditions (values to be confirmed during commissioning / operations): i = 200 j = 300 seconds k = 3 l = 300 seconds | 1 | 2025-10-06 | CR-052
HS13135 | 2000-F13-PID-PR-10003 | F13MS401 Weight Ctrl Sel | Operator Selection | [5 empty] | CRO to select SAG Mill fill controller method. 1 Selection only Faceplate Selection: Volume (XIC13135) OR Weight (WIC13135) Selection outputs relevant control CSV to WIC13121. See PID tab. | 1 | 2025-10-13 | CR-052
F13PP401CP | 2000-F13-PID-PR-10002 | F13PP401CP Synertrex | [6 empty] | Configured using Modbus Spec, 2000-SPC-CS-11001_AC Cyclone Feed Pump Rev A Captured for checking purposes. | 1 | 2025-11-17 | Moved from AI tab
F13PO4XX_T1 | 2000-F13-PID-PR-10010 | F13PO4XX HP RestartDelay | Timer: 15 minutes (TBC) | [5 empty] | Include a minimum-off-time timer before any individual SAG Mill HP Lube Pump (F13-PO-429/430/431) is permitted to restart. Supervisor level access | 2 | 2026-05-22
F13PO5XX_T1 | 2000-F13-PID-PR-10011 | F13PO5XX HP RestartDelay | Timer: 15 minutes (TBC) | [5 empty] | Include a minimum-off-time timer before any individual Ball Mill HP Lube Pump (F13-PO-529/530/531) is permitted to restart. Supervisor level access | 2 | 2026-05-22
F13MS401PSR | N/A | 13MS401PSR Pwr. Stn. Contacted? | Operator Activated | [5 empty] | Operator to activate from drive faceplate. Included as start permissive. Activate for 20 minutes or F13MS401 running | 2 | 2026-07-03 | NOV233
F13MB401PSR | N/A | 13MB401PSR Pwr. Stn. Contacted? | Operator Activated | [5 empty] | Operator to activate from drive faceplate. Included as start permissive. Activate for 20 minutes or F13MB401 running | 2 | 2026-07-03 | NOV233
F13PP401PSR | N/A | 13PP401PSR Pwr. Stn. Contacted? | Operator Activated | [5 empty] | Operator to activate from drive faceplate. Included as start permissive. Activate for 20 minutes or F13PP401 running | 2 | 2026-07-03 | NOV233
F13PP401_STOP | 2000-F13-PID-PR-10002 | F13PP401 Stop Feed | Logic |  | N |  |  |  | If F13-PP-401 = not running (falling edge), one shot: - FIC13075 to MAN and set MV=0 and - FIC13141 to MAN and set MV=0 and - FIC13121 to MAN and set MV = 0 and - FIC14001 to MAN and set MV=0 and - FIC14002 to MAN and set MV=0 and If F13-PP-401 = not running (falling edge), after 1 minute (stop timer if F13-PP-401 running) one shot: - FIC13123 to MAN and set MV=0 and - FIC13143 to MAN and set MV=0 | 2
F13SC401_STOP | 2000-F13-PID-PR-10002 | F13SC401 Stop Sprays | Logic |  | N |  |  |  | If F13-SC-401 = not running (falling edge) for 3 minutes (stop timer if F13-SC-401 running): - FIC13071 to MAN and set MV=0 | 2
231

## 13. Alarm Database
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - MILLING & CLASSIFICATION (F13)
2000-F13-LST-PR-10001
ALARM DATABASE
[16 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Abbreviated Description (Faceplate) | Type | Alarm State | Alarm Value | Alarm Units | On Delay (sec) | Alarm Masking Condition | Impact | Urgency | Priority | Operator Response | Rev | Change Date | Change Reference | OK | Date | OK | Date | C1 Sign Off Comments
LI13036 | 2000-F13-PID-PR-10001 | F13BN402 Level | Analogue Input | A_HH | 90 | % | 5 | Mask A_Lo AND A_LL if Emergency Feeder is not selected for Duty operation on faceplate, F13FA400_FP1. | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Operator to advise FEL operator to cease loading of bin and/or increase Emergency Feeder throughput | A
LI13036 | 2000-F13-PID-PR-10001 | F13BN402 Level | Analogue Input | A_Hi | 80 | % | 5 | Mask A_Lo AND A_LL if Emergency Feeder is not selected for Duty operation on faceplate, F13FA400_FP1. | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to advise FEL operator to cease loading of bin and/or increase Emergency Feeder throughput | A
LI13036 | 2000-F13-PID-PR-10001 | F13BN402 Level | Analogue Input | A_LL | 20 | % | 5 | Mask A_Lo AND A_LL if Emergency Feeder is not selected for Duty operation on faceplate, F13FA400_FP1. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to resolve F13-BN-402 feed issues and restart Emergency Feeder, and/or utilise other Reclaim Feeders | A
LI13036 | 2000-F13-PID-PR-10001 | F13BN402 Level | Analogue Input | A_Lo | 30 | % | 5 | Mask A_Lo AND A_LL if Emergency Feeder is not selected for Duty operation on faceplate, F13FA400_FP1. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to resolve F13-BN-402 feed issues, reduce throughput / stop Emergency Feeder, and/or utilise other duty operating Feeders. | A
TI13003A | 2000-F13-PID-PR-10001 | F13FA411 U RTD | Analogue Input | A_HH | 180 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. Swap to standby Feeder if available, else Maintenance team to advise if a shutdown of F13-FA-411 is required | A
TI13003B | 2000-F13-PID-PR-10001 | F13FA411 V RTD | Analogue Input | A_HH | 180 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. Swap to standby Feeder if available, else Maintenance team to advise if a shutdown of F13-FA-411 is required | A
TI13003C | 2000-F13-PID-PR-10001 | F13FA411 W RTD | Analogue Input | A_HH | 180 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. Swap to standby Feeder if available, else Maintenance team to advise if a shutdown of F13-FA-411 is required | A
TI13003D | 2000-F13-PID-PR-10001 | F13FA411 DE Brg RTD | Analogue Input | A_HH | 120 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Swap to standby Feeder if available, else Maintenance team to advise if a shutdown of F13-FA-411 is required | A
TI13003E | 2000-F13-PID-PR-10001 | F13FA411 NDE Brg RTD | Analogue Input | A_HH | 120 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Swap to standby Feeder if available, else Maintenance team to advise if a shutdown of F13-FA-411 is required | A
TI13004A | 2000-F13-PID-PR-10001 | F13FA412 U RTD | Analogue Input | A_HH | 180 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. Swap to standby Feeder if available, else Maintenance team to advise if a shutdown of F13-FA-412 is required | A
TI13004B | 2000-F13-PID-PR-10001 | F13FA412 V RTD | Analogue Input | A_HH | 180 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. Swap to standby Feeder if available, else Maintenance team to advise if a shutdown of F13-FA-412 is required | A
TI13004C | 2000-F13-PID-PR-10001 | F13FA412 W RTD | Analogue Input | A_HH | 180 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. Swap to standby Feeder if available, else Maintenance team to advise if a shutdown of F13-FA-412 is required | A
LI13037 | 2000-F13-PID-PR-10001 | F13BN403 Level | Analogue Input | A_HH | 90 | % | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Immediate (<5 minutes) | High | Operator to advise FEL operator to cease loading of mill balls into F13-BN-403 | A
LI13037 | 2000-F13-PID-PR-10001 | F13BN403 Level | Analogue Input | A_Hi | 80 | % | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Rapid (>5 to <15 minutes) | Low | Operator to advise FEL operator to cease loading of mill balls into F13-BN-403 | A
LI13037 | 2000-F13-PID-PR-10001 | F13BN403 Level | Analogue Input | A_LL | 20 | % | 5 |  | None | Prompt (>15 to <30 minutes) | No Alarm | Operator to advise FEL operator to load F13-BN-403 with mill balls | A
LI13037 | 2000-F13-PID-PR-10001 | F13BN403 Level | Analogue Input | A_Lo | 30 | % | 5 |  | None | Not Urgent (>30 minutes) | No Alarm | Operator to advise FEL operator to load F13-BN-403 with mill balls | A
VI13060A | 2000-F13-PID-PR-10001 | F13CV403 Drive Pulley | Analogue Input | A_HH | 10 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment. Advise Maintenance/Field Operators to investigate immediately. | A
VI13060B | 2000-F13-PID-PR-10001 | F13CV403 Drive Pulley | Analogue Input | A_HH | 10 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment. Advise Maintenance/Field Operators to investigate immediately. | A
VI13172A | 2000-F13-PID-PR-10005 | F13CV404 Drive Pulley | Analogue Input | A_HH | 10 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment. Advise Maintenance/Field Operators to investigate immediately. | A
VI13172B | 2000-F13-PID-PR-10005 | F13CV404 Drive Pulley | Analogue Input | A_HH | 10 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment. Advise Maintenance/Field Operators to investigate immediately. | A
WI13055 | 2000-F13-PID-PR-10001 | F13CV403 SAG Feed Wet | Analogue Input | A_Lo | 1200 | t/h | 5 | 1. Mask A_Lo if F13-FA-411, F13-FA-412 AND F13-FA-414 Not Running 2. Mask A_Lo for 120 seconds (TBC) after F13-FA-411, F13-FA-412 OR F13-FA-414 Start Signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Nearing minimum operating capacities. Increase throughput. | A
WI13055 | 2000-F13-PID-PR-10001 | F13CV403 SAG Feed Wet | Analogue Input | A_Hi | 2180 | t/h | 5 | 1. Mask A_Lo if F13-FA-411, F13-FA-412 AND F13-FA-414 Not Running 2. Mask A_Lo for 120 seconds (TBC) after F13-FA-411, F13-FA-412 OR F13-FA-414 Start Signal | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Nearing maximum operating capacities. Decrease throughput. | A
LI13130 | 2000-F13-PID-PR-10003 | F13PS404 Level | Analogue Input | A_HH | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Operator to check pump is in automatic mode, else advise Field Operator / Maintenance to investigate sump area | A
LI13130 | 2000-F13-PID-PR-10003 | F13PS404 Level | Analogue Input | A_Hi | 80 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Operator to check pump is in automatic mode, else advise Field Operator / Maintenance to investigate sump area | A
VI13199A | 2000-F13-PID-PR-10005 | F13CV405 Drive Pulley | Analogue Input | A_HH | 10 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment. Advise Maintenance/Field Operators to investigate immediately. | A
VI13199B | 2000-F13-PID-PR-10005 | F13CV405 Drive Pulley | Analogue Input | A_HH | 10 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment. Advise Maintenance/Field Operators to investigate immediately. | A
VI13357A | 2000-F13-PID-PR-10006 | F13CV406 Drive Pulley | Analogue Input | A_HH | 10 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment. Advise Maintenance/Field Operators to investigate immediately. | A
VI13357B | 2000-F13-PID-PR-10006 | F13CV406 Drive Pulley | Analogue Input | A_HH | 10 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment. Advise Maintenance/Field Operators to investigate immediately. | A
VI13254A | 2000-F13-PID-PR-10006 | F13CC401 Drive DE | Analogue Input | A_HH | 8 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance to investigate immediately. Swap to standby Crusher if available, else Maintenance team to advise if a shutdown of F13-CC-401 is required | A
VI13254B | 2000-F13-PID-PR-10006 | F13CC401 Drive NDE | Analogue Input | A_HH | 8 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance to investigate immediately. Swap to standby Crusher if available, else Maintenance team to advise if a shutdown of F13-CC-401 is required | A
VI13256 | 2000-F13-PID-PR-10006 | F13CC401 Adj. Ring 1 | Analogue Input | A_HH | 8 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment. Advise Maintenance/Field Operators to investigate immediately. | A
VI13257 | 2000-F13-PID-PR-10006 | F13CC401 Adj. Ring 2 | Analogue Input | A_HH | 8 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment. Advise Maintenance/Field Operators to investigate immediately. | A
F13CC401_CSS | 2000-F13-PID-PR-10006 | F13CC401 Crusher CSS | Analogue Input | A_HH | F13CC401_MAX | mm | 5 | 1. Mask if F13CC401_CAL (See Misc sheet) is ACTIVE | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Conduct recalibration of F13-CC-401 CSS. | A
LI13142 | 2000-F13-PID-PR-10004 | F13BN404 MB Ball Lvl | Analogue Input | A_HH | 90 | % | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Immediate (<5 minutes) | High | Operator to advise FEL operator to cease loading of mill balls into F13-BN-404 | A
LI13142 | 2000-F13-PID-PR-10004 | F13BN404 MB Ball Lvl | Analogue Input | A_Hi | 80 | % | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Rapid (>5 to <15 minutes) | Low | Operator to advise FEL operator to cease loading of mill balls into F13-BN-404 | A
LI13142 | 2000-F13-PID-PR-10004 | F13BN404 MB Ball Lvl | Analogue Input | A_LL | 20 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to advise FEL operator to load F13-BN-404 with mill balls | 1 | 1900-01-22 | 22
LI13142 | 2000-F13-PID-PR-10004 | F13BN404 MB Ball Lvl | Analogue Input | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to advise FEL operator to load F13-BN-404 with mill balls | 1 | 1900-01-22 | 22
LI13221 | 2000-F13-PID-PR-10006 | F13BN411 Crusher C | Analogue Input | A_HH | 90 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to check Feed Bin Bypass Gate is in Bypass position. If not, advise Field Operator to check for blockages. If restrictions have been cleared, restart F13 with Bypass active whilst recovering bin level. Interlock must be bypassed to start F13-CV-405. | A
LI13221 | 2000-F13-PID-PR-10006 | F13BN411 Crusher C | Analogue Input | A_Hi | 85 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Feed Bin Bypass Gate (F13-DG-467) should be forced Bypass via XV13220 at the A_Hi Feed Bin level. Operator to monitor Feed Bin level and consider decreasing F13 throughput whilst levels recover. | A
LI13221 | 2000-F13-PID-PR-10006 | F13BN411 Crusher C | Analogue Input | A_LL | 20 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to consider single duty or intermittent Recycle Crusher operation and / or increase F13 throughput. | A
LI13221 | 2000-F13-PID-PR-10006 | F13BN411 Crusher C | Analogue Input | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to consider single duty or intermittent Recycle Crusher operation and / or increase F13 throughput. | A
VI13258 | 2000-F13-PID-PR-10006 | F13CC401 Adj. Ring 3 | Analogue Input | A_HH | 8 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment. Advise Maintenance/Field Operators to investigate immediately. | A
VI13259 | 2000-F13-PID-PR-10006 | F13CC401 Adj. Ring 4 | Analogue Input | A_HH | 8 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment. Advise Maintenance/Field Operators to investigate immediately. | A
VI13314A | 2000-F13-PID-PR-10006 | F13CC402 Drive DE | Analogue Input | A_HH | 8 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately. Swap to standby Crusher if available, else Maintenance team to advise if a shutdown of F13-CC-402 is required | A
VI13314B | 2000-F13-PID-PR-10006 | F13CC402 Drive NDE | Analogue Input | A_HH | 8 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately. Swap to standby Crusher if available, else Maintenance team to advise if a shutdown of F13-CC-402 is required | A
LI13222 | 2000-F13-PID-PR-10006 | F13BN411 Crusher D | Analogue Input | A_HH | 90 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to check Feed Bin Bypass Gate is in Bypass position. If not, advise Field Operator to check for blockages. If restrictions have been cleared, restart F13 with Bypass active whilst recovering bin level. Interlock must be bypassed to start F13-CV-405. | A
LI13222 | 2000-F13-PID-PR-10006 | F13BN411 Crusher D | Analogue Input | A_Hi | 85 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Feed Bin Bypass Gate (F13-DG-467) should be forced Bypass via XV13220 at the A_Hi Feed Bin level. Operator to monitor Feed Bin level and consider decreasing F13 throughput whilst levels recover. | A
LI13222 | 2000-F13-PID-PR-10006 | F13BN411 Crusher D | Analogue Input | A_LL | 20 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to consider single duty or intermittent Recycle Crusher operation and / or increase F13 throughput. | A
LI13222 | 2000-F13-PID-PR-10006 | F13BN411 Crusher D | Analogue Input | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to consider single duty or intermittent Recycle Crusher operation and / or increase F13 throughput. | A
F13CC401_CSS | 2000-F13-PID-PR-10006 | F13CC401 Crusher CSS | Analogue Input | A_Hi | 0.9 * F13CC401_MAX | mm | 5 | 1. Mask if F13CC401_CAL (See Misc sheet) is ACTIVE | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Monitor CSS and conduct recalibration of F13-CC-401 CSS when practical. | A
F13CC401_CSS | 2000-F13-PID-PR-10006 | F13CC401 Crusher CSS | Analogue Input | A_LL | F13CC401_MIN | mm | 5 | 1. Mask if F13CC401_CAL (See Misc sheet) is ACTIVE | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Conduct recalibration of F13-CC-401 CSS. | A
F13CC401_CSS | 2000-F13-PID-PR-10006 | F13CC401 Crusher CSS | Analogue Input | A_Lo | 1.1 * F13CC401_MIN | mm | 5 | 1. Mask if F13CC401_CAL (See Misc sheet) is ACTIVE | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Monitor CSS and conduct recalibration of F13-CC-401 CSS when practical. | A
F13CC402_CSS | 2000-F13-PID-PR-10006 | F13CC402 Crusher CSS | Analogue Input | A_HH | F13CC402_MAX | mm | 5 | 1. Mask if F13CC402_CAL (See Misc sheet) is ACTIVE | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Conduct recalibration of F13-CC-402 CSS. | A
F13CC402_CSS | 2000-F13-PID-PR-10006 | F13CC402 Crusher CSS | Analogue Input | A_Hi | 0.9 * F13CC402_MAX | mm | 5 | 1. Mask if F13CC402_CAL (See Misc sheet) is ACTIVE | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Monitor CSS and conduct recalibration of F13-CC-401 CSS when practical. | A
F13CC402_CSS | 2000-F13-PID-PR-10006 | F13CC402 Crusher CSS | Analogue Input | A_LL | F13CC402_MIN | mm | 5 | 1. Mask if F13CC402_CAL (See Misc sheet) is ACTIVE | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Conduct recalibration of F13-CC-402 CSS. | A
F13CC402_CSS | 2000-F13-PID-PR-10006 | F13CC402 Crusher CSS | Analogue Input | A_Lo | 1.1 * F13CC402_MIN | mm | 5 | 1. Mask if F13CC402_CAL (See Misc sheet) is ACTIVE | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Monitor CSS and conduct recalibration of F13-CC-401 CSS when practical. | A
PI13572 | 2000-ME001.3-D02-50004 | F13MS401A Motor DE Lube | Analogue Input | A_HH | 17500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
FI13461 | 2000-F13-PID-PR-10011 | F13PP401 Gland Water | Analogue Input | A_LL | 1 | m3/h | 10 | 1. F13-PP-401 Not Running 2. Mask for 10 seconds (TBC) after F13-PP-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check gland water system is healthy and inline auto valves are in the correct position. Else, advise Field Operator / Maintenance to investigate immediately. | A
FI13461 | 2000-F13-PID-PR-10011 | F13PP401 Gland Water | Analogue Input | A_Lo | 1.2 | m3/h | 10 | 1. F13-PP-401 Not Running 2. Mask for 10 seconds (TBC) after F13-PP-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check gland water system is healthy and inline auto valves are in the correct position. Else, advise Field Operator / Maintenance to investigate immediately. | A
FI13630 | 2000-ME001.2-D07-50002 | F13LU413 LP Lube Flow | Analogue Input | A_LL | 22 | m3/h | 5 | 1. F13-PO-427 AND F13-PO-428 Not Running 2. Mask for 20 seconds (TBC) on Pump (F13-PO-427 OR 428) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Swap to standby pump if required. | A
FI13630 | 2000-ME001.2-D07-50002 | F13LU413 LP Lube Flow | Analogue Input | A_Lo | 40 | m3/h | 5 | 1. F13-PO-427 AND F13-PO-428 Not Running 2. Mask for 20 seconds (TBC) on Pump (F13-PO-427 OR 428) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Swap to standby pump if required. | A
PI13573 | 2000-ME001.3-D02-50004 | F13MS401A Motor NDE Lube | Analogue Input | A_HH | 17500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
PI13574 | 2000-ME001.3-D02-50004 | F13MS401B Motor DE Lube | Analogue Input | A_HH | 17500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
PI13575 | 2000-ME001.3-D02-50004 | F13MS401B Motor NDE Lube | Analogue Input | A_HH | 17500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
TI13004D | 2000-F13-PID-PR-10001 | F13FA412 DE Brg RTD | Analogue Input | A_HH | 120 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Swap to standby Feeder if available, else Maintenance team to advise if a shutdown of F13-FA-412 is required | A
TI13004E | 2000-F13-PID-PR-10001 | F13FA412 NDE Brg RTD | Analogue Input | A_HH | 120 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Swap to standby Feeder if available, else Maintenance team to advise if a shutdown of F13-FA-412 is required | A
TI13255A | 2000-F13-PID-PR-10006 | F13CC401 U RTD 1 | Analogue Input | A_HH | 165 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. Swap to standby crusher if available, else Maintenance team to advise if a shutdown of F13-CC-401 is required | A
TI13255B | 2000-F13-PID-PR-10006 | F13CC401 V RTD 1 | Analogue Input | A_HH | 165 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. Swap to standby crusher if available, else Maintenance team to advise if a shutdown of F13-CC-401 is required | A
TI13255C | 2000-F13-PID-PR-10006 | F13CC401 W RTD 1 | Analogue Input | A_HH | 165 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. Swap to standby crusher if available, else Maintenance team to advise if a shutdown of F13-CC-401 is required | A
TI13255D | 2000-F13-PID-PR-10006 | F13CC401 NDE RTD | Analogue Input | A_HH | 165 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Swap to standby Crusher if available, else Maintenance team to advise if a shutdown of F13-CC-401 is required | A
PI13823 | 2000-F13-PID-PR-10011 | F13MB401A Motor DE Lube | Analogue Input | A_HH | 17500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
PI13824 | 2000-F13-PID-PR-10011 | F13MB401A Motor NDE Lube | Analogue Input | A_HH | 17500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
PI13825 | 2000-ME001.3-D02-50004 | F13MB401B Motor DE Lube | Analogue Input | A_HH | 17500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
PI13826 | 2000-F13-PID-PR-10011 | F13MB401B Motor NDE Lube | Analogue Input | A_HH | 17500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
TI13255E | 2000-F13-PID-PR-10006 | F13CC401 DE RTD | Analogue Input | A_HH | 165 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Swap to standby Crusher if available, else Maintenance team to advise if a shutdown of F13-CC-401 is required | A
FI13640 | 2000-ME001.2-D07-50002 | F13LU413 Flow Divider | Analogue Input | A_LL | 12.24 | m3/h | 5 | 1. F13-PO-429, 430 AND 431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Swap to standby pump if required. | A
FI13640 | 2000-ME001.2-D07-50002 | F13LU413 Flow Divider | Analogue Input | A_Lo | 12.96 | m3/h | 5 | 1. F13-PO-429, 430 AND 431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Swap to standby pump if required. | A
FI13641 | 2000-ME001.2-D07-50002 | F13LU413 Thrst Rail Flow | Analogue Input | A_LL | 12.24 | m3/h | 5 | 1. F13-PO-429, 430 AND 431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Swap to standby pump if required. | A
FI13641 | 2000-ME001.2-D07-50002 | F13LU413 Thrst Rail Flow | Analogue Input | A_Lo | 12.96 | m3/h | 5 | 1. F13-PO-429, 430 AND 431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Swap to standby pump if required. | A
FI13657 | 2000-ME001.2-D07-50002 | F13LU413 Float. Pinion R | Analogue Input | A_LL | 9 | L/min | 5 | 1. F13-PO-434 Not Running AND F13-PO-435 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-434 OR 435) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends and swap to standby pump if required. | A
FI13657 | 2000-ME001.2-D07-50002 | F13LU413 Float. Pinion R | Analogue Input | A_Lo | 9.5 | L/min | 5 | 1. F13-PO-434 Not Running AND F13-PO-435 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-434 OR 435) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points when practical. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends are healthy and swap to standby pump if required. Check in line valves and non-return valves for blockages. Monitor bearing temperature and vibration and upgrade urgency as required. | A
FI13658 | 2000-ME001.2-D07-50002 | F13LU413 Fxd Pinion R | Analogue Input | A_LL | 9 | L/min | 5 | 1. F13-PO-434 Not Running AND F13-PO-435 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-434 OR 435) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends and swap to standby pump if required. | A
FI13658 | 2000-ME001.2-D07-50002 | F13LU413 Fxd Pinion R | Analogue Input | A_Lo | 9.5 | L/min | 5 | 1. F13-PO-434 Not Running AND F13-PO-435 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-434 OR 435) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points when practical. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends are healthy and swap to standby pump if required. Check in line valves and non-return valves for blockages. Monitor bearing temperature and vibration and upgrade urgency as required. | A
FI13659 | 2000-ME001.2-D07-50002 | F13LU413 Float. Pinion L | Analogue Input | A_LL | 9 | L/min | 5 | 1. F13-PO-434 Not Running AND F13-PO-435 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-434 OR 435) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends and swap to standby pump if required. | A
FI13659 | 2000-ME001.2-D07-50002 | F13LU413 Float. Pinion L | Analogue Input | A_Lo | 9.5 | L/min | 5 | 1. F13-PO-434 Not Running AND F13-PO-435 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-434 OR 435) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points when practical. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends are healthy and swap to standby pump if required. Check in line valves and non-return valves for blockages. Monitor bearing temperature and vibration and upgrade urgency as required. | A
TI13282 | 2000-F13-PID-PR-10006 | F13CC402 C/Shaft Temp | Analogue Input | A_HH | 59 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check lubrication systems are running and that Crusher temperature and vibration indicators are healthy. Else, advise Maintenance team to investigate immediately. Swap to standby Crusher if available. | A
FI13660 | 2000-ME001.2-D07-50002 | F13LU413 Fxd Pinion L | Analogue Input | A_LL | 9 | L/min | 5 | 1. F13-PO-434 Not Running AND F13-PO-435 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-434 OR 435) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends and swap to standby pump if required. | A
FI13660 | 2000-ME001.2-D07-50002 | F13LU413 Fxd Pinion L | Analogue Input | A_Lo | 9.5 | L/min | 5 | 1. F13-PO-434 Not Running AND F13-PO-435 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-434 OR 435) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points when practical. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends are healthy and swap to standby pump if required. Check in line valves and non-return valves for blockages. Monitor bearing temperature and vibration and upgrade urgency as required. | A
LI13426 | 2000-F13-PID-PR-10012 | F13TK408 Level | Analogue Input | A_HH | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Plant Tripped | Logging | Advise Field Operator to inspect area and to ensure Scheme Water fill valves are closed. It may be necessary to drain Tank to an acceptable level (check line fill). | B
FI13881 | 2000-F13-PID-PR-10011 | F13LU423 LP Lube Flow | Analogue Input | A_LL | 22 | m3/h | 5 | F13-PO-527 AND F13-PO-528 Not Running Mask alarms for 20 seconds on Pump (F13-PO-527 OR 528) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Trip duty pump. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Swap to standby pump if required. | B
FI13881 | 2000-F13-PID-PR-10011 | F13LU423 LP Lube Flow | Analogue Input | A_Lo | 40 | m3/h | 5 | F13-PO-527 AND F13-PO-528 Not Running Mask alarms for 20 seconds on Pump (F13-PO-527 OR 528) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Swap to standby pump if required. | B
FI13891 | 2000-F13-PID-PR-10011 | F13LU423 Flow Divider | Analogue Input | A_LL | 12.24 | m3/h | 5 | F13-PO-529, 530 AND 531 Not Running Mask alarms for 10 seconds on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Swap to standby pump if required. | B
FI13891 | 2000-F13-PID-PR-10011 | F13LU423 Flow Divider | Analogue Input | A_Lo | 12.96 | m3/h | 5 | F13-PO-529, 530 AND 531 Not Running Mask alarms for 10 seconds on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Swap to standby pump if required. | B
FI13892 | 2000-F13-PID-PR-10011 | F13LU423 Thrst Rail Flow | Analogue Input | A_LL | 12.24 | m3/h | 5 | F13-PO-529, 530 AND 531 Not Running Mask alarms for 10 seconds on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Trip duty pump. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Swap to standby pump if required. | B
FI13892 | 2000-F13-PID-PR-10011 | F13LU423 Thrst Rail Flow | Analogue Input | A_Lo | 12.96 | m3/h | 5 | F13-PO-529, 530 AND 531 Not Running Mask alarms for 10 seconds on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Swap to standby pump if required. | B
FI13908 | 2000-F13-PID-PR-10011 | F13LU423 Float. Pinion R | Analogue Input | A_LL | 9 | L/min | 5 | F13-PO-534 Not Running AND F13-PO-535 Not Running Mask alarms for 10 seconds on Pump (F13-PO-534 OR 535) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Trip ball mill. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends and swap to standby pump if required. | B
FI13908 | 2000-F13-PID-PR-10011 | F13LU423 Float. Pinion R | Analogue Input | A_Lo | 9.5 | L/min | 5 | F13-PO-534 Not Running AND F13-PO-535 Not Running Mask alarms for 10 seconds on Pump (F13-PO-534 OR 535) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points when practical. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends are healthy and swap to standby pump if required. Check in line valves and non-return valves for blockages. Monitor bearing temperature and vibration and upgrade urgency as required. | B
VI13517 | 2000-ME001.2-D07-50002 | F13MS401A Motor NDE Brg | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. | A
VI13316 | 2000-F13-PID-PR-10006 | F13CC402 Adj. Ring 1 | Analogue Input | A_HH | 8 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment and advise Maintenance team to investigate immediately. | A
VI13317 | 2000-F13-PID-PR-10006 | F13CC402 Adj. Ring 2 | Analogue Input | A_HH | 8 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment and advise Maintenance team to investigate immediately. | A
VI13318 | 2000-F13-PID-PR-10006 | F13CC402 Adj. Ring 3 | Analogue Input | A_HH | 8 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment and advise Maintenance team to investigate immediately. | A
VI13319 | 2000-F13-PID-PR-10006 | F13CC402 Adj. Ring 4 | Analogue Input | A_HH | 8 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Attempt restart of conveyor and upstream equipment and advise Maintenance team to investigate immediately. | A
LI13426 | 2000-F13-PID-PR-10012 | F13TK408 Level | Analogue Input | A_Hi | 80 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Potential overflow to grade. Advise Field Operator to inspect area and to ensure Scheme Water manual fill valves are closed. It may be necessary to drain Tank to an acceptable level (check line fill). | B
LI13426 | 2000-F13-PID-PR-10012 | F13TK408 Level | Analogue Input | A_LL | 20 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check for Cooling Water distribution issues. Potential leakage. Refill with manual valves once Cooling Water losses resolved. | B
LI13426 | 2000-F13-PID-PR-10012 | F13TK408 Level | Analogue Input | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check for Cooling Water distribution issues. Potential leakage. Refill with manual valves once Cooling Water losses resolved. If levels are declining rapidly, consider shutting down affected areas as soon as possible. | B
FI13909 | 2000-F13-PID-PR-10011 | F13LU423 Fxd Pin. Brg R | Analogue Input | A_LL | 9 | L/min | 5 | F13-PO-534 Not Running AND F13-PO-535 Not Running Mask alarms for 10 seconds on Pump (F13-PO-534 OR 535) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Trip ball mill. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends and swap to standby pump if required. | B
LI13268 | 2000-F13-PID-PR-10006 | F13HU403 Hyd. Oil Tank | Analogue Input | A_Hi | 90 | % | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Operator to advise Field Operator to check for hydraulic oil tank overflow. Maintenance to check and drain oil as required. | A
TI13315A | 2000-F13-PID-PR-10006 | F13CC402 U RTD 1 | Analogue Input | A_HH | 165 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. Swap to standby crusher if available, else Maintenance team to advise if a shutdown of F13-CC-402 is required | A
TI13315B | 2000-F13-PID-PR-10006 | F13CC402 V RTD 1 | Analogue Input | A_HH | 165 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. Swap to standby crusher if available, else Maintenance team to advise if a shutdown of F13-CC-402 is required | A
TI13315C | 2000-F13-PID-PR-10006 | F13CC402 W RTD 1 | Analogue Input | A_HH | 165 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. Swap to standby crusher if available, else Maintenance team to advise if a shutdown of F13-CC-402 is required | A
TI13315D | 2000-F13-PID-PR-10006 | F13CC402 NDE RTD | Analogue Input | A_HH | 165 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Swap to standby Crusher if available, else Maintenance team to advise if a shutdown of F13-CC-402 is required | A
TDI13763 | 2000-F13-PID-PR-10011 | F13MB401A Pin. Gear R dT | Analogue Input | A_HH | 17 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
TI13315E | 2000-F13-PID-PR-10006 | F13CC402 DE RTD | Analogue Input | A_HH | 165 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Swap to standby Crusher if available, else Maintenance team to advise if a shutdown of F13-CC-402 is required | A
TDI13786 | 2000-F13-PID-PR-10011 | F13MB401B Pin. Gear L dT | Analogue Input | A_HH | 17 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
FI13909 | 2000-F13-PID-PR-10011 | F13LU423 Fxd Pin. Brg R | Analogue Input | A_Lo | 9.5 | L/min | 5 | F13-PO-534 Not Running AND F13-PO-535 Not Running Mask alarms for 10 seconds on Pump (F13-PO-534 OR 535) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points when practical. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends are healthy and swap to standby pump if required. Check in line valves and non-return valves for blockages. Monitor bearing temperature and vibration and upgrade urgency as required. | B
FI13910 | 2000-F13-PID-PR-10011 | F13LU423 Float. Pinion L | Analogue Input | A_LL | 9 | L/min | 5 | F13-PO-534 Not Running AND F13-PO-535 Not Running Mask alarms for 10 seconds on Pump (F13-PO-534 OR 535) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Trip ball mill. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends and swap to standby pump if required. | B
VI13539 | 2000-ME001.2-D07-50002 | F13MS401B Motor NDE Brg | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
LI13268 | 2000-F13-PID-PR-10006 | F13HU403 Hyd. Oil Tank | Analogue Input | A_LL | 15 | % | 60 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to advise Field Operator / Maintenance to investigate for hydraulic system leakages / ruptures. Repair if required and refill reservoir with oil. | A
LI13268 | 2000-F13-PID-PR-10006 | F13HU403 Hyd. Oil Tank | Analogue Input | A_Lo | 47 | % | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to advise Field Operator / Maintenance to investigate for hydraulic system leakages / ruptures. Repair if required and refill reservoir with oil. | A
FI13910 | 2000-F13-PID-PR-10011 | F13LU423 Float. Pinion L | Analogue Input | A_Lo | 9.5 | L/min | 5 | F13-PO-534 Not Running AND F13-PO-535 Not Running Mask alarms for 10 seconds on Pump (F13-PO-534 OR 535) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points when practical. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends are healthy and swap to standby pump if required. Check in line valves and non-return valves for blockages. Monitor bearing temperature and vibration and upgrade urgency as required. | B
FI13911 | 2000-F13-PID-PR-10011 | F13LU423 Fxd Pin. Brg L | Analogue Input | A_LL | 9 | L/min | 5 | F13-PO-534 Not Running AND F13-PO-535 Not Running Mask alarms for 10 seconds on Pump (F13-PO-534 OR 535) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Trip ball mill. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends and swap to standby pump if required. | B
FI13911 | 2000-F13-PID-PR-10011 | F13LU423 Fxd Pin. Brg L | Analogue Input | A_Lo | 9.5 | L/min | 5 | F13-PO-534 Not Running AND F13-PO-535 Not Running Mask alarms for 10 seconds on Pump (F13-PO-534 OR 535) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential blockage, rupture or pump issues. Advise Field Operator and Maintenance team to check the lines and bearing supply points when practical. Check the lubrication unit and delivery system is healthy. Check alternate supply lines flowrate trends are healthy and swap to standby pump if required. Check in line valves and non-return valves for blockages. Monitor bearing temperature and vibration and upgrade urgency as required. | B
TDI13511 | 2000-F13-PID-PR-10010 | F13MS401 Pin. Gear R dT | Analogue Input | A_HH | 17 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
TDI13515 | 2000-F13-PID-PR-10010 | F13MS401 Pin. Gear L dT | Analogue Input | A_HH | 17 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
PDI13261 | 2000-F13-PID-PR-10006 | F13HU403 Hyd. Filter dP | Analogue Input | A_Hi | 8600 | kPa | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Hydraulic oil filter clog alarm. Advise Field Operator / Maintenace to replace when practical. Monitor hydraulic oil systems and upgrade urgency as required. | A
PDI13321 | 2000-F13-PID-PR-10006 | F13HU404 Hyd. Filter dP | Analogue Input | A_Hi | 8600 | kPa | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Hydraulic oil filter clog alarm. Advise Field Operator / Maintenace to replace when practical. Monitor hydraulic oil systems and upgrade urgency as required. | A
PI13263 | 2000-F13-PID-PR-10006 | F13HU403 Clamping | Analogue Input | A_LL | 16500 | kPa | 5 | 1. F13CC401_CLMP Inactive | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check that hydraulic system is in auto and healthy. If issues persist, advise Field Operator / Maintenance to check hydraulic unit clamping cylinders, solenoid valves etc. Utilise alternate Crusher if available. | A
PI13263 | 2000-F13-PID-PR-10006 | F13HU403 Clamping | Analogue Input | A_Lo | 17900 | kPa | 10 | 1. F13CC401_CLMP Inactive | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check that hydraulic system is in auto and healthy. If issues persist, advise Field Operator / Maintenance to check hydraulic unit clamping cylinders, solenoid valves etc. Utilise alternate Crusher if available. | A
VI13518 | 2000-ME001.2-D07-50002 | F13MS401A Motor DE Brg | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. | A
VI13767 | 2000-F13-PID-PR-10011 | F13MB401A Motor NDE Brg | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check Mill speed and Mill weight is within setpoint range. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. | B
TI13570 | 2000-ME001.3-D02-50004 | F13LU411 Tank Temp. | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check the Motor Lubrication unit is operating in auto and is healthy. Check the Main Motor DE and NDE vibration and temperature indicators. Check the Cooler Fan and Lube Unit Heater are operating in auto and are healthy. | A
VI13789 | 2000-F13-PID-PR-10011 | F13MB401B Motor NDE Brg | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check Mill speed and Mill weight is within setpoint range. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. | B
TI13511 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank R 1 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
TI13512 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank R 2 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
TI13513 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank R 3 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
TI13514 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank R 4 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
PI13264 | 2000-F13-PID-PR-10006 | F13HU403 Tramp | Analogue Input | A_LL | 9600 | kPa | 5 | 1. F13CC401_TRMP Inactive | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check that hydraulic system is in auto and healthy. If issues persist, advise Field Operator / Maintenance to check hydraulic unit tramp cylinders, solenoid valves etc. Utilise alternate Crusher if available. | A
PI13264 | 2000-F13-PID-PR-10006 | F13HU403 Tramp | Analogue Input | A_Lo | 11000 | kPa | 60 | 1. F13CC401_TRMP Inactive | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check that hydraulic system is in auto and healthy. If issues persist, advise Field Operator / Maintenance to check hydraulic unit tramp cylinders, solenoid valves etc. Utilise alternate Crusher if available. | A
LI13328 | 2000-F13-PID-PR-10006 | F13HU404 Hyd. Oil Tank | Analogue Input | A_Hi | 90 | % | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Operator to advise Field Operator to check for hydraulic oil tank overflow. Maintenance to check and drain oil as required. | A
VI13540 | 2000-ME001.2-D07-50002 | F13MS401B Motor DE Brg | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
VI13060A | 2000-F13-PID-PR-10001 | F13CV403 Drive Pulley | Analogue Input | A_Hi | 7 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Field Operator / Maintenance team to monitor and investigate when practical. Monitor vibration trends and upgrade urgency as required | A
VI13060B | 2000-F13-PID-PR-10001 | F13CV403 Drive Pulley | Analogue Input | A_Hi | 7 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Field Operator / Maintenance team to monitor and investigate when practical. Monitor vibration trends and upgrade urgency as required | A
VI13172A | 2000-F13-PID-PR-10005 | F13CV404 Drive Pulley | Analogue Input | A_Hi | 7 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Field Operator / Maintenance team to monitor and investigate when practical. Monitor vibration trends and upgrade urgency as required | A
VI13172B | 2000-F13-PID-PR-10005 | F13CV404 Drive Pulley | Analogue Input | A_Hi | 7 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Field Operator / Maintenance team to monitor and investigate when practical. Monitor vibration trends and upgrade urgency as required | A
TI13255D | 2000-F13-PID-PR-10006 | F13CC401 NDE RTD | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
LI13328 | 2000-F13-PID-PR-10006 | F13HU404 Hyd. Oil Tank | Analogue Input | A_LL | 15 | % | 60 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to advise Field Operator / Maintenance to investigate for hydraulic system leakages / ruptures. Repair if required and refill reservoir with oil. | A
LI13328 | 2000-F13-PID-PR-10006 | F13HU404 Hyd. Oil Tank | Analogue Input | A_Lo | 47 | % | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to advise Field Operator / Maintenance to investigate for hydraulic system leakages / ruptures. Repair if required and refill reservoir with oil. | A
F13CC401II | 2000-F13-PID-PR-10006 | F13CC401 Current | Analogue Input | A_Hi | 650 | Amps | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Feeder tripped. Check tramping cylinders are operating as intended. Engage clearing cylinders to clear Crusher cavity and restart. Start standby Crusher if available. Advise Field Operator to investigate. Setpoint TBC during commissioning. NOTE: HAZOP Action Item 85 | 1 | 2025-08-08 | PL294
F13CC401II | 2000-F13-PID-PR-10006 | F13CC401 Current | Analogue Input | A_HH | 710 | Amps | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Crusher tripped. Check tramping cylinders are operating as intended. Engage clearing cylinders to clear Crusher cavity and restart. Start standby Crusher if available. Advise Field Operator to investigate. Setpoint TBC during commissioning. NOTE: HAZOP Action Item 85 | 1 | 2025-04-29 | RE: Recycle Crushing Punchlist Items
F13CC402II | 2000-F13-PID-PR-10006 | F13CC402 Current | Analogue Input | A_Hi | 650 | Amps | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Feeder tripped. Check tramping cylinders are operating as intended. Engage clearing cylinders to clear Crusher cavity and restart. Start standby Crusher if available. Advise Field Operator to investigate. Setpoint TBC during commissioning. NOTE: HAZOP Action Item 85 | 1 | 2025-04-29 | RE: Recycle Crushing Punchlist Items
F13CC402II | 2000-F13-PID-PR-10006 | F13CC402 Current | Analogue Input | A_HH | 710 | Amps | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Crusher tripped. Check tramping cylinders are operating as intended. Engage clearing cylinders to clear Crusher cavity and restart. Start standby Crusher if available. Advise Field Operator to investigate. Setpoint TBC during commissioning. NOTE: HAZOP Action Item 85 | 1 | 2025-08-08 | PL294
PI13323 | 2000-F13-PID-PR-10006 | F13HU404 Clamping | Analogue Input | A_LL | 16500 | kPa | 5 | 1. F13CC402_CLMP Inactive | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check that hydraulic system is in auto and healthy. If issues persist, advise Field Operator / Maintenance to check hydraulic unit clamping cylinders, solenoid valves etc. Utilise alternate Crusher if available. | A
PI13323 | 2000-F13-PID-PR-10006 | F13HU404 Clamping | Analogue Input | A_Lo | 17900 | kPa | 10 | 1. F13CC402_CLMP Inactive | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check that hydraulic system is in auto and healthy. If issues persist, advise Field Operator / Maintenance to check hydraulic unit clamping cylinders, solenoid valves etc. Utilise alternate Crusher if available. | A
PI13324 | 2000-F13-PID-PR-10006 | F13HU404 Tramp | Analogue Input | A_LL | 9600 | kPa | 5 | 1. F13CC402_TRMP Inactive | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check that hydraulic system is in auto and healthy. If issues persist, advise Field Operator / Maintenance to check hydraulic unit tramp cylinders, solenoid valves etc. Utilise alternate Crusher if available. | A
PI13324 | 2000-F13-PID-PR-10006 | F13HU404 Tramp | Analogue Input | A_Lo | 11000 | kPa | 60 | 1. F13CC402_TRMP Inactive | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check that hydraulic system is in auto and healthy. If issues persist, advise Field Operator / Maintenance to check hydraulic unit tramp cylinders, solenoid valves etc. Utilise alternate Crusher if available. | A
SI13253 | 2000-F13-PID-PR-10006 | F13CC401 C/Shaft Speed | Analogue Input | A_LL | 90 | % | 18 | 1. F13-CC-401 Not Running 2. Mask for 10 seconds (TBC) after F13-CC-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check hydraulic system is healthy, no tramp material is causing underspeed and CSS at correct setpoint. Else, advise Maintenance to investigate immediately for mechanical issues / belt slippage etc. Utilise alternate Crusher if available. | A
TI13515 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank L 1 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
TI13516 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank L 2 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
SI13253 | 2000-F13-PID-PR-10006 | F13CC401 C/Shaft Speed | Analogue Input | A_Lo | 95 | % | 10 | 1. F13-CC-401 Not Running 2. Mask for 10 seconds (TBC) after F13-CC-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check hydraulic system is healthy, no tramp material is causing underspeed and CSS at correct setpoint. Else, advise Maintenance to investigate immediately for mechanical issues / belt slippage etc. Utilise alternate Crusher if available. | A
SI13313 | 2000-F13-PID-PR-10006 | F13CC402 C/Shaft Speed | Analogue Input | A_LL | 90 | % | 18 | 1. F13-CC-402 Not Running 2. Mask for 10 seconds (TBC) after F13-CC-402 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check hydraulic system is healthy, no tramp material is causing underspeed and CSS at correct setpoint. Else, advise Maintenance to investigate immediately for mechanical issues / belt slippage etc. Utilise alternate Crusher if available. | A
SI13313 | 2000-F13-PID-PR-10006 | F13CC402 C/Shaft Speed | Analogue Input | A_Lo | 95 | % | 10 | 1. F13-CC-402 Not Running 2. Mask for 10 seconds (TBC) after F13-CC-402 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check hydraulic system is healthy, no tramp material is causing underspeed and CSS at correct setpoint. Else, advise Maintenance to investigate immediately for mechanical issues / belt slippage etc. Utilise alternate Crusher if available. | A
TI13232 | 2000-F13-PID-PR-10006 | F13CC401 C/Shaft Temp | Analogue Input | A_HH | 59 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check the lubrication system is healthy, no tramp material is causing overloading and CSS at correct setpoint. Else, advise Maintenance to investigate immediately for mechanical issues / misalignment etc. Utilise alternate Crusher if available. | A
TI13232 | 2000-F13-PID-PR-10006 | F13CC401 C/Shaft Temp | Analogue Input | A_Hi | 54 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check the lubrication system is healthy, no tramp material is causing overloading and CSS at correct setpoint. Else, advise Maintenance to investigate immediately for mechanical issues / misalignment etc. Utilise alternate Crusher if available. | A
TI13267 | 2000-F13-PID-PR-10006 | F13HU403 Hyd. Oil Tank | Analogue Input | A_HH | 65 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check hydraulic pump and pressure trends in hydraulic system are healthy. Advise Maintenance to investigate immediately if issues persist or cannot be identified. Utilise alternate Crusher if available. | A
TI13960B | 2000-F13-PID-PR-10011 | F13MB401 Dsch Trn L Ctr | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13960C | 2000-F13-PID-PR-10011 | F13MB401 Dsch Trn L IB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13960A | 2000-F13-PID-PR-10011 | F13MB401 Dsch Trn L OB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13958B | 2000-F13-PID-PR-10011 | F13MB401 Dsch Trn R Ctr | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13958C | 2000-F13-PID-PR-10011 | F13MB401 Dsch Trn R IB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13958A | 2000-F13-PID-PR-10011 | F13MB401 Dsch Trn R OB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13966B | 2000-F13-PID-PR-10011 | F13MB401 Feed Trn L Ctr | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13966C | 2000-F13-PID-PR-10011 | F13MB401 Feed Trn L IB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13713A | 2000-ME001.2-D07-50002 | F13MS401 Dsch Thst R OB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13713B | 2000-ME001.2-D07-50002 | F13MS401 Dsch Thst R IB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13715A | 2000-ME001.2-D07-50002 | F13MS401 Dsch Thst L OB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13715B | 2000-ME001.2-D07-50002 | F13MS401 Dsch Thst L IB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13519 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank L 3 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
TI13520 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank L 4 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
TI13704 | 2000-ME001.2-D07-50002 | F13MS401 Dsch Fxd Pin. R | Analogue Input | A_HH | 75 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Check for excess Vibration on respective indicator. Advise Maintenance team to investigate immediately if unresolved. | A
TI13705 | 2000-ME001.2-D07-50002 | F13MS401 Dsch Fxd Pin. L | Analogue Input | A_HH | 75 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Check for excess Vibration on respective indicator. Advise Maintenance team to investigate immediately if unresolved. | A
TI13706 | 2000-ME001.2-D07-50002 | F13MS401 Feed Fl. Pin. R | Analogue Input | A_HH | 75 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Check for excess Vibration on respective indicator. Advise Maintenance team to investigate immediately if unresolved. | A
TI13707 | 2000-ME001.2-D07-50002 | F13MS401 Feed Fl. Pin. L | Analogue Input | A_HH | 75 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Check for excess Vibration on respective indicator. Advise Maintenance team to investigate immediately if unresolved. | A
TI13763 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank R 1 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
TI13764 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank R 2 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
TI13765 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank R 3 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
TI13766 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank R 4 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
TI13783 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank L 1 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
TI13784 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank L 2 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
TI13712A | 2000-ME001.2-D07-50002 | F13MS401 Feed Trn R OB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13966A | 2000-F13-PID-PR-10011 | F13MB401 Feed Trn L OB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13964B | 2000-F13-PID-PR-10011 | F13MB401 Feed Trn R Ctr | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13964C | 2000-F13-PID-PR-10011 | F13MB401 Feed Trn R IB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13964A | 2000-F13-PID-PR-10011 | F13MB401 Feed Trn R OB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13712B | 2000-ME001.2-D07-50002 | F13MS401 Feed Trn R Ctr | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13712C | 2000-ME001.2-D07-50002 | F13MS401 Feed Trn R IB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13714A | 2000-ME001.2-D07-50002 | F13MS401 Feed Trn L OB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
LI13241 | 2000-F13-PID-PR-10006 | F13LU403 Lube Oil Tank | Analogue Input | A_HH | 90 | % | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Operator to advise Field Operator to check for lubrication oil tank overflow. Maintenance to check and drain oil as required. | A
TI13282 | 2000-F13-PID-PR-10006 | F13CC402 C/Shaft Temp | Analogue Input | A_Hi | 54 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check the lubrication system is healthy, no tramp material is causing overloading and CSS at correct setpoint. Else, advise Maintenance to investigate immediately for mechanical issues / misalignment etc. Utilise alternate Crusher if available. | A
TI13327 | 2000-F13-PID-PR-10006 | F13HU404 Hyd. Oil Tank | Analogue Input | A_HH | 65 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check hydraulic pump and pressure trends in hydraulic system are healthy. Advise Maintenance to investigate immediately if issues persist or cannot be identified. Utilise alternate Crusher if available. | A
TI13785 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank L 3 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
TI13786 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank L 4 | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate immediately for proper gear alignment, tooth damage etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
VI13199A | 2000-F13-PID-PR-10005 | F13CV405 Drive Pulley | Analogue Input | A_Hi | 7 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Field Operator / Maintenance team to monitor and investigate when practical. Monitor vibration trends and upgrade urgency as required | A
VI13199B | 2000-F13-PID-PR-10005 | F13CV405 Drive Pulley | Analogue Input | A_Hi | 7 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Field Operator / Maintenance team to monitor and investigate when practical. Monitor vibration trends and upgrade urgency as required | A
VI13357A | 2000-F13-PID-PR-10006 | F13CV406 Drive Pulley | Analogue Input | A_Hi | 7 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Field Operator / Maintenance team to monitor and investigate when practical. Monitor vibration trends and upgrade urgency as required | A
VI13357B | 2000-F13-PID-PR-10006 | F13CV406 Drive Pulley | Analogue Input | A_Hi | 7 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Field Operator / Maintenance team to monitor and investigate when practical. Monitor vibration trends and upgrade urgency as required | A
TI13420 | 2000-F13-PID-PR-10009 | F13HE420 Cool Water In | Analogue Input | A_Hi | 45 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Cooling Water users for high temperatures. Check Chillers are healthy and meeting setpoint. Bring additional Chillers online as required. | B
TI13420 | 2000-F13-PID-PR-10009 | F13HE420 Cool Water In | Analogue Input | A_Lo | 5 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Chillers are in auto and healthy. | B
TI13714B | 2000-ME001.2-D07-50002 | F13MS401 Feed Trn L Ctr | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13714C | 2000-ME001.2-D07-50002 | F13MS401 Feed Trn L IB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
LI13241 | 2000-F13-PID-PR-10006 | F13LU403 Lube Oil Tank | Analogue Input | A_LL | 10 | % | 60 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures. Repair if required and refill reservoir with oil. | A
TI13716A | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn R OB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13716B | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn R Ctr | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
VI13254A | 2000-F13-PID-PR-10006 | F13CC401 Drive DE | Analogue Input | A_Hi | 6 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
VI13254B | 2000-F13-PID-PR-10006 | F13CC401 Drive NDE | Analogue Input | A_Hi | 6 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
VI13256 | 2000-F13-PID-PR-10006 | F13CC401 Adj. Ring 1 | Analogue Input | A_Hi | 6 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
VI13257 | 2000-F13-PID-PR-10006 | F13CC401 Adj. Ring 2 | Analogue Input | A_Hi | 6 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
TI13716C | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn R IB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13717A | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn L OB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13717B | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn L Ctr | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13717C | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn L IB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13315D | 2000-F13-PID-PR-10006 | F13CC402 NDE RTD | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
TI13003E | 2000-F13-PID-PR-10001 | F13FA411 NDE Brg RTD | Analogue Input | A_Hi | 110 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check lubrication systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Feeders, else monitor temperature trends and upgrade urgency as required | A
TI13954 | 2000-F13-PID-PR-10011 | F13MB401 Feed Fl. Pin. L | Analogue Input | A_HH | 75 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Check for excess Vibration on respective indicator. Advise Maintenance team to investigate immediately if unresolved. | B
TI13955 | 2000-F13-PID-PR-10011 | F13MB401 Feed Fl. Pin. R | Analogue Input | A_HH | 75 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Check for excess Vibration on respective indicator. Advise Maintenance team to investigate immediately if unresolved. | B
TI13956 | 2000-F13-PID-PR-10011 | F13MB401 Dsch Fxd Pin. L | Analogue Input | A_HH | 75 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Check for excess Vibration on respective indicator. Advise Maintenance team to investigate immediately if unresolved. | B
TI13957 | 2000-F13-PID-PR-10011 | F13MB401 Dsch Fxd Pin. R | Analogue Input | A_HH | 75 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Check for excess Vibration on respective indicator. Advise Maintenance team to investigate immediately if unresolved. | B
LI13241 | 2000-F13-PID-PR-10006 | F13LU403 Lube Oil Tank | Analogue Input | A_Lo | 50 | % | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to advise Field Operator / Maintenance to investigate for lubrication system for leakages / ruptures. Repair if required and refill reservoir with oil. | A
LI13301 | 2000-F13-PID-PR-10006 | F13LU404 Lube Oil Tank | Analogue Input | A_HH | 90 | % | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Operator to advise Field Operator to check for lubrication oil tank overflow. Maintenance to check and drain oil as required. | A
LI13301 | 2000-F13-PID-PR-10006 | F13LU404 Lube Oil Tank | Analogue Input | A_LL | 10 | % | 60 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures. Repair if required and refill reservoir with oil. | A
LI13301 | 2000-F13-PID-PR-10006 | F13LU404 Lube Oil Tank | Analogue Input | A_Lo | 50 | % | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures. Repair if required and refill reservoir with oil. | A
LI13619 | 2000-ME001.2-D07-50002 | F13LU413 Lube Set. Comp. | Analogue Input | A_LL | 10 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures or internal restrictions. Repair if required and refill reservoir with oil. | A
LI13619 | 2000-ME001.2-D07-50002 | F13LU413 Lube Set. Comp. | Analogue Input | A_Lo | 38 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures or internal restrictions. Repair if required and refill reservoir with oil. | A
TDI13712 | 2000-ME001.2-D07-50002 | F13MS401 Fd TrnBrgR dT | Analogue Input | A_Hi | 5 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TDI13714 | 2000-ME001.2-D07-50002 | F13MS401 Fd TrnBrgL dT | Analogue Input | A_Hi | 5 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TDI13716 | 2000-ME001.2-D07-50002 | F13MS401 Dsch TrnBrgR dT | Analogue Input | A_Hi | 5 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TDI13717 | 2000-ME001.2-D07-50002 | F13MS401 Dsch TrnBrgL dT | Analogue Input | A_Hi | 5 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
VI13708 | 2000-ME001.2-D07-50002 | F13MS401 Feed Fxd Pin. R | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
VI13709 | 2000-ME001.2-D07-50002 | F13MS401 Feed Fxd Pin. L | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
VI13710 | 2000-ME001.2-D07-50002 | F13MS401 Feed Fl. Pin. R | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
VI13711 | 2000-ME001.2-D07-50002 | F13MS401 Feed Fl. Pin. L | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Maintenance team to advise if a shutdown of F13-MS-401 is required | A
VI13971 | 2000-ME001.3-D07-50002 | F13MB401 Feed Fl. Pin. L | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
VI13258 | 2000-F13-PID-PR-10006 | F13CC401 Adj. Ring 3 | Analogue Input | A_Hi | 6 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
VI13259 | 2000-F13-PID-PR-10006 | F13CC401 Adj. Ring 4 | Analogue Input | A_Hi | 6 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
VI13314A | 2000-F13-PID-PR-10006 | F13CC402 Drive DE | Analogue Input | A_Hi | 6 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
VI13314B | 2000-F13-PID-PR-10006 | F13CC402 Drive NDE | Analogue Input | A_Hi | 6 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
VI13770 | 2000-F13-PID-PR-10011 | F13MB401A Motor DE Brg | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check Mill speed and Mill weight is within setpoint range. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. | B
TI13004E | 2000-F13-PID-PR-10001 | F13FA412 NDE Brg RTD | Analogue Input | A_Hi | 110 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check lubrication systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Feeders, else monitor temperature trends and upgrade urgency as required | A
VI13792 | 2000-F13-PID-PR-10011 | F13MB401B Motor DE Brg | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check Mill speed and Mill weight is within setpoint range. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. | B
TI13821 | 2000-F13-PID-PR-10011 | F13LU421 Tank Temp. | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check the Motor Lubrication unit is operating in auto and is healthy. Check the Main Motor DE and NDE vibration and temperature indicators. Check the Cooler Fan and Lube Unit Heater are operating in auto and are healthy. | B
PI13823 | 2000-ME001.3-D02-50004 | F13MB401A Motor DE Lube | Analogue Input | A_Hi | 15000 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
PI13825 | 2000-ME001.3-D02-50004 | F13MB401B Motor DE Lube | Analogue Input | A_Hi | 15000 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
VI13972 | 2000-ME001.3-D07-50002 | F13MB401 Feed Fl. Pin. R | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
VI13973 | 2000-ME001.3-D07-50002 | F13MB401 Feed Fxd Pin. L | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
VI13974 | 2000-ME001.3-D07-50002 | F13MB401 Feed Fxd Pin. R | Analogue Input | A_HH | 7.1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. Maintenance team to advise if a shutdown of F13-MB-401 is required | A
TDI13511 | 2000-F13-PID-PR-10010 | F13MS401 Pin. Gear R dT | Analogue Input | A_Hi | 8 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required. | A
TDI13515 | 2000-F13-PID-PR-10010 | F13MS401 Pin. Gear L dT | Analogue Input | A_Hi | 8 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required. | A
PI13824 | 2000-F13-PID-PR-10011 | F13MB401A Motor NDE Lube | Analogue Input | A_Hi | 15000 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
PI13826 | 2000-F13-PID-PR-10011 | F13MB401B Motor NDE Lube | Analogue Input | A_Hi | 15000 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
TI13511 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank R 1 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | A
TI13512 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank R 2 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | A
TI13513 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank R 3 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | A
TI13514 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank R 4 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | A
PI13574 | 2000-ME001.3-D02-50004 | F13MS401B Motor DE Lube | Analogue Input | A_Hi | 15000 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
PI13575 | 2000-ME001.3-D02-50004 | F13MS401B Motor NDE Lube | Analogue Input | A_Hi | 15000 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
LI13620 | 2000-ME001.2-D07-50002 | F13LU413 Lube Cond. Comp | Analogue Input | A_LL | 25 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures or internal restrictions. Repair if required and refill reservoir with oil. | A
TI13003A | 2000-F13-PID-PR-10001 | F13FA411 U RTD | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check motor cooling systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Feeders, else monitor temperature trends and upgrade urgency as required | A
TI13003B | 2000-F13-PID-PR-10001 | F13FA411 V RTD | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check motor cooling systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Feeders, else monitor temperature trends and upgrade urgency as required | A
TI13003C | 2000-F13-PID-PR-10001 | F13FA411 W RTD | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check motor cooling systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Feeders, else monitor temperature trends and upgrade urgency as required | A
PI13572 | 2000-ME001.3-D02-50004 | F13MS401A Motor DE Lube | Analogue Input | A_Hi | 15000 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
VI13316 | 2000-F13-PID-PR-10006 | F13CC402 Adj. Ring 1 | Analogue Input | A_Hi | 6 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
VI13317 | 2000-F13-PID-PR-10006 | F13CC402 Adj. Ring 2 | Analogue Input | A_Hi | 6 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
VI13318 | 2000-F13-PID-PR-10006 | F13CC402 Adj. Ring 3 | Analogue Input | A_Hi | 6 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
VI13319 | 2000-F13-PID-PR-10006 | F13CC402 Adj. Ring 4 | Analogue Input | A_Hi | 6 | mm/s | 10 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
LI13620 | 2000-ME001.2-D07-50002 | F13LU413 Lube Cond. Comp | Analogue Input | A_Lo | 76 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures or internal restrictions. Repair if required and refill reservoir with oil. | A
PI13573 | 2000-ME001.3-D02-50004 | F13MS401A Motor NDE Lube | Analogue Input | A_Hi | 15000 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
LI13872 | 2000-F13-PID-PR-10011 | F13LU423 Lube Cond. Comp | Analogue Input | A_LL | 25 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures or internal restrictions. Repair if required and refill reservoir with oil. | N
LI13872 | 2000-F13-PID-PR-10011 | F13LU423 Lube Cond. Comp | Analogue Input | A_Lo | 75 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures or internal restrictions. Repair if required and refill reservoir with oil. | B
LI13874 | 2000-F13-PID-PR-10011 | F13LU423 Lube Set. Comp. | Analogue Input | A_LL | 10 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures or internal restrictions. Repair if required and refill reservoir with oil. | B
LI13874 | 2000-F13-PID-PR-10011 | F13LU423 Lube Set. Comp. | Analogue Input | A_Lo | 38 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures or internal restrictions. Repair if required and refill reservoir with oil. | B
TI13960B | 2000-F13-PID-PR-10011 | F13MB401 Dsch Trn L Ctr | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13960C | 2000-F13-PID-PR-10011 | F13MB401 Dsch Trn L IB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13960A | 2000-F13-PID-PR-10011 | F13MB401 Dsch Trn L OB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13958B | 2000-ME001.3-D07-50002 | F13MB401 Dsch Trn R Ctr | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13958C | 2000-ME001.3-D07-50002 | F13MB401 Dsch Trn R IB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13958A | 2000-ME001.3-D07-50002 | F13MB401 Dsch Trn R OB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TDI13960 | 2000-F13-PID-PR-10011 | F13MB401 Dsch TrnBrgL dT | Analogue Input | A_Hi | 5 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TDI13958 | 2000-F13-PID-PR-10011 | F13MB401 Dsch TrnBrgR dT | Analogue Input | A_Hi | 5 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TDI13966 | 2000-F13-PID-PR-10011 | F13MB401 Fd TrnBrgL dT | Analogue Input | A_Hi | 5 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TDI13964 | 2000-F13-PID-PR-10011 | F13MB401 Fd TrnBrgR dT | Analogue Input | A_Hi | 5 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13966B | 2000-ME001.3-D07-50002 | F13MB401 Feed Trn L Ctr | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13966C | 2000-ME001.3-D07-50002 | F13MB401 Feed Trn L IB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13712A | 2000-ME001.2-D07-50002 | F13MS401 Feed Trn R OB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13966A | 2000-ME001.3-D07-50002 | F13MB401 Feed Trn L OB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13964A | 2000-ME001.3-D07-50002 | F13MB401 Feed Trn R OB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13964B | 2000-ME001.3-D07-50002 | F13MB401 Feed Trn R Ctr | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13964C | 2000-ME001.3-D07-50002 | F13MB401 Feed Trn R IB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13712B | 2000-ME001.2-D07-50002 | F13MS401 Feed Trn R Ctr | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13712C | 2000-ME001.2-D07-50002 | F13MS401 Feed Trn R IB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13714A | 2000-ME001.2-D07-50002 | F13MS401 Feed Trn L OB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13714B | 2000-ME001.2-D07-50002 | F13MS401 Feed Trn L Ctr | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13714C | 2000-ME001.2-D07-50002 | F13MS401 Feed Trn L IB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13716A | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn R OB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13716B | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn R Ctr | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13515 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank L 1 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | A
TI13516 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank L 2 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | A
TI13519 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank L 3 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | A
TI13520 | 2000-ME001.2-D07-50002 | F13MS401 Pin. Flank L 4 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | A
TI13704 | 2000-ME001.2-D07-50002 | F13MS401 Dsch Fxd Pin. R | Analogue Input | A_Hi | 70 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13705 | 2000-ME001.2-D07-50002 | F13MS401 Dsch Fxd Pin. L | Analogue Input | A_Hi | 70 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13706 | 2000-ME001.2-D07-50002 | F13MS401 Feed Fl. Pin. R | Analogue Input | A_Hi | 70 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13707 | 2000-ME001.2-D07-50002 | F13MS401 Feed Fl. Pin. L | Analogue Input | A_Hi | 70 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13004A | 2000-F13-PID-PR-10001 | F13FA412 U RTD | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check motor cooling systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Feeders, else monitor temperature trends and upgrade urgency as required | A
TI13004B | 2000-F13-PID-PR-10001 | F13FA412 V RTD | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check motor cooling systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Feeders, else monitor temperature trends and upgrade urgency as required | A
TI13004C | 2000-F13-PID-PR-10001 | F13FA412 W RTD | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check motor cooling systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Feeders, else monitor temperature trends and upgrade urgency as required | A
TI13255A | 2000-F13-PID-PR-10006 | F13CC401 U RTD 1 | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check motor cooling systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
TI13255B | 2000-F13-PID-PR-10006 | F13CC401 V RTD 1 | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check motor cooling systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
TI13255C | 2000-F13-PID-PR-10006 | F13CC401 W RTD 1 | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check motor cooling systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
TDI13763 | 2000-F13-PID-PR-10011 | F13MB401A Pin. Gear R dT | Analogue Input | A_Hi | 8 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required. | A
TI13255E | 2000-F13-PID-PR-10006 | F13CC401 DE RTD | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
TI13315A | 2000-F13-PID-PR-10006 | F13CC402 U RTD 1 | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check motor cooling systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
TI13315B | 2000-F13-PID-PR-10006 | F13CC402 V RTD 1 | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check motor cooling systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
TI13315C | 2000-F13-PID-PR-10006 | F13CC402 W RTD 1 | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check motor cooling systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
PDI13237 | 2000-F13-PID-PR-10006 | F13LU403 Lube Filter dP | Analogue Input | A_Hi | 241 | kPa | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Filter blocked. Swap to standby filter and swap out blocked filter when practical. | A
TI13315E | 2000-F13-PID-PR-10006 | F13CC402 DE RTD | Analogue Input | A_Hi | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Advise Maintenance team to monitor and investigate when practical. Swap to standby Crusher if available, else monitor temperature trends and upgrade urgency as required | A
TI13716C | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn R IB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13717A | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn L OB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13717B | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn L Ctr | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13717C | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn L IB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
PDI13296 | 2000-F13-PID-PR-10006 | F13LU404 Lube Filter dP | Analogue Input | A_Hi | 241 | kPa | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Filter blocked. Swap to standby filter and swap out blocked filter when practical. | A
PDI13628 | 2000-ME001.2-D07-50002 | F13LU413 LP Lube Fltr dP | Analogue Input | A_HH | 345 | kPa | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Filter blocked. Swap to standby filter immediately and swap out blocked filter when practical. | A
PDI13628 | 2000-ME001.2-D07-50002 | F13LU413 LP Lube Fltr dP | Analogue Input | A_Hi | 207 | kPa | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Filter blocked. Swap to standby filter and swap out blocked filter when practical. | A
PDI13879 | 2000-F13-PID-PR-10011 | F13LU423 LP Lube Fltr dP | Analogue Input | A_HH | 345 | kPa | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Filter blocked. Swap to standby filter immediately and swap out blocked filter when practical. | B
PDI13879 | 2000-F13-PID-PR-10011 | F13LU423 LP Lube Fltr dP | Analogue Input | A_Hi | 207 | kPa | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Filter blocked. Swap to standby filter and swap out blocked filter when practical. | B
TI13962A | 2000-F13-PID-PR-10011 | F13MB401 Dsch Thst R OB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13962B | 2000-F13-PID-PR-10011 | F13MB401 Dsch Thst R IB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13967A | 2000-F13-PID-PR-10011 | F13MB401 Dsch Thst L OB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13967B | 2000-F13-PID-PR-10011 | F13MB401 Dsch Thst L IB | Analogue Input | A_HH | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate immediately if unresolved. | A
TI13763 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank R 1 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | B
TI13764 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank R 2 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | B
TI13765 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank R 3 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | B
TI13766 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank R 4 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | B
TI13783 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank L 1 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | A
TI13784 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank L 2 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | A
TI13785 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank L 3 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | A
TI13786 | 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank L 4 | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required | A
TI13954 | 2000-F13-PID-PR-10011 | F13MB401 Feed Fl. Pin. L | Analogue Input | A_Hi | 70 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13955 | 2000-F13-PID-PR-10011 | F13MB401 Feed Fl. Pin. R | Analogue Input | A_Hi | 70 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13956 | 2000-F13-PID-PR-10011 | F13MB401 Dsch Fxd Pin. L | Analogue Input | A_Hi | 70 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13957 | 2000-F13-PID-PR-10011 | F13MB401 Dsch Fxd Pin. R | Analogue Input | A_Hi | 70 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TDI13786 | 2000-F13-PID-PR-10011 | F13MB401B Pin. Gear L dT | Analogue Input | A_Hi | 8 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Advise Maintenance team to investigate when practical for proper gear alignment, tooth damage etc. Monitor temperature trends and upgrade urgency as required. | A
PI13592 | 2000-ME001.2-D07-50002 | F13LU424 MS Rng Spry Air | Analogue Input | A_Hi | 415 | kPa | 5 | SV13591 Deenergised (see OnOff Valves tab) | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Nozzles may not have been properly purged last spray cycle. Check pressure regulator is properly set and actuating as intended. Check supply air pressure is okay. Attempt a manual spray cycle or air purge. Else, escalate to Maintenance team to remove and check for restrictions. | A
PI13592 | 2000-ME001.2-D07-50002 | F13LU424 MS Rng Spry Air | Analogue Input | A_Lo | 310 | kPa | 5 | SV13591 Deenergised (see OnOff Valves tab) | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check pressure regulator is properly set and actuating as intended. Check supply air pressure is okay. Check for any ruptures or air leakage. | A
PI13595 | 2000-ME001.2-D07-50002 | F13LU424 MS Rng Spry Oil | Analogue Input | A_Hi | 11032 | kPa | 5 | SV13588 Deenergised (see OnOff Valves tab) | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Nozzles may not have been properly purged last spray cycle. Check pressure regulators are properly set and actuating as intended. Check supply air pressure is okay. Attempt a manual spray cycle or air purge. Else, escalate to Maintenance team to remove and check for restrictions. | A
PI13595 | 2000-ME001.2-D07-50002 | F13LU424 MS Rng Spry Oil | Analogue Input | A_Lo | 8273 | kPa | 5 | SV13588 Deenergised (see OnOff Valves tab) | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check pressure regulators are properly set and actuating as intended. Check pump supply air pressure is okay and the pump is healthy. Attempt a manual spray cycle or air purge. | A
PI13644 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 1 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately. | A
VI13517 | 2000-ME001.2-D07-50002 | F13MS401A Motor NDE Brg | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Monitor vibration trends and upgrade urgency as required | A
VI13518 | 2000-ME001.2-D07-50002 | F13MS401A Motor DE Brg | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate when practical for wear, misalingment/inbalance and/or debris etc. Monitor vibration trends and upgrade urgency as required. | A
TI13570 | 2000-ME001.3-D02-50004 | F13LU411 Tank Temp. | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check the Motor Lubrication unit is operating in auto and is healthy. Check the Main Motor DE and NDE vibration and temperature indicators. Check the Cooler Fan and Lube Unit Heater are operating in auto and are healthy. | A
TI13003D | 2000-F13-PID-PR-10001 | F13FA411 DE Brg RTD | Analogue Input | A_Hi | 110 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check lubrication systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Feeders, else monitor temperature trends and upgrade urgency as required | A
TI13004D | 2000-F13-PID-PR-10001 | F13FA412 DE Brg RTD | Analogue Input | A_Hi | 110 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check lubrication systems are healthy. Advise Maintenance team to monitor and investigate when practical. Swap to standby Feeders, else monitor temperature trends and upgrade urgency as required | A
VI13708 | 2000-ME001.2-D07-50002 | F13MS401 Feed Fxd Pin. R | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate when practical for wear, misalingment/inbalance and/or debris etc. Monitor vibration trends and upgrade urgency as required. | A
VI13709 | 2000-ME001.2-D07-50002 | F13MS401 Feed Fxd Pin. L | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate when practical for wear, misalingment/inbalance and/or debris etc. Monitor vibration trends and upgrade urgency as required. | A
VI13710 | 2000-ME001.2-D07-50002 | F13MS401 Feed Fl. Pin. R | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate when practical for wear, misalingment/inbalance and/or debris etc. Monitor vibration trends and upgrade urgency as required. | A
VI13711 | 2000-ME001.2-D07-50002 | F13MS401 Feed Fl. Pin. L | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate when practical for wear, misalingment/inbalance and/or debris etc. Monitor vibration trends and upgrade urgency as required. | A
PI13644 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 1 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Feed Trunnion bearing temperature readings and upgrade urgency as required. | A
VI13971 | 2000-ME001.3-D07-50002 | F13MB401 Feed Fl. Pin. L | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate when practical for wear, misalingment/inbalance and/or debris etc. Monitor vibration trends and upgrade urgency as required. | A
VI13972 | 2000-ME001.3-D07-50002 | F13MB401 Feed Fl. Pin. R | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate when practical for wear, misalingment/inbalance and/or debris etc. Monitor vibration trends and upgrade urgency as required. | A
VI13973 | 2000-ME001.3-D07-50002 | F13MB401 Feed Fxd Pin. L | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate when practical for wear, misalingment/inbalance and/or debris etc. Monitor vibration trends and upgrade urgency as required. | A
VI13974 | 2000-ME001.3-D07-50002 | F13MB401 Feed Fxd Pin. R | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to investigate when practical for wear, misalingment/inbalance and/or debris etc. Monitor vibration trends and upgrade urgency as required. | A
VI13539 | 2000-ME001.2-D07-50002 | F13MS401B Motor NDE Brg | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Monitor vibration trends and upgrade urgency as required | A
VI13540 | 2000-ME001.2-D07-50002 | F13MS401B Motor DE Brg | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Advise Maintenance team to monitor and investigate when practical. Monitor vibration trends and upgrade urgency as required | A
VI13767 | 2000-F13-PID-PR-10011 | F13MB401A Motor NDE Brg | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
VI13789 | 2000-F13-PID-PR-10011 | F13MB401B Motor NDE Brg | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
PI13644 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 1 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13644 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 1 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
VI13770 | 2000-F13-PID-PR-10011 | F13MB401A Motor DE Brg | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
VI13792 | 2000-F13-PID-PR-10011 | F13MB401B Motor DE Brg | Analogue Input | A_Hi | 4.5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13821 | 2000-F13-PID-PR-10011 | F13LU421 Tank Temp. | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check the Motor Lubrication unit is operating in auto and is healthy. Check the Main Motor DE and NDE vibration and temperature indicators. Check the Cooler Fan and Lube Unit Heater are operating in auto and are healthy. | B
FI13827 | 2000-F13-PID-PR-10011 | F13MB401A Motor DE Lube | Analogue Input | A_LL | 0.6 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | B
FI13829 | 2000-F13-PID-PR-10011 | F13MB401B Motor DE Lube | Analogue Input | A_LL | 0.6 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | B
PI13823 | 2000-ME001.3-D02-50004 | F13MB401A Motor DE Lube | Analogue Input | A_LL | 6200 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | A
PI13825 | 2000-F13-PID-PR-10011 | F13MB401B Motor DE Lube | Analogue Input | A_LL | 6200 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | A
LI13822 | 2000-F13-PID-PR-10011 | F13LU421 Tank Level | Analogue Input | A_LL | 25 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures. Check the lines and bearing supply points immediately. | B
FI13578 | 2000-ME001.3-D02-50004 | F13MS401B Motor DE Lube | Analogue Input | A_LL | 0.6 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | A
PI13574 | 2000-ME001.3-D02-50004 | F13MS401B Motor DE Lube | Analogue Input | A_LL | 6200 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | A
PI13645 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 2 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately. | A
PI13645 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 2 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Feed Trunnion bearing temperature readings and upgrade urgency as required. | A
PI13645 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 2 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13645 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 2 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13646 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 3 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately. | A
PI13646 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 3 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Feed Trunnion bearing temperature readings and upgrade urgency as required. | A
FI13576 | 2000-ME001.3-D02-50004 | F13MS401A Motor DE Lube | Analogue Input | A_LL | 0.6 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | A
PI13572 | 2000-ME001.3-D02-50004 | F13MS401A Motor DE Lube | Analogue Input | A_LL | 6200 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | A
PI13646 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 3 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13646 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 3 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
TI13437 | 2000-F13-PID-PR-10009 | F13HE420 Chill Water In | Analogue Input | A_Hi | 25 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Chillers are in auto and healthy. Bring additional Chillers online as required. Check Cooling Water end users are healthy. | B
TI13437 | 2000-F13-PID-PR-10009 | F13HE420 Chill Water In | Analogue Input | A_Lo | 5 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Chillers are in auto and healthy. Take Chillers offline as required. Check Cooling Water end users are healthy. | B
LI13571 | 2000-ME001.3-D02-50004 | F13LU411 Tank Level | Analogue Input | A_LL | 25 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures. Check the lines and bearing supply points immediately. | A
FI13577 | 2000-ME001.3-D02-50004 | F13MS401A Motor NDE Lube | Analogue Input | A_LL | 0.6 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | A
FI13579 | 2000-ME001.3-D02-50004 | F13MS401B Motor NDE Lube | Analogue Input | A_LL | 0.6 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | A
PI13573 | 2000-ME001.3-D02-50004 | F13MS401A Motor NDE Lube | Analogue Input | A_LL | 6200 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | A
FI13828 | 2000-F13-PID-PR-10011 | F13MB401A Motor NDE Lube | Analogue Input | A_LL | 0.6 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | B
FI13830 | 2000-F13-PID-PR-10011 | F13MB401B Motor NDE Lube | Analogue Input | A_LL | 0.6 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | B
PI13575 | 2000-ME001.3-D02-50004 | F13MS401B Motor NDE Lube | Analogue Input | A_LL | 6200 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | A
PI13824 | 2000-ME001.3-D02-50004 | F13MB401A Motor NDE Lube | Analogue Input | A_LL | 6200 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | A
TI13117 | 2000-F13-PID-PR-10009 | F13CU407 Cool Wtr Rturn | Analogue Input | A_Hi | 43 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Cyclone Feed Pump operating conditions and Cooling Water system is healthy. Increase Cooling Water flowrate to F13-CU-409 as required. Advise Maintenance to inspect VSD and cooling unit if unusual. | B
PI13647 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 4 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately. | A
PI13647 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 4 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Feed Trunnion bearing temperature readings and upgrade urgency as required. | A
PI13826 | 2000-ME001.3-D02-50004 | F13MB401B Motor NDE Lube | Analogue Input | A_LL | 6200 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate immediately. | A
FI13827 | 2000-F13-PID-PR-10011 | F13MB401A Motor DE Lube | Analogue Input | A_Lo | 0.9 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | B
FI13829 | 2000-F13-PID-PR-10011 | F13MB401B Motor DE Lube | Analogue Input | A_Lo | 0.9 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | B
PI13823 | 2000-ME001.3-D02-50004 | F13MB401A Motor DE Lube | Analogue Input | A_Lo | 8500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
PI13825 | 2000-F13-PID-PR-10011 | F13MB401B Motor DE Lube | Analogue Input | A_Lo | 8500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
PI13647 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 4 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13647 | 2000-ME001.2-D07-50002 | F13LU413 Feed Trn Brg 4 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13648 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 1 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately. | A
PI13648 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 1 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Discharge Trunnion bearing temperature readings and upgrade urgency as required. | A
PI13648 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 1 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13648 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 1 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13649 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 2 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately. | A
PI13649 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 2 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Discharge Trunnion bearing temperature readings and upgrade urgency as required. | A
PI13649 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 2 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13649 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 2 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13650 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 3 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately. | A
PI13650 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 3 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Discharge Trunnion bearing temperature readings and upgrade urgency as required. | A
PI13650 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 3 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
TI13713A | 2000-ME001.2-D07-50002 | F13MS401 Dsch Thst R OB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13713B | 2000-ME001.2-D07-50002 | F13MS401 Dsch Thst R IB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13715A | 2000-ME001.2-D07-50002 | F13MS401 Dsch Thst L OB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
TI13715B | 2000-ME001.2-D07-50002 | F13MS401 Dsch Thst L IB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | A
PI13650 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 3 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13651 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 4 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately. | A
TI13962A | 2000-F13-PID-PR-10011 | F13MB401 Dsch Thst R OB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13962B | 2000-F13-PID-PR-10011 | F13MB401 Dsch Thst R IB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13967A | 2000-F13-PID-PR-10011 | F13MB401 Dsch Thst L OB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
TI13967B | 2000-F13-PID-PR-10011 | F13MB401 Dsch Thst L IB | Analogue Input | A_Hi | 55 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check for over or under lubrication and that the lubrication unit and delivery system is healthy. Check Mill speed/weight and power draw trends are healthy and within acceptable ranges. Advise Maintenance team to monitor and investigate when practical. Monitor temperature trends and upgrade urgency as required | B
PI13651 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 4 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Discharge Trunnion bearing temperature readings and upgrade urgency as required. | A
PI13651 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 4 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13651 | 2000-ME001.2-D07-50002 | F13LU413 Dsch Trn Brg 4 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-429, F13-PO-430 AND F13-PO-431 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-429 OR 430 OR 431) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13842 | 2000-F13-PID-PR-10013 | F13LU424 MB Rng Spry Air | Analogue Input | A_Hi | 415 | kPa | 5 | SV13841 Deenergised (see OnOff Valves tab) | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Nozzles may not have been properly purged last spray cycle. Check pressure regulator is properly set and actuating as intended. Check supply air pressure is okay. Attempt a manual spray cycle or air purge. Else, escalate to Maintenance team to remove and check for restrictions. | B
PI13842 | 2000-F13-PID-PR-10013 | F13LU424 MB Rng Spry Air | Analogue Input | A_Lo | 310 | kPa | 5 | SV13841 Deenergised (see OnOff Valves tab) | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check pressure regulator is properly set and actuating as intended. Check supply air pressure is okay. Check for any ruptures or air leakage. | B
PI13845 | 2000-F13-PID-PR-10013 | F13LU424 MB Rng Spry Oil | Analogue Input | A_Hi | 11032 | kPa | 5 | SV13838 Deenergised (see OnOff Valves tab) | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Nozzles may not have been properly purged last spray cycle. Check pressure regulators are properly set and actuating as intended. Check supply air pressure is okay. Attempt a manual spray cycle or air purge. Else, escalate to Maintenance team to remove and check for restrictions. | B
PI13845 | 2000-F13-PID-PR-10013 | F13LU424 MB Rng Spry Oil | Analogue Input | A_Lo | 8273 | kPa | 5 | SV13838 Deenergised (see OnOff Valves tab) | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check pressure regulators are properly set and actuating as intended. Check pump supply air pressure is okay and the pump is healthy. Attempt a manual spray cycle or air purge. | B
PI13895 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 1 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately if alarm persists | B
PI13895 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 1 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Feed Trunnion bearing temperature readings and upgrade urgency as required. | B
PI13895 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 1 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
TI13117 | 2000-F13-PID-PR-10009 | F13CU407 Cool Wtr Rturn | Analogue Input | A_Lo | 5 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Chillers are in auto and operating as expected. Take Chillers offline if other systems are also experiencing low return temperatures. | B
PI13895 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 1 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13896 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 2 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately if alarm persists | B
PI13896 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 2 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Feed Trunnion bearing temperature readings and upgrade urgency as required. | B
PI13896 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 2 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13896 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 2 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13897 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 3 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately if alarm persists | B
PI13897 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 3 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Feed Trunnion bearing temperature readings and upgrade urgency as required. | B
PI13897 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 3 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13897 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 3 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13898 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 4 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately if alarm persists | B
PI13898 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 4 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Feed Trunnion bearing temperature readings and upgrade urgency as required. | B
PI13898 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 4 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13898 | 2000-F13-PID-PR-10013 | F13LU423 Feed Trn Brg 4 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13899 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 1 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately if alarm persists | B
TI13118 | 2000-F13-PID-PR-10009 | F13CU408 Cool Wtr Rturn | Analogue Input | A_Hi | 43 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Ball Mill operating conditions and Cooling Water system is healthy. Increase Cooling Water flowrate to F13-CU-408 as required. Advise Maintenance to inspect VSD and cooling unit if unusual. | B
TI13118 | 2000-F13-PID-PR-10009 | F13CU408 Cool Wtr Rturn | Analogue Input | A_Lo | 5 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Chillers are in auto and operating as expected. Take Chillers offline if other systems are also experiencing low return temperatures. | B
PI13899 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 1 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Discharge Trunnion bearing temperature readings and upgrade urgency as required. | B
PI13899 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 1 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13899 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 1 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13900 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 2 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately if alarm persists | B
PI13900 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 2 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Discharge Trunnion bearing temperature readings and upgrade urgency as required. | B
PI13900 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 2 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13900 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 2 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13901 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 3 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately if alarm persists | B
PI13901 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 3 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Discharge Trunnion bearing temperature readings and upgrade urgency as required. | B
PI13901 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 3 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13901 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 3 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13902 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 4 | Analogue Input | A_HH | 9000 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Potential line blockage. Attempt lube system restart, else advise Maintenance team to investigate immediately if alarm persists | B
PI13902 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 4 | Analogue Input | A_Hi | 8900 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential line blockage. Check flow diver flowrate and pressure readings from alternate lubrication supply points. Advise Maintenance team to investigate as soon as practical. Monitor Discharge Trunnion bearing temperature readings and upgrade urgency as required. | B
PI13902 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 4 | Analogue Input | A_LL | 3300 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points immediately. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
PI13902 | 2000-F13-PID-PR-10013 | F13LU423 Dsch Trn Brg 4 | Analogue Input | A_Lo | 3400 | kPa | 10 | Mask A_LL and A_Lo if: 1. F13-PO-529, F13-PO-530 AND F13-PO-531 Not Running 2. Mask for 5 seconds (TBC) on Pump (F13-PO-529 OR 530 OR 531) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Potential blockage or rupture. Advise Field Operator and Maintenance team to check the lines and bearing supply points as soon as practical. Check the lubrication unit and delivery system is healthy. Check the flow divider and alternate supply lines were registering a flow / pressure reading. | 2 | 2026-05-20 | https://nrwholdings.sharepoint.com/sites/Primero-23517KCGM/Lists/Software%20Change%20Request/DispForm.aspx?ID=512&pa=1&e=oO1ZNA
TI13119 | 2000-F13-PID-PR-10009 | F13CU409 Cool Wtr Rturn | Analogue Input | A_Hi | 37 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check SAG Mill operating conditions and Cooling Water system is healthy. Increase Cooling Water flowrate to F13-CU-407 as required. Advise Maintenance to inspect VSD and cooling unit if unusual. | B
LI13822 | 2000-F13-PID-PR-10011 | F13LU421 Tank Level | Analogue Input | A_Lo | 35 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures. Check the lines and bearing supply points immediately. | B
FI13578 | 2000-ME001.3-D02-50004 | F13MS401B Motor DE Lube | Analogue Input | A_Lo | 0.9 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
PI13574 | 2000-ME001.3-D02-50004 | F13MS401B Motor DE Lube | Analogue Input | A_Lo | 8500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
TDI13247 | 2000-F13-PID-PR-10006 | F13LU403 Lube Oil dT 1 | Analogue Input | A_HH | 17 | °C | 600 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check the lubrication system, air cooler fans are healthy and operating in auto. Check the Recycle Crusher temperature and vibration indicators are healthy. Else, swap to standby Crusher if available and advise Maintenance to investigate immediately. | A
TDI13247 | 2000-F13-PID-PR-10006 | F13LU403 Lube Oil dT 1 | Analogue Input | A_Hi | 17 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check the lubrication system, air cooler fans are healthy and operating in auto. Check the Recycle Crusher temperature and vibration indicators are healthy. Else, swap to standby Crusher if available and advise Maintenance to investigate when practical | A
TDI13307 | 2000-F13-PID-PR-10006 | F13LU404 Lube Oil dT 1 | Analogue Input | A_HH | 17 | °C | 600 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check the lubrication system, air cooler fans are healthy and operating in auto. Check the Recycle Crusher temperature and vibration indicators are healthy. Else, swap to standby Crusher if available and advise Maintenance to investigate immediately. | A
TDI13307 | 2000-F13-PID-PR-10006 | F13LU404 Lube Oil dT 1 | Analogue Input | A_Hi | 17 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check the lubrication system, air cooler fans are healthy and operating in auto. Check the Recycle Crusher temperature and vibration indicators are healthy. Else, swap to standby Crusher if available and advise Maintenance to investigate when practical | A
TI13242 | 2000-F13-PID-PR-10006 | F13LU403 Lube Oil Tank | Analogue Input | A_HH | 42 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to check the lubrication unit, the air coolers and lubrication heaters are operating in auto and as intended, and the Crusher temperature and vibration indicators are reading healthy. Attempt restart. If issues persist, request Maintenance to investigate immediately. | A
TI13242 | 2000-F13-PID-PR-10006 | F13LU403 Lube Oil Tank | Analogue Input | A_LL | 15 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to check the lubrication unit and lubrication heaters are operating in auto and as intended. | A
TI13243 | 2000-F13-PID-PR-10006 | F13LU403 Lube Oil Return | Analogue Input | A_HH | 60 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to check the lubrication unit, the air coolers and lubrication heaters are operating in auto and as intended, and the Crusher temperature and vibration indicators are reading healthy. Attempt restart. If issues persist, request Maintenance to investigate immediately. | A
TI13243 | 2000-F13-PID-PR-10006 | F13LU403 Lube Oil Return | Analogue Input | A_Hi | 55 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to check the lubrication unit, the air coolers and lubrication heaters are operating in auto and as intended, and the Crusher temperature and vibration indicators are reading healthy. Monitor and if issues persist, request Maintenance to investigate when practical. | A
TI13247 | 2000-F13-PID-PR-10006 | F13LU403 Lube Oil Supply | Analogue Input | A_Lo | 20 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to check the lubrication unit and lubrication heaters are operating in auto and as intended. | A
TI13302 | 2000-F13-PID-PR-10006 | F13LU404 Lube Oil Tank | Analogue Input | A_HH | 42 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to check the lubrication unit, the air coolers and lubrication heaters are operating in auto and as intended, and the Crusher temperature and vibration indicators are reading healthy. Attempt restart. If issues persist, request Maintenance to investigate immediately. | A
FI13576 | 2000-ME001.3-D02-50004 | F13MS401A Motor DE Lube | Analogue Input | A_Lo | 0.9 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
PI13572 | 2000-ME001.3-D02-50004 | F13MS401A Motor DE Lube | Analogue Input | A_Lo | 8500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
FI13828 | 2000-F13-PID-PR-10011 | F13MB401A Motor NDE Lube | Analogue Input | A_Lo | 0.9 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | B
FI13830 | 2000-F13-PID-PR-10011 | F13MB401B Motor NDE Lube | Analogue Input | A_Lo | 0.9 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | B
FI13579 | 2000-ME001.3-D02-50004 | F13MS401B Motor NDE Lube | Analogue Input | A_Lo | 0.9 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
LI13571 | 2000-ME001.3-D02-50004 | F13LU411 Tank Level | Analogue Input | A_Lo | 35 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures. Check the lines and bearing supply points immediately. | A
PI13575 | 2000-ME001.3-D02-50004 | F13MS401B Motor NDE Lube | Analogue Input | A_Lo | 8500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
TI13302 | 2000-F13-PID-PR-10006 | F13LU404 Lube Oil Tank | Analogue Input | A_LL | 15 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to check the lubrication unit and lubrication heaters are operating in auto and as intended. | A
TI13303 | 2000-F13-PID-PR-10006 | F13LU404 Lube Oil Return | Analogue Input | A_HH | 60 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to check the lubrication unit, the air coolers and lubrication heaters are operating in auto and as intended, and the Crusher temperature and vibration indicators are reading healthy. Attempt restart. If issues persist, request Maintenance to investigate immediately. | A
TI13303 | 2000-F13-PID-PR-10006 | F13LU404 Lube Oil Return | Analogue Input | A_Hi | 55 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to check the lubrication unit, the air coolers and lubrication heaters are operating in auto and as intended, and the Crusher temperature and vibration indicators are reading healthy. Monitor and if issues persist, request Maintenance to investigate when practical. | A
TI13307 | 2000-F13-PID-PR-10006 | F13LU404 Lube Oil Supply | Analogue Input | A_Lo | 20 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to check the lubrication unit and lubrication heaters are operating in auto and as intended. | A
PI13824 | 2000-ME001.3-D02-50004 | F13MB401A Motor NDE Lube | Analogue Input | A_Lo | 8500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
PI13826 | 2000-F13-PID-PR-10011 | F13MB401B Motor NDE Lube | Analogue Input | A_Lo | 8500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-521 AND F13-PO-522 Not Running Mask alarms for 10 seconds on Pump (F13-PO-521 OR 522) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
TI13615 | 2000-ME001.2-D07-50002 | F13LU413 Lube Set. Comp. | Analogue Input | A_HH | 47 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate trip. Check the Motor Lubrication unit is operating in auto and is healthy. Check the SAG Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. | A
TI13615 | 2000-ME001.2-D07-50002 | F13LU413 Lube Set. Comp. | Analogue Input | A_Hi | 45 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate. Check the Motor Lubrication unit is operating in auto and is healthy. Check the SAG Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. | A
TI13615 | 2000-ME001.2-D07-50002 | F13LU413 Lube Set. Comp. | Analogue Input | A_LL | 26.6 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate trip. Check the Motor Lubrication unit is operating in auto and is healthy. Check the SAG Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. Check the Lubrication Heaters are in auto and healthy. | A
TI13615 | 2000-ME001.2-D07-50002 | F13LU413 Lube Set. Comp. | Analogue Input | A_Lo | 32 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate. Check the Motor Lubrication unit is operating in auto and is healthy. Check the SAG Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. Check the Lubrication Heaters are in auto and healthy. | A
TI13623 | 2000-ME001.2-D07-50002 | F13LU413 Lube Cond. Comp | Analogue Input | A_HH | 47 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate trip. Check the Motor Lubrication unit is operating in auto and is healthy. Check the SAG Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. | A
TI13623 | 2000-ME001.2-D07-50002 | F13LU413 Lube Cond. Comp | Analogue Input | A_Hi | 45 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate. Check the Motor Lubrication unit is operating in auto and is healthy. Check the SAG Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. | A
TI13623 | 2000-ME001.2-D07-50002 | F13LU413 Lube Cond. Comp | Analogue Input | A_LL | 26.6 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate trip. Check the Motor Lubrication unit is operating in auto and is healthy. Check the SAG Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. Check the Lubrication Heaters are in auto and healthy. | A
TI13623 | 2000-ME001.2-D07-50002 | F13LU413 Lube Cond. Comp | Analogue Input | A_Lo | 32 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate. Check the Motor Lubrication unit is operating in auto and is healthy. Check the SAG Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. Check the Lubrication Heaters are in auto and healthy. | A
FI13577 | 2000-ME001.3-D02-50004 | F13MS401A Motor NDE Lube | Analogue Input | A_Lo | 0.9 | L/min | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check respective line pressure. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
PI13573 | 2000-ME001.3-D02-50004 | F13MS401A Motor NDE Lube | Analogue Input | A_Lo | 8500 | kPa | 5 | Mask A_LL and A_Lo if: F13-PO-421 AND F13-PO-422 Not Running Mask alarms for 10 seconds on Pump (F13-PO-421 OR 422) start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. Advise Field Operator to investigate immediately; check upstream pressure filter is not blocked, flow valves are in correct positions, leakages, PRV is operating as intended and that the pump is healthy. If troubleshooting is unsuccessful, advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | A
TI13866 | 2000-F13-PID-PR-10011 | F13LU423 Lube Set. Comp. | Analogue Input | A_HH | 47 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate trip. Check the Motor Lubrication unit is operating in auto and is healthy. Check the Ball Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. | B
TI13866 | 2000-F13-PID-PR-10011 | F13LU423 Lube Set. Comp. | Analogue Input | A_Hi | 45 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate. Check the Motor Lubrication unit is operating in auto and is healthy. Check the Ball Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. | B
TI13866 | 2000-F13-PID-PR-10011 | F13LU423 Lube Set. Comp. | Analogue Input | A_LL | 26.6 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate trip. Check the Motor Lubrication unit is operating in auto and is healthy. Check the Ball Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. Check the Lubrication Heaters are in auto and healthy. | B
TI13866 | 2000-F13-PID-PR-10011 | F13LU423 Lube Set. Comp. | Analogue Input | A_Lo | 32 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate. Check the Motor Lubrication unit is operating in auto and is healthy. Check the Ball Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. Check the Lubrication Heaters are in auto and healthy. | B
TI13873 | 2000-F13-PID-PR-10011 | F13LU423 Lube Cond. Comp | Analogue Input | A_HH | 47 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate trip. Check the Motor Lubrication unit is operating in auto and is healthy. Check the Ball Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. | B
TI13873 | 2000-F13-PID-PR-10011 | F13LU423 Lube Cond. Comp | Analogue Input | A_Hi | 45 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate. Check the Motor Lubrication unit is operating in auto and is healthy. Check the Ball Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. | B
TI13873 | 2000-F13-PID-PR-10011 | F13LU423 Lube Cond. Comp | Analogue Input | A_LL | 26.6 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate trip. Check the Motor Lubrication unit is operating in auto and is healthy. Check the Ball Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. Check the Lubrication Heaters are in auto and healthy. | B
TI13873 | 2000-F13-PID-PR-10011 | F13LU423 Lube Cond. Comp | Analogue Input | A_Lo | 32 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate. Check the Motor Lubrication unit is operating in auto and is healthy. Check the Ball Mill bearings' vibration and temperature indicators are healthy. Check the Lube Oil Heat Exchanger cooling water supply is in auto and at temperature setpoint. Check the Lubrication Heaters are in auto and healthy. | B
TI13119 | 2000-F13-PID-PR-10009 | F13CU409 Cool Wtr Rturn | Analogue Input | A_Lo | 15 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Chillers are in auto and operating as expected. Take Chillers offline if other systems are also experiencing low return temperatures. | B
WI13195 | 2000-F13-PID-PR-10005 | F13CV405 RC Feed Wet | Analogue Input | A_Hi | 610 | t/h | 20 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Decrease throughput. Reaching design throughputs through Recycle Crusher circuit. | A
PDI13067 | 2000-F13-PID-PR-10001 | F13DC402 Pressure Delta | Analogue Input | A_HH | 1800 | Pa | 5 | Mask if F13-DC-402 Not Running Mask for 10 seconds (TBC) on F13-DC-402 start-up | Personnel1: First Aid Injury, Reversible health effects | Plant Tripped | Logging | Check dust collector systems immediately. Ensure compressed air at pressure setpoint. Ensure pulsing solenoid valves are actuating as intended. Attempt restart when possible. | A
PDI13067 | 2000-F13-PID-PR-10001 | F13DC402 Pressure Delta | Analogue Input | A_LL | 300 | Pa | 5 | Mask if F13-DC-402 Not Running Mask for 10 seconds (TBC) on F13-DC-402 start-up | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Advise Field Operator / Maintenance to investigate dust collector and instrumentation for faults. Check discharged air is clean and contains minimal dust. Potential filter cartridge damage. | A
TI13012 | 2000-F13-PID-PR-10001 | F13FA411 G/box Sump | Analogue Input | A_HH | 90 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Gearbox oil overheating. Advise Maintenance to investigate immediately. Swap to standby Feeders if available. | A
TI13013 | 2000-F13-PID-PR-10001 | F13FA411 G/box HS Brg | Analogue Input | A_Hi | 60 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Bearing overheating. Advise Maintenance to investigate immediately. Swap to standby Feeders if available. | A
TI13013 | 2000-F13-PID-PR-10001 | F13FA411 G/box HS Brg | Analogue Input | A_HH | 90 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Bearing overheating. Advise Maintenance to investigate immediately. Swap to standby Feeders if available. | A
TI13022 | 2000-F13-PID-PR-10001 | F13FA412 G/box Sump | Analogue Input | A_HH | 90 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Gearbox oil overheating. Advise Maintenance to investigate immediately. Swap to standby Feeders if available. | A
TI13023 | 2000-F13-PID-PR-10001 | F13FA412 G/box HS Brg | Analogue Input | A_Hi | 60 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Bearing overheating. Advise Maintenance to investigate immediately. Swap to standby Feeders if available. | A
TI13023 | 2000-F13-PID-PR-10001 | F13FA412 G/box HS Brg | Analogue Input | A_HH | 90 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Bearing overheating. Advise Maintenance to investigate immediately. Swap to standby Feeders if available. | A
TI13032 | 2000-F13-PID-PR-10001 | F13FA414 G/box Sump | Analogue Input | A_HH | 90 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Gearbox oil overheating. Advise Maintenance to investigate immediately. Swap to standby Feeders if available. | A
TI13033 | 2000-F13-PID-PR-10001 | F13FA414 G/box HS Brg | Analogue Input | A_Hi | 60 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Bearing overheating. Advise Maintenance to investigate immediately. Swap to standby Feeders if available. | A
TI13033 | 2000-F13-PID-PR-10001 | F13FA414 G/box HS Brg | Analogue Input | A_HH | 90 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Bearing overheating. Advise Maintenance to investigate immediately. Swap to standby Feeders if available. | A
TI13242 | 2000-F13-PID-PR-10006 | F13LU403 Lube Oil Tank | Analogue Input | A_Lo | 27 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to check the lubrication unit, the air coolers and lubrication heaters are operating in auto and as intended, and the Crusher temperature and vibration indicators are reading healthy. | A
TI13242 | 2000-F13-PID-PR-10006 | F13LU403 Lube Oil Tank | Analogue Input | A_Hi | 38 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to check the lubrication unit and lubrication heaters are operating in auto and as intended. | A
TI13302 | 2000-F13-PID-PR-10006 | F13LU404 Lube Oil Tank | Analogue Input | A_Lo | 27 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to check the lubrication unit, the air coolers and lubrication heaters are operating in auto and as intended, and the Crusher temperature and vibration indicators are reading healthy. | A
TI13302 | 2000-F13-PID-PR-10006 | F13LU404 Lube Oil Tank | Analogue Input | A_Hi | 38 | °C | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to check the lubrication unit and lubrication heaters are operating in auto and as intended. | A
TI13991A | 2000-F13-PID-PR-10001 | F13CV403 U RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. | A
TI13991A | 2000-F13-PID-PR-10001 | F13CV403 U RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. | A
TI13991B | 2000-F13-PID-PR-10001 | F13CV403 V RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. | A
TI13991B | 2000-F13-PID-PR-10001 | F13CV403 V RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. | A
TI13991C | 2000-F13-PID-PR-10001 | F13CV403 W RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. | A
TI13991C | 2000-F13-PID-PR-10001 | F13CV403 W RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check motor cooling systems are healthy. Advise Maintenance team to investigate immediately. | A
TI13991D | 2000-F13-PID-PR-10001 | F13CV403 DE Brg RTD | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. | A
TI13991D | 2000-F13-PID-PR-10001 | F13CV403 DE Brg RTD | Analogue Input | A_HH | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. | A
TI13991E | 2000-F13-PID-PR-10001 | F13CV403 NDE Brg RTD | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. | A
TI13991E | 2000-F13-PID-PR-10001 | F13CV403 NDE Brg RTD | Analogue Input | A_HH | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Maintenance team to investigate immediately for wear, misalingment/inbalance and/or debris etc. | A
YI13059A | 2000-F13-PID-PR-10001 | F13CV403 p80 | Analogue Input | A_Hi | 130 | mm | 30 | Mask if F13-CV-403 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | High PSD from COS. Check Gyratory crusher is operating as intended and CSS is at appropriate setpoint. Conduct calibration if required. | A
YI13059B | 2000-F13-PID-PR-10001 | F13CV403 Top Size | Analogue Input | A_Hi | 240 | mm | 30 | Mask if F13-CV-403 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | High top size from COS. Check Gyratory crusher is operating as intended and CSS is at appropriate setpoint. Conduct calibration if required. | A
FI13112 | 2000-F13-PID-PR-10002 | F14CY411 Feed | Analogue Input | A_Lo | 500 | m3/h | 10 | 1. Mask if XV13110 closed or F13-PP-401 stopped. 2. Mask for 5 seconds after XV13110 is opened. 3. Mask for 10 seconds on F13-PP-401 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Potential restriction in Gravity Cyclone line. Conduct flush of line. | A
FI13112 | 2000-F13-PID-PR-10002 | F14CY411 Feed | Analogue Input | A_Hi | A_Hi | m3/h | 10 | 1. Mask if XV13110 closed or F13-PP-401 stopped. 2. Mask for 5 seconds after XV13110 is opened. 3. Mask for 10 seconds on F13-PP-401 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | High flow through Gravity Cyclones. Check Cyclone Cluster controllers are in automatic or cascade mode and are operating as intended | 2
FI13113 | 2000-F13-PID-PR-10002 | F14CY412 Feed | Analogue Input | A_Lo | 500 | m3/h | 10 | 1. Mask if XV13111 closed or F13-PP-401 stopped. 2. Mask for 5 seconds after XV13111 is opened. 3. Mask for 10 seconds on F13-PP-401 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Potential restriction in Gravity Cyclone line. Conduct flush of line. | A
FI13113 | 2000-F13-PID-PR-10002 | F14CY412 Feed | Analogue Input | A_Hi | 1500 | m3/h | 10 | 1. Mask if XV13111 closed or F13-PP-401 stopped. 2. Mask for 5 seconds after XV13111 is opened. 3. Mask for 10 seconds on F13-PP-401 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | High flow through Gravity Cyclones. Check Cyclone Cluster controllers are in automatic or cascade mode and are operating as intended | 2
FI13363 | 2000-F13-PID-PR-10007 | F13SL401 PW Spray | Analogue Input | A_Lo | 25 | m3/h | 5 | Mask A_Lo if F13-SL-401 Not Running Mask A_Lo for 10 seconds on F13-SL-401 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low flow through Trash Screen sprays. Advise Field Operator to check valves are appropriately lined up and in correct position. Check Filter is not clogged. Adjust inline manual flow control valve to appropriate flowrate setting. | A
FI13363 | 2000-F13-PID-PR-10007 | F13SL401 PW Spray | Analogue Input | A_Hi | 75 | m3/h | 5 | Mask A_Lo if F13-SL-401 Not Running Mask A_Lo for 10 seconds on F13-SL-401 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | High flow through Trash Screen sprays. Advise Field Operator to adjust inline manual flow control valve to appropriate flowrate setting. Check filter is correctly installed. | A
FI13373 | 2000-F13-PID-PR-10007 | F13SL402 PW Spray | Analogue Input | A_Lo | 25 | m3/h | 5 | Mask A_Lo if F13-SL-402 Not Running Mask A_Lo for 10 seconds on F13-SL-402 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low flow through Trash Screen sprays. Advise Field Operator to check valves are appropriately lined up and in correct position. Check Filter is not clogged. Adjust inline manual flow control valve to appropriate flowrate setting. | A
FI13373 | 2000-F13-PID-PR-10007 | F13SL402 PW Spray | Analogue Input | A_Hi | 75 | m3/h | 5 | Mask A_Lo if F13-SL-402 Not Running Mask A_Lo for 10 seconds on F13-SL-402 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | High flow through Trash Screen sprays. Advise Field Operator to adjust inline manual flow control valve to appropriate flowrate setting. Check filter is correctly installed. | A
FI13403 | 2000-F13-PID-PR-10008 | F13SL403 PW Spray | Analogue Input | A_Lo | 25 | m3/h | 5 | Mask A_Lo if F13-SL-403 Not Running Mask A_Lo for 10 seconds on F13-SL-403 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low flow through Trash Screen sprays. Advise Field Operator to check valves are appropriately lined up and in correct position. Check Filter is not clogged. Adjust inline manual flow control valve to appropriate flowrate setting. | A
FI13403 | 2000-F13-PID-PR-10008 | F13SL403 PW Spray | Analogue Input | A_Hi | 75 | m3/h | 5 | Mask A_Lo if F13-SL-403 Not Running Mask A_Lo for 10 seconds on F13-SL-403 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | High flow through Trash Screen sprays. Advise Field Operator to adjust inline manual flow control valve to appropriate flowrate setting. Check filter is correctly installed. | A
FI13393 | 2000-F13-PID-PR-10008 | F13SL404 PW Spray | Analogue Input | A_Lo | 25 | m3/h | 5 | Mask A_Lo if F13-SL-404 Not Running Mask A_Lo for 10 seconds on F13-SL-404 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low flow through Trash Screen sprays. Advise Field Operator to check valves are appropriately lined up and in correct position. Check Filter is not clogged. Adjust inline manual flow control valve to appropriate flowrate setting. | A
FI13393 | 2000-F13-PID-PR-10008 | F13SL404 PW Spray | Analogue Input | A_Hi | 75 | m3/h | 5 | Mask A_Lo if F13-SL-404 Not Running Mask A_Lo for 10 seconds on F13-SL-404 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | High flow through Trash Screen sprays. Advise Field Operator to adjust inline manual flow control valve to appropriate flowrate setting. Check filter is correctly installed. | A
LI13430 | 2000-F13-PID-PR-10012 | F13TK407 Level | Analogue Input | A_LL | 20 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Chiller Recirculation Pumps tripped. Check system for water loss. Refill once resolved. | A
LI13430 | 2000-F13-PID-PR-10012 | F13TK407 Level | Analogue Input | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check system for water loss. Refill once resolved. | A
LI13430 | 2000-F13-PID-PR-10012 | F13TK407 Level | Analogue Input | A_Hi | 80 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | High level. Check water fill solenoid valve is closed and not passing. | A
LI13430 | 2000-F13-PID-PR-10012 | F13TK407 Level | Analogue Input | A_HH | 90 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Close trip fill valve XV13419 Advise Field Operator to inspect area and to ensure Scheme Water manual fill valves are closed. It may be necessary to drain Tank to an acceptable level (check line fill). | B
FI13187 | 2000-F13-PID-PR-10006 | F13CC401 Seal Water Flow | Analogue Input | A_LL | 1.32 | m3/h | 3 | Mask if SV13185 closed | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Crusher at risk of tripping. Check seal water pumps are running. Advise Field Operator to check seal water valve are properly lined up and for leaks around the area. Else escalate to Maintenance. | A
FI13187 | 2000-F13-PID-PR-10006 | F13CC401 Seal Water Flow | Analogue Input | A_Lo | 1.56 | m3/h | 3 | Mask if SV13185 closed | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder at risk of tripping. Check seal water pumps are running. Advise Field Operator to check seal water valve are properly lined up and for leaks around the area. Else escalate to Maintenance. | A
FI13294 | 2000-F13-PID-PR-10006 | F13CC402 Seal Water Flow | Analogue Input | A_LL | 1.32 | m3/h | 3 | Mask if SV13292 closed | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Crusher at risk of tripping. Check seal water pumps are running. Advise Field Operator to check seal water valve are properly lined up and for leaks around the area. Else escalate to Maintenance. | A
FI13294 | 2000-F13-PID-PR-10006 | F13CC402 Seal Water Flow | Analogue Input | A_Lo | 1.56 | m3/h | 3 | Mask if SV13292 closed | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder at risk of tripping. Check seal water pumps are running. Advise Field Operator to check seal water valve are properly lined up and for leaks around the area. Else escalate to Maintenance. | A
TI13427 | 2000-F13-PID-PR-10012 | F13HE420 Chill Water Out | Analogue Input | A_Lo | 5 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Chilled water temperature is low. Check Chiller setpoints and/or take Chillers offline. | B
TI13427 | 2000-F13-PID-PR-10012 | F13HE420 Chill Water Out | Analogue Input | A_Hi | 30 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Chilled water temperature is high. Check Chiller setpoints and/or bring Chillers online. | B
TI13421 | 2000-F13-PID-PR-10009 | F13HE420 Cool Water Out | Analogue Input | A_Lo | 5 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Cooling water temperature is low. Check Chiller setpoints and/or take Chillers offline. | B
TI13421 | 2000-F13-PID-PR-10009 | F13HE420 Cool Water Out | Analogue Input | A_Hi | 38 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Cooling water temperature is high. Check Chiller setpoints and/or bring Chillers online. | B
MS_MSTR_T | 2000-F13-PID-PR-10003 | F13MS401 Master Torque | Analogue Input | A_HH | 700 | kNm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | SAG Mill torque high. Check against power and mill weight trends to ensure SAG Mill is not centrifuging. Consider grinding out. | A
JI13136A | 2000-F13-PID-PR-10003 | F13MS401 Master Power | Analogue Input | A_Hi | 9900 | kW | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | SAG Mill power high. Check against mill weight trends to ensure SAG Mill is not over charged. Consider grinding out and reducing mill ball addition. Check LoadIQ data is healthy. | 1 | 2025-10-06 | CR-052
JI13136A | 2000-F13-PID-PR-10003 | F13MS401 Master Power | Analogue Input | A_HH | 10000 | kW | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Mill tripped. SAG Mill power high. Check against mill weight trends to ensure SAG Mill is not over charged. Consider grinding out and reducing mill ball addition. Check LoadIQ data is healthy. | 2 | 2025-05-20 | F13 High High Alarm on Mill Power Missing
MS_SLVE_T | 2000-F13-PID-PR-10003 | F13MS401 Slave Torque | Analogue Input | A_Hi | 700 | kNm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | SAG Mill speed high. Ensure speed is in Auto or Cascade control. Decrease speed setpoint to normal operating setpoint. Check LoadIQ data is healthy. | A
JI13136B | 2000-F13-PID-PR-10003 | F13MS401 Slave Power | Analogue Input | A_Hi | 9900 | kW | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | SAG Mill power high. Check against mill weight trends to ensure SAG Mill is not over charged. Consider grinding out and reducing mill ball addition. Check LoadIQ data is healthy. | A
JI13136B | 2000-F13-PID-PR-10003 | F13MS401 Slave Power | Analogue Input | A_HH | 10000 | kW | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Mill tripped. SAG Mill power high. Check against mill weight trends to ensure SAG Mill is not over charged. Consider grinding out and reducing mill ball addition. Check LoadIQ data is healthy. | 2 | 2025-05-20 | F13 High High Alarm on Mill Power Missing
MS_COOL_COND | 2000-F13-PID-PR-10003 | F13MS401 Pure Water Cond | Analogue Input | A_Hi | 0.8 | µS/cm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | High conductivity in SAG Mill VSD Pure Water circuit. Check for leaks into the circuit. | A
MB_MSTR_T | 2000-F13-PID-PR-10004 | F13MB401 Master Torque | Analogue Input | A_HH | 700 | kNm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Ball Mill torque high. Check against power and mill weight trends to ensure Ball Mill is not centrifuging. Consider grinding out. | A
JI13149A | 2000-F13-PID-PR-10004 | F13MB401 Master Power | Analogue Input | A_Hi | 9900 | kW | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Ball Mill power high. Check against mill weight trends to ensure Ball Mill is not over charged. Consider grinding out and reducing mill ball addition. Check LoadIQ data is healthy. | A
JI13149A | 2000-F13-PID-PR-10004 | F13MB401 Master Power | Analogue Input | A_HH | 10000 | kW | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Mill tripped. Ball Mill power high. Check against mill weight trends to ensure Ball Mill is not over charged. Consider grinding out and reducing mill ball addition. | 2 | 2025-05-20 | F13 High High Alarm on Mill Power Missing
MB_SLVE_T | 2000-F13-PID-PR-10004 | F13MB401 Slave Torque | Analogue Input | A_Hi | 700 | kNm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Ball Mill speed high. Ensure speed is in Auto or Cascade control. Decrease speed setpoint to normal operating setpoint. Check LoadIQ data is healthy. | A
JI13149B | 2000-F13-PID-PR-10004 | F13MB401 Slave Power | Analogue Input | A_Hi | 9900 | kW | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Ball Mill power high. Check against mill weight trends to ensure Ball Mill is not over charged. Consider grinding out and reducing mill ball addition. Check LoadIQ data is healthy. | A
JI13149B | 2000-F13-PID-PR-10004 | F13MB401 Slave Power | Analogue Input | A_HH | 10000 | kW | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Mill tripped. Ball Mill power high. Check against mill weight trends to ensure Ball Mill is not over charged. Consider grinding out and reducing mill ball addition. | 2 | 2025-05-20 | F13 High High Alarm on Mill Power Missing
MB_COOL_COND | 2000-F13-PID-PR-10004 | F13MB401 Pure Water Cond | Analogue Input | A_Hi | 0.8 | µS/cm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | High conductivity in SAG Mill VSD Pure Water circuit. Check for leaks into the circuit. | A
LI13608 | 2000-ME001.2-D07-50002 | F13LU416 Grease Level | Analogue Input | A_Lo | 25 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Low grease drum level. Replace or refill drum immediately. Failed greasing will cause the Mill to eventually trip. | 1 | 2025-05-28 | https://pastech-2955.atlassian.net/browse/KAN-1938
LI13859 | 2000-F13-PID-PR-10013 | F13LU426 Grease Level | Analogue Input | A_Lo | 25 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Low grease drum level. Replace or refill drum immediately. Failed greasing will cause the Mill to eventually trip. | 1 | 2025-05-28 | https://pastech-2955.atlassian.net/browse/KAN-1938
WI13834 | 2000-ME001.3-D07-50002 | F13LU424 IBC Weight | Analogue Input | A_Lo | 15 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Low gear spray lube IBC level. Replace or refill IBC immediately. Failed gear spray cycle will cause the Mill to eventually trip. | A
WI13148 | 2000-F13-PID-PR-10004 | F13MB401 Mill Weight | Analogue Input | A_Hi | 1495 | t | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | High mill weight. Check mill weight trend against power draw for centrifuging. Grind out mill as required. Check mill feed water flow controllers are operating as required. Check ball charging system is operating as required. Check feed rate. | A
WI13148 | 2000-F13-PID-PR-10004 | F13MB401 Mill Weight | Analogue Input | A_HH | 1525 | t | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | High mill weight. Check mill weight trend against power draw for centrifuging. Grind out mill as required. Check mill feed water flow controllers are operating as required. Check ball charging system is operating as required. Check feed rate. | A
TI13060A | 2000-F13-PID-PR-10001 | F13CV403 Drive Pulley | Analogue Input | A_Hi | 60 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | High drive pulley temperature. Advise Field Operator / Maintenance to investigate when practical. | B
TI13060A | 2000-F13-PID-PR-10001 | F13CV403 Drive Pulley | Analogue Input | A_HH | 70 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | High drive pulley temperature. Advise Field Operator / Maintenance to investigate immediately. | B
TI13060B | 2000-F13-PID-PR-10001 | F13CV403 Drive Pulley | Analogue Input | A_Hi | 60 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | High drive pulley temperature. Advise Field Operator / Maintenance to investigate when practical. | B
TI13060B | 2000-F13-PID-PR-10001 | F13CV403 Drive Pulley | Analogue Input | A_HH | 70 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | High drive pulley temperature. Advise Field Operator / Maintenance to investigate immediately. | B
TI13172A | 2000-F13-PID-PR-10005 | F13CV404 Drive Pulley | Analogue Input | A_Hi | 60 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | High drive pulley temperature. Advise Field Operator / Maintenance to investigate when practical. | B
TI13172A | 2000-F13-PID-PR-10005 | F13CV404 Drive Pulley | Analogue Input | A_HH | 70 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | High drive pulley temperature. Advise Field Operator / Maintenance to investigate immediately. | B
TI13172B | 2000-F13-PID-PR-10005 | F13CV404 Drive Pulley | Analogue Input | A_Hi | 60 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | High drive pulley temperature. Advise Field Operator / Maintenance to investigate when practical. | B
TI13172B | 2000-F13-PID-PR-10005 | F13CV404 Drive Pulley | Analogue Input | A_HH | 70 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | High drive pulley temperature. Advise Field Operator / Maintenance to investigate immediately. | B
TI13199A | 2000-F13-PID-PR-10005 | F13CV405 Drive Pulley | Analogue Input | A_Hi | 60 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | High drive pulley temperature. Advise Field Operator / Maintenance to investigate when practical. | B
TI13199A | 2000-F13-PID-PR-10005 | F13CV405 Drive Pulley | Analogue Input | A_HH | 70 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | High drive pulley temperature. Advise Field Operator / Maintenance to investigate immediately. | B
TI13199B | 2000-F13-PID-PR-10005 | F13CV405 Drive Pulley | Analogue Input | A_Hi | 60 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | High drive pulley temperature. Advise Field Operator / Maintenance to investigate when practical. | B
TI13199B | 2000-F13-PID-PR-10005 | F13CV405 Drive Pulley | Analogue Input | A_HH | 70 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | High drive pulley temperature. Advise Field Operator / Maintenance to investigate immediately. | B
TI13357A | 2000-F13-PID-PR-10006 | F13CV406 Drive Pulley | Analogue Input | A_Hi | 60 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | High drive pulley temperature. Advise Field Operator / Maintenance to investigate when practical. | B
TI13357A | 2000-F13-PID-PR-10006 | F13CV406 Drive Pulley | Analogue Input | A_HH | 70 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | High drive pulley temperature. Advise Field Operator / Maintenance to investigate immediately. | B
TI13357B | 2000-F13-PID-PR-10006 | F13CV406 Drive Pulley | Analogue Input | A_Hi | 60 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | High drive pulley temperature. Advise Field Operator / Maintenance to investigate when practical. | B
TI13357B | 2000-F13-PID-PR-10006 | F13CV406 Drive Pulley | Analogue Input | A_HH | 70 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | High drive pulley temperature. Advise Field Operator / Maintenance to investigate immediately. | B
FI13244 | 2000-F13-PID-PR-10006 | F13CC401 Lube Oil Supply | Analogue Input | A_LL | 10.2 | m3/h | 3 | 1. F13-PO-401/402 Not Running 2. Mask for 10 seconds (TBC) after F13-PO-401 OR 402 start signal | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance to investigate immediately. Check pump is healthy, valves are in correct position, blockages and filter. Swap to standby if available. | B
FI13244 | 2000-F13-PID-PR-10006 | F13CC401 Lube Oil Supply | Analogue Input | A_Lo | 12.48 | m3/h | 3 | 1. F13-PO-401/402 Not Running 2. Mask for 10 seconds (TBC) after F13-PO-401 OR 402 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise Field Operator / Maintenance to investigate immediately. Check pump is healthy, valves are in correct position, blockages and filter. Swap to standby if available. | 2
PI13233 | 2000-F13-PID-PR-10006 | F13CC401 Lube Oil Supply | Analogue Input | A_LL | 13 | kPa | 3 | 1. F13-PO-401/402 Not Running 2. Mask for 10 seconds (TBC) after F13-PO-401 OR 402 start signal | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance to investigate immediately. Check pump is healthy, check for damaged piping, spillage etc. Swap to standby if available. | B
PI13233 | 2000-F13-PID-PR-10006 | F13CC401 Lube Oil Supply | Analogue Input | A_Lo | 41 | kPa | 3 | 1. F13-PO-401/402 Not Running 2. Mask for 10 seconds (TBC) after F13-PO-401 OR 402 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance to investigate immediately. Check pump is healthy, check for damaged piping, spillage etc. Swap to standby if available. | B
FI13304 | 2000-F13-PID-PR-10006 | F13CC402 Lube Oil Supply | Analogue Input | A_LL | 10.2 | m3/h | 3 | 1. F13-PO-406/407 Not Running 2. Mask for 10 seconds (TBC) after F13-PO-406 OR 407 start signal | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance to investigate immediately. Check pump is healthy, valves are in correct position, blockages and filter. Swap to standby if available. | B
FI13304 | 2000-F13-PID-PR-10006 | F13CC402 Lube Oil Supply | Analogue Input | A_Lo | 12.48 | m3/h | 3 | 1. F13-PO-406/407 Not Running 2. Mask for 10 seconds (TBC) after F13-PO-406 OR 407 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise Field Operator / Maintenance to investigate immediately. Check pump is healthy, valves are in correct position, blockages and filter. Swap to standby if available. | 2
PI13283 | 2000-F13-PID-PR-10006 | F13CC402 Lube Oil Supply | Analogue Input | A_LL | 13 | kPa | 3 | 1. F13-PO-406/407 Not Running 2. Mask for 10 seconds (TBC) after F13-PO-406 OR 407 start signal | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance to investigate immediately. Check pump is healthy, check for damaged piping, spillage etc. Swap to standby if available. | B
PI13283 | 2000-F13-PID-PR-10006 | F13CC402 Lube Oil Supply | Analogue Input | A_Lo | 41 | kPa | 3 | 1. F13-PO-406/407 Not Running 2. Mask for 10 seconds (TBC) after F13-PO-406 OR 407 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance to investigate immediately. Check pump is healthy, check for damaged piping, spillage etc. Swap to standby if available. | B
SI13137A | 2000-F13-PID-PR-10003 | F13MS401 Master Speed | Analogue Input | A_LL | 115 | RPM | 5 | 1. Mask if F13-MS-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MS-401 start signal 3. MS_OP_MODE = Inching | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
SI13137A | 2000-F13-PID-PR-10003 | F13MS401 Master Speed | Analogue Input | A_Lo | 120 | RPM | 5 | 1. Mask if F13-MS-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MS-401 start signal 3. MS_OP_MODE = Inching | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
SI13137A | 2000-F13-PID-PR-10003 | F13MS401 Master Speed | Analogue Input | A_Hi | 160 | RPM | 5 | 1. Mask if F13-MS-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MS-401 start signal 3. MS_OP_MODE = Inching | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
SI13137A | 2000-F13-PID-PR-10003 | F13MS401 Master Speed | Analogue Input | A_HH | 164 | RPM | 5 | 1. Mask if F13-MS-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MS-401 start signal 3. MS_OP_MODE = Inching | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
MS_MSTR_I | 2000-F13-PID-PR-10003 | F13MS401 Master Current | Analogue Input | A_HH | 1700 | Amps | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check for VSD common fault alarms. Check other variables are healthy. Advise Maintenance to investigate immediately. | B
SI13137B | 2000-F13-PID-PR-10003 | F13MS401 Slave Speed | Analogue Input | A_LL | 115 | RPM | 5 | 1. Mask if F13-MS-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MS-401 start signal 3. MS_OP_MODE = Inching | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
SI13137B | 2000-F13-PID-PR-10003 | F13MS401 Slave Speed | Analogue Input | A_Lo | 120 | RPM | 5 | 1. Mask if F13-MS-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MS-401 start signal 3. MS_OP_MODE = Inching | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
SI13137B | 2000-F13-PID-PR-10003 | F13MS401 Slave Speed | Analogue Input | A_Hi | 160 | RPM | 5 | 1. Mask if F13-MS-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MS-401 start signal 3. MS_OP_MODE = Inching | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
SI13137B | 2000-F13-PID-PR-10003 | F13MS401 Slave Speed | Analogue Input | A_HH | 164 | RPM | 5 | 1. Mask if F13-MS-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MS-401 start signal 3. MS_OP_MODE = Inching | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
MS_SLVE_I | 2000-F13-PID-PR-10003 | F13MS401 Slave Current | Analogue Input | A_HH | 1700 | Amps | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check for VSD common fault alarms. Check other variables are healthy. Advise Maintenance to investigate immediately. | B
SI13150A | 2000-F13-PID-PR-10004 | F13MB401 Master Speed | Analogue Input | A_LL | 115 | RPM | 5 | 1. Mask if F13-MB-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MB-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
SI13150A | 2000-F13-PID-PR-10004 | F13MB401 Master Speed | Analogue Input | A_Lo | 120 | RPM | 5 | 1. Mask if F13-MB-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MB-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
SI13150A | 2000-F13-PID-PR-10004 | F13MB401 Master Speed | Analogue Input | A_Hi | 160 | RPM | 5 | 1. Mask if F13-MB-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MB-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
SI13150A | 2000-F13-PID-PR-10004 | F13MB401 Master Speed | Analogue Input | A_HH | 164 | RPM | 5 | 1. Mask if F13-MB-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MB-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
MB_MSTR_I | 2000-F13-PID-PR-10004 | F13MB401 Master Current | Analogue Input | A_HH | 1700 | Amps | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check for VSD common fault alarms. Check other variables are healthy. Advise Maintenance to investigate immediately. | B
SI13150B | 2000-F13-PID-PR-10004 | F13MB401 Slave Speed | Analogue Input | A_LL | 115 | RPM | 5 | 1. Mask if F13-MB-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MB-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
SI13150B | 2000-F13-PID-PR-10004 | F13MB401 Slave Speed | Analogue Input | A_Lo | 120 | RPM | 5 | 1. Mask if F13-MB-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MB-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
SI13150B | 2000-F13-PID-PR-10004 | F13MB401 Slave Speed | Analogue Input | A_Hi | 160 | RPM | 5 | 1. Mask if F13-MB-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MB-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
SI13150B | 2000-F13-PID-PR-10004 | F13MB401 Slave Speed | Analogue Input | A_HH | 164 | RPM | 5 | 1. Mask if F13-MB-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MB-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check for VSD common fault alarms. Check other variables are healthy and Manta cube is operating as intended. | B
MB_SLVE_I | 2000-F13-PID-PR-10004 | F13MB401 Slave Current | Analogue Input | A_HH | 1700 | Amps | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check for VSD common fault alarms. Check other variables are healthy. Advise Maintenance to investigate immediately. | B
SI13137A | 2000-F13-PID-PR-10003 | F13MS401 Master Speed | Analogue Input | DV Alarm | 2 | % of SV | 10 | 1. Mask if F13-MS-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MS-401 start signal 3. MS_OP_MODE = Inching | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | B
SI13137B | 2000-F13-PID-PR-10003 | F13MS401 Slave Speed | Analogue Input | DV Alarm | 2 | % of SV | 10 | 1. Mask if F13-MS-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MS-401 start signal 3. MS_OP_MODE = Inching | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | B
SI13150A | 2000-F13-PID-PR-10004 | F13MB401 Master Speed | Analogue Input | DV Alarm | 2 | % of SV | 10 | 1. Mask if F13-MB-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MB-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | B
SI13150B | 2000-F13-PID-PR-10004 | F13MB401 Slave Speed | Analogue Input | DV Alarm | 2 | % of SV | 10 | 1. Mask if F13-MB-401 Not Running 2. Mask for 30 seconds (TBC) after F13-MB-401 start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | B
FIC13413 | 2000-F13-PID-PR-10011 | F13MB401A Cool Wtr Feed | Analogue PID | A_Lo | 55 | m3/h | 5 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MB-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check and confirm flowrate for Ball Mill Main Motor inching interlocks. Investigate for issues with the pump or control valve | 2
FIC13415 | 2000-F13-PID-PR-10011 | F13MB401B Cool Wtr Feed | Analogue PID | A_Lo | 55 | m3/h | 5 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MB-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check and confirm flowrate for Ball Mill Main Motor inching interlocks. Investigate for issues with the pump or control valve | 2
FIC13128 | 2000-F13-PID-PR-10009 | F13PP401 Cool Wtr Spply | Analogue PID | A_Lo | 50 | m3/h | 5 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-PP-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low cooling water supply. Check controllers are operating as intended. Advise Field Operator / Maintenance to investigate | 2
FIC13409 | 2000-F13-PID-PR-10010 | F13MS401A Cool Wtr Feed | Analogue PID | A_Lo | 55 | m3/h | 5 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MS-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low cooling water supply. Check controllers are operating as intended. Advise Field Operator / Maintenance to investigate | 2
FIC13411 | 2000-F13-PID-PR-10010 | F13MS401B Cool Wtr Feed | Analogue PID | A_Lo | 55 | m3/h | 5 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MS-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low cooling water supply. Check controllers are operating as intended. Advise Field Operator / Maintenance to investigate | 2
EI13285A | 2000-F13-PID-PR-10004 | F13BLC402 Voltage | Analogue Input | A_Hi | 285 | V DC | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | High magnet voltage. Advise Maintenance to investigate if high alarm persists. | 0
II13285B | 2000-F13-PID-PR-10004 | F13BLC402 Current | Analogue Input | A_Hi | 47.5 | A DC | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | High magnet current. Advise Maintenance to investigate if high alarm persists. | 0
WI13285C | 2000-F13-PID-PR-10004 | F13BLC402 Load Cell | Analogue Input | A_Hi | x = 1575 y = 1125 See comments for logic | kg | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check Hoist is not entangled or in contact with surrounding structure. Attempt to lower and de-energise magnet. Run homing sequence if required. | 0
WI13285C | 2000-F13-PID-PR-10004 | F13BLC402 Load Cell | Analogue Input | A_HH | x = 1750 y = 1250 See comments for logic | kg | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator to check Hoist is not entangled or in contact with surrounding structure. Attempt to lower and de-energise magnet and rehome, else advise Maintenance to action when practical. Interlock bypass required. | 0
TI13129 | 2000-F13-PID-PR-10009 | F13PP401 Cool Wtr Rturn | Analogue Input | A_Lo | 5 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check Mill Cooling Water Circuit is healthy and cooling water supply flow controller is in auto and at appropriate flowrate setpoint. Else, advise Maintenance team to investigate when practical. Monitor temperature trends and upgrade urgency as required. | 2
TI13129 | 2000-F13-PID-PR-10009 | F13PP401 Cool Wtr Rturn | Analogue Input | A_Hi | 41 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Mill Cooling Water Circuit is healthy and operating at appropriate cooling water temperature setpoint. Check return water temperature control valve is in auto and operating as intended. | 2
TI13414 | 2000-F13-PID-PR-10011 | F13MB401A Cool Wtr Rturn | Analogue Input | A_Hi | 43 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check Mill Cooling Water Circuit is healthy and cooling water supply flow controller is in auto and at appropriate flowrate setpoint. Else, advise Maintenance team to investigate when practical. Monitor temperature trends and upgrade urgency as required. | 2
TI13416 | 2000-F13-PID-PR-10011 | F13MB401B Cool Wtr Rturn | Analogue Input | A_Hi | 43 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check Mill Cooling Water Circuit is healthy and cooling water supply flow controller is in auto and at appropriate flowrate setpoint. Else, advise Maintenance team to investigate when practical. Monitor temperature trends and upgrade urgency as required. | 2
TI13410 | 2000-F13-PID-PR-10010 | F13MS401A Cool Wtr Rturn | Analogue Input | A_Hi | 43 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check Mill Cooling Water Circuit is healthy and cooling water supply flow controller is in auto and at appropriate flowrate setpoint. Else, advise Maintenance team to investigate when practical. Monitor temperature trends and upgrade urgency as required. | 2
TI13412 | 2000-F13-PID-PR-10010 | F13MS401B Cool Wtr Rturn | Analogue Input | A_Hi | 43 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Check Mill Cooling Water Circuit is healthy and cooling water supply flow controller is in auto and at appropriate flowrate setpoint. Else, advise Maintenance team to investigate when practical. Monitor temperature trends and upgrade urgency as required. | 2
TI13414 | 2000-F13-PID-PR-10011 | F13MB401A Cool Wtr Rturn | Analogue Input | A_Lo | 5 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Mill Cooling Water Circuit is healthy and operating at appropriate cooling water temperature setpoint. Check return water temperature control valve is in auto and operating as intended. | 2
TI13416 | 2000-F13-PID-PR-10011 | F13MB401B Cool Wtr Rturn | Analogue Input | A_Lo | 5 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Mill Cooling Water Circuit is healthy and operating at appropriate cooling water temperature setpoint. Check return water temperature control valve is in auto and operating as intended. | 2
TI13412 | 2000-F13-PID-PR-10010 | F13MS401B Cool Wtr Rturn | Analogue Input | A_Lo | 5 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Mill Cooling Water Circuit is healthy and operating at appropriate cooling water temperature setpoint. Check return water temperature control valve is in auto and operating as intended. | 2
TI13410 | 2000-F13-PID-PR-10010 | F13MS401A Cool Wtr Rturn | Analogue Input | A_Lo | 5 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Mill Cooling Water Circuit is healthy and operating at appropriate cooling water temperature setpoint. Check return water temperature control valve is in auto and operating as intended. | 2
FIC13090 | 2000-F13-PID-PR-10002 | F13PP401 Flowrate | Analogue PID | A_Lo | 12160 | m3/h | 300 | 1. Mask A_Lo if DNIC13090A.PV <= P_Lo 2. Mask if F13-PP-401 Not Running 3. Mask for 20 seconds (TBC) on Pump start up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Increase Cyclone Feed Pump flowrate. Below settling velocity. Ensure line is flushed prior to shutdown or intermittently flush lines with water during low flow operation. | 1 | 2025-03-06 | PCT alignment action register (density transmitters to align with F16,17,18)
LIC13076A | 2000-F13-PID-PR-10002 | F13HP401 Level A | Analogue PID | A_HH | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Potential overflow to grade. Ensure Cyclone Feed Pump and hopper feed water controllers are set to Cascade/Auto mode and the 'Density & Level' control method is selected on faceplate F13HP401_FP1 | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
LIC13076A | 2000-F13-PID-PR-10002 | F13HP401 Level A | Analogue PID | A_Hi | 80 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Potential overflow to grade. Ensure Cyclone Feed Pump and hopper feed water controllers are set to Cascade/Auto mode and the 'Density & Level' control method is selected on faceplate F13HP401_FP1 | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
LIC13076A | 2000-F13-PID-PR-10002 | F13HP401 Level A | Analogue PID | A_LL | 20 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to identify cause of low feed to hopper and resolve prior to restarting area F13. Ensure Cyclone Feed Pump and hopper feed water controllers are set to Cascade/Auto mode and the 'Density & Level' control method is selected on faceplate F13HP401_FP1 | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
LIC13076A | 2000-F13-PID-PR-10002 | F13HP401 Level A | Analogue PID | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to identify cause of low feed to hopper and resolve prior to restarting area F13. Ensure Cyclone Feed Pump and hopper feed water controllers are set to Cascade/Auto mode and the 'Density & Level' control method is selected on faceplate F13HP401_FP1 | 1 | 2025-04-07 | Cyclones design change following F28 FAT.
LIC13076A | 2000-F13-PID-PR-10002 | F13HP401 Level | Analogue PID | DV Alarm | 5 |  | - |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | PV Deviation alarm. Operator to investigate deviation and to manually select a healthy level instrument. | 1 | 7/04/2025 22/05/2025 | Cyclones design change following F28 FAT. https://pastech-2955.atlassian.net/browse/KAN-1910
LIC13223 | 2000-F13-PID-PR-10006 | F13CH461 Level | Analogue PID | A_HH | 90 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check Feeder is set to auto mode. Check Recycle Crusher for tramp / ensure hydraulic unit operating as expected. | A
LIC13223 | 2000-F13-PID-PR-10006 | F13CH461 Level | Analogue PID | A_Hi | 80 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check Feeder is set to auto mode. Check Recycle Crusher for tramp / ensure hydraulic unit operating as expected. | A
LIC13223 | 2000-F13-PID-PR-10006 | F13CH461 Level | Analogue PID | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Feeder is set to auto mode. Check Recycle Crusher CSS correct. | A
LIC13227 | 2000-F13-PID-PR-10006 | F13CH464 Level | Analogue PID | A_HH | 90 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check Feeder is set to auto mode. Check Recycle Crusher for tramp / ensure hydraulic unit operating as expected. | A
LIC13227 | 2000-F13-PID-PR-10006 | F13CH464 Level | Analogue PID | A_Hi | 80 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check Feeder is set to auto mode. Check Recycle Crusher for tramp / ensure hydraulic unit operating as expected. | A
LIC13227 | 2000-F13-PID-PR-10006 | F13CH464 Level | Analogue PID | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Feeder is set to auto mode. Check Recycle Crusher CSS correct. | A
LIC13381 | 2000-F13-PID-PR-10007 | F13HP402 Level | Analogue PID | A_HH | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Potential overflow to grade. Ensure Trash Dewatering Screen Hopper Underflow Pump is set to Auto mode. | A
LIC13381 | 2000-F13-PID-PR-10007 | F13HP402 Level | Analogue PID | A_Hi | 80 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Potential overflow to grade. Ensure Trash Dewatering Screen Hopper Underflow Pump is set to Auto mode. | A
LIC13381 | 2000-F13-PID-PR-10007 | F13HP402 Level | Analogue PID | A_LL | 20 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Ensure Trash Dewatering Screen Hopper Underflow Pump is set to Auto mode. | A
LIC13381 | 2000-F13-PID-PR-10007 | F13HP402 Level | Analogue PID | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Ensure Trash Dewatering Screen Hopper Underflow Pump is set to Auto mode. | A
PIC13092 | 2000-F13-PID-PR-10002 | F13CY401 Feed | Analogue PID | A_HH | 110 | kPag | 30 | Mask A_Lo and A_LL if F13-PP-401 = Not Running Mask A_Lo AND A_Hi if all of the DUTY Cyclone Feed Valves (XV13094 to XV13108) are in AUTOMATIC mode. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check Cyclone Feed Pump and Cyclone Feed Valve controllers are healthy and in Auto/Cascade mode. Ensure that the pump is running above settling flowrate. Conduct flush of line if issues persist. | A
PIC13092 | 2000-F13-PID-PR-10002 | F13CY401 Feed | Analogue PID | A_Hi | PIC13092.SV + Y | kPag | 100 | Mask A_Lo and A_LL if F13-PP-401 = Not Running Mask A_Lo AND A_Hi if all of the DUTY Cyclone Feed Valves (XV13094 to XV13108) are in AUTOMATIC mode. | None | Immediate (<5 minutes) | No Alarm | Open Cyclone Feed Valve | A
PIC13092 | 2000-F13-PID-PR-10002 | F13CY401 Feed | Analogue PID | A_LL | 60 | kPag | 30 | Mask A_Lo and A_LL if F13-PP-401 = Not Running Mask A_Lo AND A_Hi if all of the DUTY Cyclone Feed Valves (XV13094 to XV13108) are in AUTOMATIC mode. | None | Immediate (<5 minutes) | No Alarm | Close Cyclone Feed Valve | A
PIC13092 | 2000-F13-PID-PR-10002 | F13CY401 Feed | Analogue PID | A_Lo | PIC13092.SV - Y | kPag | 100 | Mask A_Lo and A_LL if F13-PP-401 = Not Running Mask A_Lo AND A_Hi if all of the DUTY Cyclone Feed Valves (XV13094 to XV13108) are in AUTOMATIC mode. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check Cyclone Feed Pump and Cyclone Feed Valve controllers are healthy and in Auto/Cascade mode. Ensure that the pump is running above settling flowrate. Conduct flush of line if issues persist. | A
TIC13629 | 2000-ME001.2-D07-50002 | F13LU413 Spply Lube Temp | Analogue PID | A_HH | 41 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check the Lube Oil Heat Exchanger cooling water supply is in auto, at temperature setpoint and healthy. Check the Mill Chiller system is in auto and healthy. Check the Lubrication Heaters are in auto and healthy. | A
TIC13629 | 2000-ME001.2-D07-50002 | F13LU413 Spply Lube Temp | Analogue PID | A_Hi | 39 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Check the Lube Oil Heat Exchanger cooling water supply is in auto, at temperature setpoint and healthy. Check the Mill Chiller system is in auto and healthy. Check the Lubrication Heaters are in auto and healthy. | A
TIC13629 | 2000-ME001.2-D07-50002 | F13LU413 Spply Lube Temp | Analogue PID | A_Lo | 0 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check the Lube Oil Heat Exchanger cooling water supply is in auto, at temperature setpoint and healthy. Check the Mill Chiller system is in auto and healthy. Check the Lubrication Heaters are in auto and healthy. | A
TIC13880 | 2000-F13-PID-PR-10011 | F13LU423 Spply Lube Temp | Analogue PID | A_HH | 41 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check the Lube Oil Heat Exchanger cooling water supply is in auto, at temperature setpoint and healthy. Check the Mill Chiller system is in auto and healthy. Check the Lubrication Heaters are in auto and healthy. | B
TIC13880 | 2000-F13-PID-PR-10011 | F13LU423 Spply Lube Temp | Analogue PID | A_Hi | 39 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Check the Lube Oil Heat Exchanger cooling water supply is in auto, at temperature setpoint and healthy. Check the Mill Chiller system is in auto and healthy. Check the Lubrication Heaters are in auto and healthy. | B
TIC13880 | 2000-F13-PID-PR-10011 | F13LU423 Spply Lube Temp | Analogue PID | A_Lo | 0 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Check the Lube Oil Heat Exchanger cooling water supply is in auto, at temperature setpoint and healthy. Check the Mill Chiller system is in auto and healthy. Check the Lubrication Heaters are in auto and healthy. | B
WIC13135 | 2000-F13-PID-PR-10001 | F13MS401 Mill Weight | Analogue PID | A_Hi | 960 | t | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | High mill weight. Check mill weight trend against power draw for centrifuging. Grind out mill as required. Check mill feed water flow controllers are operating as required. Check ball charging system is operating as required. Check feed rate. | A
WIC13135 | 2000-F13-PID-PR-10001 | F13MS401 Mill Weight | Analogue PID | A_HH | 1000 | t | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | High mill weight. Check mill weight trend against power draw for centrifuging. Grind out mill as required. Check mill feed water flow controllers are operating as required. Check ball charging system is operating as required. Check feed rate. | A
FIC13125 | 2000-F13-PID-PR-10009 | F13CU407 Cool Wtr Spply | Analogue PID | A_Lo | 37.5 | m3/h | 5 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MS-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low cooling water supply. Check controllers are operating as intended. Advise Field Operator / Maintenance to investigate | B
FIC13126 | 2000-F13-PID-PR-10009 | F13CU408 Cool Wtr Spply | Analogue PID | A_Lo | 37.5 | m3/h | 5 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MB-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low cooling water supply. Check controllers are operating as intended. Advise Field Operator / Maintenance to investigate | B
FIC13127 | 2000-F13-PID-PR-10009 | F13CU409 Cool Wtr Spply | Analogue PID | A_Lo | 10 | m3/h | 5 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-PP-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low cooling water supply. Check controllers are operating as intended. Advise Field Operator / Maintenance to investigate | B
FIC13075 | 2000-F13-PID-PR-10002 | F13HP401 Dilution | Analogue PID | DV Alarm | 5 | % of SV | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
DNIC13090A | 2000-F13-PID-PR-10002 | F13CY401 Feed Density | Analogue PID | DV Alarm | 5 | % of SV | 10 | Mask DV alarm if DNIC13090A is not selected on HS13090 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Controller not controlling to setpoint. Investigate. | 1 | 6/03/2025 22/05/2025 | PCT alignment action register (density transmitters to align with F16,17,18) https://pastech-2955.atlassian.net/browse/KAN-1910
DNIC13090B | 2000-F13-PID-PR-10002 | F13CY401 OF Density | Analogue PID | DV Alarm | 5 | % of SV | 10 | Mask DV alarm if DNIC13090B is not selected on HS13090 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Controller not controlling to setpoint. Investigate. | 1 | 6/03/2025 22/05/2025 | PCT alignment action register (density transmitters to align with F16,17,18) https://pastech-2955.atlassian.net/browse/KAN-1910
FIC13123 | 2000-F13-PID-PR-10003 | F13SC404 PW Spray | Analogue PID | DV Alarm | 5 | % of SV | 10 | 1. FCV13123 = Manual 2. Mask for 10 seconds (TBC) when changed to Auto mode | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
FIC13121 | 2000-F13-PID-PR-10003 | F13MS401 Feed Water | Analogue PID | DV Alarm | 5 | % of SV | 10 | 1. FCV13121 = Manual 2. Mask for 10 seconds (TBC) when changed to Auto mode | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
FIC13143 | 2000-F13-PID-PR-10004 | F13SC402 PW Spray | Analogue PID | DV Alarm | 5 | % of SV | 10 | 1. FCV13143 = Manual 2. Mask for 10 seconds (TBC) when changed to Auto mode | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
FIC13141 | 2000-F13-PID-PR-10004 | F13MB401 Feed Water | Analogue PID | DV Alarm | 5 | % of SV | 10 | 1. FCV13141 = Manual 2. Mask for 10 seconds (TBC) when changed to Auto mode | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
FIC13125 | 2000-F13-PID-PR-10009 | F13CU407 Cool Wtr Spply | Analogue PID | DV Alarm | 5 | % of SV | 10 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MS-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
FIC13126 | 2000-F13-PID-PR-10009 | F13CU408 Cool Wtr Spply | Analogue PID | DV Alarm | 5 | % of SV | 10 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MB-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
FIC13127 | 2000-F13-PID-PR-10009 | F13CU409 Cool Wtr Spply | Analogue PID | DV Alarm | 5 | % of SV | 10 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-PP-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
FIC13128 | 2000-F13-PID-PR-10009 | F13PP401 Cool Wtr Spply | Analogue PID | DV Alarm | 5 | % of SV | 10 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-PP-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | 1 | 2025-06-05 | https://pastech-2955.atlassian.net/browse/KAN-1910
FIC13411 | 2000-F13-PID-PR-10010 | F13MS401B Cool Wtr Feed | Analogue PID | DV Alarm | 5 | % of SV | 10 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MS-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | 1 | 2025-06-05 | https://pastech-2955.atlassian.net/browse/KAN-1910
FIC13409 | 2000-F13-PID-PR-10010 | F13MS401A Cool Wtr Feed | Analogue PID | DV Alarm | 5 | % of SV | 10 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MS-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | 1 | 2025-06-05 | https://pastech-2955.atlassian.net/browse/KAN-1910
FIC13413 | 2000-F13-PID-PR-10011 | F13MB401A Cool Wtr Feed | Analogue PID | DV Alarm | 5 | % of SV | 10 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MB-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | 1 | 2025-06-05 | https://pastech-2955.atlassian.net/browse/KAN-1910
FIC13415 | 2000-F13-PID-PR-10011 | F13MB401B Cool Wtr Feed | Analogue PID | DV Alarm | 5 | % of SV | 10 | Mask alarm if: [F13-PW-413 AND F13-PW-414 Not Running] OR F13-MB-401 = Not Running] Include 10 seconds (TBC) off-delay on mask conditions | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | 1 | 2025-06-05 | https://pastech-2955.atlassian.net/browse/KAN-1910
TIC13129 | 2000-F13-PID-PR-10009 | F13PP401 Cool Wtr Rturn | Analogue PID | DV Alarm | 5 | % of SV | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
TIC13412 | 2000-F13-PID-PR-10010 | F13MS401B Cool Wtr Rturn | Analogue PID | DV Alarm | 5 | % of SV | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
TIC13410 | 2000-F13-PID-PR-10010 | F13MS401A Cool Wtr Rturn | Analogue PID | DV Alarm | 5 | % of SV | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
TIC13414 | 2000-F13-PID-PR-10011 | F13MB401A Cool Wtr Rturn | Analogue PID | DV Alarm | 5 | % of SV | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
TIC13416 | 2000-F13-PID-PR-10011 | F13MB401B Cool Wtr Rturn | Analogue PID | DV Alarm | 5 | % of SV | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
FIC13071 | 2000-F13-PID-PR-10002 | F13SC401 PW Spray | Analogue PID | DV Alarm | 5 | % of SV | 10 | 1. F13-SC-401 Not Running 2. Mask for 10 seconds (TBC) after start signal | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Controller not controlling to setpoint. Investigate. | 1 | 2025-05-22 | https://pastech-2955.atlassian.net/browse/KAN-1910
PAL13225 | 2000-F13-PID-PR-10006 | F13DG467-CP Air | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Investigate bypass gate air pressure. | 1 | 2025-04-30 | https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-296?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
BDA13053A | 2000-F13-PID-PR-10001 | F13CV403 TE Drift RHS | Digital Input | Alarm |  |  | 3 | F13-CV-403 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13053B | 2000-F13-PID-PR-10001 | F13CV403 TE Drift LHS | Digital Input | Alarm |  |  | 3 | F13-CV-403 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13053C | 2000-F13-PID-PR-10001 | F13CV403 RQ Drift RHS | Digital Input | Alarm |  |  | 3 | F13-CV-403 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13053D | 2000-F13-PID-PR-10001 | F13CV403 RQ Drift LHS | Digital Input | Alarm |  |  | 3 | F13-CV-403 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13053E | 2000-F13-PID-PR-10001 | F13CV403 FQ Drift RHS | Digital Input | Alarm |  |  | 3 | F13-CV-403 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13053F | 2000-F13-PID-PR-10001 | F13CV403 FQ Drift LHS | Digital Input | Alarm |  |  | 3 | F13-CV-403 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13053G | 2000-F13-PID-PR-10001 | F13CV403 HE Drift RHS | Digital Input | Alarm |  |  | 3 | F13-CV-403 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13053H | 2000-F13-PID-PR-10001 | F13CV403 HE Drift LHS | Digital Input | Alarm |  |  | 3 | F13-CV-403 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13168A | 2000-F13-PID-PR-10005 | F13CV404 HE Drift RHS | Digital Input | Alarm |  |  | 3 | F13-CV-404 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13168B | 2000-F13-PID-PR-10005 | F13CV404 HE Drift LHS | Digital Input | Alarm |  |  | 3 | F13-CV-404 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13193A | 2000-F13-PID-PR-10005 | F13CV405 TE Drift RHS | Digital Input | Alarm |  |  | 3 | F13-CV-405 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13193B | 2000-F13-PID-PR-10005 | F13CV405 TE Drift LHS | Digital Input | Alarm |  |  | 3 | F13-CV-405 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13193C | 2000-F13-PID-PR-10005 | F13CV405 ME Drift RHS | Digital Input | Alarm |  |  | 3 | F13-CV-405 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13193D | 2000-F13-PID-PR-10005 | F13CV405 ME Drift LHS | Digital Input | Alarm |  |  | 3 | F13-CV-405 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13193E | 2000-F13-PID-PR-10005 | F13CV405 HE Drift RHS | Digital Input | Alarm |  |  | 3 | F13-CV-405 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13193F | 2000-F13-PID-PR-10005 | F13CV405 HE Drift LHS | Digital Input | Alarm |  |  | 3 | F13-CV-405 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13353A | 2000-F13-PID-PR-10006 | F13CV406 Drift RHS | Digital Input | Alarm |  |  | 3 | F13-CV-406 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13353B | 2000-F13-PID-PR-10006 | F13CV406 Drift LHS | Digital Input | Alarm |  |  | 3 | F13-CV-406 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BDA13367B | 2000-F13-PID-PR-10007 | F13SL401 Drift RHS Alarm | Digital Input | Alarm |  |  | 3 | 1. F13-SL-401 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-401 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
BDA13367D | 2000-F13-PID-PR-10007 | F13SL401 Drift RHS Trip | Digital Input | Alarm |  |  | 3 | 1. F13-SL-401 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-401 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
BDA13367A | 2000-F13-PID-PR-10007 | F13SL401 Drift LHS Alarm | Digital Input | Alarm |  |  | 3 | 1. F13-SL-401 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-401 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
BDA13367C | 2000-F13-PID-PR-10007 | F13SL401 Drift LHS Trip | Digital Input | Alarm |  |  | 3 | 1. F13-SL-401 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-401 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PAL13369 | 2000-F13-PID-PR-10007 | F13SL401 Instr. Air Lo | Digital Input | Alarm |  |  | 300 | F13-SL-401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate low instrument air pressure immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
PWA13365D | 2000-F13-PID-PR-10007 | F13SL401 PW Lower RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PWA13365C | 2000-F13-PID-PR-10007 | F13SL401 PW Lower LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PAL13368 | 2000-F13-PID-PR-10007 | F13SL401 PW Sprays Lo | Digital Input | Alarm |  |  | 3 | F13-SL-401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate low spray water pressure immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
PAL13370 | 2000-F13-PID-PR-10007 | F13SL401 PW Sprays Lo | Digital Input | Alarm |  |  | 3 | F13-SL-401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate low spray water pressure immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
PWA13365B | 2000-F13-PID-PR-10007 | F13SL401 PW Upper RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PWA13365A | 2000-F13-PID-PR-10007 | F13SL401 PW Upper LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
SAL13366 | 2000-F13-PID-PR-10007 | F13SL401 Underspeed | Digital Input | Alarm (see Comments) |  |  | 3 | 1. F13-SL-401 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-401 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate underspeed immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if available. | B
BDA13377B | 2000-F13-PID-PR-10007 | F13SL402 Drift RHS Alarm | Digital Input | Alarm |  |  | 3 | 1. F13-SL-402 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-402 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
BDA13377D | 2000-F13-PID-PR-10007 | F13SL402 Drift RHS Trip | Digital Input | Alarm |  |  | 3 | 1. F13-SL-402 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-402 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
BDA13377A | 2000-F13-PID-PR-10007 | F13SL402 Drift LHS Alarm | Digital Input | Alarm |  |  | 3 | 1. F13-SL-402 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-402 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
BDA13377C | 2000-F13-PID-PR-10007 | F13SL402 Drift LHS Trip | Digital Input | Alarm |  |  | 3 | 1. F13-SL-402 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-402 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
BRA13054 | 2000-F13-PID-PR-10001 | F13CV403 Belt Rip | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt rip switch immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BRA13169 | 2000-F13-PID-PR-10005 | F13CV404 Belt Rip | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt rip switch immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BRA13194 | 2000-F13-PID-PR-10005 | F13CV405 Belt Rip | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt rip switch immediately. Restart plant on Field Operator / Maintenance confirmation. | B
BRA13354 | 2000-F13-PID-PR-10006 | F13CV406 Belt Rip | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt rip switch immediately. Restart plant on Field Operator / Maintenance confirmation. | B
FAL13465 | 2000-F13-PID-PR-10008 | F13PP403 Flow Switch | Digital Input | Alarm |  |  | 3 | F13-PP-403 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check gland water system is healthy and inline auto valves are in the correct position. Advise Field Operator / Maintenance to investigate when practical. Ensure Screen bypass is active. | B
FALL13435 | 2000-F13-PID-PR-10012 | F13PW415/416 Flow LL | Digital Input | Alarm |  |  | 3 | F13-PW-415 AND F13-PW-416 Not Running Mask for 10 seconds on F13-PW-415 OR 416 start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check valves are properly lined up and limit switches are reading. Check heat exchanger is operating as intended. | B
FALL13436 | 2000-F13-PID-PR-10012 | F13PW413/414 Flow LL | Digital Input | Alarm |  |  | 3 | F13-PW-413 AND F13-PW-414 Not Running Mask for 10 seconds on F13-PW-413 OR 414 start | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check valves are properly lined up and limit switches are reading. Check heat exchanger is operating as intended. Check flow and temperature control valve to end users is healthy | B
HS13678BOFF | 2000-ME001.2-D07-50002 | F13LU413 Res Htr Off | Digital Input | Active (Off) |  |  | 0 |  | None | Plant Tripped | Logging \ Review the alarm priority (Invalid Alarm Ranking) | F13-LU-413 Resevoir Heaters turned OFF at control panel. Confirm reason with Field personnel. Ensure switch is changed back to AUTO when possible. | A
HS13678CTEST | 2000-ME001.2-D07-50002 | F13LU413 Res Htr Test | Digital Input | Active (Test) |  |  | 0 |  | None | Immediate (<5 minutes) | No Alarm | F13-LU-413 Resevoir Heaters turned ON (Test) at control panel. Confirm reason with Field personnel. Ensure switch is changed back to AUTO when test is complete. | A
HS13733BOFF | 2000-ME001.2-D02-50001 | F13LU413 Cond Htr Off | Digital Input | Active (Off) |  |  | 0 |  | None | Plant Tripped | Logging \ Review the alarm priority (Invalid Alarm Ranking) | F13-LU-413 Resevoir Heaters turned OFF at control panel. Confirm reason with Field personnel. Ensure switch is changed back to AUTO when possible. | A
HS13733CTEST | 2000-ME001.2-D02-50001 | F13LU413 Cond Htr Test | Digital Input | Active (Test) |  |  | 0 |  | None | Immediate (<5 minutes) | No Alarm | F13-LU-413 Resevoir Heaters turned ON (Test) at control panel. Confirm reason with Field personnel. Ensure switch is changed back to AUTO when test is complete. | A
HS13925BOFF | 2000-F13-PID-PR-10011 | F13LU423 Res Htr Off | Digital Input | Active (Off) |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | F13-LU-423 Resevoir Heaters turned OFF at control panel. Confirm reason with Field personnel. Ensure switch is changed back to AUTO when possible. | B
HS13925CTEST | 2000-F13-PID-PR-10011 | F13LU423 Res Htr Test | Digital Input | Active (Test) |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | F13-LU-423 Resevoir Heaters turned ON (Test) at control panel. Confirm reason with Field personnel. Ensure switch is changed back to AUTO when test complete. | B
HS13968BOFF | 2000-F13-PID-PR-10011 | F13LU423 Cond Htr Off | Digital Input | Active (Off) |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | F13-LU-423 Resevoir Heaters turned OFF at control panel. Confirm reason with Field personnel. Ensure switch is changed back to AUTO when possible. | B
HS13968CTEST | 2000-F13-PID-PR-10011 | F13LU423 Cond Htr Test | Digital Input | Active (Test) |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | F13-LU-423 Resevoir Heaters turned ON (Test) at control panel. Confirm reason with Field personnel. Ensure switch is changed back to AUTO when test I scomplete. | B
LAH13011 | 2000-F13-PID-PR-10001 | F13CH422 Blocked Chute | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Blocked chute. Advise Field Operator to investigate. Start standby Feeder if available. | A
LAH13021 | 2000-F13-PID-PR-10001 | F13CH425 Blocked Chute | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Blocked chute. Advise Field Operator to investigate. Start standby Feeder if available. | A
LAH13031 | 2000-F13-PID-PR-10001 | F13CH440 Blocked Chute | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Blocked chute. Advise Field Operator to investigate. Start standby Feeder if available. | A
LAH13058 | 2000-F13-PID-PR-10003 | F13CH430 Blocked Chute | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Blocked chute. Advise Field Operator to investigate immediately. | A
LAH13064 | 2000-F13-PID-PR-10001 | F13PS402 Level | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | High sump level for greater than 10 minutes. Advise Field Operator to investigate sump and sump area when practical. | A
LAHH13073 | 2000-F13-PID-PR-10002 | F13CH433 Blocked Chute | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Blocked chute. Advise Field Operator to investigate immediately. | A
LAH13131 | 2000-F13-PID-PR-10003 | F13PS405 Level | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | High sump level for greater than 10 minutes. Advise Field Operator to investigate sump and sump area when practical. | A
LAH13171 | 2000-F13-PID-PR-10005 | F13CH452 Blocked Chute | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Plant Tripped | Logging | Blocked chute. Advise Field Operator to investigate immediately. Restart, else shutdown plant if overflows become excessive. | A
LAH13198 | 2000-F13-PID-PR-10005 | F13CH455 Blocked Chute | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Plant Tripped | Logging | Blocked chute. Advise Field Operator to investigate immediately. Restart, else shutdown plant if overflows become excessive. | A
LAH13209 | 2000-F13-PID-PR-10005 | F13PS403 Level | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | High sump level for greater than 10 minutes. Advise Field Operator to investigate sump and sump area when practical. | A
LAH13356 | 2000-F13-PID-PR-10006 | F13CH463 Blocked Chute | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Plant Tripped | Logging | Blocked chute. Advise Field Operator to investigate immediately. Restart, else shutdown plant if overflows become excessive. | A
LAH13385 | 2000-F13-PID-PR-10007 | F13PS409 Level | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | High sump level for greater than 10 minutes. Advise Field Operator to investigate sump and sump area when practical. | B
LAL13009 | 2000-F13-PID-PR-10001 | F13FA411 Lube Level | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Low lube oil level in system causing a failed cycle timer to commence (24 hours resposne time before Feeder trips). Swap to standby Feeder if available. Check for leaks. Advise Maintenance to investigate immediately. | B
LAL13019 | 2000-F13-PID-PR-10001 | F13FA412 Lube Level | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Low lube oil level in system causing a failed cycle timer to commence (24 hours resposne time before Feeder trips). Swap to standby Feeder if available. Check for leaks. Advise Maintenance to investigate immediately. | B
LAL13029 | 2000-F13-PID-PR-10001 | F13FA414 Lube Level | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Low lube oil level in system causing a failed cycle timer to commence (24 hours resposne time before Feeder trips). Swap to standby Feeder if available. Check for leaks. Advise Maintenance to investigate immediately. | B
LAL13551 | 2000-ME001.2-D07-50002 | F13HU416 Hyd Res Lvl | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator to investigate hydraulic unit area for oil spillage due to loss of containment. If no issues are present, refill Hydraulic Unit oil to appropriate level. | B
LALL13568 | 2000-ME001.3-D02-50004 | F13LU411 Lube Res Lvl LL | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures. Check the lines and bearing supply points immediately. | B
LAL13802 | 2000-F13-PID-PR-10013 | F13HU417 Hyd Res Lvl | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Advise Field Operator to investigate hydraulic unit area for oil spillage due to loss of containment. If no issues are present, refill Hydraulic Unit oil to appropriate level. | B
LAL13819 | 2000-F13-PID-PR-10011 | F13LU421 Lube Res Lvl Lo | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures. Check the lines and bearing supply points immediately. | B
LAL13568 | 2000-ME001.3-D02-50004 | F13LU411 Lube Res Lvl L | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures. Check the lines and bearing supply points immediately. | B
LALL13819 | 2000-F13-PID-PR-10011 | F13LU421 LubeRes. Lvl LL | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to advise Field Operator / Maintenance to investigate for lubrication system leakages / ruptures. Check the lines and bearing supply points immediately. | B
PAL13156 | 2000-F13-PID-PR-10001 | F13FA411 G/box Clr Pump | Digital Input | Alarm |  |  | 30 | Mask if F13-PO-437 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | High pressure in lube oil system. Swap to standby Feeder if available. Check isolation valves are properly lined up. Check filter for blockages. Advise Maintenance to investigate immediately. | A
PAL13159 | 2000-F13-PID-PR-10001 | F13FA412 G/box Clr Pump | Digital Input | Alarm |  |  | 30 | Mask if F13-PO-438 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | High pressure in lube oil system. Swap to standby Feeder if available. Check isolation valves are properly lined up. Check filter for blockages. Advise Maintenance to investigate immediately. | A
PAL13162 | 2000-F13-PID-PR-10001 | F13FA414 G/box Clr Pump | Digital Input | Alarm |  |  | 30 | Mask if F13-PO-439 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | High pressure in lube oil system. Swap to standby Feeder if available. Check isolation valves are properly lined up. Check filter for blockages. Advise Maintenance to investigate immediately. | A
PAL13572 | 2000-ME001.3-D02-50004 | F13LU411 A Lube Sup. DE | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | 2
PAL13573 | 2000-ME001.3-D02-50004 | F13LU411 A Lube Sup. NDE | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | 2
PAL13574 | 2000-ME001.3-D02-50004 | F13LU411 B Lube Sup. DE | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | 2
PAL13575 | 2000-ME001.3-D02-50004 | F13LU411 B Lube Sup. NDE | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | 2
PAL13823 | 2000-F13-PID-PR-10011 | F13LU421 A Lube Sup. DE | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as practical. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | 2
PAL13824 | 2000-F13-PID-PR-10011 | F13LU421 A Lube Sup. NDE | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Trip ball mill main motor lube system. Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as possible. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | 2
PAL13825 | 2000-F13-PID-PR-10011 | F13LU421 B Lube Sup. DE | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Trip ball mill main motor lube system. Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as possible. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | 2
PAH13826 | 2000-F13-PID-PR-10011 | F13LU421 B Lube Sup. NDE | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Trip ball mill main motor lube system. Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate as soon as possible. Monitor Main Motor bearing temperature and vibration trends and upgrade urgency as required. | 2
PAL13379 | 2000-F13-PID-PR-10007 | F13SL402 Instr. AirLo | Digital Input | Alarm |  |  | 300 | F13-SL-402 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate low instrument air pressure immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
PWA13375D | 2000-F13-PID-PR-10007 | F13SL402 PW Lower RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PWA13375C | 2000-F13-PID-PR-10007 | F13SL402 PW Lower LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PAL13378 | 2000-F13-PID-PR-10007 | F13SL402 PW Sprays Lo | Digital Input | Alarm |  |  | 3 | F13-SL-402 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate low spray water pressure immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
PAL13380 | 2000-F13-PID-PR-10007 | F13SL402 PW Sprays Lo | Digital Input | Alarm |  |  | 3 | F13-SL-402 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate low spray water pressure immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
PWA13375B | 2000-F13-PID-PR-10007 | F13SL402 PW Upper RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PWA13375A | 2000-F13-PID-PR-10007 | F13SL402 PW Upper LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
SAL13376 | 2000-F13-PID-PR-10007 | F13SL402 Underspeed | Digital Input | Alarm (see Comments) |  |  | 3 | 1. F13-SL-402 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-402 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate underspeed immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if available. | B
BDA13397B | 2000-F13-PID-PR-10008 | F13SL403 Drift RHS Alarm | Digital Input | Alarm |  |  | 3 | 1. F13-SL-403 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-403 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
BDA13397D | 2000-F13-PID-PR-10008 | F13SL403 Drift RHS Trip | Digital Input | Alarm |  |  | 3 | 1. F13-SL-403 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-403 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
BDA13397A | 2000-F13-PID-PR-10008 | F13SL403 Drift LHS Alarm | Digital Input | Alarm |  |  | 3 | 1. F13-SL-403 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-403 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
BDA13397C | 2000-F13-PID-PR-10008 | F13SL403 Drift LHS Trip | Digital Input | Alarm |  |  | 3 | 1. F13-SL-403 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-403 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PDAH13014 | 2000-F13-PID-PR-10001 | F13FA411 G/box Clr Fltr | Digital Input | Alarm |  |  | 3 | Mask if F13-PO-437 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Filter blocked. Swap out blocked filter when practical. Monitor cycle switch during grease cycle. If gear cycle fails, ensure filter is attended to as soon as practical to prevent trip. Swap to standby Feeder if available. | A
PDAH13024 | 2000-F13-PID-PR-10001 | F13FA412 G/box Clr Fltr | Digital Input | Alarm |  |  | 3 | Mask if F13-PO-438 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Filter blocked. Swap out blocked filter when practical. Monitor cycle switch during grease cycle. If gear cycle fails, ensure filter is attended to as soon as practical to prevent trip. Swap to standby Feeder if available. | A
PDAH13034 | 2000-F13-PID-PR-10001 | F13FA414 G/box Clr Fltr | Digital Input | Alarm |  |  | 3 | Mask if F13-PO-439 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Filter blocked. Swap out blocked filter when practical. Monitor cycle switch during grease cycle. If gear cycle fails, ensure filter is attended to as soon as practical to prevent trip. Swap to standby Feeder if available. | A
PDAH13362 | 2000-F13-PID-PR-10007 | F13FI404 DP Switch | Digital Input | Alarm |  |  | 3 | Mask if XV13361 Closed | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Filter blocked. Swap out blocked filter when practical. Monitor spray water flow indicator to Trash Screen. Consider using bypass line if required. | B
PDAH13372 | 2000-F13-PID-PR-10007 | F13FI405 DP Switch | Digital Input | Alarm |  |  | 3 | Mask if XV13371 Closed | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Filter blocked. Swap out blocked filter when practical. Monitor spray water flow indicator to Trash Screen. Consider using bypass line if required. | B
PDAH13392 | 2000-F13-PID-PR-10008 | F13FI407 DP Switch | Digital Input | Alarm |  |  | 3 | Mask if XV13391 Closed | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Filter blocked. Swap out blocked filter when practical. Monitor spray water flow indicator to Trash Screen. Consider using bypass line if required. | B
PDAH13402 | 2000-F13-PID-PR-10008 | F13FI406 DP Switch | Digital Input | Alarm |  |  | 3 | Mask if XV13401 Closed | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Filter blocked. Swap out blocked filter when practical. Monitor spray water flow indicator to Trash Screen. Consider using bypass line if required. | B
PDAH13565 | 2000-ME001.3-D02-50004 | F13LU411 Lbe Fltr 2 Hi | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Filter blocked. Swap out blocked filter when practical. Monitor flow and pressure indicators to lube users. | A
PDAH13566 | 2000-ME001.3-D02-50004 | F13LU411 Lbe Fltr 1 Hi | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Filter blocked. Swap out blocked filter when practical. Monitor flow and pressure indicators to lube users. | A
PDAH13720 | 2000-ME001.2-D07-50002 | F13MS401 Fd Trn DP1 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
PDAH13721 | 2000-ME001.2-D07-50002 | F13MS401 Fd Trn DP2 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
PDAH13722 | 2000-ME001.2-D07-50002 | F13MS401 Fd Trn DP3 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
PDAH13723 | 2000-ME001.2-D07-50002 | F13MS401 Fd Trn DP4 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
PDAH13724 | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn DP1 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
PDAH13725 | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn DP2 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
PDAH13726 | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn DP3 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
PDAH13727 | 2000-ME001.2-D07-50002 | F13MS401 Dsch Trn DP4 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | A
PDAH13728 | 2000-ME001.2-D07-50002 | F13MS401 Dsch ThrBrg DP1 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | 1 | 2025-07-07 | CR-018
PDAH13729 | 2000-ME001.2-D07-50002 | F13MS401 Dsch ThrBrg DP2 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | 1 | 2025-07-07 | CR-018
PDAH13730 | 2000-ME001.2-D07-50002 | F13MS401 Dsch ThrBrg DP3 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | 1 | 2025-07-07 | CR-018
PDAH13731 | 2000-ME001.2-D07-50002 | F13MS401 Dsch ThrBrg DP4 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | 1 | 2025-07-07 | CR-018
PDAH13816 | 2000-F13-PID-PR-10011 | F13LU421 Lbe Fltr 2 Hi | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Filter blocked. Swap out blocked filter when practical. Monitor flow and pressure indicators to lube users. | B
PDAH13817 | 2000-F13-PID-PR-10011 | F13LU421 Lbe Fltr 1 Hi | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Filter blocked. Swap out blocked filter when practical. Monitor flow and pressure indicators to lube users. | B
PDAH13977 | 2000-F13-PID-PR-10013 | F13MB401 Fd Trn DP1 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | B
PDAH13978 | 2000-F13-PID-PR-10013 | F13MB401 Fd Trn DP2 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | B
PDAH13979 | 2000-F13-PID-PR-10013 | F13MB401 Fd Trn DP3 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | B
PDAH13980 | 2000-F13-PID-PR-10013 | F13MB401 Fd Trn DP4 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | B
PDAH13981 | 2000-F13-PID-PR-10013 | F13MB401 Dsch Trn DP1 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | B
PDAH13982 | 2000-F13-PID-PR-10013 | F13MB401 Dsch Trn DP2 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | B
PDAH13983 | 2000-F13-PID-PR-10013 | F13MB401 Dsch Trn DP3 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | B
PDAH13984 | 2000-F13-PID-PR-10013 | F13MB401 Dsch Trn DP4 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | B
PDAH13985 | 2000-F13-PID-PR-10013 | F13MB401 Dsch ThrBrg DP1 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | 1 | 2025-07-07 | CR-018
PDAH13986 | 2000-F13-PID-PR-10013 | F13MB401 Dsch ThrBrg DP2 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | 1 | 2025-07-07 | CR-018
PDAH13987 | 2000-F13-PID-PR-10013 | F13MB401 Dsch ThrBrg DP3 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | 1 | 2025-07-07 | CR-018
PDAH13988 | 2000-F13-PID-PR-10013 | F13MB401 Dsch ThrBrg DP4 | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check if flowrate is healthy on respective line flowmeter. If low/none, blockage might be evident. Advise Maintenance team to investigate immediately. Monitor Main Motor bearing temperature and vibration trends. Shutdown at Maintenance/Supervisor direction. | 1 | 2025-07-07 | CR-018
PDAHH13565 | 2000-ME001.3-D02-50004 | F13LU411 LbeFltr 2 Sw HH | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Filter blocked. Swap out blocked filter immediately. Check flow and pressure transmitters to lube users is healthy. | A
PDAHH13566 | 2000-ME001.3-D02-50004 | F13LU411 LbeFltr 1 Sw HH | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Filter blocked. Swap out blocked filter immediately. Check flow and pressure transmitters to lube users is healthy. | A
PDAHH13816 | 2000-F13-PID-PR-10011 | F13LU421 LbeFltr 2 Sw HH | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Filter blocked. Swap out blocked filter immediately. Check flow and pressure transmitters to lube users is healthy. | B
PDAHH13817 | 2000-F13-PID-PR-10011 | F13LU421 LbeFltr 1 Sw HH | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Filter blocked. Swap out blocked filter immediately. Check flow and pressure transmitters to lube users is healthy. | B
PWA13005A | 2000-F13-PID-PR-10001 | F13FA411 Pullwire RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation or swap to standby Feeders if available. | 0
PWA13005B | 2000-F13-PID-PR-10001 | F13FA411 Pullwire LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation or swap to standby Feeders if available. | 0
PWA13015A | 2000-F13-PID-PR-10001 | F13FA412 Pullwire RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation or swap to standby Feeders if available. | 0
PWA13015B | 2000-F13-PID-PR-10001 | F13FA412 Pullwire LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation or swap to standby Feeders if available. | 0
PWA13025A | 2000-F13-PID-PR-10001 | F13FA414 Pullwire RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation or swap to standby Feeders if available. | 0
PWA13025B | 2000-F13-PID-PR-10001 | F13FA414 Pullwire LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation or swap to standby Feeders if available. | 0
PWA13050A | 2000-F13-PID-PR-10001 | F13CV403 Pullwire1 RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PWA13050B | 2000-F13-PID-PR-10001 | F13CV403 Pullwire1 LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PWA13050C | 2000-F13-PID-PR-10001 | F13CV403 Pullwire2 RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PWA13050D | 2000-F13-PID-PR-10001 | F13CV403 Pullwire2 LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PWA13050E | 2000-F13-PID-PR-10001 | F13CV403 Pullwire3 RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PWA13050F | 2000-F13-PID-PR-10001 | F13CV403 Pullwire3 LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PWA13050G | 2000-F13-PID-PR-10001 | F13CV403 Pullwire4 RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 2 | 2026-01-31 | CR-065
PWA13050H | 2000-F13-PID-PR-10001 | F13CV403 Pullwire4 LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 2 | 2026-01-31 | CR-065
PWA13165A | 2000-F13-PID-PR-10005 | F13CV404 Pullwire RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PWA13165B | 2000-F13-PID-PR-10005 | F13CV404 Pullwire LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PWA13190A | 2000-F13-PID-PR-10005 | F13CV405 Pullwire1 RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PWA13190B | 2000-F13-PID-PR-10005 | F13CV405 Pullwire1 LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PWA13190C | 2000-F13-PID-PR-10005 | F13CV405 Pullwire2 RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PWA13190D | 2000-F13-PID-PR-10005 | F13CV405 Pullwire2 LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PWA13350A | 2000-F13-PID-PR-10006 | F13CV406 Pullwire RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PWA13350B | 2000-F13-PID-PR-10006 | F13CV406 Pullwire LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Restart on confirmation. | 0
PAL13399 | 2000-F13-PID-PR-10008 | F13SL403 Instr. Air Lo | Digital Input | Active |  |  | 300 | F13-SL-403 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate low instrument air pressure immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
PWA13395D | 2000-F13-PID-PR-10008 | F13SL403 PW Lower RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PWA13395C | 2000-F13-PID-PR-10008 | F13SL403 PW Lower LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PAL13398 | 2000-F13-PID-PR-10008 | F13SL403 PW Sprays Lo | Digital Input | Active |  |  | 3 | F13-SL-403 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate low spray water pressure immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
PAL13400 | 2000-F13-PID-PR-10008 | F13SL403 PW Sprays Lo | Digital Input | Active |  |  | 3 | F13-SL-403 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate low spray water pressure immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
PWA13395B | 2000-F13-PID-PR-10008 | F13SL403 PW Upper RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PWA13395A | 2000-F13-PID-PR-10008 | F13SL403 PW Upper LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
SAL13396 | 2000-F13-PID-PR-10008 | F13SL403 Underspeed | Digital Input | Alarm (see Comments) |  |  | 3 | 1. F13-SL-403 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-403 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate underspeed immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if available. | B
BDA13407B | 2000-F13-PID-PR-10008 | F13SL404 Drift RHS Alarm | Digital Input | Alarm |  |  | 3 | 1. F13-SL-404 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-404 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
BDA13407D | 2000-F13-PID-PR-10008 | F13SL404 Drift RHS Trip | Digital Input | Alarm |  |  | 3 | 1. F13-SL-404 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-404 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
BDA13407A | 2000-F13-PID-PR-10008 | F13SL404 Drift LHS Alarm | Digital Input | Alarm |  |  | 3 | 1. F13-SL-404 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-404 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
BDA13407C | 2000-F13-PID-PR-10008 | F13SL404 Drift LHS Trip | Digital Input | Alarm |  |  | 3 | 1. F13-SL-404 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-404 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate belt drift immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PAL13404 | 2000-F13-PID-PR-10008 | F13SL404 Instr. Air Lo | Digital Input | Alarm |  |  | 300 | F13-SL-404 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate low instrument air pressure immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
PWA13405D | 2000-F13-PID-PR-10008 | F13SL404 PW Lower RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PWA13405C | 2000-F13-PID-PR-10008 | F13SL404 PW Lower LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PAL13394 | 2000-F13-PID-PR-10008 | F13SL404 PW Sprays Lo | Digital Input | Alarm |  |  | 3 | F13-SL-404 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate low spray water pressure immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | A
SAL13006 | 2000-F13-PID-PR-10001 | F13FA411 Underspeed | Digital Input | Alarm |  |  | 3 | 1. F13-FA-411 Not Running 2. Mask for 10 seconds (TBC) on F13-FA-411 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate underspeed immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if available. | B
SAL13051 | 2000-F13-PID-PR-10001 | F13CV403 TE Underspeed | Digital Input | Alarm |  |  | 3 | 1. F13-CV-403 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-403 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check for belt slippage and build up around conveyor pulleys. If problem persists or worsens, advise Maintenance to investigate and action when practical. | B
SAL13052 | 2000-F13-PID-PR-10001 | F13CV403 FE Underspeed | Digital Input | Alarm |  |  | 3 | 1. F13-CV-403 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-403 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check for belt slippage and build up around conveyor pulleys. If problem persists or worsens, advise Maintenance to investigate and action when practical. | B
SAL13166 | 2000-F13-PID-PR-10005 | F13CV404 Underspeed 1 | Digital Input | Alarm |  |  | 3 | 1. F13-CV-404 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-404 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check for belt slippage and build up around conveyor pulleys. If problem persists or worsens, advise Maintenance to investigate and action when practical. | B
SAL13167 | 2000-F13-PID-PR-10005 | F13CV404 Underspeed 2 | Digital Input | Alarm |  |  | 3 | 1. F13-CV-404 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-404 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check for belt slippage and build up around conveyor pulleys. If problem persists or worsens, advise Maintenance to investigate and action when practical. | B
SAL13191 | 2000-F13-PID-PR-10005 | F13CV405 TE Underspeed | Digital Input | Alarm |  |  | 3 | 1. F13-CV-405 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-405 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check for belt slippage and build up around conveyor pulleys. If problem persists or worsens, advise Maintenance to investigate and action when practical. | B
SAL13192 | 2000-F13-PID-PR-10005 | F13CV405 DE Underspeed | Digital Input | Alarm |  |  | 3 | 1. F13-CV-405 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-405 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check for belt slippage and build up around conveyor pulleys. If problem persists or worsens, advise Maintenance to investigate and action when practical. | B
SAL13351 | 2000-F13-PID-PR-10006 | F13CV406 Underspeed | Digital Input | Alarm |  |  | 3 | 1. F13-CV-406 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-406 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check for belt slippage and build up around conveyor pulleys. If problem persists or worsens, advise Maintenance to investigate and action when practical. | B
SAL13352 | 2000-F13-PID-PR-10006 | F13CV406 Underspeed | Digital Input | Alarm |  |  | 3 | 1. F13-CV-406 Not Running 2. Mask for 120 seconds (TBC) on F13-CV-406 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Field Operator to check for belt slippage and build up around conveyor pulleys. If problem persists or worsens, advise Maintenance to investigate and action when practical. | B
PAL13408 | 2000-F13-PID-PR-10008 | F13SL404 PW Sprays Lo | Digital Input | Alarm |  |  | 3 | F13-SL-404 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate low spray water pressure immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | A
PWA13405B | 2000-F13-PID-PR-10008 | F13SL404 PW Upper RHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
PWA13405A | 2000-F13-PID-PR-10008 | F13SL404 PW Upper LHS | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Advise Field Operator to investigate pull wire trip immediately. Confirm personnel and area is safe. Swap to Standby if required. | 1 | 2025-07-03 | https://pastech-2955.atlassian.net/browse/PL-354
SAL13406 | 2000-F13-PID-PR-10008 | F13SL404 Underspeed | Digital Input | Alarm (see Comments) |  |  | 3 | 1. F13-SL-404 Not Running 2. Mask for 10 seconds (TBC) on F13-SL-404 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate underspeed immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
SAL13693 | 2000-ME001.2-D07-50002 | F13LU413 HP Lube P1 U/S | Digital Input | Alarm |  |  | 10 | 1. F13-PO-429 Not Running 2. Mask for 60 seconds (TBC) on F13-PO-429 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate underspeed immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
SAL13694 | 2000-ME001.2-D07-50002 | F13LU413 HP Lube P2 U/S | Digital Input | Alarm |  |  | 10 | 1. F13-PO-430 Not Running 2. Mask for 60 seconds (TBC) on F13-PO-430 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate underspeed immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
SAL13695 | 2000-ME001.2-D07-50002 | F13LU413 HP Lube P3 U/S | Digital Input | Alarm |  |  | 10 | 1. F13-PO-431 Not Running 2. Mask for 60 seconds (TBC) on F13-PO-431 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate underspeed immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
SAL13863 | 2000-F13-PID-PR-10011 | F13LU423 HP Lube P1 U/S | Digital Input | Alarm |  |  | 10 | F13-PO-529 Not Running Mask for 60 seconds (TBC) on F13-PO-529 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate underspeed immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
SAL13864 | 2000-F13-PID-PR-10011 | F13LU423 HP Lube P2 U/S | Digital Input | Alarm |  |  | 10 | F13-PO-530 Not Running Mask for 60 seconds (TBC) on F13-PO-530 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate underspeed immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
SAL13865 | 2000-F13-PID-PR-10011 | F13LU423 HP Lube P3 U/S | Digital Input | Alarm |  |  | 10 | F13-PO-531 Not Running Mask for 60 seconds (TBC) on F13-PO-531 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate underspeed immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if required. | B
TAH13552 | 2000-ME001.2-D07-50002 | F13HU416 Hyd Res Temp | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check hydraulic pump and pressure trends in hydraulic system are healthy. Advise Maintenance to investigate immediately if issues persist or cannot be identified. | A
TAH13803 | 2000-F13-PID-PR-10013 | F13HU417 Hyd Res Temp | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Check hydraulic pump and pressure trends in hydraulic system are healthy. Advise Maintenance to investigate immediately if issues persist or cannot be identified. | B
XA13202 | 2000-F13-PID-PR-10005 | F13MD401 Metal Detect | Digital Input | Alarm (Detected) |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Metal detected. Ensure Bypass Gate has successfully opened. | A
SAL13016 | 2000-F13-PID-PR-10001 | F13FA412 Underspeed | Digital Input | Alarm |  |  | 3 | 1. F13-FA-412 Not Running 2. Mask for 10 seconds (TBC) on F13-FA-412 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate underspeed immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if available. | B
SAL13026 | 2000-F13-PID-PR-10001 | F13FA414 Underspeed | Digital Input | Alarm |  |  | 3 | 1. F13-FA-442 Not Running 2. Mask for 10 seconds (TBC) on F13-FA-442 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate underspeed immediately. Restart plant on Field Operator / Maintenance confirmation. Swap to Standby if available. | B
ZSA13057A | 2000-F13-PID-PR-10001 | F13CV403 TakeUp LHS | Digital Input | Alarm |  |  | 3 | F13-CV-403 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate take up pulley immediately. | B
ZSA13057B | 2000-F13-PID-PR-10001 | F13CV403 TakeUp RHS | Digital Input | Alarm |  |  | 3 | F13-CV-403 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate take up pulley immediately. | B
ZSA13197A | 2000-F13-PID-PR-10005 | F13CV405 TakeUp LHS | Digital Input | Alarm |  |  | 3 | F13-CV-405 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate take up pulley immediately. | B
ZSA13197B | 2000-F13-PID-PR-10005 | F13CV405 TakeUp RHS | Digital Input | Alarm |  |  | 3 | F13-CV-405 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Field Operator / Maintenance team to investigate take up pulley immediately. | B
ZAH13546 | 2000-ME001.2-D07-50002 | F13HU416 Brake 1 Wear | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Maintenance that brake pads must be replaced immediately. | A
ZAH13548 | 2000-ME001.2-D07-50002 | F13HU416 Brake 2 Wear | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Maintenance that brake pads must be replaced immediately. | A
ZAH13796 | 2000-F13-PID-PR-10013 | F13HU417 Brake 1 Wear | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Maintenance that brake pads must be replaced immediately. | B
ZAH13798 | 2000-ME001.3-D07-50002 | F13HU417 Brake 2 Wear | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Maintenance that brake pads must be replaced immediately. | B
XA13182 | 2000-F13-PID-PR-10005 | F13MG403 Fault | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Fault feedback from Recycle Conveyor Magnet 1. Advise Field Operator / Maintenance to investigate. If unable to resolve. If Recycle Conveyor Magnet 1 AND 2 are fault, consider bypassing Recycle Crusher circuit until resolved. | A
XA13212 | 2000-F13-PID-PR-10005 | F13MG404 Fault | Digital Input | Fault |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | . | A
SAL13070 | 2000-F13-PID-PR-10001 | F13DC402 Rotary Vlv U/S | Digital Input | Alarm (see Comments) |  |  | 3 | 1. F13-VR-402 Not Running 2. Mask for 10 seconds (TBC) on F23-VR-402 start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Attempt to restart. If rotary valve trips on underspeed again, advise Field Operator or Maintenance to investigate rotary valve for blockages. | B
LAL13216 | 2000-F13-PID-PR-10006 | F13HU405 HPU Res Lvl Lo | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | The HPU level gauge should be inspected and confirmed that the oil level is low. Inspect the hydraulic lines to see if there are any leaks. If there are no leaks, refill the hydraulic oil tank to the recommended level. | B
TAH13216 | 2000-F13-PID-PR-10006 | F13HU405 HPU Res Temp Hi | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | The HPU temperature gauge should be inspected and confirmed that the oil temperature is high. The HPU should be manually shutdown if not in use in order to reduce heat build-up or as soon as possible. | A
LALL13216 | 2000-F13-PID-PR-10006 | F13HU405 HPU Res Lvl LL | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | The HPU level gauge should be inspected and confirmed that the oil level is low. Inspect the hydraulic lines to see if there are any leaks. If there are no leaks, refill the hydraulic oil tank to the recommended level. | B
TAHH13216 | 2000-F13-PID-PR-10006 | F13HU405 HPU Res Temp HH | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | The HPU temperature gauge should be inspected and confirmed that the oil temperature is high. The HPU should be manually shutdown if not in use in order to reduce heat build-up or as soon as possible. | A
PDAH13217 | 2000-F13-PID-PR-10006 | F13HU405 HPU Res Fltr | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Advise Maintenance or Field Operator to replace hydraulic filter when practical. | A
PAH13265 | 2000-F13-PID-PR-10006 | F13HU403 Bowl Close | Digital Input | Closed |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Bowl at the maximum open limit. Conduct manual or automatic calibration. | A
PAH13266 | 2000-F13-PID-PR-10006 | F13HU403 Bowl Open | Digital Input | Open |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Bowl at the maximum closed limit. Conduct manual or automatic calibration. | A
ZAO13238 | 2000-F13-PID-PR-10006 | F13LU403 Pump 1 Disch. | Digital Input | N_Open |  |  | 3 | Mask if F13-PO-401 is Standby on F13CC401_FP2 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | F13-PO-401 in Duty and discharge valve is not open. Swap to standby pump or advise Field Operator to open / close appropriate valves at the lubrication unit. | A
ZAO13239 | 2000-F13-PID-PR-10006 | F13LU403 Pump 2 Disch. | Digital Input | N_Open |  |  | 3 | Mask if F13-PO-402 is Standby on F13CC401_FP2 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | F13-PO-402 in Duty and discharge valve is not open. Swap to standby pump or advise Field Operator to open / close appropriate valves at the lubrication unit. | A
PAH13325 | 2000-F13-PID-PR-10006 | F13HU404 Bowl Close | Digital Input | Closed |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Bowl at the maximum close limit. Conduct manual or automatic calibration. | A
PAH13326 | 2000-F13-PID-PR-10006 | F13HU404 Bowl Open | Digital Input | Open |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Bowl at the maximum open limit. Conduct manual or automatic calibration. | A
ZAO13298 | 2000-F13-PID-PR-10006 | F13LU404 Pump 1 Disch. | Digital Input | N_Open |  |  | 3 | Mask if F13-PO-406 is Standby on F13CC402_FP2 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | F13-PO-406 in Duty and discharge valve is not open. Swap to standby pump or advise Field Operator to open / close appropriate valves at the lubrication unit. | A
ZAO13299 | 2000-F13-PID-PR-10006 | F13LU404 Pump 2 Disch. | Digital Input | N_Open |  |  | 3 | Mask if F13-PO-407 is Standby on F13CC402_FP2 | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | F13-PO-407 in Duty and discharge valve is not open. Swap to standby pump or advise Field Operator to open / close appropriate valves at the lubrication unit. | A
MS_COM_ALARM | 2000-F13-PID-PR-10003 | F13MS401 Common Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | A
XA13139 | 2000-F13-PID-PR-10003 | F13MS401 Common Fault | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | A
MS_ESTOP | 2000-F13-PID-PR-10003 | F13MS401 E-Stop | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | F13-MS-401A/B VSD E-Stop activated. Advise Field Operator to immediately check area and E-Stop in the field. | A
MS_M_INV_ALM | 2000-F13-PID-PR-10003 | F13MS401 M.Inverter Alrm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | 0
MS_M_INV_FLT | 2000-F13-PID-PR-10003 | F13MS401 M.Inverter Flt | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | 0
MS_S_INV_ALM | 2000-F13-PID-PR-10003 | F13MS401 S.Inverter Alrm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | 0
MS_S_INV_FLT | 2000-F13-PID-PR-10003 | F13MS401 S.Inverter Flt | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | 0
MS_FUNC_ALM | 2000-F13-PID-PR-10003 | F13MS401 Function Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | 0
MS_FUNC_FLT | 2000-F13-PID-PR-10003 | F13MS401 Function Module | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | 0
MS_FRZN_CHRG | 2000-F13-PID-PR-10003 | F13MS401 Frozen Charge | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Frozen charge detected. Inch mill following SOP to release frozen charge. | 0
MB_COM_ALARM | 2000-F13-PID-PR-10004 | F13MB401 Common Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | 0
XA13147 | 2000-F13-PID-PR-10004 | F13MB401 Common Fault | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | A
MB_ESTOP | 2000-F13-PID-PR-10004 | F13MB401 E-Stop | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | F13-MS-401A/B VSD E-Stop activated. Advise Field Operator to immediately check area and E-Stop in the field. | A
MB_M_INV_ALM | 2000-F13-PID-PR-10004 | F13MB401 M.Inverter Alrm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | 0
MB_M_INV_FLT | 2000-F13-PID-PR-10004 | F13MB401 M.Inverter Flt | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | 0
MB_S_INV_ALM | 2000-F13-PID-PR-10004 | F13MB401 S.Inverter Alrm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | 0
MB_S_INV_FLT | 2000-F13-PID-PR-10004 | F13MB401 S.Inverter Flt | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | 0
MB_FUNC_ALM | 2000-F13-PID-PR-10004 | F13MB401 Function Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | 0
MB_FUNC_FLT | 2000-F13-PID-PR-10004 | F13MB401 Function Module | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | F13-MS-401A/B VSD Fault alarm. Advise Maintenance to check fault codes from the VSD. | 0
MB_FRZN_CHRG | 2000-F13-PID-PR-10004 | F13MB401 Frozen Charge | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Frozen charge detected. Inch mill following SOP to release frozen charge. | 0
XA13470C | 2000-F13-PID-PR-10012 | F13CU402 Fault | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise Field Operator or Maintenance to investigate fault alarm on local Chiller HMI | B
XA13471C | 2000-F13-PID-PR-10012 | F13CU403 Fault | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise Field Operator or Maintenance to investigate fault alarm on local Chiller HMI | B
XA13472C | 2000-F13-PID-PR-10012 | F13CU404 Fault | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise Field Operator or Maintenance to investigate fault alarm on local Chiller HMI | B
XA13473C | 2000-F13-PID-PR-10012 | F13CU405 Fault | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise Field Operator or Maintenance to investigate fault alarm on local Chiller HMI | B
MS_STATUS | 2000-F13-PID-PR-10003 | F13MS401 IQ Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | LoadIQ unhealthy. Refer to IOM for troubleshooting | A
XA13055 | 2000-F13-PID-PR-10001 | F13WD403 Fault | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Weightometer fault. Advise Field Operator / Maintenance to investigate as soon as practical. | B
XA13078 | 2000-F13-PID-PR-10001 | F13DC402 Alarm | Digital Input | Alarm |  |  | 3 |  | Personnel1: First Aid Injury, Reversible health effects | Immediate (<5 minutes) | High | Dust collector controller fault. Advise Field Operator / Maintenance to investigate as soon as practical. | B
XA13195 | 2000-F13-PID-PR-10005 | F13WD405 Fault | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Weightometer fault. Advise Field Operator / Maintenance to investigate as soon as practical. | B
XA13204 | 2000-F13-PID-PR-10005 | F13MD401 Fault | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Metal detector fault. Advise Field Operator / Maintenance to investigate as soon as practical. | B
FAL13364 | 2000-F13-PID-PR-10007 | F13SC403 Spray Flow | Digital Input | Alarm |  |  | 3 | F13-SC-403 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Low Trash Dewatering Screen spray water flow. Advise Field Operator / Maintenance to investigate as soon as practical. | B
PDAH13260 | 2000-F13-PID-PR-10006 | F13HU403 Filter Blocked | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Filter blocked. Replace filter when practical. Monitor flow and pressure transmitters. | B
PDAH13320 | 2000-F13-PID-PR-10006 | F13HU404 Filter Blocked | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Filter blocked. Replace filter when practical. Monitor flow and pressure transmitters. | B
F13DCS402_PS1 | N/A | F13DCS402 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 0
F13DCS402_PS2 | N/A | F13DCS402 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 0
F13SW002_PS | N/A | F13SW002 ACB SHUNT 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | B
F13SW002_AF | N/A | F13SW002 ARC FLASH | Digital Input | Alarm |  |  | 0 |  | Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness. | Prompt (>15 to <30 minutes) | High | Electrician to investigate | B
F13SW002_TRP | N/A | F13SW002 C BREAKER TRIP | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Switchroom tripped. Electrician to investigate | B
F13SW002_SD | N/A | F13SW002 INC SURGE DIV | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | B
F13SR001_ESTP | N/A | F13SR001 SR ESHUT DCS IN | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Switchroom tripped. Electrician to investigate | 0
F13SW002_PS1 | N/A | F13SW002 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | B
F13SW002_PS2 | N/A | F13SW002 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | B
F13FIP001_ALM | N/A | F13-FIP-001 Alarm | Digital Input | Alarm |  |  | 0 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm Milling & Classification Area Switchroom. Follow site specific Fire Emergency Plan. | 0
F13FIP001_ISL | N/A | F13-FIP-001 Isolated | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 0
F13FIP001_FLT | N/A | F13-FIP-001 Fault | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 0
F13DCS403_PS1 | N/A | F13DCS403 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 0
F13DCS403_PS2 | N/A | F13DCS403 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 0
F13SW003_PS | N/A | F13SW003 ACB SHUNT 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | B
F13SW003_AF | N/A | F13-SW-003 ARC FLASH | Digital Input | Alarm |  |  | 0 |  | Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness. | Prompt (>15 to <30 minutes) | High | Electrician to investigate | B
F13SW003_TRP | N/A | F13SW003 C BREAKER TRIP | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Switchroom tripped. Electrician to investigate | B
F13SW003_SD | N/A | F13SW003 INC SURGE DIV | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | B
F13SR002_ESTP | N/A | F13SR002 SR ESHUT DCS IN | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Switchroom tripped. Electrician to investigate | 0
F13SW003_PS1 | N/A | F13SW003 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | B
F13SW003_PS2 | N/A | F13SW003 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | B
F13FIP002_ALM | N/A | F13-FIP-002 Alarm | Digital Input | Alarm |  |  | 0 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm Milling & Classification Area Switchroom. Follow site specific Fire Emergency Plan. | 0
F13FIP002_ISL | N/A | F13-FIP-002 Isolated | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 0
F13FIP002_FLT | N/A | F13-FIP-002 Fault | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 0
F13SW103_SD | N/A | F13SW103 Surge Div Ok | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | B
LAH13039 | N/A | F13-GE-103 Gen Fuel Hi | Digital Input | Alarm |  |  | 0 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | High fuel level in generator fuel reservoir. Operator to radio local field operator to cease re-fuelling. | B
LAL13039 | N/A | F13-GE-103 Gen Fuel Lo | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operational risk for backup power. Operator to organise re-fuelling. | B
F13DCS404_PS1 | N/A | F13DCS404 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 0
F13DCS404_PS2 | N/A | F13DCS404 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 0
F13SR003_ESTP | N/A | F13SR003 SR ESHUT DCS IN | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Switchroom tripped. Electrician to investigate | 0
F13FIP003_ALM | N/A | F13-FIP-003 Alarm | Digital Input | Alarm |  |  | 0 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm Milling & Classification Area Switchroom. Follow site specific Fire Emergency Plan. | 0
F13FIP003_ISL | N/A | F13-FIP-003 Isolated | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 0
F13FIP003_FLT | N/A | F13-FIP-003 Fault | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 0
F13DCS405_PS1 | N/A | F13DCS405 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 0
F13DCS405_PS2 | N/A | F13DCS405 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 0
F13DCS406_PS1 | N/A | F13DCS406 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 0
F13DCS406_PS2 | N/A | F13DCS406 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 0
F13SW014_PS | N/A | F13SW014 ACB SHUNT 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | B
F13SW014_AF | N/A | F13-SW-014 ARC FLASH | Digital Input | Alarm |  |  | 0 |  | Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness. | Prompt (>15 to <30 minutes) | High | Electrician to investigate | B
F13SW014_TRP | N/A | F13SW014 C BREAKER TRIP | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Switchroom tripped. Electrician to investigate | B
F13SW014_SD | N/A | F13SW014 INC SURGE DIVOK | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | B
F13SR004_ESTP | N/A | F13SR014 SR ESHUT DCS IN | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Switchroom tripped. Electrician to investigate | 0
F13SW014_PS1 | N/A | F13SW014 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | B
F13SW014_PS2 | N/A | F13SW014 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | B
F13FIP004_ALM | N/A | F13-FIP-004 Alarm | Digital Input | Alarm |  |  | 0 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm Milling & Classification Area Switchroom. Follow site specific Fire Emergency Plan. | 0
F13FIP004_ISL | N/A | F13-FIP-004 Isolated | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 0
F13FIP004_FLT | N/A | F13-FIP-004 Fault | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 0
F13SW114_SD | N/A | F13-SW-114 Surge Div Ok | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | B
LAH13049 | N/A | F13-GE-114 Gen Fuel Hi | Digital Input | Alarm |  |  | 0 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | High fuel level in generator fuel reservoir. Operator to radio local field operator to cease re-fuelling. | B
LAL13049 | N/A | F13-GE-114 Gen Fuel Lo | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operational risk for backup power. Operator to organise re-fuelling. | B
F13DCS407_PS1 | N/A | F13DCS407 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 0
F13DCS407_PS2 | N/A | F13DCS407 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 0
F13SW020_PS | N/A | F13SW020 ACB SHUNT 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | B
F13SW020_AF | N/A | F13-SW-020 ARC FLASH | Digital Input | Alarm |  |  | 0 |  | Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness. | Prompt (>15 to <30 minutes) | High | Electrician to investigate | B
F13SW020_TRP | N/A | F13SW020 C BREAKER TRIP | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Switchroom tripped. Electrician to investigate | B
F13SW020_SD | N/A | F13SW020 INC SURGE DIVOK | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | B
F13SR005_ESTP | N/A | F13SR005 SR ESHUT DCS IN | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Switchroom tripped. Electrician to investigate | 0
F13SW020_PS1 | N/A | F13SW020 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | B
F13SW020_PS2 | N/A | F13SW020 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | B
F13FIP005_ALM | N/A | F13-FIP-005 Alarm | Digital Input | Alarm |  |  | 0 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm Milling & Classification Area Switchroom. Follow site specific Fire Emergency Plan. | 0
F13FIP005_ISL | N/A | F13-FIP-005 Isolated | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 0
F13FIP005_FLT | N/A | F13-FIP-005 Fault | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 0
F13SW120_SD | N/A | F13-SW-120 Surge Div Ok | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | B
LAH13438 | N/A | F13-GE-120 Gen Fuel Hi | Digital Input | Alarm |  |  | 0 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | High fuel level in generator fuel reservoir. Operator to radio local field operator to cease re-fuelling. | B
LAL13438 | N/A | F13-GE-120 Gen Fuel Lo | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operational risk for backup power. Operator to organise re-fuelling. | B
F00RIO100_PS1 | N/A | F00RIO100 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F00RIO100_PS2 | N/A | F00RIO100 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F00SR001_ESTP | N/A | F00SR001 SR ESHUT DCS IN | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Switchroom tripped. Electrician to investigate | 0
F00BC001_FL1 | N/A | F00BC001 48VDCChargeMain | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | B
F00FIP001_ALM | N/A | F00-FIP-001 Alarm | Digital Input | Alarm |  |  | 0 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm Milling & Classification Area Switchroom. Follow site specific Fire Emergency Plan. | 0
F00FIP001_ISL | N/A | F00-FIP-001 Isolated | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 0
F00FIP001_FLT | N/A | F00-FIP-001 Fault | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 0
F13RIO001_PS1 | N/A | F13RIO001 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO001_PS2 | N/A | F13RIO001 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO011_PS1 | N/A | F13RIO011 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO011_PS2 | N/A | F13RIO011 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO012_PS1 | N/A | F13RIO012 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO012_PS2 | N/A | F13RIO012 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO013_PS1 | N/A | F13RIO013 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO013_PS2 | N/A | F13RIO013 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO021_PS1 | N/A | F13RIO021 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO021_PS2 | N/A | F13RIO021 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO022_PS1 | N/A | F13RIO022 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO022_PS2 | N/A | F13RIO022 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO031_PS1 | N/A | F13RIO031 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO031_PS2 | N/A | F13RIO031 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO032_PS1 | N/A | F13RIO032 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO032_PS2 | N/A | F13RIO032 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO041_PS1 | N/A | F13RIO041 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO041_PS2 | N/A | F13RIO041 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO042_PS1 | N/A | F13RIO042 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO042_PS2 | N/A | F13RIO042 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO051_PS1 | N/A | F13RIO051 PS1 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
F13RIO051_PS2 | N/A | F13RIO051 PS2 24VDC HTHY | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
ZAC13010 | N/A | F13TR002 415VMCC Door | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Restricted work area potential safety breach/issue | 0
ZAC13020 | N/A | F13TR003 415VMCC Door | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Restricted work area potential safety breach/issue | 0
ZAC13030 | N/A | F13TR014 415VMCC Door | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Restricted work area potential safety breach/issue | 0
ZAC13068 | N/A | F13TR020 415VMCC Door | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Restricted work area potential safety breach/issue | 0
YI13059C | 2000-F13-PID-PR-10001 | F13CAM101 Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Electrician to investigate camera fault. Last YI13059A.PV and YI13059B.PV is held whilst fault is active. | 0
XI13206A | 2000-F13-PID-PR-10004 | F13BLC402 E-Stop | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Advise Field Operator to investigate area immediately. Reset E-stop and reenergise system if safe to do so. | 0
XI13206B | 2000-F13-PID-PR-10004 | F13BLC402 MCB Trip | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Electrician to investigate and reset tripped breaker. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | 0
XI13206C | 2000-F13-PID-PR-10004 | F13BLC402 Earth Fault | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Electrician to investigate and reset fault condition. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | 0
F00BC001_FL2 | N/A | F00BC001 48VDCChargeCom | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 0
XA13200 | 2000-F13-PID-PR-10010 | F13LU413 OCM Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 0 | 2025-03-18 | Should be XA not XI
XA13201 | 2000-F13-PID-PR-10010 | F13LU423 OCM Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 0 | 2025-03-18 | Should be XA not XI
F13FD401_ALM | 2000-F13-PID-PR-10002 | F13FD401 SingleStageSAG | Misc | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Cyclone UF Boil Box discharge valves are not in typical position. Disregard if operating in Single Stage SAG mode. | B
F13LU451_T3A | 2000-F13-PID-PR-10001 | F13FA411 24Hr Fault Time | Misc | Timer Elapsed |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Advise Maintenance or Field Operator to investigate grease fault on the Feeder's lube system. | 1 | 4/04/2025 30/4/2025 | https://pastech-2955.atlassian.net/browse/KAN-1637 https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-295?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
F13LU452_T3A | 2000-F13-PID-PR-10001 | F13FA412 24Hr Fault Time | Misc | Timer Elapsed |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Advise Maintenance or Field Operator to investigate grease fault on the Feeder's lube system. | 1 | 4/04/2025 30/4/2025 | https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-295?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
F13LU453_T3A | 2000-F13-PID-PR-10001 | F13FA414 24Hr Fault Time | Misc | Timer Elapsed |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Advise Maintenance or Field Operator to investigate grease fault on the Feeder's lube system. | 1 | 4/04/2025 30/4/2025 | https://pastech-2955.atlassian.net/jira/software/c/projects/PL/issues/PL-295?jql=project%20%3D%20%22PL%22%20ORDER%20BY%20created%20DESC
F13CC401_CRP | 2000-F13-PID-PR-10006 | F13CC401 Bowl Creep | Misc | Active |  |  | 3 | Mask alarm and interlocks when: F13CC401_CAL = Active OR PI13263 < A_LL | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Bowl creep alarm. Swap to standby Cone Crusher if available else conduct an auto or manual calibration of F13-CC-402 | A
F13CC402_CRP | 2000-F13-PID-PR-10006 | F13CC402 Bowl Creep | Misc | Active |  |  | 3 | Mask alarm and interlocks when: F13CC402_CAL = Active OR PI13323 < A_LL | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Bowl creep alarm. Swap to standby Cone Crusher if available else conduct an auto or manual calibration of F13-CC-402 | A
MS_PBL_NCR | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 PinBrg Lube NCr | Misc | [5 empty] | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | SAG Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_PBL_CR | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 PinBrg Lube Cr | Misc | [5 empty] | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | SAG Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_PBT_NCR | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 PinBrgTemp NCr | Misc | [5 empty] | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | SAG Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_PBT_CR | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 PinBrgTemp Cr | Misc | [5 empty] | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | SAG Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_MBL_NCR | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 2000-F13-PID-PR-10013 | F13MS401 MainBrgLube NCr | Misc | [5 empty] | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | SAG Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_MBL_CR | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 2000-F13-PID-PR-10013 | F13MS401 MainBrgLbe Cr | Misc | [5 empty] | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | SAG Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_MBT_NCR | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 MainBrgTemp NCr | Misc | [5 empty] | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | SAG Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_MBT_CR | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 MainBrgTemp Cr | Misc | [5 empty] | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | SAG Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_SPRY_CR | 2000-F13-PID-PR-10013 | F13MS401 Gear Spry Cr | Misc | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | SAG Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_GRSE_CR | 2000-F13-PID-PR-10013 | F13MS401 Seal Grse Cr | Misc | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | SAG Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_BRKFLT1 | 2000-F13-PID-PR-10013 | F13MS401 Brake NormFault | Misc | Alarm |  |  | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | SAG Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_SPR_NCR | 2000-F13-PID-PR-10013 | F13MS401 Gear Spry NCr | Misc | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | SAG Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_GRS_NCR | 2000-F13-PID-PR-10013 | F13MS401 Seal Grse NCr | Misc | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | SAG Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
F13MS401FEEDA | 2000-F13-PID-PR-10003 | F13MS401 No Feed Alarm | Misc | Timer Elapsed |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | No feed registered on WI13055. Resolve feed issues else consider shutting down area F13. | 1 | 2025-05-04 | "A" suffix added to end of timer alarms as per AH comment
MS_ML_NCR | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 Motor Lube NCr | Misc | [5 empty] | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | SAG Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_ML_CR | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 Motor Lube Cr | Misc | [5 empty] | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | SAG Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_PFL_NCR | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 Pin. Flank NCr | Misc | [5 empty] | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | SAG Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_PFL_CR | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 Pin. Flank Cr | Misc | [5 empty] | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | SAG Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MS_NCR_ILK | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 Delayed Intlk | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | SAG Mill Delayed Stop Interlock active. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | 1 | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1877
MS_CR_ILK | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13MS401 Instant Intlk | Misc | Alarm |  |  | 1 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | SAG Mill Instantaneous Stop Interlock active. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | 1 | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1877
MB_PBL_NCR | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 PinBrg Lube NCr | Misc | [5 empty] | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Ball Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_PBL_CR | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 PinBrg Lube Cr | Misc | [5 empty] | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Ball Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_PBT_NCR | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 PinBrgTemp NCr | Misc | [5 empty] | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Ball Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_PBT_CR | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 PinBrgTemp Cr | Misc | [5 empty] | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Ball Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_MBL_NCR | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 2000-F13-PID-PR-10013 | F13MB401 MainBrgLube NCr | Misc | [5 empty] | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Ball Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_MBL_CR | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 2000-F13-PID-PR-10013. | F13MB401 MainBrgLbe Cr | Misc | [5 empty] | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Ball Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_MBT_NCR | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 MainBrgTemp NCr | Misc | [5 empty] | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Ball Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_MBT_CR | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 MainBrgTemp Cr | Misc | [5 empty] | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Ball Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_SPRY_CR | 2000-F13-PID-PR-10013 | F13MB401 Gear Spry Cr | Misc | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Ball Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_GRSE_CR | 2000-F13-PID-PR-10013 | F13MB401 Seal Grse Cr | Misc | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Ball Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_BRKFLT1 | 2000-F13-PID-PR-10013 | F13MS401 Brake NormFault | Misc | Alarm |  |  | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Ball Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_SPR_NCR | 2000-F13-PID-PR-10013 | F13MB401 Gear Spry NCr | Misc | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Ball Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_GRS_NCR | 2000-F13-PID-PR-10013 | F13MB401 Seal Grse NCr | Misc | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Ball Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_ML_NCR | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 Motor Lube NCr | Misc | [5 empty] | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Ball Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_ML_CR | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 Motor Lube Cr | Misc | [5 empty] | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Ball Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_PFL_NCR | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank NCr | Misc | [5 empty] | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Ball Mill Non Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_PFL_CR | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 Pin. Flank Cr | Misc | [5 empty] | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Ball Mill Critical group interlock. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | A
MB_NCR_ILK | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 Delayed Intlk | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Ball Mill Delayed Stop Interlock active. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | 1 | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1877
MB_CR_ILK | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13MB401 Instant Intlk | Misc | Alarm |  |  | 1 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Ball Mill Instantaneous Stop Interlock active. Investigate what condition is causing this group interlock to be active and refer to the condition's operator response. | 1 | 2025-05-19 | https://pastech-2955.atlassian.net/browse/KAN-1877
F13HU405_T1A | 2000-F13-PID-PR-10006 | F13HU405 Max SV Timer | Misc | Timer Elapsed |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Isolation gate not getting into position within the maximum energisation time frame. Visually inspect for material impeding door position. Check limit switch position. Attempt to open then close isolation gate (or vice versa). | 1 | 2025-05-04 | "A" suffix added to end of timer alarms as per AH comment
F13HP401_LVL | 2000-F13-PID-PR-10002 | F13PP401 Level Tran Sel. | Misc | [5 empty] | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | The duty level transmitter signal has failed and the standby transmitter has automatically taken control. Advise Maintenance to investigate when possible | B
F13HU405_T3A | 2000-F13-PID-PR-10006 | F13HU405 Shutdown Timer | Misc | Timer Elapsed |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Isolation gate hydraulic unit was running without an operator action. Ensure isolation gate is in intended position. | 1 | 2025-05-04 | "A" suffix added to end of timer alarms as per AH comment
F13CY401A_RPG | 2000-F13-PID-PR-10002 | F13CY401A Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401B_RPG | 2000-F13-PID-PR-10002 | F13CY401B Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401C_RPG | 2000-F13-PID-PR-10002 | F13CY401C Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401D_RPG | 2000-F13-PID-PR-10002 | F13CY401D Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401E_RPG | 2000-F13-PID-PR-10002 | F13CY401E Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401F_RPG | 2000-F13-PID-PR-10002 | F13CY401F Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401G_RPG | 2000-F13-PID-PR-10002 | F13CY401G Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401H_RPG | 2000-F13-PID-PR-10002 | F13CY401H Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401J_RPG | 2000-F13-PID-PR-10002 | F13CY401J Roping Alarm | Misc | 13077 |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401K_RPG | 2000-F13-PID-PR-10002 | F13CY401K Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401M_RPG | 2000-F13-PID-PR-10002 | F13CY401M Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401N_RPG | 2000-F13-PID-PR-10002 | F13CY401N Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401P_RPG | 2000-F13-PID-PR-10002 | F13CY401P Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401Q_RPG | 2000-F13-PID-PR-10002 | F13CY401Q Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401R_RPG | 2000-F13-PID-PR-10002 | F13CY401R Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401S_RPG | 2000-F13-PID-PR-10002 | F13CY401S Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401T_RPG | 2000-F13-PID-PR-10002 | F13CY401T Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13CY401U_RPG | 2000-F13-PID-PR-10002 | F13CY401U Roping Alarm | Misc | Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check Cyclone pressure and density at setpoint, and that related controllers are operating as intended. Advise Metallurgist to investigate. | 0
F13MB401_OCM | 2000-F13-PID-PR-10004 2000-F13-PID-PR-10011 | F13PO446 Test Fail | Misc | Alarm |  |  | 60 | Mask if F13-PO-446 = Manual mode | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Report to Maintenance. High solid contamination in Ball Mill lubrication oil | 1
F13MS401_OCM | 2000-F13-PID-PR-10003 2000-F13-PID-PR-10010 | F13PO445 Test Fail | Misc | Alarm |  |  | 60 | Mask if F13-PO-445 = Manual mode | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Report to Maintenance. High solid contamination in SAG Mill lubrication oil | 1
F13BLC402_HOME | 2000-F13-PID-PR-10004 | F13BLC402 Homing Alarm | Misc | Homing Request Alarm |  |  | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to rehome ball charging system | 0
F13CR453_MXDUTY | 2000-F13-PID-PR-10004 | F13CR453 Max Duty | Misc | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate trolley max duty cycle event | 0
F13BLC402_MXDUTY | 2000-F13-PID-PR-10004 | F13BLC402 Max Duty | Misc | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Operator to investigate magnet max duty cycle event | 1 | 2025-07-15 | CR-028
F13BLC402_LOADA | 2000-F13-PID-PR-10004 | F13BLC402 Load Warning | Misc | Timer Elapsed |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Operator to investigate prolonged mill ball loading on magnet | 1 | 4/05/2025 15/07/2025 | "A" suffix added to end of timer alarms as per AH comment CR-028
F13FN419_OFF | 2000-F13-PID-PR-10001 | F13FN419 Stopped | Misc | Alarm |  |  | 0 |  | Personnel1: First Aid Injury, Reversible health effects | Prompt (>15 to <30 minutes) | Low | Operator to restart fan | 1 | 2025-04-29 | https://pastech-2955.atlassian.net/browse/KAN-1673
XC13250C | 2000-F13-PID-PR-10004 | F13BLC402 Fault | Digital Output | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Restart remotely if possible, else Advise Electrician to reset and monitor for recurring issues. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | 0
XC13250E | 2000-F13-PID-PR-10004 | F13CR453 Trolley O/load | Digital Output | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Restart remotely if possible, else Advise Electrician to reset and monitor for recurring issues. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | 0
XC13250F | 2000-F13-PID-PR-10004 | F13CR453 Hoist Overload | Digital Output | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Restart remotely if possible, else Advise Electrician to reset and monitor for recurring issues. Check magnet is unloaded else unload manually in local manual mode. Run auto homing sequence to home the trolley and hoist if required. | 0
XA13000A | 2000-F13-PID-PR-10001 | F13CV403 BRS Status | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Investigate belt rip sensor unhealthy alarm | 1 | 2025-03-06 | Variation NOFD153
XA13000B | 2000-F13-PID-PR-10001 | F13CV403 BRS Fault | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Investigate belt rip sensor fault alarm | 1 | 2025-03-06 | Variation NOFD153
XA13000C | 2000-F13-PID-PR-10001 | F13CV403 BRS Critical | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Investigate belt rip alarm | 1 | 2025-03-06 | Variation NOFD153
TI00010 | N/A | F13SR001 33kV SR Temp | Analogue Input | A_Hi | 30 | °C | 600 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 1 | 2025-06-25 | https://pastech-2955.atlassian.net/browse/PL-321
TI13040 | N/A | F13SR001 415V SR Temp | Analogue Input | A_Hi | 30 | °C | 600 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 1 | 2025-06-25 | https://pastech-2955.atlassian.net/browse/PL-321
TI13041 | N/A | F13SR001 415V SR TF | Analogue Input | A_Hi | 30 | °C | 600 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 1 | 2025-06-25 | https://pastech-2955.atlassian.net/browse/PL-321
TI13042 | N/A | F13SR002 415V SR Temp | Analogue Input | A_Hi | 30 | °C | 600 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 1 | 2025-06-25 | https://pastech-2955.atlassian.net/browse/PL-321
TI13043 | N/A | F13SR002 415V SR TF | Analogue Input | A_Hi | 30 | °C | 600 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 1 | 2025-06-25 | https://pastech-2955.atlassian.net/browse/PL-321
TI13044 | N/A | F13SR003 VSD SR Temp | Analogue Input | A_Hi | 30 | °C | 600 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 1 | 2025-06-25 | https://pastech-2955.atlassian.net/browse/PL-321
TI13045 | N/A | F13SR004 415V SR Temp | Analogue Input | A_Hi | 30 | °C | 600 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 1 | 2025-06-25 | https://pastech-2955.atlassian.net/browse/PL-321
TI13046 | N/A | F13SR004 415V SR TF | Analogue Input | A_Hi | 30 | °C | 600 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 1 | 2025-06-25 | https://pastech-2955.atlassian.net/browse/PL-321
TI13047 | N/A | F13SR005 415V SR Temp | Analogue Input | A_Hi | 30 | °C | 600 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 1 | 2025-06-25 | https://pastech-2955.atlassian.net/browse/PL-321
TI13048 | N/A | F13SR005 415V SR Temp TF | Analogue Input | A_Hi | 30 | °C | 600 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 1 | 2025-06-25 | https://pastech-2955.atlassian.net/browse/PL-321
FAH13207 | 2000-F24-PID-PR-10005 | F13SE404 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | 2025-07-01 | CR-019
FAH13208 | 2000-F24-PID-PR-10005 | F13SE408 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | 2025-07-01 | CR-019
PI13535 | 2000-F13-PID-PR-10002 | F13HU407 Hyd Supply | Analogue Input | A_Hi | 15000 | kPa | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise Maintenance or Field Operator to check F13HU407 hydraulic oil filter and/or investigate hydraulic skid for other issues. | 2 | 2025-07-03 | CR-021
PI13535 | 2000-F13-PID-PR-10002 | F13HU407 Hyd Supply | Analogue Input | A_HH | 16000 | kPa | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Maintenance or Field Operator to check F13HU407 hydraulic oil filter and/or investigate hydraulic skid for other issues. | 2 | 2025-07-03 | CR-021
TI13536 | 2000-F13-PID-PR-10002 | F13HU407 Hyd Reservoir | Analogue Input | A_Hi | 65 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise Maintenance or Field Operator to check F13HU407 hydraulic oil filter and/or investigate hydraulic skid for other issues. | 1 | 2025-07-03 | CR-021
TI13536 | 2000-F13-PID-PR-10002 | F13HU407 Hyd Reservoir | Analogue Input | A_HH | 70 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Maintenance or Field Operator to check F13HU407 hydraulic oil filter and/or investigate hydraulic skid for other issues. | 1 | 2025-07-03 | CR-021
LI13537 | 2000-F13-PID-PR-10002 | F13HU407 Hyd Reservoir | Analogue Input | A_LL | 50 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Maintenance or Field Operator to check F13HU407 hydraulic oil level and/or investigate hydraulic skid for other issues. | 1 | 2025-07-03 | CR-021
LI13537 | 2000-F13-PID-PR-10002 | F13HU407 Hyd Reservoir | Analogue Input | A_Lo | 60 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise Maintenance or Field Operator to check F13HU407 hydraulic oil level and/or investigate hydraulic skid for other issues. | 1 | 2025-07-03 | CR-021
PAH13538 | 2000-F13-PID-PR-10002 | F13HU407 Filter Blocked | Digital Input | Alarm (see comment) |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Maintenance or Field Operator to check F13HU407 hydraulic oil filter and/or investigate hydraulic skid for other issues. | 1 | 2025-07-03 | CR-021
F13TR002_WTH | - | F13TR002 Temp Hi | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrican to investigate high transformer winding temperature alarm | 1 | 2025-08-19 | CR-034
F13TR003_WTH | - | F13TR003 Temp Hi | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrican to investigate high transformer winding temperature alarm | 1 | 2025-08-19 | CR-034
F13TR014_WTH | - | F13TR014 Temp Hi | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrican to investigate high transformer winding temperature alarm | 1 | 2025-08-19 | CR-034
F13TR020_WTH | - | F13TR020 Temp Hi | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrican to investigate high transformer winding temperature alarm | 1 | 2025-08-19 | CR-034
F13XM421_ANS | 2000-F13-PID-PR-10003 | F13XM421 Install Error | Misc | Alarm |  |  | 20 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Inching drive install feedback error. Check proximity switches at SAG and Ball Mill inching drive soleplates. | 1 | 2025-08-20 | CR-045
XIC13135 | 2000-F13-PID-PR-10003 | F13MS401 IQ Volume | Analogue Input | A_Lo | 22 | % | 300 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Low volumetric fill. Check SAG Mill conditions. | 1 | 2025-10-06 | CR-052
XIC13135 | 2000-F13-PID-PR-10003 | F13MS401 IQ Volume | Analogue Input | A_Hi | 32 | % | 300 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | High volumetric fill. Check SAG Mill conditions. | 1 | 2025-10-06 | CR-052
JIC13136_LIM | 2000-F13-PID-PR-10003 | JIC13136 Limiter | Misc | Alarm |  |  |  |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | JIC13136 Output to SAG Mill speed limited due to high LoadIQ intensity, indicating potential mill ball impacts on liners. Check SAG Mill conditions. | 1 | 2025-10-06 | CR-052
F13GE103CBTRP | - | F13-GE-103 GEN CB TRP | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to manually change over generator | 1
F13GE114CBTRP | - | F13-GE-114 GEN CB TRP | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to manually change over generator | 1
13GE120CBTRP | - | F13-GE-120 GEN CB TRP | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to manually change over generator | 1

## 14. Cause & Effect
SAG MILL TAG | BALL MILL TAG | CAUSE | in inch mode, and not running | inch mode and running | inch mode, interlock | inch mode, estop | inch mode and brake in local, applied | inch mode and brake in local, released | normal mode | normal mode interlock | normal mode and estop | normal mode for local brake engaged | normal mode for local brake release
MS_OP_MODE = INCHING | MB_OP_MODE = INCHING | Inch Mode | Y | Y | Y | Y | Y | Y | N | N | N | N | N
MS_OP_MODE = NORMAL | MB_OP_MODE = NORMAL | Normal Mode | N | N | N | N | N | N | Y | Y | Y | Y | Y
HS13737MODE = LOCAL | HS13748MODE = LOCAL | Brake Local | N | . | . | . | Y | Y | N | . | . | Y | Y
HS13737MODE = AUTOMATIC | HS13748MODE = AUTOMATIC | Brake Auto | Y | . | . | . | N | N | Y | . | . | N | N
HS13738BRK = ENGAGE | HS13749BRK = ENGAGE | Local Brake On | . | . | . | . | Y | N | . | . | . | Y | N
HS13738BRK = RELEASE | HS13749BRK = RELEASE | Local Brake Release | . | . | . | . | N | Y | . | . | . | N | Y
MS_ESTOP | MB_ESTOP | Estop | . | . | . | Y | . | . | N | . | Y | . | N
MS_CR_ILK | MB_CR_ILK | Interlock | . | . | Y | . | . | . | N | Y | . | . | N
MS_SIREN_REQ (Falling Edge) | MB_SIREN_REQ (Falling Edge) | Siren Complete (one shot) | . | Y | . | . | . | . | . | . | . | . | .
MS_RUNNING = NOT RUNNING | MB_RUNNING = NOT RUNNING | Stopped | Y | . | . | . | . | . | . | . | . | Y | .
(ZSH13545 OR ZSH13547 = Inactive (Brake Engaged) OR SV13561 = Denergised OR SV13562 = Deenergised) | (ZSH13795 OR ZSH13797 = Inactive (Brake Engaged) OR SV13812 = Energised OR SV13813 = Deenergised) | Park Brake Engaged | . | . | . | . | . | . | . | N | N | . | .
EFFECT
MS_EN_BRK | MB_EN_BRK | Park Brake | Y | N | Y | Y | Y | N | N | N | N | Y | N
MS_2S_BRK | MB_2S_BRK | 2 Stage Brake | N | N | N | N | N | N | N | Y | Y | N | N
MS_RL_BRK | MB_RL_BRK | Brake Released | N | Y | N | N | N | Y |  | N | N | N | Y

## RiskMatrix
Consequence | None | Personnel1: First Aid Injury, Reversible health effects | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Environmental2: Minor on-site environmental impact, reportable to regulators. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness. | Environmental3: Moderate environmental impacts, extends beyond site boundary or regulatory violations with fines. | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k
Not Urgent (>30 minutes) | No Alarm | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Low \ Review the alarm for urgency | Low \ Review the alarm for urgency | Low \ Review the alarm for urgency | High \ Review the alarm for urgency | High \ Review the alarm for urgency | High \ Review the alarm for urgency
Prompt (>15 to <30 minutes) | No Alarm | Low | Low | Low | Low | Low | Low | High | High | High
Rapid (>5 to <15 minutes) | No Alarm | Low | Low | Low | High | High | High | Urgent | Urgent | Urgent
Immediate (<5 minutes) | No Alarm | High | High | High | Urgent | Urgent | Urgent | Invalid | Invalid | Invalid
Plant Tripped | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Logging | Logging | Logging | Logging | Logging | Logging | Logging | Logging | Logging
|  | Priority | Description
|  | Low | Indicates that the process in no longer within nominal operational limits and a prompt operator intervention is required before the process becomes unrecoverable, resulting in minor safety, environmental or financial impacts.
|  | High | Indicates that the process is no longer within nominal operational limits and a rapid operator intervention is required before the process becomes unrecoverable resulting in serious safety, environmental or financial impacts.
|  | Urgent | Indicates that the process is no longer within nominal operational limits and a immediate operator intervention is required before the process becomes unrecoverable resulting in catastrophic safety, environmental or financial impacts.
|  | Logging | Indicates that the process or equipment has reached a unrecoverable or inoperable state and has been stopped. Logging alarms are for post event investigation and are not to enunciate to the operator.
|  | No Alarm | This condition does not meet the minimum requirements required under ISA 18.2 for a alarm to be generated. Including being a abnormal event\condition, requiring an operator response, undertaking a defined action within a defined time limit and having a defined consequences of no action is taken.
|  | Invalid | This senario is likely to be already unrecovreable and as such is unacceptable. Additional solutions such as automated repsonses, re-engeering or modifications the the process \ equipment is required.

## ReferenceList
Consequences
None
Personnel1: First Aid Injury, Reversible health effects
Environmental1: Localised environmental impact, contained, with no regulatory reporting
Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000
Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment.
Environmental2: Minor on-site environmental impact, reportable to regulators.
Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k.
Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness.
Environmental3: Moderate environmental impacts, extends beyond site boundary or regulatory violations with fines.
Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k
Type
Analogue
Digital
Alarm State
High-High
High
Low
Low-Low
Active