## Revisions
PROCESS CONTROL TABLES
REVISION HISTORY
KCGM GROWTH PROJECT
2000-F16-LST-PR-10001
NORTHERN STAR RESOURCES LIMITED
Revision | Document Changes | Date
A for Sequence Flowchart Review Only | - Yellow highlight indicates TBC | 2023-12-14
- Does not include the remainder of the Process Control Tables
B for Internal Review | - Yellow highlight indicates TBC | 2024-04-16
C for Client Review | - Yellow highlight indicates TBC | 2024-05-28
0 for Design | - Yellow highlight indicates TBC | 2024-07-19
1 for Design | - Yellow highlight indicates TBC | 2024-08-28
- Revision 2 changes highlighted in light orange
- Revision aligns with Rev 0 P&IDs for Areas F16,17,18
2 for Design | - Yellow highlight indicates TBC | 2024-11-01
- Revision 2 changes highlighted in light orange
3 for Post-FAT Updates | - Revision 3 changes highlighted in orange | 2025-10-17
- Strikethrough indicates removal from design
5 Prepared for SAT | - Remove strikethough text and highlighting
Operator to get electrician to inspect unit for potential failure

## 1. Analogue Input
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION (F16, F17, F18)
2000-F16-LST-PR-10001
ANALOGUE INSTRUMENTS (AI)
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [10 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date | Comments
|  |  |  | FIT16001 | FI16001 | 2000-F16-PID-PR-10001 | F16-CF-411 Rougher Flotation Cell 1 Process Water Flow Indicating Transmitter | Flotation HP Prcss Water | 1 | 0 | 1700 | m3/h | [14 empty] | 200 | 5 | 500 | 5 |  |  | DUTY F24PW417/418 NOT RUNNING Alarm enabled delay of 20 seconds on HP Process Water Pump start-up (duration to be confirmed during commissioning). | Alarm setpoints to be confirmed during commissioning. | 3 |  |  |  |  | Range changed by sparky darren from 700 m3/hr to 1700m3/hr 24/08/2026
|  |  |  | PIT16012 | PI16012 | 2000-F16-PID-PR-10001 | F16-CF-411 Rougher Flotation Cell 1 Low Pressure Air Pressure Transmitter | F16CF411 Blower Air | 1 | 0 | 500 | kPa | [14 empty] | 90 | 5 | 130 | 5 |  |  | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Nominal pressure: 104.5 kPa(g) Maximum pressure: 119.7 kPa(g) Alarm setpoints to be confirmed during commissioning. . | 3
|  |  |  | TT16014 | TI16014 | 2000-F16-PID-PR-10001 | F16-CF-411 Rougher Flotation Cell 1 Gear Box Oil Temperature Transmitter | F16CF411 G/Box Oil | 1 | -50 | 200 | °C | 15 | 5 |  | 23 | 5 |  | 55 | 5 |  | 65 | 5 | [5 empty] | 80 | 5 | 90 | 5 |  | Source: 2000-ME001.4-F16-50001 and 2000-ME001.4-M02-50001. P_HH > F16-FN-497 turns on P_Hi < F16-FN-497 turns off P_Lo > F16-HT-562 and F16-HT-563 turns off P_LL < F16-HT-562 and F16-HT-563 turns on A_Hi > Alarm - inspection of gear unit required A_HH > F16-AG-421 trips | 3
|  |  |  | PT16015 | PI16015 | 2000-F16-PID-PR-10001 | F16-CF-411 Rougher Flotation Cell 1 Gear Box Oil Pressure Transmitter | F16CF411 G/Box Oil | 1 | -101 | 1034 | kPa | [12 empty] | 50 | 5 | 70 | 5 | 800 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-421 start-up. | Source: 2000-ME001.4-M02-50001. A_Hi > Alarm - inspection of gearbox required A_Lo < Alarm - inspection of gearbox required A_LL < Agitator Trip | 3 |  |  |  |  | MOC 605
|  |  |  | PDIT16018 | PDI16018 | 2000-F16-PID-PR-10001 | F16-CF-411 Rougher Flotation Cell 1 Gear Box Filter Pressure Differential Transmitter | F16CF411 G/Box Fltr Dlta | 1 | -100 | 600 | kPa | [16 empty] | 200 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-421 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16019 | VI16019 | 2000-F16-PID-PR-10001 | F16-CF-411 ROUGHER FLOTATION CELL 1 GEAR BOX INPUT SHAFT VIBRATION TRANSMITTER | F16CF411 G/Box In | 1 | 0 | 15 | mm/s | [16 empty] | 8 | 5 | 12 | 5 | Alarm enabled delay of 10 seconds on F16-AG-421 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16020 | VI16020 | 2000-F16-PID-PR-10001 | F16-CF-411 ROUGHER FLOTATION CELL 1 GEAR BOX OUTPUT SHAFT VIBRATION TRANSMITTER | F16CF411 G/Box Out | 1 | 0 | 15 | mm/s | [16 empty] | 4 | 5 | 7.1 | 5 | Alarm enabled delay of 10 seconds on F16-AG-421 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | PIT16052 | PI16052 | 2000-F16-PID-PR-10002 | F16-CF-412 Rougher Flotation Cell 2 Low Pressure Air Pressure Transmitter | F16CF412 Blower Air | 1 | 0 | 500 | kPa | [14 empty] | 90 | 5 | 130 | 5 |  |  | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Nominal pressure: 104.5 kPa(g) Maximum pressure: 119.7 kPa(g) Alarm setpoints to be confirmed during commissioning. . | 3
|  |  |  | TT16054 | TI16054 | 2000-F16-PID-PR-10002 | F16-CF-412 Rougher Flotation Cell 2 Gear Box Oil Temperature Transmitter | F16CF412 G/Box Oil | 1 | -50 | 200 | °C | 15 | 5 |  | 23 | 5 |  | 55 | 5 |  | 65 | 5 | [5 empty] | 80 | 5 | 90 | 5 |  | Source: 2000-ME001.4-F16-50001 and 2000-ME001.4-M02-50001. P_HH ≥ F16-FN-498 turns on P_Hi ≤ F16-FN-498 turns off P_Lo ≥ F16-HT-564 and F16-HT-565 turns off P_LL ≤ F16-HT-564 and F16-HT-565 turns on A_Hi ≥ Alarm - inspection of gear unit required A_HH ≥ F16-AG-422 trips | 3
|  |  |  | PT16055 | PI16055 | 2000-F16-PID-PR-10002 | F16-CF-412 Rougher Flotation Cell 2 Gear Box Oil Pressure Transmitter | F16CF412 G/Box Oil | 1 | -101 | 1034 | kPa | [12 empty] | 50 | 5 | 70 | 5 | 800 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-422 start-up. | Source: 2000-ME001.4-M02-50001. A_Hi > Alarm - inspection of gearbox required A_Lo < Alarm - inspection of gearbox required A_LL < Agitator Trip | 3 |  |  |  |  | MOC605
|  |  |  | PDIT16058 | PDI16058 | 2000-F16-PID-PR-10002 | F16-CF-412 Rougher Flotation Cell 2 Gear Box Filter Pressure Differential Transmitter | F16CF412 G/Box Fltr Dlta | 1 | -100 | 600 | kPa | [16 empty] | 200 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-422 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16059 | VI16059 | 2000-F16-PID-PR-10002 | F16-CF-412 ROUGHER FLOTATION CELL 2 GEAR BOX INPUT SHAFT VIBRATION TRANSMITTER | F16CF412 G/Box In | 1 | 0 | 15 | mm/s | [16 empty] | 8 | 5 | 12 | 5 | Alarm enabled delay of 10 seconds on F16-AG-422 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16060 | VI16060 | 2000-F16-PID-PR-10002 | F16-CF-412 ROUGHER FLOTATION CELL 2 GEAR BOX OUTPUT SHAFT VIBRATION TRANSMITTER | F16CF412 G/Box Out | 1 | 0 | 15 | mm/s | [16 empty] | 4 | 5 | 7.1 | 5 | Alarm enabled delay of 10 seconds on F16-AG-422 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | PIT16062 | PI16062 | 2000-F16-PID-PR-10002 | F16-CF-413 Rougher Flotation Cell 3 Low Pressure Air Pressure Transmitter | F16CF413 Blower Air | 1 | 0 | 500 | kPa | [14 empty] | 90 | 5 | 130 | 5 |  |  | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Nominal pressure: 104.5 kPa(g) Maximum pressure: 119.7 kPa(g) Alarm setpoints to be confirmed during commissioning. | 3
|  |  |  | TT16064 | TI16064 | 2000-F16-PID-PR-10002 | 8 | F16CF413 G/Box Oil | 1 | -50 | 200 | °C | 15 | 5 |  | 23 | 5 |  | 55 | 5 |  | 65 | 5 | [5 empty] | 80 | 5 | 90 | 5 |  | Source: 2000-ME001.4-F16-50001 and 2000-ME001.4-M02-50001. P_HH ≥ F16-FN-499 turns on P_Hi ≤ F16-FN-499 turns off P_Lo ≥ F16-HT-566 and F16-HT-567 turns off P_LL ≤ F16-HT-566 and F16-HT-567 turns on A_Hi ≥ Alarm - inspection of gear unit required A_HH ≥ F16-AG-423 trips | 3
|  |  |  | PT16065 | PI16065 | 2000-F16-PID-PR-10002 | F16-CF-413 Rougher Flotation Cell 3 Gear Box Oil Pressure Transmitter | F16CF413 G/Box Oil | 1 | -101 | 1034 | kPa | [12 empty] | 50 | 5 | 70 | 5 | 800 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-423 start-up. | Source: 2000-ME001.4-M02-50001. A_Hi > Alarm - inspection of gearbox required A_Lo < Alarm - inspection of gearbox required A_LL < Agitator Trip | 3 |  |  |  |  | MOC-605
|  |  |  | PDIT16068 | PDI16068 | 2000-F16-PID-PR-10002 | F16-CF-413 Rougher Flotation Cell 3 Gear Box Filter Pressure Differential Transmitter | F16CF413 G/Box Fltr Dlta | 1 | -100 | 600 | kPa | [16 empty] | 200 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-423 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16069 | VI16069 | 2000-F16-PID-PR-10002 | F16-CF-413 ROUGHER FLOTATION CELL 3 GEAR BOX INPUT SHAFT VIBRATION TRANSMITTER | F16CF413 G/Box In | 1 | 0 | 15 | mm/s | [16 empty] | 8 | 5 | 12 | 5 | Alarm enabled delay of 10 seconds on F16-AG-423 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16070 | VI16070 | 2000-F16-PID-PR-10002 | F16-CF-413 ROUGHER FLOTATION CELL 3 GEAR BOX OUTPUT SHAFT VIBRATION TRANSMITTER | F16CF413 G/Box Out | 1 | 0 | 15 | mm/s | [16 empty] | 4 | 5 | 7.1 | 5 | Alarm enabled delay of 10 seconds on F16-AG-423 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | PIT16082 | PI16082 | 2000-F16-PID-PR-10003 | F16-CF-414 Scavenger Flotation Cell 1 Low Pressure Air Pressure Indicating Transmitter | F16CF414 Blower Air | 1 | 0 | 500 | kPa | [14 empty] | 90 | 5 | 130 | 5 |  |  | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Nominal pressure: 104.5 kPa(g) Maximum pressure: 119.7 kPa(g) Alarm setpoints to be confirmed during commissioning. . | 3
|  |  |  | TT16084 | TI16084 | 2000-F16-PID-PR-10003 | F16-CF-414 Scavenger Flotation Cell 1 Gear Box Oil Temperature Transmitter | F16CF414 G/Box Oil | 1 | -50 | 200 | °C | 15 | 5 |  | 23 | 5 |  | 55 | 5 |  | 65 | 5 | [5 empty] | 80 | 5 | 90 | 5 |  | Source: 2000-ME001.4-F16-50001 and 2000-ME001.4-M02-50001. P_HH ≥ F16-FN-500 turns on P_Hi ≤ F16-FN-500 turns off P_Lo ≥ F16-HT-568 and F16-HT-569 turns off P_LL ≤ F16-HT-568 and F16-HT-569 turns on A_Hi ≥ Alarm - inspection of gear unit required A_HH ≥ F16-AG-424 trips | 3
|  |  |  | PT16085 | PI16085 | 2000-F16-PID-PR-10003 | F16-CF-414 Scavenger Flotation Cell 1 Gear Box Oil Pressure Transmitter | F16CF414 G/Box Oil | 1 | -101 | 1034 | kPa | [12 empty] | 50 | 5 | 70 | 5 | 800 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-424 start-up. | Source: 2000-ME001.4-M02-50001. A_Hi > Alarm - inspection of gearbox required A_Lo < Alarm - inspection of gearbox required A_LL < Agitator Trip | 3 |  |  |  |  | MOC-605
|  |  |  | PDIT16088 | PDI16088 | 2000-F16-PID-PR-10003 | F16-CF-414 Scavenger Flotation Cell 1 Gear Box Filter Pressure Differential Transmitter | F16CF414 G/Box Fltr Dlta | 1 | -100 | 600 | kPa | [16 empty] | 200 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-424 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16089 | VI16089 | 2000-F16-PID-PR-10003 | F16-CF-414 SCAVENGER FLOTATION CELL 1 GEAR BOX INPUT SHAFT VIBRATION TRANSMITTER | F16CF414 G/Box In | 1 | 0 | 15 | mm/s | [16 empty] | 8 | 5 | 12 | 5 | Alarm enabled delay of 10 seconds on F16-AG-424 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16090 | VI16090 | 2000-F16-PID-PR-10003 | F16-CF-414 SCAVENGER FLOTATION CELL 1 GEAR BOX OUTPUT SHAFT VIBRATION TRANSMITTER | F16CF414 G/Box Out | 1 | 0 | 15 | mm/s | [16 empty] | 4 | 5 | 7.1 | 5 | Alarm enabled delay of 10 seconds on F16-AG-424 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | PIT16092 | PI16092 | 2000-F16-PID-PR-10003 | F16-CF-415 Scavenger Flotation Cell 2 Low Pressure Air Pressure Indicating Transmitter | F16CF415 Blower Air | 1 | 0 | 500 | kPa | [14 empty] | 90 | 5 | 130 | 5 |  |  | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Nominal pressure: 104.5 kPa(g) Maximum pressure: 119.7 kPa(g) Alarm setpoints to be confirmed during commissioning. . | 3
|  |  |  | TT16094 | TI16094 | 2000-F16-PID-PR-10003 | F16-CF-415 Scavenger Flotation Cell 2 Gear Box Oil Temperature Transmitter | F16CF415 G/Box Oil | 1 | -50 | 200 | °C | 15 | 5 |  | 23 | 5 |  | 55 | 5 |  | 65 | 5 | [5 empty] | 80 | 5 | 90 | 5 |  | Source: 2000-ME001.4-F16-50001 and 2000-ME001.4-M02-50001. P_HH ≥ F16-FN-501 turns on P_Hi ≤ F16-FN-501 turns off P_Lo ≥ F16-HT-570 and F16-HT-571 turns off P_LL ≤ F16-HT-570 and F16-HT-571 turns on A_Hi ≥ Alarm - inspection of gear unit required A_HH ≥ F16-AG-425 trips | 3
|  |  |  | PT16095 | PI16095 | 2000-F16-PID-PR-10003 | F16-CF-415 Scavenger Flotation Cell 2 Gear Box Oil Pressure Transmitter | F16CF415 G/Box Oil | 1 | -101 | 1034 | kPa | [12 empty] | 50 | 5 | 70 | 5 | 800 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-425 start-up. | Source: 2000-ME001.4-M02-50001. A_Hi > Alarm - inspection of gearbox required A_Lo < Alarm - inspection of gearbox required A_LL < Agitator Trip | 3 |  |  |  |  | MOC605
|  |  |  | PDIT16098 | PDI16098 | 2000-F16-PID-PR-10003 | F16-CF-415 Scavenger Flotation Cell 2 Gear Box Filter Pressure Differential Transmitter | F16CF415 G/Box Fltr Dlta | 1 | -100 | 600 | kPa | [16 empty] | 200 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-425 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16099 | VI16099 | 2000-F16-PID-PR-10003 | F16-CF-415 SCAVENGER FLOTATION CELL 2 GEAR BOX INPUT SHAFT VIBRATION TRANSMITTER | F16CF415 G/Box In | 1 | 0 | 15 | mm/s | [16 empty] | 8 | 5 | 12 | 5 | Alarm enabled delay of 10 seconds on F16-AG-425 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16100 | VI16100 | 2000-F16-PID-PR-10003 | F16-CF-415 SCAVENGER FLOTATION CELL 2 GEAR BOX OUTPUT SHAFT VIBRATION TRANSMITTER | F16CF415 G/Box Out | 1 | 0 | 15 | mm/s | [16 empty] | 4 | 5 | 7.1 | 5 | Alarm enabled delay of 10 seconds on F16-AG-425 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | PIT16102 | PI16102 | 2000-F16-PID-PR-10003 | F16-CF-416 Scavenger Flotation Cell 3 Low Pressure Air Pressure Indicating Transmitter | F16CF416 Blower Air | 1 | 0 | 500 | kPa | [14 empty] | 90 | 5 | 130 | 5 |  |  | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Nominal pressure: 104.5 kPa(g) Maximum pressure: 119.7 kPa(g) Alarm setpoints to be confirmed during commissioning. . | 3
|  |  |  | TT16104 | TI16104 | 2000-F16-PID-PR-10003 | F16-CF-416 Scavenger Flotation Cell 3 Gear Box Oil Temperature Transmitter | F16CF416 G/Box Oil | 1 | -50 | 200 | °C | 15 | 5 |  | 23 | 5 |  | 55 | 5 |  | 65 | 5 | [5 empty] | 80 | 5 | 90 | 5 |  | Source: 2000-ME001.4-F16-50001 and 2000-ME001.4-M02-50001. P_HH > F16-FN-502 turns on P_Hi < F16-FN-502 turns off P_Lo > F16-HT-572 and F16-HT-573 turns off P_LL < F16-HT-572 and F16-HT-573 turns on A_Hi > Alarm - inspection of gear unit required A_HH > F16-AG-426 trips | 3
|  |  |  | PT16105 | PI16105 | 2000-F16-PID-PR-10003 | F16-CF-416 Scavenger Flotation Cell 3 Gear Box Oil Pressure Transmitter | F16CF416 G/Box Oil | 1 | -101 | 1034 | kPa | [12 empty] | 50 | 5 | 70 | 5 | 800 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-426 start-up. | Source: 2000-ME001.4-M02-50001. A_Hi > Alarm - inspection of gearbox required A_Lo < Alarm - inspection of gearbox required A_LL < Agitator Trip | 3 |  |  |  |  | MOC-605
|  |  |  | PDIT16108 | PDI16108 | 2000-F16-PID-PR-10003 | F16-CF-416 Scavenger Flotation Cell 3 Gear Box Filter Pressure Differential Transmitter | F16CF416 G/Box Fltr Dlta | 1 | -100 | 600 | kPa | [16 empty] | 200 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-426 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16109 | VI16109 | 2000-F16-PID-PR-10003 | F16-CF-416 SCAVENGER FLOTATION CELL 3 GEAR BOX INPUT SHAFT VIBRATION TRANSMITTER | F16CF416 G/Box In | 1 | 0 | 15 | mm/s | [16 empty] | 8 | 5 | 12 | 5 | Alarm enabled delay of 10 seconds on F16-AG-426 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16110 | VI16110 | 2000-F16-PID-PR-10003 | F16-CF-416 SCAVENGER FLOTATION CELL 3 GEAR BOX OUTPUT SHAFT VIBRATION TRANSMITTER | F16CF416 G/Box Out | 1 | 0 | 15 | mm/s | [16 empty] | 4 | 5 | 7.1 | 5 | Alarm enabled delay of 10 seconds on F16-AG-426 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | PIT16112 | PI16112 | 2000-F16-PID-PR-10003 | F16-CF-417 Scavenger Flotation Cell 4 Low Pressure Air Pressure Indicating Transmitter | F16CF417 Blower Air | 1 | 0 | 500 | kPa | [14 empty] | 90 | 5 | 130 | 5 |  |  | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Nominal pressure: 104.5 kPa(g) Maximum pressure: 119.7 kPa(g) Alarm setpoints to be confirmed during commissioning. . | 3
|  |  |  | TT16114 | TI16114 | 2000-F16-PID-PR-10003 | F16-CF-417 Scavenger Flotation Cell 4 Gear Box Temperature Transmitter | F16CF417 G/Box Oil | 1 | -50 | 200 | °C | 15 | 5 |  | 23 | 5 |  | 55 | 5 |  | 65 | 5 | [5 empty] | 80 | 5 | 90 | 5 |  | Source: 2000-ME001.4-F16-50001 and 2000-ME001.4-M02-50001. P_HH > F16-FN-503 turns on P_Hi < F16-FN-503 turns off P_Lo > F16-HT-574 and F16-HT-575 turns off P_LL < F16-HT-574 and F16-HT-575 turns on A_Hi > Alarm - inspection of gear unit required A_HH > F16-AG-427 trips | 3
|  |  |  | PT16115 | PI16115 | 2000-F16-PID-PR-10003 | F16-CF-417 Scavenger Flotation Cell 4 Gear Box Pressure Transmitter | F16CF417 G/Box Oil | 1 | -101 | 1034 | kPa | [12 empty] | 50 | 5 | 70 | 5 | 800 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-427 start-up. | Source: 2000-ME001.4-M02-50001. A_Hi > Alarm - inspection of gearbox required A_Lo < Alarm - inspection of gearbox required A_LL < Agitator Trip | 3 |  |  |  |  | MOC-605
|  |  |  | PDIT16118 | PDI16118 | 2000-F16-PID-PR-10003 | F16-CF-417 Scavenger Flotation Cell 4 Gear Box Filter Pressure Differential Transmitter | F16CF417 G/Box Fltr Dlta | 1 | -100 | 600 | kPa | [16 empty] | 200 | 5 |  |  | Alarm enabled delay of 10 seconds on F16-AG-427 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16119 | VI16119 | 2000-F16-PID-PR-10003 | F16-CF-417 SCAVENGER FLOTATION CELL 4 GEAR BOX INPUT SHAFT VIBRATION TRANSMITTER | F16CF417 G/Box In | 1 | 0 | 15 | mm/s | [16 empty] | 8 | 5 | 12 | 5 | Alarm enabled delay of 10 seconds on F16-AG-427 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | VT16120 | VI16120 | 2000-F16-PID-PR-10003 | F16-CF-417 SCAVENGER FLOTATION CELL 4 GEAR BOX OUTPUT SHAFT VIBRATION TRANSMITTER | F16CF417 G/Box Out | 1 | 0 | 15 | mm/s | [16 empty] | 4 | 5 | 7.1 | 5 | Alarm enabled delay of 10 seconds on F16-AG-427 start-up. | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | PT16182 | PI16182 | 2000-F24-PID-PR-10008 | F16-RA-402 Flotation/Thickener Air Receiver Outlet Pressure Indicating Transmitter | F16RA402 Discharge | 1 | 0 | 1000 | kPa | [14 empty] | 600 | 5 | 980 | 5 |  |  | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are stopped Mask A_Lo for 30 seconds during F24-CM-401, 402 OR 403 start up Duration to be confirmed during commissioning. | A_Hi = Warning A_Lo = Warning Normal operating = 9.8 bar Maximum operating pressure = 10 bar Minimum system outlet pressure = 6 bar Nominal values and alarm setpoints to be confirmed during commissioning. | 4 |  |  |  |  | VG: Alarm masking not tested yet
|  |  |  | TE16198A | TI16198A | 2000-F16-PID-PR-10006 | F16-BW-401 Flotation Blower 1 Motor Phase U RTD | F16BW401 Motor P.U RTD | 1 | -5 | 200 | °C | [16 empty] | 130 | 5 | 155 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-401 | 1
|  |  |  | TE16198B | TI16198B | 2000-F16-PID-PR-10006 | F16-BW-401 Flotation Blower 1 Motor Phase V RTD | F16BW401 Motor P.V RTD | 1 | -5 | 200 | °C | [16 empty] | 130 | 5 | 155 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-401 | 1
|  |  |  | TE16198C | TI16198C | 2000-F16-PID-PR-10006 | F16-BW-401 Flotation Blower 1 Motor Phase W RTD | F16BW401 Motor P.W RTD | 1 | -5 | 200 | °C | [16 empty] | 130 | 5 | 155 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-401 | 1
|  |  |  | TE16198D | TI16198D | 2000-F16-PID-PR-10006 | F16-BW-401 Flotation Blower 1 Motor DE Bearing RTD | F16BW401 Mtr DE Brg RTD | 1 | -5 | 200 | °C | [16 empty] | 90 | 5 | 110 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-401 | 1
|  |  |  | TE16198E | TI16198E | 2000-F16-PID-PR-10006 | F16-BW-401 Flotation Blower 1 Motor NDE Bearing RTD | F16BW401 Mtr NDE Brg RTD | 1 | -5 | 200 | °C | [16 empty] | 90 | 5 | 110 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-401 | 1
|  |  |  | PT16261 | PI16261 | 2000-F16-PID-PR-10006 | F16-BW-401 Flotation Blower 1 Inlet Pressure Indicating Transmitter | F16BW401 Blower 1 Inlet | 1 | -100 | 150 | kPa | [12 empty] | -8 | 5 | -6 | 5 |  |  |  |  | F16BW401 NOT RUNNING | Source: Vendor document 2000-ME001.4-M02-50001. A_Lo = Alarm A_LL = F16-BW-401 Trip | 3
|  |  |  | TT16263 | TI16263 | 2000-F16-PID-PR-10006 | F16-BW-401 Flotation Blower 1 Outlet Temperature Transmitter | F16BW401 Blower 1 Outlet | 1 | -50 | 200 | °C | [16 empty] | 172 | 5 | 177 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-401 | C
|  |  |  | TT16264 | TI16264 | 2000-F16-PID-PR-10006 | F16-BW-401 Flotation Blower 1 Gearbox Temperature Transmitter | F16BW401 Blower 1 G/Box | 1 | -50 | 200 | °C | [16 empty] | 113 | 5 | 118 | 5 |  | Source: Vendor document: 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-401 | C
|  |  |  | TT16265 | TI16265 | 2000-F16-PID-PR-10006 | F16-BW-401 Flotation Blower 1 Temperature Transmitter | F16BW401 Blower 1 | 1 | -50 | 200 | °C | [16 empty] | 50 | 5 | 52 | 5 |  | Blower 1 enclosure temperature. Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-401 | C
|  |  |  | TE16208A | TI16208A | 2000-F16-PID-PR-10006 | F16-BW-402 Flotation Blower 2 Motor Phase U RTD | F16BW402 Motor P.U RTD | 1 | -5 | 200 | °C | [16 empty] | 130 | 5 | 155 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-402 | C
|  |  |  | TE16208B | TI16208B | 2000-F16-PID-PR-10006 | F16-BW-402 Flotation Blower 2 Motor Phase V RTD | F16BW402 Motor P.V RTD | 1 | -5 | 200 | °C | [16 empty] | 130 | 5 | 155 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-402 | C
|  |  |  | TE16208C | TI16208C | 2000-F16-PID-PR-10006 | F16-BW-402 Flotation Blower 2 Motor Phase W RTD | F16BW402 Motor P.W RTD | 1 | -5 | 200 | °C | [16 empty] | 130 | 5 | 155 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-402 | C
|  |  |  | TE16208D | TI16208D | 2000-F16-PID-PR-10006 | F16-BW-402 Flotation Blower 2 Motor DE Bearing RTD | F16BW402 DE Bearing RTD | 1 | -5 | 200 | °C | [16 empty] | 90 | 5 | 110 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-402 | 1
|  |  |  | TE16208E | TI16208E | 2000-F16-PID-PR-10006 | F16-BW-402 Flotation Blower 2 Motor NDE Bearing RTD | F16BW402 NDE Bearing RTD | 1 | -5 | 200 | °C | [16 empty] | 90 | 5 | 110 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-402 | 1
|  |  |  | PT16271 | PI16271 | 2000-F16-PID-PR-10006 | F16-BW-402 Flotation Blower 2 Inlet Pressure Indicating Transmitter | F16BW402 Blower 2 Inlet | 1 | -100 | 150 | kPa | [12 empty] | -8 | 5 | -6 | 5 |  |  |  |  | F16BW402 NOT RUNNING | Source: Vendor document 2000-ME001.4-M02-50001. A_Lo = Alarm A_LL = F16-BW-402 Trip | 3
|  |  |  | TT16273 | TI16273 | 2000-F16-PID-PR-10006 | F16-BW-402 Flotation Blower 2 Outlet Temperature Transmitter | F16BW402 Blower 2 Outlet | 1 | -50 | 200 | °C | [16 empty] | 172 | 5 | 177 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-402 | C
|  |  |  | TT16274 | TI16274 | 2000-F16-PID-PR-10006 | F16-BW-402 Flotation Blower 2 Gearbox Temperature Transmitter | F16BW402 Blower 2 G/Box | 1 | -50 | 200 | °C | [16 empty] | 113 | 5 | 118 | 5 |  | Source: Vendor document: 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-402 | C
|  |  |  | TT16275 | TI16275 | 2000-F16-PID-PR-10006 | F16-BW-402 Flotation Blower 2 Temperature Transmitter | F16BW402 Blower 2 | 1 | -50 | 200 | °C | [16 empty] | 50 | 5 | 52 | 5 |  | Blower 2 enclosure temperature. Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-402 | C
|  |  |  | TE16218A | TI16218A | 2000-F16-PID-PR-10006 | F16-BW-403 Flotation Blower 3 Motor Phase U RTD | F16BW403 Motor P.U RTD | 1 | -5 | 200 | °C | [16 empty] | 130 | 5 | 155 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-403 | C
|  |  |  | TE16218B | TI16218B | 2000-F16-PID-PR-10006 | F16-BW-403 Flotation Blower 3 Motor Phase V RTD | F16BW403 Motor P.V RTD | 1 | -5 | 200 | °C | [16 empty] | 130 | 5 | 155 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-403 | C
|  |  |  | TE16218C | TI16218C | 2000-F16-PID-PR-10006 | F16-BW-403 Flotation Blower 3 Motor Phase W RTD | F16BW403 Motor P.W RTD | 1 | -5 | 200 | °C | [16 empty] | 130 | 5 | 155 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-403 | C
|  |  |  | TE16218D | TI16218D | 2000-F16-PID-PR-10006 | F16-BW-403 Flotation Blower 3 Motor DE Bearing RTD | F16BW403 DE Bearing RTD | 1 | -5 | 200 | °C | [16 empty] | 90 | 5 | 110 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-403 | 1
|  |  |  | TE16218E | TI16218E | 2000-F16-PID-PR-10006 | F16-BW-403 Flotation Blower 3 Motor NDE Bearing RTD | F16BW403 NDE Bearing RTD | 1 | -5 | 200 | °C | [16 empty] | 90 | 5 | 110 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-403 | 1
|  |  |  | PT16281 | PI16281 | 2000-F16-PID-PR-10006 | F16-BW-403 Flotation Blower 3 Inlet Pressure Indicating Transmitter | F16BW403 Blower 3 Inlet | 1 | -100 | 150 | kPa | [12 empty] | -8 | 5 | -6 | 5 |  |  |  |  | F16BW403 NOT RUNNING | Source: Vendor document 2000-ME001.4-M02-50001. A_Lo = Alarm A_LL = F16-BW-403 Trip | 3
|  |  |  | TT16283 | TI16283 | 2000-F16-PID-PR-10006 | F16-BW-403 Flotation Blower 3 Outlet Temperature Transmitter | F16BW403 Blower 3 Outlet | 1 | -50 | 200 | °C | [16 empty] | 172 | 5 | 177 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-403 | C
|  |  |  | TT16284 | TI16284 | 2000-F16-PID-PR-10006 | F16-BW-403 Flotation Blower 3 Gearbox Temperature Transmitter | F16BW403 Blower 3 G/Box | 1 | -50 | 200 | °C | [16 empty] | 113 | 5 | 118 | 5 |  | Source: Vendor document: 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-403 | C
|  |  |  | TT16285 | TI16285 | 2000-F16-PID-PR-10006 | F16-BW-403 Flotation Blower 3 Temperature Transmitter | F16BW403 Blower 3 | 1 | -50 | 200 | °C | [16 empty] | 50 | 5 | 52 | 5 |  | Blower 3 enclosure temperature. Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-403 | C
|  |  |  | TE16228A | TI16228A | 2000-F16-PID-PR-10006 | F16-BW-404 Flotation Blower 4 Motor Phase U RTD | F16BW404 Motor P.U RTD | 1 | -5 | 200 | °C | [16 empty] | 130 | 5 | 155 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-404 | 3 |  |  |  |  | offset done and checked good
|  |  |  | TE16228B | TI16228B | 2000-F16-PID-PR-10006 | F16-BW-404 Flotation Blower 4 Motor Phase V RTD | F16BW404 Motor P.V RTD | 1 | -5 | 200 | °C | [16 empty] | 130 | 5 | 155 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-404 | C |  |  |  |  | offset done and checked good
|  |  |  | TE16228C | TI16228C | 2000-F16-PID-PR-10006 | F16-BW-404 Flotation Blower 4 Motor Phase W RTD | F16BW404 Motor P.W RTD | 1 | -5 | 200 | °C | [16 empty] | 130 | 5 | 155 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-404 | C |  |  |  |  | offset done and checked good
|  |  |  | TE16228D | TI16228D | 2000-F16-PID-PR-10006 | F16-BW-404 Flotation Blower 4 Motor DE Bearing RTD | F16BW404 Mtr DE Brg RTD | 1 | -5 | 200 | °C | [16 empty] | 90 | 5 | 110 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-404 | 1
|  |  |  | TE16228E | TI16228E | 2000-F16-PID-PR-10006 | F16-BW-404 Flotation Blower 4 Motor NDE Bearing RTD | F16BW404 Mtr NDE Brg RTD | 1 | -5 | 200 | °C | [16 empty] | 90 | 5 | 110 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-404 | 1
|  |  |  | PT16291 | PI16291 | 2000-F16-PID-PR-10006 | F16-BW-404 Flotation Blower 4 Inlet Pressure Indicating Transmitter | F16BW404 Blower 4 Inlet | 1 | -100 | 150 | kPa | [12 empty] | -8 | 5 | -6 | 5 |  |  |  |  | F16BW404 NOT RUNNING | Source: Vendor document 2000-ME001.4-M02-50001. A_Lo = Alarm A_LL = F16-BW-404 Trip | 3
|  |  |  | TT16293 | TI16293 | 2000-F16-PID-PR-10006 | F16-BW-404 Flotation Blower 4 Outlet Temperature Transmitter | F16BW404 Blower 4 Outlet | 1 | -50 | 200 | °C | [16 empty] | 172 | 5 | 177 | 5 |  | Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-404 | C
|  |  |  | TT16294 | TI16294 | 2000-F16-PID-PR-10006 | F16-BW-404 Flotation Blower 4 Gearbox Temperature Transmitter | F16BW404 Blower 4 G/Box | 1 | -50 | 200 | °C | [16 empty] | 113 | 5 | 118 | 5 |  | Source: Vendor document: 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-404 | C
|  |  |  | TT16295 | TI16295 | 2000-F16-PID-PR-10006 | F16-BW-404 Flotation Blower 4 Temperature Transmitter | F16BW404 Blower 4 | 1 | -50 | 200 | °C | [16 empty] | 50 | 5 | 52 | 5 |  | Blower 4 enclosure temperature. Source: Vendor document 2000-ME001.4-M02-50001. A_Hi = Alarm A_HH = Trip F16-BW-404 | C
|  |  |  | PT17002 | PI17002 | 2000-F17-PID-PR-10001 | Flotation Tailings Thickener Water Monitors Pressure Indicating Transmitter | F17TH401 Water Monitors | 1 | 0 | 1000 | kPa | [22 empty] | 1
|  |  |  | ZIT17013 | ZI17013 | 2000-F17-PID-PR-10001 | F17-TH-401 Flotation Tailings Thickener Rake Lift Position Transmitter | F17TH401 Rake Lift Posn | 1 | -12.8 | 100 | % | [22 empty] | B |  |  |  |  | Re-ranged so 0 and 100% correspond to limit switches
|  |  |  | NIT17030 | NI17030 | 2000-F17-PID-PR-10001 | F17-TH-401 Flotation Tailings Thickener Rake Torque Indicating Transmitter | F17TH401 Rake Torque | 1 | 0 | 100 | % (kPa) |  |  |  | 30 (6123) | 5 |  | 40 (8163) | 5 | [8 empty] | 50 (10204) | 5 | 85 (17347) | 5 |  | Rake lift sequence initiated on P_Hi. To be logging alarm to DCS. On A_Hi. Feed off. UF Pumps = 100% VSD. Rake trips on >= A_HH. See torque calibrations table (Table 2) on 2000-ME001.5-M02-50001 for conversions of kPa to percent or alarm setpoints in brackets to the left. | C
|  |  |  | AIT17019 | AI17019 | 2000-F17-PID-PR-10001 | F17-TH-401 Flotation Tailings Thickener Overflow Turbidity Indicating Transmitter | F17TH401 O/F Turbidity | 1 | 0 | 1000 | NTU | [16 empty] | 180 | 5 | 200 | 5 |  | Alarm setpoints to be confirmed during commissioning. | C
|  |  |  | FIT17105 | FI17105 | 2000-F24-PID-PR-10003 | F17-PP-455 Flotation Tailings Thickener Underflow Pump 1 Gland Water Flow Indicating Transmitter | F17PP455 Gland | 1 | 0 | 9 | m3/h | [12 empty] | 1 | 5 | 1.4 | 5 |  |  |  |  | F17PP455 NOT RUNNING | Source: 2000-CAL-ME-007. Minimum: 1.6 m3/h. Alarm setpoints to be confirmed during commissioning. | 3
|  |  |  | FIT17115 | FI17115 | 2000-F24-PID-PR-10003 | F17-PP-456 Flotation Tailings Thickener Underflow Pump 2 Gland Water Flow Indicating Transmitter | F17PP456 Gland | 1 | 0 | 9 | m3/h | [12 empty] | 1 | 5 | 1.4 | 5 |  |  |  |  | F17PP456 NOT RUNNING | Source: 2000-CAL-ME-007. Minimum: 1.6 m3/h. Alarm setpoints to be confirmed during commissioning. | 3
|  |  |  | F17CALC0002 | WI17121 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps Discharge Dry Solids | F17TH401 UF Dry Solids | 1 | 0 | 4000 | t/h | [21 empty] | Maximum: 3410 t/h. | 2
|  |  |  | F17CALC0007 | DNI17121 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow %w/w solids | F17TH401 UF Solids | 1 | 0 | 100 | %w/w | [21 empty] | No alarms required. Refer to DIC17121 in PID Cont. | 3
|  |  |  | PIT17122 | PI17122 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps Discharge Pressure Indicating Transmitter | F17PP455/456 Discharge | 1 | 0 | 1000 | kPa | [16 empty] | 330 | 5 | 350 | 5 | F17PP455 AND 456 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F17-PP-455 OR 456 start-up. | Alarm setpoints to be confirmed during commissioning. | 3
|  |  |  | F17CALC0003 | WI17127 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps Discharge Dry Solids to CIL2 Feed Box | F17TH401 UF CIL2 Solids | 1 | 0 | 2000 | t/h | [12 empty] | 200 | 5 | 400 | 5 |  |  |  |  | F17PP455 AND 456 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F17-PP-455 OR 456 start-up. | Alarm setpoints to be confirmed during commissioning. | 3
|  |  |  | F17CALC0004 | WI17128 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps Discharge Dry Solids to CIL3 Feed Box | F17TH401 UF CIL3 Solids | 1 | 0 | 2000 | t/h | [12 empty] | 200 | 5 | 400 | 5 |  |  |  |  | F17PP455 AND 456 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F17-PP-455 OR 456 start-up. | Alarm setpoints to be confirmed during commissioning. | 3
|  |  |  | F17CALC0005 | FI17130 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps Discharge Slurry Flow to Final Tails Tank | F17TH401 UF Final Tails | 1 | 0 | 5000 | m3/h | [12 empty] | 800 | 5 | 1200 | 5 |  |  |  |  | F17PP455 AND 456 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F17-PP-455 OR 456 start-up. | Alarm setpoints to be confirmed during commissioning. | 3
|  |  |  | F17CALC0006 | WI17130 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps Discharge Dry Solids to Final Tails Tank | F17TH401 UF Final Tails | 1 | 0 | 2500 | t/h | [12 empty] | 200 | 5 | 500 | 5 |  |  |  |  | F17PP455 AND 456 NOT RUNNING | Alarm setpoints to be confirmed during commissioning. Nominal: 1376 t/h. | 2
|  |  |  | FIT18027 | FI18027 | 2000-F18-PID-PR-10001 | F18-PP-407/408 Final Concentrate Pumps Discharge Flow Indicating Transmitter | F18PP407/8 Final Con D/C | 1 | 0 | 650 | m3/h | [12 empty] | 50 | 5 | 90 | 5 | 380 | 5 |  |  | F18PP407 AND 408 NOT RUNNING Alarm enabled delay of 60 seconds (to be confirmed during commissioning) on F18-PP-407 OR 408 start-up. | Alarm setpoints to be confirmed during commissioning. | 3
|  |  |  | F18CALC0002 | DNI18027 | 2000-F18-PID-PR-10001 | F18-PP-407/408 Final Concentrate Pumps Discharge Density Indicating Transmitter | F18PP407/408 D/C Solids | 1 | 0 | 100 | %w/w | [16 empty] | 35 | 5 | 40 | 5 | F18PP407 AND 408 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-407 OR 408 start-up. | Minimum: 22.24% Nominal/Max: 25% | 3
|  |  |  | F18CALC0005 | WI18027 | 2000-F18-PID-PR-10001 | F18-PP-407/408 Final Concentrate Pump 1/2 Discharge Dry Solids | F18PP407/8 D/C Dry | 1 | 0 | 120 | t/h | [21 empty] | Maximum: 107 t/h. | 2
|  |  |  | PIT18054 | PI18054 | 2000-F18-PID-PR-10002 | F18-CF-501 Cleaner Flotation Cell Downcomer Feed Pressure Indicating Transmitter | F18CF501 Cleaner Feed | 1 | 0 | 250 | kPa | [12 empty] | 50 | 5 | 80 | 5 | 200 | 5 | 249 | 5 | F18PP501 AND 502 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-501 OR 502 start-up. | Source: 2000-ME073-M01-10002 Alarm setpoints to be confirmed during commissioning. A_HH - Trip Pump A_Hi - Warning A_Lo - Warning A_LL - Trip Pump | 3
|  |  |  | PIT18055 | PI18055 | 2000-F18-PID-PR-10002 | F18-CF-501 Cleaner Flotation Cell Air Distributor Pressure Indicating Transmitter | F18CF501 Feed Air | 1 | -40 | 0 | kPa | [14 empty] | -30 | 5 | -10 | 5 |  |  | F18PP501 AND 502 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-501 OR 502 start-up. | Source: 2000-ME073-M01-10002. Default values have been supplied - to be confirmed during commissioning. Low-Low and High-High alarm setpoints are not applied to limit alarm quantity. Air Distributor Flow Meter alarm setpoints provide process interlocks as required. | 3
|  |  |  | FIT18237 | FI18237 | 2000-F18-PID-PR-10003 | F18-PP-513/514 Cleaner Scavenger Flotation Cell Tails Pumps Discharge Flow Indicating Transmitter | F18PP513/514 Discharge | 1 | 0 | 1500 | m3/h | [12 empty] | 300 | 5 | 400 | 5 | 1400 | 5 |  |  | F18PP513 AND 514 NOT RUNNING Alarm enabled delay of 60 seconds (to be confirmed during commissioning) on F18-PP-513 OR 514 start-up. | Minimum: 461 m3/h Nominal: 948 m3/h Maximum: 1291 m3/h. Alarm setpoints to be confirmed during commissioning. | 3 |  |  |  |  | can't simulate IOP+
|  |  |  | F18CALC0003 | DNI18237 | 2000-F18-PID-PR-10003 | F18-PP-513/514 Cleaner Scavenger Flotation Cell Tails Pumps Discharge Density Indicating Transmitter | F18PP513/514 D/C Solids | 1 | 0 | 100 | %w/w | [14 empty] | 5 | 5 | 30 | 5 |  |  | F18PP513 AND 514 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-513 OR 514 start-up. | Minimum: 11.82% Nominal: 15.02% Maximum: 17.57% Alarm setpoints to be confirmed during commissioning. | 3
|  |  |  | F18CALC0004 | WI18237 | 2000-F18-PID-PR-10003 | F18-PP-513/514 Cleaner Scavenger Flotation Cell Tails Pumps Discharge Dry Solids Mass Flow Rate | F18PP513/514 Dry Solids | 1 | 0 | 500 | t/h | [21 empty] | Maximum: 274 t/h. | 2
|  |  |  | PIT18254 | PI18254 | 2000-F18-PID-PR-10004 |  | F18CF511 Clnr-Scav Feed | 1 | 0 | 250 | kPa | [12 empty] | 50 | 5 | 80 | 5 | 200 | 5 | 249 | 5 | F18PP511 AND 512 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-511 OR 512 start-up. | Source: 2000-ME073-M01-10001 Alarm setpoints to be confirmed during commissioning. A_HH - Trip Pump A_Hi - Warning A_Lo - Warning A_LL - Trip Pump | 3
|  |  |  | PIT18255 | PI18255 | 2000-F18-PID-PR-10004 | F18-CF-511 Cleaner-Scavenger Flotation Cell Air Distributor Pressure Indicating Transmitter | F18CF511 Feed Air | 1 | -40 | 0 | kPa | [14 empty] | -30 | 5 | -10 | 5 |  |  | F18PP511 AND 512 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-511 OR 512 start-up. | Source: 2000-ME073-M01-10001. Default values have been supplied - to be confirmed during commissioning. Low-Low and High-High alarm setpoints are not applied to limit alarm quantity. Air Distributor Flow Meter alarm setpoints provide process interlocks as required. | 3
|  |  |  | TE18542A | TI18542A | 2000-F18-PID-PR-10001 | F18-PP-501 Cleaner Flotation Cell Recirculation Pump 1 Motor Phase U RTD | F18PP501 Motor P.U RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18542B | TI18542B | 2000-F18-PID-PR-10001 | F18-PP-501 Cleaner Flotation Cell Recirculation Pump 1 Motor Phase V RTD | F18PP501 Motor P.V RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18542C | TI18542C | 2000-F18-PID-PR-10001 | F18-PP-501 Cleaner Flotation Cell Recirculation Pump 1 Motor Phase W RTD | F18PP501 Motor P.W RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18542D | TI18542D | 2000-F18-PID-PR-10001 | F18-PP-501 Cleaner Flotation Cell Recirculation Pump 1 Motor DE Bearing RTD | F18PP501 DE Bearing | 1 | -5 | 200 | °C | [16 empty] | 95 | 5 | 100 | 5 |  | Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | TE18542E | TI18542E | 2000-F18-PID-PR-10001 | F18-PP-501 Cleaner Flotation Cell Recirculation Pump 1 Motor NDE Bearing RTD | F18PP501 NDE Bearing | 1 | -5 | 200 | °C | [16 empty] | 95 | 5 | 100 | 5 |  | Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | TE18543A | TI18543A | 2000-F18-PID-PR-10001 | F18-PP-502 Cleaner Flotation Cell Recirculation Pump 2 Motor Phase U RTD | F18PP502 Motor P.U RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18543B | TI18543B | 2000-F18-PID-PR-10001 | F18-PP-502 Cleaner Flotation Cell Recirculation Pump 2 Motor Phase V RTD | F18PP502 Motor P.V RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18543C | TI18543C | 2000-F18-PID-PR-10001 | F18-PP-502 Cleaner Flotation Cell Recirculation Pump 2 Motor Phase W RTD | F18PP502 Motor P.W RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18543D | TI18543D | 2000-F18-PID-PR-10001 | F18-PP-502 Cleaner Flotation Cell Recirculation Pump 2 Motor DE Bearing RTD | F18PP502 DE Bearing | 1 | -5 | 200 | °C | [16 empty] | 95 | 5 | 100 | 5 |  | Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | TE18543E | TI18543E | 2000-F18-PID-PR-10001 | F18-PP-502 Cleaner Flotation Cell Recirculation Pump 2 Motor NDE Bearing RTD | F18PP502 NDE Bearing | 1 | -5 | 200 | °C | [16 empty] | 95 | 5 | 100 | 5 |  | Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | TE18546A | TI18546A | 2000-F18-PID-PR-10003 | F18-PP-511 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Motor Phase U RTD | F18PP511 Motor P.U RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18546B | TI18546B | 2000-F18-PID-PR-10003 | F18-PP-511 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Motor Phase V RTD | F18PP511 Motor P.V RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18546C | TI18546C | 2000-F18-PID-PR-10003 | F18-PP-511 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Motor Phase W RTD | F18PP511 Motor P.W RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18546D | TI18546D | 2000-F18-PID-PR-10003 | F18-PP-511 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Motor DE Bearing RTD | F18PP511 DE Bearing | 1 | -5 | 200 | °C | [16 empty] | 95 | 5 | 100 | 5 |  | Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | TE18546E | TI18546E | 2000-F18-PID-PR-10003 | F18-PP-511 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Motor NDE Bearing RTD | F18PP511 NDE Bearing | 1 | -5 | 200 | °C | [16 empty] | 95 | 5 | 100 | 5 |  | Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | TE18547A | TI18547A | 2000-F18-PID-PR-10003 | F18-PP-512 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Motor Phase U RTD | F18PP512 Motor P.U RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18547B | TI18547B | 2000-F18-PID-PR-10003 | F18-PP-512 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Motor Phase V RTD | F18PP512 Motor P.V RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18547C | TI18547C | 2000-F18-PID-PR-10003 | F18-PP-512 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Motor Phase W RTD | F18PP512 Motor P.W RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18547D | TI18547D | 2000-F18-PID-PR-10003 | F18-PP-512 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Motor DE Bearing RTD | F18PP512 DE Bearing | 1 | -5 | 200 | °C | [16 empty] | 95 | 5 | 100 | 5 |  | Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | TE18547E | TI18547E | 2000-F18-PID-PR-10003 | F18-PP-512 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Motor NDE Bearing RTD | F18PP512 NDE Bearing | 1 | -5 | 200 | °C | [16 empty] | 95 | 5 | 100 | 5 |  | Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | TE18550A | TI18550A | 2000-F18-PID-PR-10003 | F18-PP-513 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Motor Phase U RTD | F18PP513 Motor P.U RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18550B | TI18550B | 2000-F18-PID-PR-10003 | F18-PP-513 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Motor Phase V RTD | F18PP513 Motor P.V RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18550C | TI18550C | 2000-F18-PID-PR-10003 | F18-PP-513 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Motor Phase W RTD | F18PP513 Motor P.W RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18550D | TI18550D | 2000-F18-PID-PR-10003 | F18-PP-513 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Motor DE Bearing RTD | F18PP513 DE Bearing | 1 | -5 | 200 | °C | [16 empty] | 95 | 5 | 100 | 5 |  | Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | TE18550E | TI18550E | 2000-F18-PID-PR-10003 | F18-PP-513 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Motor NDE Bearing RTD | F18PP513 NDE Bearing | 1 | -5 | 200 | °C | [16 empty] | 95 | 5 | 100 | 5 |  | Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | TE18551A | TI18551A | 2000-F18-PID-PR-10003 | F18-PP-514 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Motor Phase U RTD | F18PP514 Motor P.U RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18551B | TI18551B | 2000-F18-PID-PR-10001 | F18-PP-514 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Motor Phase V RTD | F18PP514 Motor P.V RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18551C | TI18551C | 2000-F18-PID-PR-10003 | F18-PP-514 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Motor Phase W RTD | F18PP514 Motor P.W RTD | 1 | -5 | 200 | °C | [16 empty] | 140 | 5 | 150 | 5 |  | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1
|  |  |  | TE18551D | TI18551D | 2000-F18-PID-PR-10003 | F18-PP-514 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Motor DE Bearing RTD | F18PP514 DE Bearing | 1 | -5 | 200 | °C | [16 empty] | 95 | 5 | 100 | 5 |  | Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | TE18551E | TI18551E | 2000-F18-PID-PR-10003 | F18-PP-514 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Motor NDE Bearing RTD | F18PP514 NDE Bearing | 1 | -5 | 200 | °C | [16 empty] | 95 | 5 | 100 | 5 |  | Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | UT16031 | UI16031 | N/A | F16-SR-002 Flotation 415V Switchroom Temperature Transmitter | F16SR002 415V SR Temp | 1 | 0 | 50 | °C | [16 empty] | 30 | 60 |  |  |  |  | 3
|  |  |  | UT16032 | UI16032 | N/A | F16-SR-002 Flotation 415V Switchroom Transformer Enclosure Temperature Transmitter | F16SR002 415V SR TF1 | 1 | 0 | 50 | °C | [16 empty] | 30 | 60 |  |  |  |  | 3
|  |  |  | UT16033 | UI16033 | N/A | F16-SR-002 Flotation 415V Switchroom Transformer Enclosure Temperature Transmitter | F16SR002 415V SR TF2 | 1 | 0 | 50 | °C | [16 empty] | 30 | 60 |  |  |  |  | 3
|  |  |  | UT16034 | UI16034 | N/A | F16-SR-002 Flotation 415V Switchroom Transformer Enclosure Temperature Transmitter | F16SR002 415V SR TF3 | 1 | 0 | 50 | °C | [16 empty] | 30 | 60 |  |  |  |  | 3
|  |  |  | UT16030 | UI16030 | N/A | F16-SR-001 Flotation 11kV Switchroom Temperature Transmitter | F16SR001 11kV SR Temp | 1 | 0 | 50 | °C | [16 empty] | 30 | 60 |  |  |  |  | 3
|  |  |  | DIT17121 | DI17121 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps Discharge Density Indicating Transmitter | F17TH401 Density | 1 | 1 | 3.5 | t/m3 | [21 empty] | Direction to PCS Vendor: Do not show in DCS graphic. To show %w/w solids calculated output only. | 1
|  |  |  | PDIT17030 | PDI17030 | 2000-F17-PID-PR-10001 | F17-TH-401 Flotation Tailings Thickener Rake Torque Differential Pressure Transmitter | F17TH401 Pres Diff | 1 | 0 | 100 | % | [21 empty] | Placeholder to align with I/O List. Direction to PCS Vendor: Please omit from DCS and use NI17030 as above. | [5 empty] | VV 27/07/2026; to be deleted as per MOC-757
|  |  |  | LIT18051A | LI18051A | 2000-F18-PID-PR-10002 | F18-CF-501 Cleaner Flotation Cell Tank Slurry Level Indicating Transmitter | F18CF501 Tank Level A | 1 | 0 | 2470 | mm | [21 empty] | Used in F18-CALC-0007 See 2000-ME073-M01-10002 for probe calibration | 3
|  |  |  | LIT18051B | LI18051B | 2000-F18-PID-PR-10002 | F18-CF-501 Cleaner Flotation Cell Tank Slurry Density Compensation Level Indicating Transmitter | F18CF501 Tank Level B | 1 | 0 | 1560 | mm | [21 empty] | Used in F18-CALC-0007 See 2000-ME073-M01-10002 for probe calibration | 3
|  |  |  | F18CALC0007 | LNI18051 | 2000-F18-PID-PR-10002 | F18-CF-501 Cleaner Flotation Cell Froth Depth Calculation | F18CF501 Froth Depth | 1 | 0 | 1900 | mm | [22 empty] | 3
|  |  |  | DIT18237 | DI18237 | 2000-F18-PID-PR-10003 | F18-PP-513/514 Cleaner Scavenger Flotation Cell Tails Pumps Discharge Density Indicating Transmitter | F18PP513/4 Discharge | 1 | 1 | 1.31 | t/m3 | [21 empty] | Direction to PCS Vendor: Do not show in DCS graphic. To show %w/w solids calculated output only. | 1
|  |  |  | LIT18251A | LI18251A | 2000-F18-PID-PR-10004 | F26-CF-511 Cleaner-Scavenger Flotation Cell Tank Slurry Level Indicating Transmitter | F18CF511 Tank Level A | 1 | 0 | 2470 | mm | [21 empty] | Used in F18-CALC-0008 See 2000-ME073-M01-10001 for probe calibration | 3
|  |  |  | LIT18251B | LI18251B | 2000-F18-PID-PR-10004 | F26-CF-511 Cleaner-Scavenger Flotation Cell Tank Slurry Density Compensation Level Indicating Transmitter | F18CF511 Tank Level B | 1 | 0 | 1560 | mm | [21 empty] | Used in F18-CALC-0008 See 2000-ME073-M01-10001 for probe calibration | 3
|  |  |  | F18CALC0008 | LNI18251 | 2000-F18-PID-PR-10004 | F18-CF-511 Cleaner Flotation Cell Froth Depth Calculation | F18CF511 Froth Depth | 1 | 0 | 1900 | mm | [22 empty] | 2
|  |  |  | DIT18027 | DI18027 | 2000-F18-PID-PR-10001 | F18-PP-407/408 Final Concentrate Pumps Discharge Density Indicating Transmitter | F18PP407/8 Discharge | 1 | 1 | 1.44 | t/m3 | [21 empty] | Direction to PCS Vendor: Do not show in DCS graphic. To show %w/w solids calculated output only. | 1
|  |  |  | XI16170S | XI16170 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 1 Value | F16AN402 Flot Feed PS | 1 | 0 | 400 | µm | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier Intended to be setup as particle size assay during commissioning by Metso Engineers. Configurable. See IOM for further details. Range to be confirmed during commissioning. | 2
|  |  |  | XI16171S | XI16171 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 2 Value | F16AN402 Flot Feed PSD_D | 1 | 0 | 100 | % | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier Intended to be setup as particle size from distribution assay during commissioning by Metso Engineers. Configurable. See IOM for further details. Range to be confirmed during commissioning. | 2
|  |  |  | F16AN402ASY3S | F16AN402ASY3 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 3 Value | F16AN402 Flot Feed %Slds | 1 | 0 | 100 | % | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier Intended to be setup as Solids% assay during commissioning by Metso Engineers. Configurable. See IOM for further details. Range to be confirmed during commissioning. | 2
|  |  |  | F16AN402ASY4S | F16AN402ASY4 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 4 Value | F16AN402 Final Tail PS | 1 | 0 | 400 | µm | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier Intended to be setup as particle size assay during commissioning by Metso Engineers. Configurable. See IOM for further details. Range to be confirmed during commissioning. | 2
|  |  |  | F16AN402ASY5S | F16AN402ASY5 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 5 Value | F16AN402 FinalTail PSD_D | 1 | 0 | 100 | % | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier Intended to be setup as particle size from distribution assay during commissioning by Metso Engineers. Configurable. See IOM for further details. Range to be confirmed during commissioning. | 2
|  |  |  | F16AN402ASY6S | F16AN402ASY6 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 6 Value | F16AN402 FinalTail %Slds | 1 | 0 | 100 | % | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier Intended to be setup as Solids% assay during commissioning by Metso Engineers. Configurable. See IOM for further details. Range to be confirmed during commissioning. | 2
|  |  |  | F16AN402ASY7S | F16AN402ASY7 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 7 Value | F16AN402 Assay Value 7 | 1 | 0 | 100 | % | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier. Spare for future use on-site. To be confirmed during commissioning. | 2
|  |  |  | F16AN402ASY8S | F16AN402ASY8 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 8 Value | F16AN402 Assay Value 8 | 1 | 0 | 100 | % | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier. Spare for future use on-site. To be confirmed during commissioning. | 2
|  |  |  | F16AN402ASY9S | F16AN402ASY9 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 9 Value | F16AN402 Assay Value 9 | 1 | 0 | 100 | % | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier. Spare for future use on-site. To be confirmed during commissioning. | 2
|  |  |  | F16AN402AS10S | F16AN402ASY10 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 10 Value | F16AN402 Assay Value 10 | 1 | 0 | 100 | % | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier. Spare for future use on-site. To be confirmed during commissioning. | 2
|  |  |  | XI16173S | XI16173 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Current Line Measurement | F16AN402 Measuremnt Line | 1 | 0 | 3 | - | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier Required feedback to see stream being analysed. Contractor may need to correlate results from Flotation Feed and Final Tails streams to individual soft tags for Assays and density etc using this feeback. | 2
|  |  |  | XI16172S | XI16172 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Density Value | F16AN402 Density | 1 | 0 | 4 | g/L | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier PSDM slurry density meter optional extra by Metso. Density value depends on stream being analysed (1 or 2). Contractor may be required to create two soft-tags and related modbus add: 40086 and 40081 to return a density value for Flotation Feed and Final Tails. | 2
|  |  |  | F16AN402ATS | F16AN402AT | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA pH Value | F16AN402 pH | 1 | 0 | 14 | pH | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier | 2
|  |  |  | F16AN402LTS | F16AN402LT | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Zero Level Value | F16AN402 Zero Level | 1 | 0 | 400 | - | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier | 2
|  |  |  | F16AN402VAL2S | F16AN402VAL2 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Measurement Value | F16AN402 Measurement Val | 1 | 0 | 400 | % | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11011 Flotation Feed PSA for format and value multiplier Use to be confirmed during commissioning. | 2
|  |  |  | F16AN403S1FS | F16AN403S1F | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Flow 1 | F16AN403 Flow 1 | 1 | 0 | 400 | L/min | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Range to be confirmed during commissioning. | 3
|  |  |  | F16AN403S2FS | F16AN403S2F | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Flow 2 | F16AN403 Flow 2 | 1 | 0 | 400 | L/min | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Range to be confirmed during commissioning. | 3
|  |  |  | F16AN403S3FS | F16AN403S3F | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Flow 3 | F16AN403 Flow 3 | 1 | 0 | 400 | L/min | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Range to be confirmed during commissioning. | 3
|  |  |  | F16AN403S4FS | F16AN403S4F | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Flow 4 | F16AN403 Flow 4 | 1 | 0 | 400 | L/min | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Range to be confirmed during commissioning. | 3
|  |  |  | F16AN403S5FS | F16AN403S5F | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Flow 5 | F16AN403 Flow 5 | 1 | 0 | 400 | L/min | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Range to be confirmed during commissioning. | 3
|  |  |  | F16AN403S6FS | F16AN403S6F | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Flow 6 | F16AN403 Flow 6 | 1 | 0 | 400 | L/min | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Range to be confirmed during commissioning. | 3
|  |  |  | F16AN403S7FS | F16AN403S7F | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Flow 7 | F16AN403 Flow 7 | 1 | 0 | 400 | L/min | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Range to be confirmed during commissioning. | 3
|  |  |  | F16AN403S8FS | F16AN403S8F | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Flow 8 | F16AN403 Flow 8 | 1 | 0 | 400 | L/min | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Range to be confirmed during commissioning. | 3
|  |  |  | F16AN403S9FS | F16AN403S9F | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Flow 9 | F16AN403 Flow 9 | 1 | 0 | 400 | L/min | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Range to be confirmed during commissioning. | 3
|  |  |  | F16AN403S10FS | F16AN403S10F | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Flow 10 | F16AN403 Flow 10 | 1 | 0 | 400 | L/min | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Range to be confirmed during commissioning. | 3
|  |  |  | F16AN403S11FS | F16AN403S11F | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Flow 11 | F16AN403 Flow 11 | 1 | 0 | 400 | L/min | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Range to be confirmed during commissioning. | 3
|  |  |  | F16AN403S12FS | F16AN403S12F | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Flow 12 | F16AN403 Flow 12 | 1 | 0 | 400 | L/min | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Range to be confirmed during commissioning. | 3 |  |  |  |  | 2025-08-19 | updated
|  |  |  | F16AN403S1WS | F16AN403S1W | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Status Word 1 | F16AN403 Status Word 1 | 1 | 0 | 9 | - | [21 empty] | Soft tag. See Digital Input sheet for analyser bit map tag naming (Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details) | 2
|  |  |  | F16AN403S2WS | F16AN403S2W | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Status Word 2 | F16AN403 Status Word 2 | 1 | 0 | 9 | - | [21 empty] | Soft tag. See Digital Input sheet for analyser bit map tag naming (Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details) | 2
|  |  |  | F16AN403S3WS | F16AN403S3W | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Status Word 3 | F16AN403 Status Word 3 | 1 | 0 | 9 | - | [21 empty] | Soft tag. See Digital Input sheet for analyser bit map tag naming (Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details) | 2
|  |  |  | F16AN403S4WS | F16AN403S4W | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Status Word 4 | F16AN403 Status Word 4 | 1 | 0 | 9 | - | [21 empty] | Soft tag. See Digital Input sheet for analyser bit map tag naming (Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details) | 2
|  |  |  | F16AN403S5WS | F16AN403S5W | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Status Word 5 | F16AN403 Status Word 5 | 1 | 0 | 9 | - | [21 empty] | Soft tag. See Digital Input sheet for analyser bit map tag naming (Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details) | 2
|  |  |  | F16AN403S6WS | F16AN403S6W | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Status Word 6 | F16AN403 Status Word 6 | 1 | 0 | 9 | - | [21 empty] | Soft tag. See Digital Input sheet for analyser bit map tag naming (Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details) | 2
|  |  |  | F16AN403S7WS | F16AN403S7W | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Status Word 7 | F16AN403 Status Word 7 | 1 | 0 | 9 | - | [21 empty] | Soft tag. See Digital Input sheet for analyser bit map tag naming (Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details) | 2
|  |  |  | F16AN403S8WS | F16AN403S8W | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Status Word 8 | F16AN403 Status Word 8 | 1 | 0 | 9 | - | [21 empty] | Soft tag. See Digital Input sheet for analyser bit map tag naming (Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details) | 2
|  |  |  | F16AN403S9WS | F16AN403S9W | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Status Word 9 | F16AN403 Status Word 9 | 1 | 0 | 9 | - | [21 empty] | Soft tag. See Digital Input sheet for analyser bit map tag naming (Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details) | 2
|  |  |  | F16AN403S10WS | F16AN403S10W | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Status Word 10 | F16AN403 Status Word 10 | 1 | 0 | 9 | - | [21 empty] | Soft tag. See Digital Input sheet for analyser bit map tag naming (Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details) | 2
|  |  |  | F16AN403S11WS | F16AN403S11W | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Status Word 11 | F16AN403 Status Word 11 | 1 | 0 | 9 | - | [21 empty] | Soft tag. See Digital Input sheet for analyser bit map tag naming (Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details) | 2
|  |  |  | F16AN403S12WS | F16AN403S12W | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Sample Stream Status Word 12 | F16AN403 Status Word 12 | 1 | 0 | 9 | - | [21 empty] | Soft tag. See Digital Input sheet for analyser bit map tag naming (Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details) | 2
|  |  |  | F16AN403STS | F16AN403ST | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Status Word | F16AN403 Analyser Status | 1 | 0 | 9 | - | [21 empty] | Soft tag. See Digital Input sheet for analyser bit map tag naming (Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details) | 2
|  |  |  | F16AN403S1FeS | F16AN403S1Fe | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Iron Concentration | F16AN403 S1 Fe | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S2FeS | F16AN403S2Fe | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Iron Concentration | F16AN403 S2 Fe | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S3FeS | F16AN403S3Fe | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Iron Concentration | F16AN403 S3 Fe | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S4FeS | F16AN403S4Fe | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Iron Concentration | F16AN403 S4 Fe | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S5FeS | F16AN403S5Fe | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Iron Concentration | F16AN403 S5 Fe | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S6FeS | F16AN403S6Fe | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Iron Concentration | F16AN403 S6 Fe | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S7FeS | F16AN403S7Fe | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Iron Concentration | F16AN403 S7 Fe | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S8FeS | F16AN403S8Fe | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Iron Concentration | F16AN403 S8 Fe | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S9FeS | F16AN403S9Fe | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Iron Concentration | F16AN403 S9 Fe | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN40310FeS | F16AN403S10Fe | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Iron Concentration | F16AN403 S10 Fe | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN40311FeS | F16AN403S11Fe | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Iron Concentration | F16AN403 S11 Fe | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN40312FeS | F16AN403S12Fe | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Iron Concentration | F16AN403 S12 Fe | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S1AsS | F16AN403S1As | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Arsenic Concentration | F16AN403 S1 As | 1 | 0 | 1000 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S2AsS | F16AN403S2As | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Arsenic Concentration | F16AN403 S2 As | 1 | 0 | 1000 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S3AsS | F16AN403S3As | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Arsenic Concentration | F16AN403 S3 As | 1 | 0 | 1000 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S4AsS | F16AN403S4As | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Arsenic Concentration | F16AN403 S4 As | 1 | 0 | 1000 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S5AsS | F16AN403S5As | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Arsenic Concentration | F16AN403 S5 As | 1 | 0 | 1000 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S6AsS | F16AN403S6As | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Arsenic Concentration | F16AN403 S6 As | 1 | 0 | 1000 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S7AsS | F16AN403S7As | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Arsenic Concentration | F16AN403 S7 As | 1 | 0 | 1000 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S8AsS | F16AN403S8As | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Arsenic Concentration | F16AN403 S8 As | 1 | 0 | 1000 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S9AsS | F16AN403S9As | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Arsenic Concentration | F16AN403 S9 As | 1 | 0 | 1000 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN40310AsS | F16AN403S10As | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Arsenic Concentration | F16AN403 S10 As | 1 | 0 | 1000 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN40311AsS | F16AN403S11As | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Arsenic Concentration | F16AN403 S11 As | 1 | 0 | 1000 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN40312AsS | F16AN403S12As | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Arsenic Concentration | F16AN403 S12 As | 1 | 0 | 1000 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S1AuS | F16AN403S1Au | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Gold Concentration | F16AN403 S1 Au | 1 | 0 | 100 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S2AuS | F16AN403S2Au | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Gold Concentration | F16AN403 S2 Au | 1 | 0 | 100 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S3AuS | F16AN403S3Au | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Gold Concentration | F16AN403 S3 Au | 1 | 0 | 100 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S4AuS | F16AN403S4Au | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Gold Concentration | F16AN403 S4 Au | 1 | 0 | 100 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S5AuS | F16AN403S5Au | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Gold Concentration | F16AN403 S5 Au | 1 | 0 | 100 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S6AuS | F16AN403S6Au | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Gold Concentration | F16AN403 S6 Au | 1 | 0 | 100 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S7AuS | F16AN403S7Au | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Gold Concentration | F16AN403 S7 Au | 1 | 0 | 100 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S8AuS | F16AN403S8Au | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Gold Concentration | F16AN403 S8 Au | 1 | 0 | 100 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S9AuS | F16AN403S9Au | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Gold Concentration | F16AN403 S9 Au | 1 | 0 | 100 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN40310AuS | F16AN403S10Au | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Gold Concentration | F16AN403 S10 Au | 1 | 0 | 100 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN40311AuS | F16AN403S11Au | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Gold Concentration | F16AN403 S11 Au | 1 | 0 | 100 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN40312AuS | F16AN403S12Au | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Gold Concentration | F16AN403 S12 Au | 1 | 0 | 100 | g/t | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S1SS | F16AN403S1S | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Solids %W/W | F16AN403 S1 %Slds | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S2SS | F16AN403S2S | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Solids %W/W | F16AN403 S2 %Slds | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S3SS | F16AN403S3S | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Solids %W/W | F16AN403 S3 %Slds | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S4SS | F16AN403S4S | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Solids %W/W | F16AN403 S4 %Slds | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S5SS | F16AN403S5S | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Solids %W/W | F16AN403 S5 %Slds | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S6SS | F16AN403S6S | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Solids %W/W | F16AN403 S6 %Slds | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S7SS | F16AN403S7S | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Solids %W/W | F16AN403 S7 %Slds | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S8SS | F16AN403S8S | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Solids %W/W | F16AN403 S8 %Slds | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S9SS | F16AN403S9S | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Solids %W/W | F16AN403 S9 %Slds | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S10SS | F16AN403S10S | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Solids %W/W | F16AN403 S10 %Slds | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S11SS | F16AN403S11S | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Solids %W/W | F16AN403 S11 %Slds | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16AN403S12SS | F16AN403S12S | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Solids %W/W | F16AN403 S12 %Slds | 1 | 0 | 100 | % | [21 empty] | Soft-tag Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details | 2
|  |  |  | F16CALC0009 | F16AN403S1SU | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Gold Concentration | F16AN403 S1 S | 1 | 0 | 100 | % | [21 empty] | Include on graphic next to sample name: Flotation Feed | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-022
|  |  |  | F16CALC0009 | F16AN403S2SU | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Gold Concentration | F16AN403 S2 S | 1 | 0 | 100 | % | [21 empty] | Include on graphic next to sample name: Final Tails | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-022
|  |  |  | F16CALC0009 | F16AN403S3SU | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Gold Concentration | F16AN403 S3 S | 1 | 0 | 100 | % | [21 empty] | Include on graphic next to sample name: Scavenger Tails | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-022
|  |  |  | F16CALC0009 | F16AN403S4SU | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Gold Concentration | F16AN403 S4 S | 1 | 0 | 100 | % | [21 empty] | Include on graphic next to sample name: Cleaner Scavenger Tails | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-022
|  |  |  | F16CALC0009 | F16AN403S5SU | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Gold Concentration | F16AN403 S5 S | 1 | 0 | 100 | % | [21 empty] | Include on graphic next to sample name: Scavenger Concentrate | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-022
|  |  |  | F16CALC0009 | F16AN403S6SU | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Gold Concentration | F16AN403 S6 S | 1 | 0 | 100 | % | [21 empty] | Include on graphic next to sample name: Rougher 1 Concentrate Cleaner Feed | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-022
|  |  |  | F16CALC0009 | F16AN403S7SU | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Gold Concentration | F16AN403 S7 S | 1 | 0 | 100 | % | [21 empty] | Include on graphic next to sample name: Rougher 1 Concentrate Final Concentrate | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-022
|  |  |  | F16CALC0009 | F16AN403S8SU | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Gold Concentration | F16AN403 S8 S | 1 | 0 | 100 | % | [21 empty] | Include on graphic next to sample name: Final Flotation Concentrate | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-022
|  |  |  | F16CALC0009 | F16AN403S9SU | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Gold Concentration | F16AN403 S9 S | 1 | 0 | 100 | % | [21 empty] | Include on graphic next to sample name: Rougher 2 & 3 Concentrate | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-022
|  |  |  | F16CALC0009 | F16AN403S10SU | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Gold Concentration | F16AN403 S10 S | 1 | 0 | 100 | % | [21 empty] | Include on graphic next to sample name: Cleaner Feed | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-022
|  |  |  | F16AN403T1S | F16AN403T1 | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Ambient Temperature | F16AN403 Ambient Temp | 1 | -10 | 100 | °C | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Awaiting vendor details on range & units. | 2
|  |  |  | F16AN403T2S | F16AN403T2 | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Chiller Ambient Temperature | F16AN403 Chiller Temp | 1 | -10 | 100 | °C | [21 empty] | Soft tag. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser for format and value multiplier. Awaiting vendor details on range & units. | 2
|  |  |  | F16XM411VDS | F16XM411VDIR | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Velocity Direction | F16XM411 Velocity Dir. | 1 | 0 | 360 | ° | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411VMS | F16XM411VMAG | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Velocity Magnitude | F16XM411 Velocity Mag. | 1 | 0 | 20 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411PLS | F16XM411PULL | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Velocity Pulling Rate | F16XM411 Pulling Rate | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411VXS | F16XM411VELX | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Velocity X | F16XM411 Velocity X | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411VYS | F16XM411VELY | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Velocity Y | F16XM411 Velocity Y | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411HS | F16XM411HUE | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Colour Hue | F16XM411 Colour Hue | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411HHS | F16XM411HUEH | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Colour Max hue | F16XM411 Colour Hue Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411HLS | F16XM411HUEL | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Colour Min hue | F16XM411 Colour Hue Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411HSS | F16XM411HUES | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Colour std hue | F16XM411 Colour Hue STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411SS | F16XM411SAT | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Colour Saturation | F16XM411 Colour Sat | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411SHS | F16XM411SATH | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Colour Saturation Max | F16XM411 Colour Sat Max | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411SLS | F16XM411SATL | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Colour Saturation Min | F16XM411 Colour Sat Min | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411SAS | F16XM411SATA | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Colour Saturation Average | F16XM411 Colour Sat Avg | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411CAS | F16XM411COLA | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Colour Value Average | F16XM411 Colour Avg | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411CHS | F16XM411COLH | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Colour Value Max | F16XM411 Colour Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411CLS | F16XM411COLL | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Colour Value Min | F16XM411 Colour Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411CSS | F16XM411COLS | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Colour Value std | F16XM411 Colour STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411BXLS | F16XM411BXL | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Bubble Size - Extra Large | F16XM411 Bubble X-Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411BXSS | F16XM411BXS | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Bubble Size - Fine | F16XM411 Bubble Fine | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411BLS | F16XM411BL | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Bubble Size - Large | F16XM411 Bubble Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411BMS | F16XM411BM | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Bubble Size - Medium | F16XM411 Bubble Medium | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411BTSS | F16XM411BTS | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Bubble Size - Top Size | F16XM411 Bubble Topsize | 1 | 0 | 10 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM411LVLS | F16XM411LVL | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Lidar Level | F16XM411 Froth Depth | 1 | 0 | 500 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586VDS | F16XM586VDIR | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Velocity Direction | F16XM586 Velocity Dir. | 1 | 0 | 360 | ° | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586VMS | F16XM586VMAG | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Velocity Magnitude | F16XM586 Velocity Mag. | 1 | 0 | 20 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586PLS | F16XM586PULL | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Velocity Pulling Rate | F16XM586 Pulling Rate | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586VXS | F16XM586VELX | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Velocity X | F16XM586 Velocity X | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586VYS | F16XM586VELY | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Velocity Y | F16XM586 Velocity Y | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586HS | F16XM586HUE | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Colour Hue | F16XM586 Colour Hue | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586HHS | F16XM586HUEH | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Colour Max hue | F16XM586 Colour Hue Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586HLS | F16XM586HUEL | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Colour Min hue | F16XM586 Colour Hue Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586HSS | F16XM586HUES | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Colour std hue | F16XM586 Colour Hue STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586SS | F16XM586SAT | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Colour Saturation | F16XM586 Colour Sat | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586SHS | F16XM586SATH | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Colour Saturation Max | F16XM586 Colour Sat Max | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586SLS | F16XM586SATL | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Colour Saturation Min | F16XM586 Colour Sat Min | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586SAS | F16XM586SATA | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Colour Saturation Average | F16XM586 Colour Sat Avg | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586CAS | F16XM586COLA | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Colour Value Average | F16XM586 Colour Avg | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586CHS | F16XM586COLH | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Colour Value Max | F16XM586 Colour Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586CLS | F16XM586COLL | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Colour Value Min | F16XM586 Colour Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586CSS | F16XM586COLS | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Colour Value std | F16XM586 Colour STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586BXLS | F16XM586BXL | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Bubble Size - Extra Large | F16XM586 Bubble X-Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586BXSS | F16XM586BXS | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Bubble Size - Fine | F16XM586 Bubble Fine | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586BLS | F16XM586BL | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Bubble Size - Large | F16XM586 Bubble Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586BMS | F16XM586BM | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Bubble Size - Medium | F16XM586 Bubble Medium | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586BTSS | F16XM586BTS | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Bubble Size - Top Size | F16XM586 Bubble Topsize | 1 | 0 | 10 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM586LVLS | F16XM586LVL | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Lidar Level | F16XM586 Froth Depth | 1 | 0 | 500 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587VDS | F16XM587VDIR | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Velocity Direction | F16XM587 Velocity Dir. | 1 | 0 | 360 | ° | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587VMS | F16XM587VMAG | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Velocity Magnitude | F16XM587 Velocity Mag. | 1 | 0 | 20 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587PLS | F16XM587PULL | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Velocity Pulling Rate | F16XM587 Pulling Rate | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587VXS | F16XM587VELX | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Velocity X | F16XM587 Velocity X | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587VYS | F16XM587VELY | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Velocity Y | F16XM587 Velocity Y | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587HS | F16XM587HUE | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Colour Hue | F16XM587 Colour Hue | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587HHS | F16XM587HUEH | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Colour Max hue | F16XM587 Colour Hue Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587HLS | F16XM587HUEL | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Colour Min hue | F16XM587 Colour Hue Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587HSS | F16XM587HUES | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Colour std hue | F16XM587 Colour Hue STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587SS | F16XM587SAT | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Colour Saturation | F16XM587 Colour Sat | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587SHS | F16XM587SATH | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Colour Saturation Max | F16XM587 Colour Sat Max | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587SLS | F16XM587SATL | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Colour Saturation Min | F16XM587 Colour Sat Min | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587SAS | F16XM587SATA | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Colour Saturation Average | F16XM587 Colour Sat Avg | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587CAS | F16XM587COLA | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Colour Value Average | F16XM587 Colour Avg | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587CHS | F16XM587COLH | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Colour Value Max | F16XM587 Colour Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587CLS | F16XM587COLL | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Colour Value Min | F16XM587 Colour Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587CSS | F16XM587COLS | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Colour Value std | F16XM587 Colour STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587BXLS | F16XM587BXL | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Bubble Size - Extra Large | F16XM587 Bubble X-Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587BXSS | F16XM587BXS | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Bubble Size - Fine | F16XM587 Bubble Fine | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587BLS | F16XM587BL | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Bubble Size - Large | F16XM587 Bubble Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587BMS | F16XM587BM | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Bubble Size - Medium | F16XM587 Bubble Medium | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587BTSS | F16XM587BTS | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Bubble Size - Top Size | F16XM587 Bubble Topsize | 1 | 0 | 10 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM587LVLS | F16XM587LVL | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Lidar Level | F16XM587 Froth Depth | 1 | 0 | 500 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588VDS | F16XM588VDIR | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Velocity Direction | F16XM588 Velocity Dir. | 1 | 0 | 360 | ° | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588VMS | F16XM588VMAG | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Velocity Magnitude | F16XM588 Velocity Mag. | 1 | 0 | 20 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588PLS | F16XM588PULL | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Velocity Pulling Rate | F16XM588 Pulling Rate | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588VXS | F16XM588VELX | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Velocity X | F16XM588 Velocity X | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588VYS | F16XM588VELY | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Velocity Y | F16XM588 Velocity Y | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588HS | F16XM588HUE | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Colour Hue | F16XM588 Colour Hue | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588HHS | F16XM588HUEH | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Colour Max hue | F16XM588 Colour Hue Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588HLS | F16XM588HUEL | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Colour Min hue | F16XM588 Colour Hue Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588HSS | F16XM588HUES | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Colour std hue | F16XM588 Colour Hue STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588SS | F16XM588SAT | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Colour Saturation | F16XM588 Colour Sat | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588SHS | F16XM588SATH | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Colour Saturation Max | F16XM588 Colour Sat Max | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588SLS | F16XM588SATL | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Colour Saturation Min | F16XM588 Colour Sat Min | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588SAS | F16XM588SATA | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Colour Saturation Average | F16XM588 Colour Sat Avg | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588CAS | F16XM588COLA | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Colour Value Average | F16XM588 Colour Avg | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588CHS | F16XM588COLH | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Colour Value Max | F16XM588 Colour Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588CLS | F16XM588COLL | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Colour Value Min | F16XM588 Colour Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588CSS | F16XM588COLS | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Colour Value std | F16XM588 Colour STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588BXLS | F16XM588BXL | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Bubble Size - Extra Large | F16XM588 Bubble X-Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588BXSS | F16XM588BXS | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Bubble Size - Fine | F16XM588 Bubble Fine | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588BLS | F16XM588BL | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Bubble Size - Large | F16XM588 Bubble Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588BMS | F16XM588BM | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Bubble Size - Medium | F16XM588 Bubble Medium | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588BTSS | F16XM588BTS | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Bubble Size - Top Size | F16XM588 Bubble Topsize | 1 | 0 | 10 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM588LVLS | F16XM588LVL | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Lidar Level | F16XM588 Froth Depth | 1 | 0 | 500 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589VDS | F16XM589VDIR | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Velocity Direction | F16XM589 Velocity Dir. | 1 | 0 | 360 | ° | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589VMS | F16XM589VMAG | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Velocity Magnitude | F16XM589 Velocity Mag. | 1 | 0 | 20 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589PLS | F16XM589PULL | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Velocity Pulling Rate | F16XM589 Pulling Rate | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589VXS | F16XM589VELX | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Velocity X | F16XM589 Velocity X | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589VYS | F16XM589VELY | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Velocity Y | F16XM589 Velocity Y | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589HS | F16XM589HUE | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Colour Hue | F16XM589 Colour Hue | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589HHS | F16XM589HUEH | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Colour Max hue | F16XM589 Colour Hue Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589HLS | F16XM589HUEL | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Colour Min hue | F16XM589 Colour Hue Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589HSS | F16XM589HUES | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Colour std hue | F16XM589 Colour Hue STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589SS | F16XM589SAT | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Colour Saturation | F16XM589 Colour Sat | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589SHS | F16XM589SATH | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Colour Saturation Max | F16XM589 Colour Sat Max | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589SLS | F16XM589SATL | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Colour Saturation Min | F16XM589 Colour Sat Min | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589SAS | F16XM589SATA | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Colour Saturation Average | F16XM589 Colour Sat Avg | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589CAS | F16XM589COLA | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Colour Value Average | F16XM589 Colour Avg | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589CHS | F16XM589COLH | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Colour Value Max | F16XM589 Colour Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589CLS | F16XM589COLL | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Colour Value Min | F16XM589 Colour Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589CSS | F16XM589COLS | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Colour Value std | F16XM589 Colour STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589BXLS | F16XM589BXL | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Bubble Size - Extra Large | F16XM589 Bubble X-Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589BXSS | F16XM589BXS | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Bubble Size - Fine | F16XM589 Bubble Fine | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589BLS | F16XM589BL | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Bubble Size - Large | F16XM589 Bubble Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589BMS | F16XM589BM | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Bubble Size - Medium | F16XM589 Bubble Medium | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589BTSS | F16XM589BTS | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Bubble Size - Top Size | F16XM589 Bubble Topsize | 1 | 0 | 10 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM589LVLS | F16XM589LVL | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Lidar Level | F16XM589 Froth Depth | 1 | 0 | 500 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590VDS | F16XM590VDIR | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Velocity Direction | F16XM590 Velocity Dir. | 1 | 0 | 360 | ° | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590VMS | F16XM590VMAG | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Velocity Magnitude | F16XM590 Velocity Mag. | 1 | 0 | 20 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590PLS | F16XM590PULL | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Velocity Pulling Rate | F16XM590 Pulling Rate | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590VXS | F16XM590VELX | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Velocity X | F16XM590 Velocity X | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590VYS | F16XM590VELY | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Velocity Y | F16XM590 Velocity Y | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590HS | F16XM590HUE | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Colour Hue | F16XM590 Colour Hue | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590HHS | F16XM590HUEH | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Colour Max hue | F16XM590 Colour Hue Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590HLS | F16XM590HUEL | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Colour Min hue | F16XM590 Colour Hue Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590HSS | F16XM590HUES | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Colour std hue | F16XM590 Colour Hue STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590SS | F16XM590SAT | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Colour Saturation | F16XM590 Colour Sat | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590SHS | F16XM590SATH | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Colour Saturation Max | F16XM590 Colour Sat Max | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590SLS | F16XM590SATL | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Colour Saturation Min | F16XM590 Colour Sat Min | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590SAS | F16XM590SATA | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Colour Saturation Average | F16XM590 Colour Sat Avg | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590CAS | F16XM590COLA | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Colour Value Average | F16XM590 Colour Avg | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590CHS | F16XM590COLH | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Colour Value Max | F16XM590 Colour Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590CLS | F16XM590COLL | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Colour Value Min | F16XM590 Colour Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590CSS | F16XM590COLS | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Colour Value std | F16XM590 Colour STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590BXLS | F16XM590BXL | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Bubble Size - Extra Large | F16XM590 Bubble X-Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590BXSS | F16XM590BXS | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Bubble Size - Fine | F16XM590 Bubble Fine | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590BLS | F16XM590BL | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Bubble Size - Large | F16XM590 Bubble Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590BMS | F16XM590BM | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Bubble Size - Medium | F16XM590 Bubble Medium | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590BTSS | F16XM590BTS | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Bubble Size - Top Size | F16XM590 Bubble Topsize | 1 | 0 | 10 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM590LVLS | F16XM590LVL | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Lidar Level | F16XM590 Froth Depth | 1 | 0 | 500 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591VDS | F16XM591VDIR | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Velocity Direction | F16XM591 Velocity Dir. | 1 | 0 | 360 | ° | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591VMS | F16XM591VMAG | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Velocity Magnitude | F16XM591 Velocity Mag. | 1 | 0 | 20 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591PLS | F16XM591PULL | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Velocity Pulling Rate | F16XM591 Pulling Rate | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591VXS | F16XM591VELX | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Velocity X | F16XM591 Velocity X | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591VYS | F16XM591VELY | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Velocity Y | F16XM591 Velocity Y | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591HS | F16XM591HUE | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Colour Hue | F16XM591 Colour Hue | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591HHS | F16XM591HUEH | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Colour Max hue | F16XM591 Colour Hue Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591HLS | F16XM591HUEL | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Colour Min hue | F16XM591 Colour Hue Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591HSS | F16XM591HUES | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Colour std hue | F16XM591 Colour Hue STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591SS | F16XM591SAT | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Colour Saturation | F16XM591 Colour Sat | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591SHS | F16XM591SATH | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Colour Saturation Max | F16XM591 Colour Sat Max | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591SLS | F16XM591SATL | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Colour Saturation Min | F16XM591 Colour Sat Min | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591SAS | F16XM591SATA | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Colour Saturation Average | F16XM591 Colour Sat Avg | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591CAS | F16XM591COLA | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Colour Value Average | F16XM591 Colour Avg | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591CHS | F16XM591COLH | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Colour Value Max | F16XM591 Colour Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591CLS | F16XM591COLL | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Colour Value Min | F16XM591 Colour Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591CSS | F16XM591COLS | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Colour Value std | F16XM591 Colour STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591BXLS | F16XM591BXL | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Bubble Size - Extra Large | F16XM591 Bubble X-Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591BXSS | F16XM591BXS | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Bubble Size - Fine | F16XM591 Bubble Fine | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591BLS | F16XM591BL | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Bubble Size - Large | F16XM591 Bubble Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591BMS | F16XM591BM | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Bubble Size - Medium | F16XM591 Bubble Medium | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591BTSS | F16XM591BTS | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Bubble Size - Top Size | F16XM591 Bubble Topsize | 1 | 0 | 10 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F16XM591LVLS | F16XM591LVL | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Lidar Level | F16XM591 Froth Depth | 1 | 0 | 500 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101VDS | F18CAM101VDIR | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Velocity Direction | F18CAM101 Velocity Dir. | 1 | 0 | 360 | ° | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101VMS | F18CAM101VMAG | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Velocity Magnitude | F18CAM101 Velocity Mag. | 1 | 0 | 20 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101PLS | F18CAM101PULL | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Velocity Pulling Rate | F18CAM101 Pulling Rate | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101VXS | F18CAM101VELX | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Velocity X | F18CAM101 Velocity X | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101VYS | F18CAM101VELY | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Velocity Y | F18CAM101 Velocity Y | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101HS | F18CAM101HUE | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Colour Hue | F18CAM101 Colour Hue | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101HHS | F18CAM101HUEH | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Colour Max hue | F18CAM101 Colour Hue Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101HLS | F18CAM101HUEL | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Colour Min hue | F18CAM101 Colour Hue Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101HSS | F18CAM101HUES | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Colour std hue | F18CAM101 Colour Hue STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101SS | F18CAM101SAT | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Colour Saturation | F18CAM101 Colour Sat | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101SHS | F18CAM101SATH | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Colour Saturation Max | F18CAM101 Colour Sat Max | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101SLS | F18CAM101SATL | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Colour Saturation Min | F18CAM101 Colour Sat Min | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101SAS | F18CAM101SATA | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Colour Saturation Average | F18CAM101 Colour Sat Avg | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101CAS | F18CAM101COLA | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Colour Value Average | F18CAM101 Colour Avg | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101CHS | F18CAM101COLH | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Colour Value Max | F18CAM101 Colour Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101CLS | F18CAM101COLL | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Colour Value Min | F18CAM101 Colour Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101CSS | F18CAM101COLS | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Colour Value std | F18CAM101 Colour STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101BXLS | F18CAM101BXL | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Bubble Size - Extra Large | F18CAM101 Bubble X-Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101BXSS | F18CAM101BXS | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Bubble Size - Fine | F18CAM101 Bubble Fine | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101BLS | F18CAM101BL | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Bubble Size - Large | F18CAM101 Bubble Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101BMS | F18CAM101BM | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Bubble Size - Medium | F18CAM101 Bubble Medium | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101BTSS | F18CAM101BTS | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Bubble Size - Top Size | F18CAM101 Bubble Topsize | 1 | 0 | 10 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM101LVLS | F18CAM101LVL | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Lidar Level | F18CAM101 Froth Depth | 1 | 0 | 500 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102VDS | F18CAM102VDIR | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Velocity Direction | F18CAM102 Velocity Dir. | 1 | 0 | 360 | ° | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102VMS | F18CAM102VMAG | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Velocity Magnitude | F18CAM102 Velocity Mag. | 1 | 0 | 20 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102PLS | F18CAM102PULL | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Velocity Pulling Rate | F18CAM102 Pulling Rate | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102VXS | F18CAM102VELX | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Velocity X | F18CAM102 Velocity X | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102VYS | F18CAM102VELY | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Velocity Y | F18CAM102 Velocity Y | 1 | 0 | 20 | m/s | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102HS | F18CAM102HUE | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Colour Hue | F18CAM102 Colour Hue | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102HHS | F18CAM102HUEH | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Colour Max hue | F18CAM102 Colour Hue Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102HLS | F18CAM102HUEL | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Colour Min hue | F18CAM102 Colour Hue Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102HSS | F18CAM102HUES | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Colour std hue | F18CAM102 Colour Hue STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102SS | F18CAM102SAT | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Colour Saturation | F18CAM102 Colour Sat | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102SHS | F18CAM102SATH | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Colour Saturation Max | F18CAM102 Colour Sat Max | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102SLS | F18CAM102SATL | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Colour Saturation Min | F18CAM102 Colour Sat Min | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102SAS | F18CAM102SATA | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Colour Saturation Average | F18CAM102 Colour Sat Avg | 1 | 0 | 100 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102CAS | F18CAM102COLA | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Colour Value Average | F18CAM102 Colour Avg | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102CHS | F18CAM102COLH | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Colour Value Max | F18CAM102 Colour Max | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102CLS | F18CAM102COLL | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Colour Value Min | F18CAM102 Colour Min | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102CSS | F18CAM102COLS | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Colour Value std | F18CAM102 Colour STD | 1 | 0 | 150 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102BXLS | F18CAM102BXL | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Bubble Size - Extra Large | F18CAM102 Bubble X-Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102BXSS | F18CAM102BXS | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Bubble Size - Fine | F18CAM102 Bubble Fine | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102BLS | F18CAM102BL | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Bubble Size - Large | F18CAM102 Bubble Large | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102BMS | F18CAM102BM | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Bubble Size - Medium | F18CAM102 Bubble Medium | 1 | 0 | 1 | - | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102BTSS | F18CAM102BTS | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Bubble Size - Top Size | F18CAM102 Bubble Topsize | 1 | 0 | 10 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F18CAM102LVLS | F18CAM102LVL | 2000-F18-PID-PR-10002 | F18-CAM-102 Cleaner-Scavenger Flotation Cell Froth Camera Lidar Level | F18CAM102 Froth Depth | 1 | 0 | 500 | mm | [21 empty] | SoftTag From FLS OPC Server Ref: 2000-ME001.1-J02-50002 If signal is BAD, hold last known value and alarm. Alarm and ranges are TBC with vendor data | 3 |  |  |  |  | 2025-06-19 | Updated as per CR-020
|  |  |  | F17XM572CLHTS | F17XM572CLHT | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Clarity Hold | F17XM572 ClarityHoldTime | 1 | 0 | 60 | s | [21 empty] | SoftTag Manta Ref: Manta_Sub.CLHoldTime Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371) | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572DSDS | F17XM572DSD | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Dive Start Delay | F17XM572 DiveStartDelay | 1 | 0 | 600 | s | [21 empty] | SoftTag Manta Ref: Manta_Sub.DiveStDly Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572EPRS | F17XM572EPR | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Encode Pulse per Revolution | F17XM572 Pulse Per Rev | 1 | 0 | 1000 | pulse/rev | [21 empty] | SoftTag Manta Ref: Manta_Sub.EncPulRev Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572MDTS | F17XM572MDT | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Maximum Dive Time | F17XM572 MaxDiveTime | 1 | 0 | 300 | s | [21 empty] | SoftTag Manta Ref: Manta_Sub.MaxDiveTime Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572RCTS | F17XM572RCT | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Rake Cycle Time | F17XM572 RakeCycTime | 1 | 0 | 900 | s | [21 empty] | SoftTag Manta Ref: Manta_Sub.RakeCycTime Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572RSTS | F17XM572RST | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Rake Simulation Time | F17XM572 RakeSimTime | 1 | 0 | 900 | s | [21 empty] | SoftTag Manta Ref: Manta_Sub.RakeSimTime Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572RTS | F17XM572RT | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Rake In Time Buffer | F17XM572 Rake In Time | 1 | 0 | 900 | s | [21 empty] | SoftTag Manta Ref: Manta_Sub.RakeTime Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572RWS | F17XM572RW | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Rake Window | F17XM572 Rake Window | 1 | 0 | 60 | s | [21 empty] | SoftTag Manta Ref: Manta_Sub.RakeWindow Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572RCSDS | F17XM572RCSD | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Recover Stop Delay | F17XM572 RecoverStpDelay | 1 | 0 | 60 | s | [21 empty] | SoftTag Manta Ref: Manta_Sub.RecStpDly Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572RTSDS | F17XM572RTSD | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Retract Stop Delay | F17XM572 RetractStpDelay | 1 | 0 | 60 | s | [21 empty] | SoftTag Manta Ref: Manta_Sub.RetStpDly Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572SSS | F17XM572SS | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub System Status (Stop, Run, Fault) | F17XM572 System Status | 1 | - | - | Status | [21 empty] | SoftTag Manta Ref: Manta_Sub.SysSta Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572WTS | F17XM572WT | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Wash Time | F17XM572 Wash Time | 1 | 0 | 300 | s | [21 empty] | SoftTag Manta Ref: Manta_Sub.WashTime Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572WCSS | F17XM572WCS | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Winch Creep Speed | F17XM572 WinchCreepSpeed | 1 | 0 | 100 | % | [21 empty] | SoftTag Manta Ref: Manta_Sub.WchCrpSpd Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572WDCS | F17XM572WDC | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Winch Drum Circumference | F17XM572 WinchDrumCirc | 1 | 0 | 3 | m | [21 empty] | SoftTag Manta Ref: Manta_Sub.WchDrumCirc Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572WLSS | F17XM572WLS | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Winch Lower Speed | F17XM572 WinchLowSpeed | 1 | 0 | 100 | % | [21 empty] | SoftTag Manta Ref: Manta_Sub.WchLSpd Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572WRCSS | F17XM572WRCS | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Winch Recovery Speed | F17XM572 WnchRecoverySpd | 1 | 0 | 100 | % | [21 empty] | SoftTag Manta Ref: Manta_Sub.WchRecSpd Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572WRSSS | F17XM572WRSS | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Winch Raise Speed | F17XM572 WinchRaiseSpeed | 1 | 0 | 100 | % | [21 empty] | SoftTag Manta Ref: Manta_Sub.WchRseSpd Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572CTS | F17XM572CT | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Counter to be read by the DCS | F17XM572 Watchdog Count | 1 | 0 | 10000 | s | [21 empty] | SoftTag Manta Ref: Manta_Sub.WDCounter Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572CDRS | F17XM572CDR | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Current Depth Raw | F17XM572 Current Depth | 1 | -12 | 12 | m | [21 empty] | SoftTag Manta Ref: Manta_Sub.CurDpthRaw Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572CSRS | F17XM572CSR | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Current Solids Raw | F17XM572 Current Solids | 1 | 0 | 100 | g/L | [21 empty] | SoftTag Manta Ref: Manta_Sub.CurdBRaw Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572CSSGS | F17XM572CSGS | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Current Solids SG | F17XM572 CurrentSolidSG | 1 | 0 | 3 | SG | [21 empty] | SoftTag Manta Ref: Manta_Sub.CurdBRaw Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572CLDS | F17XM572CLD | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Clarity Depth | F17XM572 Clarity Depth | 1 | -12 | 12 | m | [21 empty] | SoftTag Manta Ref: Manta_Sub.CLDpth Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572CLRS | F17XM572CLR | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Clarity Depth Raw | F17XM572 Clarity | 1 | 0 | 100 | g/L | [21 empty] | SoftTag Manta Ref: Manta_Sub.CLRaw Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572CLHS | F17XM572CLH | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Clarity Held | F17XM572 Clarity Held | 1 | 0 | 100 | g/L | [21 empty] | SoftTag Manta Ref: Manta_Sub.CLHeld Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572I35TS | F17XM572I35T | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub 3.5 g/L Interface Target | F17XM572 IF 3.5 Target | 1 | 0 | 100 | g/L | [21 empty] | SoftTag Manta Ref: Manta_Sub.IF35Trgt Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572IF35S | F17XM572IF35 | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub 3.5 g/L Interface Depth Raw | F17XM572 IF 3.5 Raw | 1 | -12 | 12 | metres | [21 empty] | SoftTag Manta Ref: Manta_Sub.IF35Raw Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572I35HS | F17XM572I35H | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub 3.5 g/L Interface Level Held | F17XM572 IF 3.5 Held | 1 | -12 | 12 | metres | [21 empty] | SoftTag Manta Ref: Manta_Sub.IF35Held Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572I19TS | F17XM572I19T | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub 19 g/L Interface Target | F17XM572 IF 19.0 Target | 1 | 0 | 100 | g/L | [21 empty] | SoftTag Manta Ref: Manta_Sub.IF190Trgt Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572IF19S | F17XM572IF19 | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub 19 g/L Interface Depth Raw | F17XM572 IF 19.0 Raw | 1 | -12 | 12 | metres | [21 empty] | SoftTag Manta Ref: Manta_Sub.IF190Raw Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572I19HS | F17XM572I19H | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub 19 g/L Interface Held | F17XM572 IF 19.0 Held | 1 | -12 | 12 | metres | [21 empty] | SoftTag Manta Ref: Manta_Sub.IF190Held Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572CBRS | F17XM572CBR | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Bed Depth Raw | F17XM572 Bed Depth | 1 | -12 | 12 | metres | [21 empty] | SoftTag Manta Ref: Manta_Sub.CBRaw Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572CLS | F17XM572CL | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Cable Length | F17XM572 Cable Length | 1 | 0 | 30 | m | [21 empty] | SoftTag Manta Ref: Manta_Sub.CableLgth Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572CZS | F17XM572CZ | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Creep Zone | F17XM572 Creep Zone | 1 | 0 | 12 | m | [21 empty] | SoftTag Manta Ref: Manta_Sub.CZ Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572DPS | F17XM572DP | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Distance Probe is Above Liquid | F17XM572 DistAboveLiquid | 1 | 0 | 12 | m | [21 empty] | SoftTag Manta Ref: Manta_Sub.DP Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572LVLS | F17XM572LVL | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Liquid Height from Tank Bottom | F17XM572 Liquid Height | 1 | 0 | 12 | m | [21 empty] | SoftTag Manta Ref: Manta_Sub.LiqHght Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | F17XM572CALS | F17XM572CAL | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Probe Calibration | F17XM572 Probe Calib | 1 | - | - | - | [21 empty] | SoftTag Manta Ref: Manta_Sub.ProbCalib Details TBC by vendor. Refer to Manta Sub V408 Modbus Tag List (03-REG-371 | [5 empty] | 2025-06-16 | Updated as per Manta. TBC
|  |  |  | PIT17140 | PI17140 | 2000-F17-PID-PR-10001 | F17-HU-422 Flotation Tailings Thickener Feed Box Valve HPU Pressure Indicating Transmitter | F17HU422 Hyd Supply | 1 | 0 | 50000 | kPa | [16 empty] | 15000 | 5 | 16000 | 5 |  |  | 4 | [5 empty] | MOC-690
|  |  |  | TIT17141 | TI17141 | 2000-F17-PID-PR-10001 | F17-HU-422 Flotation Tailings Thickener Feed Box Valve HPU Temperature Indicating Transmitter | F17HU422 Hyd Reservoir | 1 | 0 | 100 | °C | [16 empty] | 65 | 5 | 70 | 5 |  |  | 3 |  |  |  |  | 2025-07-02 | CR-021
|  |  |  | LIT17142 | LI17142 | 2000-F17-PID-PR-10001 | F17-HU-422 Flotation Tailings Thickener Feed Box Valve HPU Level Indicating Transmitter | F17HU422 Hyd Reservoir | 1 | 0 | 100 | % | [12 empty] | 50 | 5 | 60 | 5 | [6 empty] | 3 |  |  |  |  | 2025-07-02 | CR-021
|  |  |  | TIT17100 | TI17100 | - | F17-PP-455 FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 1 GEARBOX TEMPERATURE TRANSMITTER | F17PP455 Gearbox Temp | 1 | 0 | 100 | °C | [16 empty] | 85 | 5 | 90 | 5 |  | Hi-Hi Alarm to trip F17PP455 | 4
|  |  |  | TIT17110 | TI17110 | - | F17-PP-456 FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 2 GEARBOX TEMPERATURE TRANSMITTER | F17PP456 Gearbox Temp | 1 | 0 | 100 | °C | [16 empty] | 85 | 5 | 90 | 5 |  | Hi-Hi Alarm to trip F17PP456 | 4
|  |  |  | ZIT17127 | ZI17127 |  | FCV17127 Position Feedback |  |  | 0 | 100
|  |  |  | ZIT17128 | ZI17128 |  | FCV17128 Position Feedback |  |  | 0 | 100
|  |  |  | ZIT17130 | ZI17130 |  | FCV17130 Position Feedback |  |  | 0 | 100
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 494 | 494
`

## 2. Analogue Output
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION (F16, F17, F18)
2000-F16-LST-PR-10001
ANALOGUE INSTRUMENTS (AO)
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  |  |  | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | Comments | Rev | OK | Date | OK | Date
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 0 | 0
Operator to get electrician to inspect unit for potential failure

## 3. Digital Input
`
|  |  |  | PROCESS CONTROL TABLES - FLOTATION (F16, F17, F18) |  |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)*
2000-F16-LST-PR-10001
DIGITAL INSTRUMENTS (DI)
[19 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Source | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | Change Date | Change Reference | OK | Date | OK | Date
|  |  |  | F18RIO001PS2 | F18RIO001_PS2 | 2000-F18-PID-PR-10001 | F18-RIO-001 PS2 24VDC HEALTHY | F18RIO001 PS2 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F18RIO001PS1 | F18RIO001_PS1 | 2000-F18-PID-PR-10001 | F18-RIO-001 PS1 24VDC HEALTHY | F18RIO001 PS1 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | ZS17010 | ZA17010 17XM572RSO | 2000-F17-PID-PR-10001 | F17-TH-401 Flotation Tailings Thickener Rake Drive Position Switch | F17TH401 Thickener Rake | Off | On |  | Hardwired to DCS |  |  |  | 3 | [6 empty] | VV 24/07/2026 Deleted as per Master IO lIst
|  |  |  | F17RIO002PS2 | F17RIO002_PS2 | 2000-F17-PID-PR-10001 | F17-RIO-002 PS2 24VDC HEALTHY | F17RIO002 PS2 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F17RIO002PS1 | F17RIO002_PS1 | 2000-F17-PID-PR-10001 | F17-RIO-002 PS1 24VDC HEALTHY | F17RIO002 PS1 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16RIO002PS2 | F16RIO002_PS2 | 2000-F16-PID-PR-10001 | F16-RIO-002 PS2 24VDC HEALTHY | F16RIO002 PS2 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16RIO002PS1 | F16RIO002_PS1 | 2000-F16-PID-PR-10001 | F16-RIO-002 PS1 24VDC HEALTHY | F16RIO002 PS1 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16SW104Q1OP | F16SW104Q1_OP | 2000-F16-PID-PR-10001 | F16-SW-104 Mains Supply CB Opened | F16SW104 Breaker Open | N_Active | Active |  | Hardwired to DCS |  |  |  | 3
|  |  |  | F16SW104Q1CL | F16SW104_Q1CL | 2000-F16-PID-PR-10001 | F16-SW-104 Mains Supply CB Closed | F16SW104 Breaker Closed | N_Active | Active |  | Hardwired to DCS |  |  |  | 3
|  |  |  | F16SW104SD | F16SW104_SD | 2000-F16-PID-PR-10001 | F16-SW-104 Surge Diverter Ok | F16SW104 Surge Diverter | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16SR001ESTP | F16SR001_ESTP | N/A | Flotation 11kV Switchroom Emergency Shutdown Healthy | Flot 11kV SR E Shut | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16FIP002ISL | F16FIP002_ISL | 2000-F16-PID-PR-10001 | F16-FIP-002 Isolated | F16FIP002 Isolate | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | 20/02/2026 MOC103 | 3
|  |  |  | F17RIO001PS2 | F17RIO001_PS2 | 2000-F16-PID-PR-10001 | F17-RIO-001 PS2 24VDC HEALTHY | F17RIO001 PS2 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16SW104Q2CL | F16SW104_Q2CL | 2000-F16-PID-PR-10001 | F16-SW-104 Generator Supply CB Closed | F16SW104 Gen CB Closed | N_Active | Active |  | Hardwired to DCS |  |  |  | 3
|  |  |  | F17RIO001PS1 | F17RIO001_PS1 | 2000-F16-PID-PR-10001 | F17-RIO-001 PS1 24VDC HEALTHY | F17RIO001 PS1 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16AN403S2XRS | F16AN403S2XR | 2000-F16-PID-PR-10006 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Sample X-Ray Active | F16AN403 S2 X-Ray | N_Active | Active |  | SoftTag |  |  | Status bit = 07 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S3XRS | F16AN403S3XR | 2000-F16-PID-PR-10007 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Sample X-Ray Active | F16AN403 S3 X-Ray | N_Active | Active |  | SoftTag |  |  | Status bit = 07 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S1XRS | F16AN403S1XR | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Sample X-Ray Active | F16AN403 S1 X-Ray | N_Active | Active |  | SoftTag |  |  | Status bit = 07 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S1MRS | F16AN403S1MR | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Sample Measurement Result Not Ok | F16AN403 S1 Results Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 08 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S12XS | F16AN403S12XR | 2000-F16-PID-PR-10016 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Sample X-Ray Active | F16AN403 S12 X-Ray | N_Active | Active |  | SoftTag |  |  | Status bit = 07 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S11XS | F16AN403S11XR | 2000-F16-PID-PR-10015 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Sample X-Ray Active | F16AN403 S11 X-Ray | N_Active | Active |  | SoftTag |  |  | Status bit = 07 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S4MRS | F16AN403S4MR | 2000-F16-PID-PR-10008 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Sample Measurement Result Not Ok | F16AN403 S4 Results Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 08 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S3MRS | F16AN403S3MR | 2000-F16-PID-PR-10007 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Sample Measurement Result Not Ok | F16AN403 S3 Results Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 08 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S9XRS | F16AN403S9XR | 2000-F16-PID-PR-10013 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Sample X-Ray Active | F16AN403 S9 X-Ray | N_Active | Active |  | SoftTag |  |  | Status bit = 07 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S10XS | F16AN403S10XR | 2000-F16-PID-PR-10014 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Sample X-Ray Active | F16AN403 S10 X-Ray | N_Active | Active |  | SoftTag |  |  | Status bit = 07 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S6XRS | F16AN403S6XR | 2000-F16-PID-PR-10010 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Sample X-Ray Active | F16AN403 S6 X-Ray | N_Active | Active |  | SoftTag |  |  | Status bit = 07 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S4XRS | F16AN403S4XR | 2000-F16-PID-PR-10008 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Sample X-Ray Active | F16AN403 S4 X-Ray | N_Active | Active |  | SoftTag |  |  | Status bit = 07 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S5XRS | F16AN403S5XR | 2000-F16-PID-PR-10009 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Sample X-Ray Active | F16AN403 S5 X-Ray | N_Active | Active |  | SoftTag |  |  | Status bit = 07 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S7XRS | F16AN403S7XR | 2000-F16-PID-PR-10011 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Sample X-Ray Active | F16AN403 S7 X-Ray | N_Active | Active |  | SoftTag |  |  | Status bit = 07 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S8XRS | F16AN403S8XR | 2000-F16-PID-PR-10012 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Sample X-Ray Active | F16AN403 S8 X-Ray | N_Active | Active |  | SoftTag |  |  | Status bit = 07 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S12AS | F16AN403S12AV | 2000-F16-PID-PR-10016 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Sample Analysis Values Not Ok | F16AN403 S12 AnalysisFlt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 09 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S10AS | F16AN403S10AV | 2000-F16-PID-PR-10014 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Sample Analysis Values Not Ok | F16AN403 S10 AnalysisFlt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 09 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S11AS | F16AN403S11AV | 2000-F16-PID-PR-10015 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Sample Analysis Values Not Ok | F16AN403 S11 AnalysisFlt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 09 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S9AVS | F16AN403S9AV | 2000-F16-PID-PR-10013 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Sample Analysis Values Not Ok | F16AN403 S9 Analysis Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 09 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | XS16174 | XI16174 | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Started | F16AN403 Analyser Start | N_Active | Active |  | SoftTag |  |  | Status bit = 00 From general analyser bit status F16AN403ST. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S7AVS | F16AN403S7AV | 2000-F16-PID-PR-10011 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Sample Analysis Values Not Ok | F16AN403 S7 Analysis Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 09 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S5AVS | F16AN403S5AV | 2000-F16-PID-PR-10009 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Sample Analysis Values Not Ok | F16AN403 S5 Analysis Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 09 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S6AVS | F16AN403S6AV | 2000-F16-PID-PR-10010 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Sample Analysis Values Not Ok | F16AN403 S6 Analysis Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 09 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S8AVS | F16AN403S8AV | 2000-F16-PID-PR-10012 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Sample Analysis Values Not Ok | F16AN403 S8 Analysis Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 09 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S11MS | F16AN403S11MR | 2000-F16-PID-PR-10015 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Sample Measurement Result Not Ok | F16AN403 S11 Results Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 08 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S4AVS | F16AN403S4AV | 2000-F16-PID-PR-10008 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Sample Analysis Values Not Ok | F16AN403 S4 Analysis Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 09 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S2AVS | F16AN403S2AV | 2000-F16-PID-PR-10006 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Sample Analysis Values Not Ok | F16AN403 S2 Analysis Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 09 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S3AVS | F16AN403S3AV | 2000-F16-PID-PR-10007 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Sample Analysis Values Not Ok | F16AN403 S3 Analysis Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 09 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S1AVS | F16AN403S1AV | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Sample Analysis Values Not Ok | F16AN403 S1 Analysis Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 09 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S12MS | F16AN403S12MR | 2000-F16-PID-PR-10016 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Sample Measurement Result Not Ok | F16AN403 S12 Results Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 08 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S10MS | F16AN403S10MR | 2000-F16-PID-PR-10014 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Sample Measurement Result Not Ok | F16AN403 S10 Results Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 08 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S2NMS | F16AN403S2NM | 2000-F16-PID-PR-10006 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Sample Not Measurable | F16AN403 S2 Not Meas | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 06 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S10NS | F16AN403S10NM | 2000-F16-PID-PR-10014 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Sample Not Measurable | F16AN403 S10 Not Meas | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 06 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S8NMS | F16AN403S8NM | 2000-F16-PID-PR-10012 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Sample Not Measurable | F16AN403 S8 Not Meas | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 06 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S12NS | F16AN403S12NM | 2000-F16-PID-PR-10016 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Sample Not Measurable | F16AN403 S12 Not Meas | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 06 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S11NS | F16AN403S11NM | 2000-F16-PID-PR-10015 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Sample Not Measurable | F16AN403 S11 Not Meas | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 06 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S9NMS | F16AN403S9NM | 2000-F16-PID-PR-10013 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Sample Not Measurable | F16AN403 S9 Not Meas | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 06 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S7NMS | F16AN403S7NM | 2000-F16-PID-PR-10011 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Sample Not Measurable | F16AN403 S7 Not Meas | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 06 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S6NMS | F16AN403S6NM | 2000-F16-PID-PR-10010 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Sample Not Measurable | F16AN403 S6 Not Meas | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 06 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S5NMS | F16AN403S5NM | 2000-F16-PID-PR-10009 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Sample Not Measurable | F16AN403 S5 Not Meas | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 06 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S4NMS | F16AN403S4NM | 2000-F16-PID-PR-10008 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Sample Not Measurable | F16AN403 S4 Not Meas | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 06 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S3NMS | F16AN403S3NM | 2000-F16-PID-PR-10007 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Sample Not Measurable | F16AN403 S3 Not Meas | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 06 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16SW011A19OS | F16SW011A19OP | N/A | Flotation 11kV Switchboard Panel A19 Contactor Opened | F16SW011 A19 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname |  |  |  |  | Venson: These signals have been tested in the Modpack, however, different tag naming used.
|  |  |  | F16SW011A19CS | F16SW011A19CL | N/A | Flotation 11kV Switchboard Panel A19 Contactor Closed | F16SW011 A19 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A18ECS | F16SW011A18EC | N/A | Flotation 11kV Switchboard Panel A18 Earth Switch Closed | F16SW011 A18 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A18EOS | F16SW011A18EO | N/A | Flotation 11kV Switchboard Panel A18 Earth Switch Opened | F16SW011 A18 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A20TTS | F16SW011A20TT | N/A | Flotation 11kV Switchboard Panel A20 Truck In Test | F16SW011 A20 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A20CLS | F16SW011A20CL | N/A | Flotation 11kV Switchboard Panel A20 Circuit Breaker Closed | F16SW011 A20 CB | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A20OPS | F16SW011A20OP | N/A | Flotation 11kV Switchboard Panel A20 Circuit Breaker Opened | F16SW011 A20 CB | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A19ECS | F16SW011A19EC | N/A | Flotation 11kV Switchboard Panel A19 Earth Switch Closed | F16SW011 A19 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A19EOS | F16SW011A19EO | N/A | Flotation 11kV Switchboard Panel A19 Earth Switch Opened | F16SW011 A19 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A19TTS | F16SW011A19TT | N/A | Flotation 11kV Switchboard Panel A19 Truck In Test | F16SW011 A19 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A19TSS | F16SW011A19TS | N/A | Flotation 11kV Switchboard Panel A19 Truck In Service | F16SW011 A19 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A19FHS | F16SW011A19FH | N/A | Flotation 11kV Switchboard Panel A19 Fuse Healthy | F16SW011 A19 Fuse | Alarm | Normal | Alarm | SoftTag | 0 |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A20TSS | F16SW011A20TS | N/A | Flotation 11kV Switchboard Panel A20 Truck In Service | F16SW011 A20 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A17TSS | F16SW011A17TS | N/A | Flotation 11kV Switchboard Panel A17 Truck In Service | F16SW011 A17 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A10TTS | F16SW011A10TT | N/A | Flotation 11kV Switchboard Panel A10 Truck In Test | F16SW011 A10 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A09CLS | F16SW011A09CL | N/A | Flotation 11kV Switchboard Panel A09 Circuit Breaker Closed | F16SW011 A09 CB | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A07EOS | F16SW011A07EO | N/A | Flotation 11kV Switchboard Panel A07 Earth Switch Opened | F16SW011 A07 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A06FHS | F16SW011A06FH | N/A | Flotation 11kV Switchboard Panel A06 Fuse Healthy | F16SW011 A06 Fuse | Alarm | Normal | Alarm | SoftTag | 0 |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A04ECS | F16SW011A04EC | N/A | Flotation 11kV Switchboard Panel A04 Earth Switch Closed | F16SW011 A04 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A03TSS | F16SW011A03TS | N/A | Flotation 11kV Switchboard Panel A03 Truck In Service | F16SW011 A03 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A02OPS | F16SW011A02OP | N/A | Flotation 11kV Switchboard Panel A02 Contactor Opened | F16SW011 A02 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16FIP001ISL | F16FIP001_ISL | N/A | F16-FIP-001 Isolated | F16FIP001 Isolate | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | 20/02/2026 MOC103 | 3
|  |  |  | F16SW11A16OPS | F16SW011A16OP | N/A | Flotation 11kV Switchboard Panel A16 Contactor Opened | F16SW011 A15 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname |  |  |  |  | Venson: These signals have been tested in the Modpack, however, different tag naming used.
|  |  |  | F16SW11A13TTS | F16SW011A13TT | N/A | Flotation 11kV Switchboard Panel A13 Truck In Test | F16SW011 A13 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A12OPS | F16SW011A12OP | N/A | Flotation 11kV Switchboard Panel A12 Circuit Breaker Opened | F16SW011 A12 CB | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A17CLS | F16SW011A17CL | N/A | Flotation 11kV Switchboard Panel A17 Contactor Closed | F16SW011 A17 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A10FHS | F16SW011A10FH | N/A | Flotation 11kV Switchboard Panel A10 Fuse Healthy | F16SW011 A10 Fuse | Alarm | Normal | Alarm | SoftTag | 0 |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A08ECS | F16SW011A08EC | N/A | Flotation 11kV Switchboard Panel A08 Earth Switch Closed | F16SW011 A08 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A07TSS | F16SW011A07TS | N/A | Flotation 11kV Switchboard Panel A07 Truck In Service | F16SW011 A07 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A06OPS | F16SW011A06OP | N/A | Flotation 11kV Switchboard Panel A06 Contactor Opened | F16SW011 A06 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A04TTS | F16SW011A04TT | N/A | Flotation 11kV Switchboard Panel A04 Truck In Test | F16SW011 A04 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A03CLS | F16SW011A03CL | N/A | Flotation 11kV Switchboard Panel A03 Contactor Closed | F16SW011 A03 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16BC001FL3 | F16BC001_FL3 | N/A | F16-BC-001 48VDC Charger Charger Fail | F16BC001 Charger Status | Alarm | Normal | Alarm | Hardwired to DCS |  |  |  | 3
|  |  |  | F16SW11A15EOS | F16SW011A15EO | N/A | Flotation 11kV Switchboard Panel A15 Earth Switch Opened | F16SW011 A15 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname |  |  |  |  | Venson: These signals have been tested in the Modpack, however, different tag naming used.
|  |  |  | F16SW11A13CLS | F16SW011A13CL | N/A | Flotation 11kV Switchboard Panel A13 Circuit Breaker Closed | F16SW011 A13 CB | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A11EOS | F16SW011A11EO | N/A | Flotation 11kV Switchboard Panel A11 Earth Switch Opened | F16SW011 A11 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A16EOS | F16SW011A16EO | N/A | Flotation 11kV Switchboard Panel A16 Earth Switch Opened | F16SW011 A16 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A09ECS | F16SW011A09EC | N/A | Flotation 11kV Switchboard Panel A09 Earth Switch Closed | F16SW011 A09 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A08TSS | F16SW011A08TS | N/A | Flotation 11kV Switchboard Panel A08 Truck In Service | F16SW011 A08 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A07OPS | F16SW011A07OP | N/A | Flotation 11kV Switchboard Panel A07 Contactor Opened | F16SW011 A07 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A05TTS | F16SW011A05TT | N/A | Flotation 11kV Switchboard Panel A05 Truck In Test | F16SW011 A05 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A04CLS | F16SW011A04CL | N/A | Flotation 11kV Switchboard Panel A04 Contactor Closed | F16SW011 A04 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A02EOS | F16SW011A02EO | N/A | Flotation 11kV Switchboard Panel A02 Earth Switch Opened | F16SW011 A02 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A12EOS | F16SW011A12EO | N/A | Flotation 11kV Switchboard Panel A12 Earth Switch Opened | F16SW011 A12 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A11FHS | F16SW011A11FH | N/A | Flotation 11kV Switchboard Panel A11 Fuse Healthy | F16SW011 A11 Fuse | Alarm | Normal | Alarm | SoftTag | 0 |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A17ECS | F16SW011A17EC | N/A | Flotation 11kV Switchboard Panel A17 Earth Switch Closed | F16SW011 A17 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A11OPS | F16SW011A11OP | N/A | Flotation 11kV Switchboard Panel A11 Contactor Opened | F16SW011 A11 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A09TTS | F16SW011A09TT | N/A | Flotation 11kV Switchboard Panel A09 Truck In Test | F16SW011 A09 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A08CLS | F16SW011A08CL | N/A | Flotation 11kV Switchboard Panel A08 Contactor Closed | F16SW011 A08 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A06EOS | F16SW011A06EO | N/A | Flotation 11kV Switchboard Panel A06 Earth Switch Opened | F16SW011 A06 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A05FHS | F16SW011A05FH | N/A | Flotation 11kV Switchboard Panel A05 Fuse Healthy | F16SW011 A05 Fuse | Alarm | Normal | Alarm | SoftTag | 0 |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A03ECS | F16SW011A03EC | N/A | Flotation 11kV Switchboard Panel A03 Earth Switch Closed | F16SW011 A03 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A02TSS | F16SW011A02TS | N/A | Flotation 11kV Switchboard Panel A02 Truck In Service | F16SW011 A02 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A16TSS | F16SW011A16TS | N/A | Flotation 11kV Switchboard Panel A16 Truck In Service | F16SW011 A16 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A15OPS | F16SW011A15OP | N/A | Flotation 11kV Switchboard Panel A15 Circuit Breaker Opened | F16SW011 A15 CB | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A12TSS | F16SW011A12TS | N/A | Flotation 11kV Switchboard Panel A12 Truck In Service | F16SW011 A12 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A17TTS | F16SW011A17TT | N/A | Flotation 11kV Switchboard Panel A17 Truck In Test | F16SW011 A17 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A10EOS | F16SW011A10EO | N/A | Flotation 11kV Switchboard Panel A10 Earth Switch Opened | F16SW011 A10 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A07ECS | F16SW011A07EC | N/A | Flotation 11kV Switchboard Panel A07 Earth Switch Closed | F16SW011 A07 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A06TSS | F16SW011A06TS | N/A | Flotation 11kV Switchboard Panel A06 Truck In Service | F16SW011 A06 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A05OPS | F16SW011A05OP | N/A | Flotation 11kV Switchboard Panel A05 Contactor Opened | F16SW011 A05 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A03TTS | F16SW011A03TT | N/A | Flotation 11kV Switchboard Panel A03 Truck In Test | F16SW011 A03 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A02CLS | F16SW011A02CL | N/A | Flotation 11kV Switchboard Panel A02 Contactor Closed | F16SW011 A02 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16FIP002ALM | F16FIP002_ALM | N/A | F16-FIP-002 Alarm | F16FIP002 Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | 20/02/2026 MOC103 | 3
|  |  |  | F16SW11A16CLS | F16SW011A16CL | N/A | Flotation 11kV Switchboard Panel A16 Contactor Closed | F16SW011 A15 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname |  |  |  |  | Venson: These signals have been tested in the Modpack, however, different tag naming used.
|  |  |  | F16SW11A13EOS | F16SW011A13EO | N/A | Flotation 11kV Switchboard Panel A13 Earth Switch Opened | F16SW011 A13 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A12CLS | F16SW011A12CL | N/A | Flotation 11kV Switchboard Panel A12 Circuit Breaker Closed | F16SW011 A12 CB | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A17OPS | F16SW011A17OP | N/A | Flotation 11kV Switchboard Panel A17 Contactor Opened | F16SW011 A17 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A10CLS | F16SW011A10CL | N/A | Flotation 11kV Switchboard Panel A10 Contactor Closed | F16SW011 A10 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A08EOS | F16SW011A08EO | N/A | Flotation 11kV Switchboard Panel A08 Earth Switch Opened | F16SW011 A08 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A07FHS | F16SW011A07FH | N/A | Flotation 11kV Switchboard Panel A07 Fuse Healthy | F16SW011 A07 Fuse | Alarm | Normal | Alarm | SoftTag | 0 |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A05ECS | F16SW011A05EC | N/A | Flotation 11kV Switchboard Panel A05 Earth Switch Closed | F16SW011 A05 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A04TSS | F16SW011A04TS | N/A | Flotation 11kV Switchboard Panel A04 Truck In Service | F16SW011 A04 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A03OPS | F16SW011A03OP | N/A | Flotation 11kV Switchboard Panel A03 Contactor Opened | F16SW011 A03 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16BC001FL2 | F16BC001_FL2 | 2000-F16-PID-PR-10001 | F16-BC-001 48VDC Charger Battery Fail | F16BC001 Charger Battery | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16SW11A15TTS | F16SW011A15TT | N/A | Flotation 11kV Switchboard Panel A15 Truck In Test | F16SW011 A15 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname |  |  |  |  | Venson: These signals have been tested in the Modpack, however, different tag naming used..
|  |  |  | F16SW11A13OPS | F16SW011A13OP | N/A | Flotation 11kV Switchboard Panel A13 Circuit Breaker Opened | F16SW011 A13 CB | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A11TTS | F16SW011A11TT | N/A | Flotation 11kV Switchboard Panel A11 Truck In Test | F16SW011 A11 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A16ECS | F16SW011A16EC | N/A | Flotation 11kV Switchboard Panel A16 Earth Switch Closed | F16SW011 A16 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A10OPS | F16SW011A10OP | N/A | Flotation 11kV Switchboard Panel A10 Contactor Opened | F16SW011 A10 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A08TTS | F16SW011A08TT | N/A | Flotation 11kV Switchboard Panel A08 Truck In Test | F16SW011 A08 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A07CLS | F16SW011A07CL | N/A | Flotation 11kV Switchboard Panel A07 Contactor Closed | F16SW011 A07 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A05EOS | F16SW011A05EO | N/A | Flotation 11kV Switchboard Panel A05 Earth Switch Opened | F16SW011 A05 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A04FHS | F16SW011A04FH | N/A | Flotation 11kV Switchboard Panel A04 Fuse Healthy | F16SW011 A04 Fuse | Alarm | Normal | Alarm | SoftTag | 0 |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A02ECS | F16SW011A02EC | N/A | Flotation 11kV Switchboard Panel A02 Earth Switch Closed | F16SW011 A02 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16BC001FL1 | F16BC001_FL1 | 2000-F16-PID-PR-10001 | F16-BC-001 48VDC Charger Mains Fail | F16BC001 Charger Mains | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16SW11A15TSS | F16SW011A15TS | N/A | Flotation 11kV Switchboard Panel A15 Truck In Service | F16SW011 A15 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname |  |  |  |  | Venson: These signals have been tested in the Modpack, however, different tag naming used.
|  |  |  | F16SW11A12ECS | F16SW011A12EC | N/A | Flotation 11kV Switchboard Panel A12 Earth Switch Closed | F16SW011 A12 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A11TSS | F16SW011A11TS | N/A | Flotation 11kV Switchboard Panel A11 Truck In Service | F16SW011 A11 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A16TTS | F16SW011A16TT | N/A | Flotation 11kV Switchboard Panel A16 Truck In Test | F16SW011 A16 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A09EOS | F16SW011A09EO | N/A | Flotation 11kV Switchboard Panel A09 Earth Switch Opened | F16SW011 A09 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A08FHS | F16SW011A08FH | N/A | Flotation 11kV Switchboard Panel A08 Fuse Healthy | F16SW011 A08 Fuse | Alarm | Normal | Alarm | SoftTag | 0 |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A06ECS | F16SW011A06EC | N/A | Flotation 11kV Switchboard Panel A06 Earth Switch Closed | F16SW011 A06 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A05TSS | F16SW011A05TS | N/A | Flotation 11kV Switchboard Panel A05 Truck In Service | F16SW011 A05 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A04OPS | F16SW011A04OP | N/A | Flotation 11kV Switchboard Panel A04 Contactor Opened | F16SW011 A04 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A02TTS | F16SW011A02TT | N/A | Flotation 11kV Switchboard Panel A02 Truck In Test | F16SW011 A02 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A15CLS | F16SW011A15CL | N/A | Flotation 11kV Switchboard Panel A15 Circuit Breaker Closed | F16SW011 A15 CB | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A12TTS | F16SW011A12TT | N/A | Flotation 11kV Switchboard Panel A12 Truck In Test | F16SW011 A12 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A11CLS | F16SW011A11CL | N/A | Flotation 11kV Switchboard Panel A11 Contactor Closed | F16SW011 A11 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A17FHS | F16SW011A17FH | N/A | Flotation 11kV Switchboard Panel A17 Fuse Healthy | F16SW011 A17 Fuse | Alarm | Normal | Alarm | SoftTag | 0 |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A10TSS | F16SW011A10TS | N/A | Flotation 11kV Switchboard Panel A10 Truck In Service | F16SW011 A10 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A09OPS | F16SW011A09OP | N/A | Flotation 11kV Switchboard Panel A09 Circuit Breaker Opened | F16SW011 A09 CB | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A07TTS | F16SW011A07TT | N/A | Flotation 11kV Switchboard Panel A07 Truck In Test | F16SW011 A07 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A06CLS | F16SW011A06CL | N/A | Flotation 11kV Switchboard Panel A06 Contactor Closed | F16SW011 A06 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A04EOS | F16SW011A04EO | N/A | Flotation 11kV Switchboard Panel A04 Earth Switch Opened | F16SW011 A04 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A03FHS | F16SW011A03FH | N/A | Flotation 11kV Switchboard Panel A03 Fuse Healthy | F16SW011 A03 Fuse | Alarm | Normal | Alarm | SoftTag | 0 |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A15ECS | F16SW011A15EC | N/A | Flotation 11kV Switchboard Panel A15 Earth Switch Closed | F16SW011 A15 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A13TSS | F16SW011A13TS | N/A | Flotation 11kV Switchboard Panel A13 Truck In Service | F16SW011 A13 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A11ECS | F16SW011A11EC | N/A | Flotation 11kV Switchboard Panel A11 Earth Switch Closed | F16SW011 A11 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A17EOS | F16SW011A17EO | N/A | Flotation 11kV Switchboard Panel A17 Earth Switch Opened | F16SW011 A17 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A10ECS | F16SW011A10EC | N/A | Flotation 11kV Switchboard Panel A10 Earth Switch Closed | F16SW011 A10 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A09TSS | F16SW011A09TS | N/A | Flotation 11kV Switchboard Panel A09 Truck In Service | F16SW011 A09 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A08OPS | F16SW011A08OP | N/A | Flotation 11kV Switchboard Panel A08 Contactor Opened | F16SW011 A08 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A06TTS | F16SW011A06TT | N/A | Flotation 11kV Switchboard Panel A06 Truck In Test | F16SW011 A06 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A05CLS | F16SW011A05CL | N/A | Flotation 11kV Switchboard Panel A05 Contactor Closed | F16SW011 A05 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A03EOS | F16SW011A03EO | N/A | Flotation 11kV Switchboard Panel A03 Earth Switch Opened | F16SW011 A03 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A02FHS | F16SW011A02FH | N/A | Flotation 11kV Switchboard Panel A02 Fuse Healthy | F16SW011 A02 Fuse | Alarm | Normal | Alarm | SoftTag | 0 |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16FIP002FLT | F16FIP002_FLT | N/A | F16-FIP-001 Fault | F16FIP002 Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16SW11A16FHS | F16SW011A16FH | N/A | Flotation 11kV Switchboard Panel A16 Fuse Healthy | F16SW011 A16 Fuse | Alarm | Normal | Alarm | SoftTag | 0 |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname |  |  |  |  | Venson: These signals have been tested in the Modpack, however, different tag naming used.
|  |  |  | F16SW11A13ECS | F16SW011A13EC | N/A | Flotation 11kV Switchboard Panel A13 Earth Switch Closed | F16SW011 A13 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A18OPS | F16SW011A18OP | N/A | Flotation 11kV Switchboard Panel A18 Contactor Opened | F16SW011 A18 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A18CLS | F16SW011A18CL | N/A | Flotation 11kV Switchboard Panel A18 Contactor Closed | F16SW011 A18 Contactor | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A18FHS | F16SW011A18FH | N/A | Flotation 11kV Switchboard Panel A18 Fuse Healthy | F16SW011 A18 Fuse | Alarm | Normal | Alarm | SoftTag | 0 |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A18TTS | F16SW011A18TT | N/A | Flotation 11kV Switchboard Panel A18 Truck In Test | F16SW011 A18 Truck Test | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A18TSS | F16SW011A18TS | N/A | Flotation 11kV Switchboard Panel A18 Truck In Service | F16SW011 A18 Truck Serv | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW11A20EOS | F16SW011A20EO | N/A | Flotation 11kV Switchboard Panel A20 Earth Switch Opened | F16SW011 A20 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag |  |  | Duplicated in modbus lists. Not present in other PCTs. Incorrect tagname
|  |  |  | F16SW008PS1 | F16SW008_PS1 | N/A | F16-SW-008 PS 24VDC HEALTHY | F16SW008 PS1 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16SW008SD | F16SW008_SD | N/A | F16-SW-008 INCOMER SURGE DIVERTER OK | F16SW008 Inc SurgeDivert | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3 | 2026-02-28 | MOC-125
|  |  |  | F16SW008CL | F16SW008_CL | N/A | F16-SW-008 CIRCUIT BREAKER CLOSED | F16SW008 Breaker Close | N_Active | Active |  | Hardwired to DCS |  |  |  | 3
|  |  |  | F16SW008TRP | F16SW008_TRP | N/A | F16-SW-008 CIRCUIT BREAKER TRIPPED | F16SW008 Breaker Trip | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | 3 | 2026-02-28 | MOC-125
|  |  |  | F16SW008OP | F16SW008_OP | N/A | F16-SW-008 CIRCUIT BREAKER OPENED | F16SW008 Breaker Open | N_Active | Active |  | Hardwired to DCS |  |  |  | 3
|  |  |  | F16SW008AF | F16SW008_AF | N/A | F16-SW-008 ARC FLASH DETECTION SYSTEM ALARM | F16SW008 Arc Flash | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3 | 2026-02-28 | MOC-125
|  |  |  | F16SW008PS | F16SW008_PS | N/A | F16-SW-008 ACB SHUNT TRIP 24VDC OK | F16SW008 ACBShunt 24V OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 4 | 2025-10-23
|  |  |  | F16SW005PS2 | F16SW005_PS2 | N/A | F16-SW-005 PS2 24VDC HEALTHY | F16SW005 PS2 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16SW005PS1 | F16SW005_PS1 | N/A | F16-SW-005 PS1 24VDC HEALTHY | F16SW005 PS1 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16SW005SD | F16SW005_SD | N/A | F16-SW-005 INCOMER SURGE DIVERTER OK | F16SW005 Incomer Div OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3 | 2026-02-28 | MOC-125
|  |  |  | F16SW005CL | F16SW005_CL | N/A | F16-SW-005 CIRCUIT BREAKER CLOSED | F16SW005 Breaker Close | N_Active | Active |  | Hardwired to DCS |  |  |  | 3
|  |  |  | F16SW005TRP | F16SW005_TRP | N/A | F16-SW-005 CIRCUIT BREAKER TRIPPED | F16SW005 Breaker Trip | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | 3 | 2026-02-28 | MOC-125
|  |  |  | F16SW005OP | F16SW005_OP | N/A | F16-SW-005 CIRCUIT BREAKER OPENED | F16SW005 Breaker Open | N_Active | Active |  | Hardwired to DCS |  |  |  | 3
|  |  |  | F16SW005AF | F16SW005_AF | N/A | F16-SW-005 ARC FLASH DETECTION SYSTEM ALARM | F16SW005 Arc Flash | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  | Wiring connection has been changed from terminal 10&11 to 10&12 | 3 | 2026-02-28 | MOC-125
|  |  |  | F16SW005PS | F16SW005_PS | N/A | F16-SW-005 ACB SHUNT TRIP 24VDC OK | F16SW005 ACBShunt 24V OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 4 | 2025-10-23
|  |  |  | F16SW004PS2 | F16SW004_PS2 | N/A | F16-SW-004 PS2 24VDC HEALTHY | F16SW004 PS2 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16SW004PS1 | F16SW004_PS1 | N/A | F16-SW-004 PS1 24VDC HEALTHY | F16SW004 PS1 24VDC OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16SW004TRP | F16SW004_TRP | N/A | F16-SW-004 CIRCUIT BREAKER TRIPPED | F16SW004 Breaker Trip | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | 3 | 2026-02-28 | MOC-125
|  |  |  | F16SW004SD | F16SW004_SD | N/A | F16-SW-004 INCOMER SURGE DIVERTER OK | F16 MCC Incomer Healthy | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3 | 2026-02-28 | MOC-125
|  |  |  | F16SW004CL | F16SW004_CL | N/A | F16-SW-004 CIRCUIT BREAKER CLOSED | F16SW004 MCC Breakr Clsd | N_Active | Active |  | Hardwired to DCS |  |  |  | 3
|  |  |  | F16SW004OP | F16SW004_OP | N/A | F16-SW-004 CIRCUIT BREAKER OPENED | F16SW004 MCC Breakr Opn | N_Active | Active |  | Hardwired to DCS |  |  |  | 3
|  |  |  | F16SW004AF | F16SW004_AF | N/A | F16-SW-004 ARC FLASH DETECTION SYSTEM ALARM | F16SW004 Arc Flash | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3 | 2026-02-28 | MOC-125
|  |  |  | F16SW004PS | F16SW004_PS | N/A | F16-SW-004 ACB SHUNT TRIP 24VDC OK | F16SW004 ACBShunt 24V OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 4 | 2025-10-23
|  |  |  | LSH16041 | LAH16041 | 2000-F16-PID-PR-10001 | F16-PS-411 Flotation Area Sump Pump 1 Level Switch High | F16PS411 Flot Sump 1 | Normal | Alarm | Alarm | SoftTag | 3 |  | Switch to turn on respective sump pump in Auto mode. Refer to Drives for further information. (Wired to motor starter) | 2
|  |  |  | F16AN403S6NES | F16AN403S6NE | 2000-F16-PID-PR-10010 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Sample Not Executable | F16AN403 S6 Not Exec | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 05 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S7NES | F16AN403S7NE | 2000-F16-PID-PR-10011 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Sample Not Executable | F16AN403 S7 Not Exec | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 05 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S4NES | F16AN403S4NE | 2000-F16-PID-PR-10008 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Sample Not Executable | F16AN403 S4 Not Exec | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 05 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S2NES | F16AN403S2NE | 2000-F16-PID-PR-10006 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Sample Not Executable | F16AN403 S2 Not Exec | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 05 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S8NES | F16AN403S8NE | 2000-F16-PID-PR-10012 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Sample Not Executable | F16AN403 S8 Not Exec | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 05 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16FIP001FLT | F16FIP001_FLT | N/A | Flotation 11kV Switchroom Fire Indicator Panel Fault | Flot 11kV SR Fire Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16AN403S5MRS | F16AN403S5MR | 2000-F16-PID-PR-10009 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Sample Measurement Result Not Ok | F16AN403 S5 Results Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 08 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S9MRS | F16AN403S9MR | 2000-F16-PID-PR-10013 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Sample Measurement Result Not Ok | F16AN403 S9 Results Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 08 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S8MRS | F16AN403S8MR | 2000-F16-PID-PR-10012 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Sample Measurement Result Not Ok | F16AN403 S8 Results Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 08 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | LSL16035 | LAL16035 | 2000-F16-PID-PR-10001 | F16-GE-001 Flotation Emergency Supply 11kV Generator Fuel Level Switch Low | F16GE001 Fuel Level | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 3
|  |  |  | XI16175S | XI16175 | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Normal | F16AN403 Analyser Normal | N_Active | Active |  | SoftTag |  |  | Status bit = 01 From general analyser bit status F16AN403ST. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | XA16177S | XA16177 | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Alarm | F16AN403 Analyser Alarm | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 03 From general analyser bit status F16AN403ST. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | XA16176S | XA16176 | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Warning | F16AN403 Analyser Warn | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 02 From general analyser bit status F16AN403ST. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | XI16178S | XI16178 | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Standby | F16AN403 Analyser Stby | N_Active | Active |  | SoftTag |  |  | Status bit = 04 From general analyser bit status F16AN403ST. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16RIO001PS2 | F16RIO001_PS2 | 2000-F16-PID-PR-10001 | F16-RIO-001 PS2 24VDC HEALTHY | F16RIO001 PS2 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16RIO001PS1 | F16RIO001_PS1 | 2000-F16-PID-PR-10001 | F16-RIO-001 PS1 24VDC HEALTHY | F16RIO001 PS1 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16FIP001ALM | F16FIP001_ALM | N/A | Flotation 11kV Switchroom Fire Indicator Panel Alarm | Flot 11kV SR Fire Alarm | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | 20/02/2026 MOC103 | 3
|  |  |  | LSHH16035 | LAHH16035 | 2000-F16-PID-PR-10001 | F16-GE-001 Flotation Emergency Supply 11kV Generator Fuel Level Switch High High | F16GE001 Fuel Level | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 3
|  |  |  | LSH16035 | LAH16035 | 2000-F16-PID-PR-10001 | F16-GE-001 Flotation Emergency Supply 11kV Generator Fuel Level Switch High | F16GE001 Fuel Level | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 3
|  |  |  | F16SR002ESTP | F16SR002_ESTP | 2000-F16-PID-PR-10001 | F16-SR-002 SWITCHROOM EMERGENCY SHUTDOWN DCS INPUT | F16SR002 Estop | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16DCS408PS1 | F16DCS408_PS1 | 2000-F16-PID-PR-10001 | F16-DCS-408 PS1 24VDC HEALTHY | F16DCS408 PS1 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16DCS408PS2 | F16DCS408_PS2 | 2000-F16-PID-PR-10001 | F16-DCS-408 PS2 24VDC HEALTHY | F16DCS408 PS2 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16SW104Q2OP | F16SW104Q2_OP | 2000-F16-PID-PR-10001 | F16-SW-104 Generator Supply CB Opened | F16SW104 Gen CB Open | N_Active | Active |  | Hardwired to DCS |  |  |  | 3
|  |  |  | F16AN403S7MRS | F16AN403S7MR | 2000-F16-PID-PR-10011 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Sample Measurement Result Not Ok | F16AN403 S7 Results Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 08 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S6MRS | F16AN403S6MR | 2000-F16-PID-PR-10010 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Sample Measurement Result Not Ok | F16AN403 S6 Results Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 08 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S2MRS | F16AN403S2MR | 2000-F16-PID-PR-10006 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Sample Measurement Result Not Ok | F16AN403 S2 Results Flt | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 08 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S1NMS | F16AN403S1NM | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Sample Not Measurable | F16AN403 S1 Not Meas | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 06 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S12ES | F16AN403S12E | 2000-F16-PID-PR-10016 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Sample Not Executable | F16AN403 S12 Not Exec | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 05 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S11ES | F16AN403S11E | 2000-F16-PID-PR-10015 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Sample Not Executable | F16AN403 S11 Not Exec | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 05 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S10ES | F16AN403S10E | 2000-F16-PID-PR-10014 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Sample Not Executable | F16AN403 S10 Not Exec | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 05 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S5NES | F16AN403S5NE | 2000-F16-PID-PR-10009 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Sample Not Executable | F16AN403 S5 Not Exec | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 05 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S3NES | F16AN403S3NE | 2000-F16-PID-PR-10007 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Sample Not Executable | F16AN403 S3 Not Exec | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 05 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F18RIO002PS1 | F18RIO002_PS1 | 2000-F18-PID-PR-10001 | F18-RIO-002 PS1 24VDC HEALTHY | F18RIO002 PS1 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16RIO100PS2 | F16RIO100_PS2 | 2000-F16-PID-PR-10001 | F16-RIO-100 PS2 24VDC HEALTHY | F16RIO100 PS2 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F16RIO100PS1 | F16RIO100_PS1 | 2000-F16-PID-PR-10001 | F16-RIO-100 PS1 24VDC HEALTHY | F16RIO100 PS1 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | F18RIO002PS2 | F18RIO002_PS2 | 2000-F18-PID-PR-10001 | F18-RIO-002 PS2 24VDC HEALTHY | F18RIO002 PS2 24VDC | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3
|  |  |  | LSH16036 | LAH16036 | 2000-F16-PID-PR-10001 | F16-GE-104 Flotation Essential Supply 415V Generator Fuel Level Switch High | F16GE104 Fuel Level | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  |  | 3
|  |  |  | LSHH16036 | LAHH16036 | 2000-F16-PID-PR-10001 | F16-GE-104 Flotation Essential Supply 415V Generator Fuel Level Switch High High | F16GE104 Fuel Level | Normal | Alarm | Alarm | Hardwired to DCS | 3
|  |  |  | LSL16036 | LAL16036 | 2000-F16-PID-PR-10001 | F16-GE-104 Flotation Essential Supply 415V Generator Fuel Level Switch Low | F16GE104 Fuel Level | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 3
|  |  |  | F16AN403S9NES | F16AN403S9NE | 2000-F16-PID-PR-10013 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Sample Not Executable | F16AN403 S9 Not Exec | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 05 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16SW11A20ECS | F16SW011A20EC | N/A | Flotation 11kV Switchboard Panel A20 Earth Switch Closed | F16SW011 A20 Earth Sw | N_Active | Active |  | SoftTag |  |  | Modbus/TCP Soft-Tag | 2
|  |  |  | F16AN403S11BS | F16AN403S11B | 2000-F16-PID-PR-10015 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Sample Bypass On | F16AN403 S11 Bypass | N_Active | Active |  | SoftTag |  |  | Status bit = 04 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S10BS | F16AN403S10B | 2000-F16-PID-PR-10014 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Sample Bypass On | F16AN403 S10 Bypass | N_Active | Active |  | SoftTag |  |  | Status bit = 04 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S9BYS | F16AN403S9BY | 2000-F16-PID-PR-10013 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Sample Bypass On | F16AN403 S9 Bypass | N_Active | Active |  | SoftTag |  |  | Status bit = 04 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S12BS | F16AN403S12B | 2000-F16-PID-PR-10016 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Sample Bypass On | F16AN403 S12 Bypass | N_Active | Active |  | SoftTag |  |  | Status bit = 04 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S1NES | F16AN403S1NE | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Sample Not Executable | F16AN403 S1 Not Exec | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 05 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S7BYS | F16AN403S7BY | 2000-F16-PID-PR-10011 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Sample Bypass On | F16AN403 S7 Bypass | N_Active | Active |  | SoftTag |  |  | Status bit = 04 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S8BYS | F16AN403S8BY | 2000-F16-PID-PR-10012 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Sample Bypass On | F16AN403 S8 Bypass | N_Active | Active |  | SoftTag |  |  | Status bit = 04 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S4BYS | F16AN403S4BY | 2000-F16-PID-PR-10008 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Sample Bypass On | F16AN403 S4 Bypass | N_Active | Active |  | SoftTag |  |  | Status bit = 04 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S3BYS | F16AN403S3BY | 2000-F16-PID-PR-10007 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Sample Bypass On | F16AN403 S3 Bypass | N_Active | Active |  | SoftTag |  |  | Status bit = 04 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S2BYS | F16AN403S2BY | 2000-F16-PID-PR-10006 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Sample Bypass On | F16AN403 S2 Bypass | N_Active | Active |  | SoftTag |  |  | Status bit = 04 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S5BYS | F16AN403S5BY | 2000-F16-PID-PR-10009 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Sample Bypass On | F16AN403 S5 Bypass | N_Active | Active |  | SoftTag |  |  | Status bit = 04 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S6BYS | F16AN403S6BY | 2000-F16-PID-PR-10010 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Sample Bypass On | F16AN403 S6 Bypass | N_Active | Active |  | SoftTag |  |  | Status bit = 04 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S12LS | F16AN403S12A | 2000-F16-PID-PR-10016 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Sample Alarm | F16AN403 S12 Alarm | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 03 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S1BYS | F16AN403S1BY | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Sample Bypass On | F16AN403 S1 Bypass | N_Active | Active |  | SoftTag |  |  | Status bit = 04 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S9ALS | F16AN403S9AL | 2000-F16-PID-PR-10013 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Sample Alarm | F16AN403 S9 Alarm | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 03 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S8ALS | F16AN403S8AL | 2000-F16-PID-PR-10012 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Sample Alarm | F16AN403 S8 Alarm | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 03 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S7ALS | F16AN403S7AL | 2000-F16-PID-PR-10011 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Sample Alarm | F16AN403 S7 Alarm | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 03 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S10LS | F16AN403S10A | 2000-F16-PID-PR-10014 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Sample Alarm | F16AN403 S10 Alarm | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 03 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S11LS | F16AN403S11A | 2000-F16-PID-PR-10015 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Sample Alarm | F16AN403 S11 Alarm | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 03 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S5ALS | F16AN403S5AL | 2000-F16-PID-PR-10009 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Sample Alarm | F16AN403 S5 Alarm | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 03 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S6ALS | F16AN403S6AL | 2000-F16-PID-PR-10010 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Sample Alarm | F16AN403 S6 Alarm | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 03 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S2ALS | F16AN403S2AL | 2000-F16-PID-PR-10006 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Sample Alarm | F16AN403 S2 Alarm | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 03 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S1ALS | F16AN403S1AL | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Sample Alarm | F16AN403 S1 Alarm | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 03 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S12WS | F16AN403S12W | 2000-F16-PID-PR-10016 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Sample Warning | F16AN403 S12 Warning | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 02 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S3ALS | F16AN403S3AL | 2000-F16-PID-PR-10007 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Sample Alarm | F16AN403 S3 Alarm | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 03 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S4ALS | F16AN403S4AL | 2000-F16-PID-PR-10008 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Sample Alarm | F16AN403 S4 Alarm | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 03 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S10WS | F16AN403S10W | 2000-F16-PID-PR-10014 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Sample Warning | F16AN403 S10 Warning | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 02 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S11WS | F16AN403S11W | 2000-F16-PID-PR-10015 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Sample Warning | F16AN403 S11 Warning | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 02 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S7WS | F16AN403S7W | 2000-F16-PID-PR-10011 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Sample Warning | F16AN403 S7 Warning | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 02 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S6WS | F16AN403S6W | 2000-F16-PID-PR-10010 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Sample Warning | F16AN403 S6 Warning | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 02 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S5WS | F16AN403S5W | 2000-F16-PID-PR-10009 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Sample Warning | F16AN403 S5 Warning | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 02 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S8WS | F16AN403S8W | 2000-F16-PID-PR-10012 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Sample Warning | F16AN403 S8 Warning | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 02 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S9WS | F16AN403S9W | 2000-F16-PID-PR-10013 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Sample Warning | F16AN403 S9 Warning | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 02 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S3WS | F16AN403S3W | 2000-F16-PID-PR-10007 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Sample Warning | F16AN403 S3 Warning | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 02 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S4WS | F16AN403S4W | 2000-F16-PID-PR-10008 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Sample Warning | F16AN403 S4 Warning | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 02 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S12OS | F16AN403S12N | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Sample Normal | F16AN403 S12 Normal | N_Active | Active |  | SoftTag |  |  | Status bit = 01 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S11OS | F16AN403S11N | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Sample Normal | F16AN403 S11 Normal | N_Active | Active |  | SoftTag |  |  | Status bit = 01 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S10OS | F16AN403S10N | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Sample Normal | F16AN403 S10 Normal | N_Active | Active |  | SoftTag |  |  | Status bit = 01 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S1WS | F16AN403S1W | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Sample Warning | F16AN403 S1 Warning | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 02 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S2WS | F16AN403S2W | 2000-F16-PID-PR-10006 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Sample Warning | F16AN403 S2 Warning | N_Active | Active | Active | SoftTag | 3 |  | Status bit = 02 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S8NS | F16AN403S8N | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Sample Normal | F16AN403 S8 Normal | N_Active | Active |  | SoftTag |  |  | Status bit = 01 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S9NS | F16AN403S9N | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Sample Normal | F16AN403 S9 Normal | N_Active | Active |  | SoftTag |  |  | Status bit = 01 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S5NS | F16AN403S5N | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Sample Normal | F16AN403 S5 Normal | N_Active | Active |  | SoftTag |  |  | Status bit = 01 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S4NS | F16AN403S4N | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Sample Normal | F16AN403 S4 Normal | N_Active | Active |  | SoftTag |  |  | Status bit = 01 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S3NS | F16AN403S3N | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Sample Normal | F16AN403 S3 Normal | N_Active | Active |  | SoftTag |  |  | Status bit = 01 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S6NS | F16AN403S6N | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Sample Normal | F16AN403 S6 Normal | N_Active | Active |  | SoftTag |  |  | Status bit = 01 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S7NS | F16AN403S7N | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Sample Normal | F16AN403 S7 Normal | N_Active | Active |  | SoftTag |  |  | Status bit = 01 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S1NS | F16AN403S1N | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Sample Normal | F16AN403 S1 Normal | N_Active | Active |  | SoftTag |  |  | Status bit = 01 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S2NS | F16AN403S2N | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Sample Normal | F16AN403 S2 Normal | N_Active | Active |  | SoftTag |  |  | Status bit = 01 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S10QS | F16AN403S10Q | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 10 Sample in Use | F16AN403 S10 On | N_Active | Active |  | SoftTag |  |  | Status bit = 00 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S9QS | F16AN403S9Q | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 9 Sample in Use | F16AN403 S9 On | N_Active | Active |  | SoftTag |  |  | Status bit = 00 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S8QS | F16AN403S8Q | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 8 Sample in Use | F16AN403 S8 On | N_Active | Active |  | SoftTag |  |  | Status bit = 00 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S11QS | F16AN403S11Q | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 11 Sample in Use | F16AN403 S11 On | N_Active | Active |  | SoftTag |  |  | Status bit = 00 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S12QS | F16AN403S12Q | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 12 Sample in Use | F16AN403 S12 On | N_Active | Active |  | SoftTag |  |  | Status bit = 00 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S6QS | F16AN403S6Q | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 6 Sample in Use | F16AN403 S6 On | N_Active | Active |  | SoftTag |  |  | Status bit = 00 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S7QS | F16AN403S7Q | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 7 Sample in Use | F16AN403 S7 On | N_Active | Active |  | SoftTag |  |  | Status bit = 00 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S5QS | F16AN403S5Q | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 5 Sample in Use | F16AN403 S5 On | N_Active | Active |  | SoftTag |  |  | Status bit = 00 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S2QS | F16AN403S2Q | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 2 Sample in Use | F16AN403 S2 On | N_Active | Active |  | SoftTag |  |  | Status bit = 00 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S1QS | F16AN403S1Q | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 1 Sample in Use | F16AN403 S1 On | N_Active | Active |  | SoftTag |  |  | Status bit = 00 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S3QS | F16AN403S3Q | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 3 Sample in Use | F16AN403 S3 On | N_Active | Active |  | SoftTag |  |  | Status bit = 00 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN403S4QS | F16AN403S4Q | 2000-F16-PID-PR-10005 | F16-AN-403 Onstream Sulphur Analyser Stream 4 Sample in Use | F16AN403 S4 On | N_Active | Active |  | SoftTag |  |  | Status bit = 00 Bit map for analyser status word. Tag naming convention to be replicated for all streams. Refer to 2000-SPC-CS-11001 Onstream Sulphur Analyser Modbus Map for details. | 2
|  |  |  | F16AN402FL9 | F16AN402_FL9 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 9 Invalid | F16AN402 Assy9 Alarm | Normal | Alarm | Alarm | SoftTag | 3 |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | F16AN402FL10 | F16AN402_FL10 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 10 Invalid | F16AN402 Assy10 Alarm | Normal | Alarm | Alarm | SoftTag | 3 |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | F16AN402FL6 | F16AN402_FL6 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 6 Invalid | F16AN402 Assy6 Alarm | Normal | Alarm | Alarm | SoftTag | 3 |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | F16AN402FL5 | F16AN402_FL5 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 5 Invalid | F16AN402 Assy5 Alarm | Normal | Alarm | Alarm | SoftTag | 3 |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | F16AN402FL4 | F16AN402_FL4 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 4 Invalid | F16AN402 Assy4 Alarm | Normal | Alarm | Alarm | SoftTag | 3 |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | F16AN402FL7 | F16AN402_FL7 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 7 Invalid | F16AN402 Assy7 Alarm | Normal | Alarm | Alarm | SoftTag | 3 |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | F16AN402FL8 | F16AN402_FL8 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 8 Invalid | F16AN402 Assy8 Alarm | Normal | Alarm | Alarm | SoftTag | 3 |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | F16AN402FL2 | F16AN402_FL2 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 2 Invalid | F16AN402 Assy2 Alarm | Normal | Alarm | Alarm | SoftTag | 3 |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | F16AN402FL3 | F16AN402_FL3 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 3 Invalid | F16AN402 Assy3 Alarm | Normal | Alarm | Alarm | SoftTag | 3 |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | XI16169S | XI16169 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Measurement Running | F16AN402 Measurement | Stopped | Running |  | SoftTag |  |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | F16AN402CRUN | F16AN402_CRUN | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Composite Sample Running | F16AN402 Comp Sample | Stopped | Running |  | SoftTag |  |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | XA16168S | XA16168 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA General Alarm | F16AN402 General Alarm | Normal | Alarm | Alarm | SoftTag | 3 |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | F16AN402ZRUN | F16AN402_ZRUN | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Zero Check Running | F16AN402 Zero Check | Stopped | Running |  | SoftTag |  |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | F16AN402FL1 | F16AN402_FL1 | 2000-F16-PID-PR-10005 | F16-AN-402 Flotation Feed PSA Assay 1 Invalid | F16AN402 Assy1 Alarm | Normal | Alarm | Alarm | SoftTag | 3 |  | Refer to 2000-SPC-CS-11011 Flotation Feed PSA for details. | 2
|  |  |  | FSL18533 | FAL18533 | 2000-F24-PID-PR-10003 | F18-PP-513 Cleaner Scavenger Flotation Cell Tails Pump 1 Gland Water Flow Indicating Transmitter | F18PP513 Gland | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F18PP513 Not Running |  | 3
|  |  |  | FSL18537 | FAL18537 | 2000-F24-PID-PR-10003 | F18-PP-514 Cleaner Scavenger Flotation Cell Tails Pump 2 Gland Water Flow Indicating Transmitter | F18PP514 Gland | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F18PP514 Not Running |  | 3
|  |  |  | FSL18529 | FAL18529 | 2000-F24-PID-PR-10003 | F18-PP-512 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Gland Water Flow Indicating Transmitter | F18PP512 Gland | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F18PP512 Not Running |  | 3
|  |  |  | FSL18509 | FAL18509 | 2000-F24-PID-PR-10003 | F18-PP-501 Cleaner Flotation Cell Recirculation Pump 1 Gland Water Flow Indicating Transmitter | F18PP501 Gland | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F18PP501 Not Running |  | 3
|  |  |  | FSL18505 | FAL18505 | 2000-F24-PID-PR-10003 | F18-PP-408 Final Concentrate Pump 2 Gland Water Flow Indicating Transmitter | F18PP408 Gland | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F18PP408 Not Running |  | 3
|  |  |  | FSL18513 | FAL18513 | 2000-F24-PID-PR-10003 | F18-PP-502 Cleaner Flotation Cell Recirculation Pump 2 Gland Water Flow Indicating Transmitter | F18PP502 Gland | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F18PP502 Not Running |  | 3
|  |  |  | FSL18525 | FAL18525 | 2000-F24-PID-PR-10003 | F18-PP-511 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Gland Water Flow Indicating Transmitter | F18PP511 Gland | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F18PP511 Not Running |  | 3
|  | Instrument list to be updated to be FT |  | FSL18501 | FAL18501 | 2000-F24-PID-PR-10003 | F18-PP-407 Final Concentrate Pump 1 Gland Water Flow Indicating Transmitter | F18PP407 Gland | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F18PP407 Not Running |  | 3
|  |  |  | LSH17081 | LAH17081 | 2000-F17-PID-PR-10001 | F17-PS-427 Flotation Tailings Thickener Area Sump Pump 1 Level Switch High | F17PS427 Thicknr Sump | Normal | Alarm | Alarm | SoftTag | 3 |  | Switch to turn on respective sump pump in Auto mode. Refer to Drives for further information. (Wired to motor starter) | 2
|  |  |  | PDSH17051 | PDAH17051 | 2000-F17-PID-PR-10001 | F17-HU-414 Flotation Tailings Thickener Rake Lift HPU Return Filter Pressure Differential Switch High | F17HU414 Rtrn Fltr Dlta | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | LSH18041 | LAH18041 | 2000-F18-PID-PR-10001 | F18-PS-501 Cleaner Area Sump Pump Level Switch High | F18PS501 Cleaner Sump | Normal | Alarm | Alarm | SoftTag | 3 |  | Switch to turn on respective sump pump in Auto mode. Refer to Drives for further information. (Wired to motor starter) | 3
|  |  |  | LSLL17043 | LALL17043 | 2000-F17-PID-PR-10001 | F17-HU-414 Flotation Tailings Thickener Rake Lift HPU Oil Tank Level Switch Low Low | F17HU414 Rake Lift HPU | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | TSHH17044 | TAHH17044 | 2000-F17-PID-PR-10001 | F17-HU-414 Flotation Tailings Thickener Rake Lift HPU Oil Tank Temperature Switch High High | F17HU414 Rake Lift HPU | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | TSH17042 | TAH17042 | 2000-F17-PID-PR-10001 | F17-HU-414 Flotation Tailings Thickener Rake Lift HPU Oil Tank Temperature Switch High | F17HU414 Rake Lift HPU | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | PDSH17031 | PDAH17031 | 2000-F17-PID-PR-10001 | F17-HU-406 Flotation Tailings Thickener Rake Drive HPU Outlet Differential Pressure Switch High | F17HU406 Outlet Delta | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | PDSH17037 | PDAH17037 | 2000-F17-PID-PR-10001 | F17-HU-406 Flotation Tailings Thickener Rake Drive HPU Return Filter Differential Pressure Switch High (Standby) | F17HU406 Rtrn Fltr Dlta | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | ZSO17026 | ZAO17026 | 2000-F17-PID-PR-10001 | F17-PO-408 Thickener Rake Drive Pump Suction Valve Position Switch Opened | F17PO408 Inlet Valve Opn | N_Open | Open | N_Open | Hardwired to DCS | 3 |  | To alarm when switch is NOT active. Valve must normally be in Open position (switch active). Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | LSL17041 | LAL17041 | 2000-F17-PID-PR-10001 | F17-HU-414 Flotation Tailings Thickener Rake Lift HPU Oil Tank Level Switch Low | F17HU414 Rake Lift HPU | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | PDSH17028 | PDAH17028 | 2000-F17-PID-PR-10001 | F17-HU-406 Flotation Tailings Thickener Rake Drive HPU Pump Outlet Filter Differential Pressure Switch High | F17PO408 D/C Fltr Dlta | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | PDSH17036 | PDAH17036 | 2000-F17-PID-PR-10001 | F17-HU-406 Flotation Tailings Thickener Rake Drive HPU Return Filter Differential Pressure Switch High (Working) | F17HU406 Rtrn Fltr Dlta | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | LSLL17023 | LALL17023 | 2000-F17-PID-PR-10001 | F17-HU-406 Flotation Tailings Thickener Rake Drive HPU Oil Tank Level Switch Low Low | F17HU406 Rake Drive HPU | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | See Drives for interlock to Rake Drive Pump. Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | TSH17022 | TAH17022 | 2000-F17-PID-PR-10001 | F17-HU-406 Flotation Tailings Thickener Rake Drive HPU Oil Tank Temperature Switch High | F17HU406 Rake Drive HPU | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | LSL17021 | LAL17021 | 2000-F17-PID-PR-10001 | F17-HU-406 Flotation Tailings Thickener Rake Drive HPU Oil Tank Level Switch Low | F17HU406 Rake Drive HPU | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | TSHH17024 | TAHH17024 | 2000-F17-PID-PR-10001 | F17-HU-406 Flotation Tailings Thickener Rake Drive HPU Oil Tank Temperature Switch High High | F17HU406 Rake Drive HPU | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001 | 3
|  |  |  | TSH17025 | TAH17025 | 2000-F17-PID-PR-10001 | F17-HU-406 Flotation Tailings Thickener Rake Drive HPU Oil Tank Cooling Fan Temperature Switch High | F17HU406 HPU Cooling Fan | Active | N_Active |  | Hardwired to DCS |  |  | When switch is active, start Thickener Rake Drive Oil Tank Cooling Fan (on-delay 3s) when in AUT. | 3
|  |  |  | HS17065A | HS17065ASTT | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel Raise Rake Request Push Button | F17TH401 Raise Rake | Active | N_Active |  | Hardwired to DCS |  |  | F17TH401 must be in LOCAL mode for local control panel button to have effect. Please see 12. Misc for further information. When HS17065A Activated: Energise SV17048 AND Start F17PO409. When HS17065A De-Activated / Released (Falling Edge): De-Energise SV17048. DCS Graphic button to be programmed to raise rake remotely by CRO. | 3
|  |  |  | HS17065B | HS17065BSTT | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel Lower Rake Request Push Button | F17TH401 Lower Rake | Normal | Active |  | Hardwired to DCS |  |  | F17TH401 must be in LOCAL mode for local control panel button to have effect. Please see 12. Misc for further information. When HS17065B Activated: Energise SV17047 AND Start F17PO409. When HS17065B De-Activated / Released (Falling Edge): De-Energise SV17047. DCS Graphic button to be programmed to lower rake remotely by CRO. | 3
|  |  |  | HS17061 | HS17061STT | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel Rake Drive Local Start Request Push Button | F17TH401 Fwd Local Start | Normal | Active |  | Hardwired to DCS |  |  | F17TH401 must be in LOCAL mode for local control panel button to have effect. Please see 12. Misc for further information. 1. If F17TH401 in LOCAL mode (F17TH401_LCL Active) AND HS17061 Active AND Reverse Enable Not Active (F17TH401_REV Not Active): - Start F17PO408 - Energise SV17033 2. If F17TH401 in LOCAL mode (F17TH401_LCL Active) and HS17061 Active AND Reverse Enable Active (F17TH401_REV Active): - Start F17PO408 - Energise SV17034 Lock-out timers exist for Reverse Jogging. Please refer to 12. Misc for details. | 3
|  |  |  | HS17060 | XA17060 | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel Emergency Stop Switch | F17TH401 EStop | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  | Additional contact to MCC for motor interlock. Indication only. | 3
|  |  |  | HS17063 | HS17063STT | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel Reverse Jog Request Push Button | F17TH401 Reverse Jog | Normal | Alarm | Alarm | Hardwired to DCS | 3 |  | F17TH401 must be in LOCAL mode (F17TH401_LCL Active) AND Reverse Enable (F17TH401_REV Active) must be active for local control panel button (HS17063) to have effect. Please see 12. Misc for further information. When HS17063 Activated: Energise SV17034 and Start F17PO408. When HS17063 De-Activated / Released (Falling Edge): De-Energise SV17034. Lock-out timers exist for Reverse Jogging. Please refer to 12. Misc for details. | 3
|  |  |  | HS17064 | HS17064STT | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel Rake Drive Local Stop Push Button | F17TH401 Local Stop | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | F17TH401 must be in LOCAL mode (F17TH401_LCL Active) for local control panel button to have effect. Please see 12. Misc for further information. When HS17064 Active: Stop F17PO408 AND F17PO409. De-Energise SV17033, SV17034, SV17047, SV17048. | 3
|  |  |  | LSL17017 | LAL17017 | 2000-F17-PID-PR-10001 | F17-TH-401 Flotation Tailings Thickener Gear Reducer Oil Level Switch Low 1 | F17TH401 Gear Redcr Oil1 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001. | 3
|  |  |  | LSL17018 | LAL17018 | 2000-F17-PID-PR-10001 | F17-TH-401 Flotation Tailings Thickener Gear Reducer Oil Level Switch Low 2 | F17TH401 Gear Redcr Oil2 | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Source: 2000-ME001.5-M02-50001. | 3
|  |  |  | ZSH17014 | ZAH17014 | 2000-F17-PID-PR-10001 | F17-TH-401 Flotation Tailings Thickener Rake Lift Position Switch High | F17TH401 Rake Hi Limit | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Inductive proximity sensor. Closes Rake Raise Solenoid Valve. Refer to On/Off valves. Alarm if switch active. Source: 2000-ME001.5-M02-50001. | 3
|  |  |  | ZSL17015 | ZAL17015 | 2000-F17-PID-PR-10001 | F17-TH-401 Flotation Tailings Thickener Rake Lift Position Switch Low | F17TH401 Rake Lo Limit | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Inductive proximity sensor. Closes Rake Lower Solenoid Valve. Refer to On/Off valves. Alarm if switch active. Source: 2000-ME001.5-M02-50001. | 3
|  |  |  | SSL17016 | SAL17016 | 2000-F17-PID-PR-10001 | F17-TH-401 Flotation Tailings Thickener Rake Underspeed Switch | F17TH401 Rake Speed | Alarm | Normal | Alarm | Hardwired to DCS | 20 | Mask if F17PO408 Not Running | 17060 | 3 | [6 empty] | tested IO, havent tested by running motor yet
|  |  |  | XS17008 | XAH17008 | 2000-F17-PID-PR-10001 | F16-PP-634 Final Tails Sample Pump Hose Leak Detection Switch | F16PP634 Hose Leak | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Part of Vendor Package. ME042. | 3
|  |  |  | XS17066 | XI17066 | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel 24VDC Power Healthy Indicator Light | F17TH401 Pwr Healthy | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  | 24V DCS Power Healthy | 3
|  |  |  | FSL16156 | FAL16156 | 2000-F24-PID-PR-10003 | F16-PP-638 Sample Return Pump 1 Gland Water Flow Indicating Transmitter | F16PP638 Gland | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F16PP638 Not Running |  | 3
|  |  |  | XS16046 | XAH16046 | 2000-F16-PID-PR-10004 | F16-PP-633 Scavenger Tails Sample Pump Hose Leak Detection Switch | F16PP633 Hose Leak | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Part of Vendor Package. ME042. | 3
|  |  |  | XS16045 | XAH16045 | 2000-F16-PID-PR-10004 | F16-PP-632 Scavenger Concentrate Sample Pump Hose Leak Detection Switch | F16PP632 Hose Leak | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Part of Vendor Package. ME042. | 3
|  |  |  | FSL16166 | FAL16166 | 2000-F24-PID-PR-10003 | F16-PP-639 Sample Return Pump 2 Gland Water Flow Indicating Transmitter | F16PP639 Gland | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F16PP639 Not Running |  | 3
|  | Instrument list to be updated to be FT |  | FSL16358 | FAL16358 | 2000-F24-PID-PR-10003 | F16-PP-515 Flotation Cell Drain Pump Gland Water Flow Switch | F16PP515 Gland | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F16PP515 Not Running |  | 3
|  |  |  | LSH16121 | LAH16121 | 2000-F16-PID-PR-10003 | F16-PS-412 Flotation Area Sump Pump 2 Level Switch High | F16PS412 Flot Sump 2 | Normal | Alarm | Alarm | SoftTag | 3 |  | Switch to turn on respective sump pump in Auto mode. Refer to Drives for further information. (Wired to motor starter) | 2
|  |  |  | LSH16141 | LAH16141 | 2000-F16-PID-PR-10004 | F16-PS-413 Flotation Area Sump Pump 3 Level Switch High | F16PS413 Flot Sump 3 | Normal | Alarm | Alarm | SoftTag | 3 |  | Switch to turn on respective sump pump in Auto mode. Refer to Drives for further information. (Wired to motor starter) | 2
|  |  |  | XS16044 | XAH16044 | 2000-F16-PID-PR-10002 | F16-PP-631 Rougher 2 & 3 Concentrate Sample Pump Hose Leak Detection Switch | F16PP631 Hose Leak | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Part of Vendor Package. ME042. | 3
|  |  |  | XS16042 | XAH16042 | 2000-F16-PID-PR-10001 | F16-PP-629 Rougher 1 Concentrate Cleaner Feed Sample Pump Hose Leak Detection Switch | F16PP629 Hose Leak | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Part of Vendor Package. ME042. | 2
|  |  |  | XS16043 | XAH16043 | 2000-F16-PID-PR-10001 | F16-PP-630 Rougher 1 Concentrate Sample Pump Hose Leak Detection Switch | F16PP630 Hose Leak | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  | Part of Vendor Package. ME042. | 2
|  |  |  | F16SW011HTY | F16SW011_HTY | N/A | F16-SW-011 Fuse Healthy | F16SW011 Fuse Healthy | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2
|  |  |  | F16SW011ESCL | F16SW011_ESCL | N/A | F16-SW-011 Earth Switch Closed | F16SW011 ES Closed | N_Active | Active |  | Hardwired to DCS |  |  |  | 2
|  |  |  | F16SW011ESOP | F16SW011_ESOP | N/A | F16-SW-011 Earth Switch Opened | F16SW011 ES Open | N_Active | Active |  | Hardwired to DCS |  |  |  | 2
|  |  |  | ZSC16037 | ZAC16037 | N/A | F16-TR-004 Flotation 415V MCC Transformer Enclosure Door Position Switch Closed | F16TR004 415VMCC Door | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2
|  |  |  | ZSC16038 | ZAC16038 | N/A | F16-TR-005 Flotation Blowers And Compressors 415V MCC Transformer Enclosure Door Position Switch Closed | F16TR005 415VMCC Door | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2
|  |  |  | ZSC16039 | ZAC16039 | N/A | F16-TR-008 Thickener Emergency Power 415V MCC Transformer Enclosure Door Position Switch Closed | F16TR008 415VMCC Door | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2
|  |  |  | F16XM411STS1 | F16XM411VSTS | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Velocity Status | F16XM411 VelocityStatus | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM411STS2 | F16XM411CSTS | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Colour Status | F16XM411 Colour Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM411STS3 | F16XM411BSTS | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Bubble Size Status | F16XM411 Bubble Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM411STS4 | F16XM411LSTS | 2000-F16-PID-PR-10001 | F16-XM-411 Rougher Flotation Cell 1 Froth Camera Lidar Status | F16XM411 Lidar Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM586STS1 | F16XM586VSTS | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Velocity Status | F16XM586 VelocityStatus | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM586STS2 | F16XM586CSTS | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Colour Status | F16XM586 Colour Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM586STS3 | F16XM586BSTS | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Bubble Size Status | F16XM586 Bubble Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM586STS4 | F16XM586LSTS | 2000-F16-PID-PR-10002 | F16-XM-586 Rougher Flotation Cell 2 Froth Camera Lidar Status | F16XM586 Lidar Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM587STS1 | F16XM587VSTS | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Velocity Status | F16XM587 VelocityStatus | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM587STS2 | F16XM587CSTS | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Colour Status | F16XM587 Colour Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM587STS3 | F16XM587BSTS | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Bubble Size Status | F16XM587 Bubble Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM587STS4 | F16XM587LSTS | 2000-F16-PID-PR-10002 | F16-XM-587 Rougher Flotation Cell 3 Froth Camera Lidar Status | F16XM587 Lidar Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM588STS1 | F16XM588VSTS | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Velocity Status | F16XM588 VelocityStatus | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM588STS2 | F16XM588CSTS | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Colour Status | F16XM588 Colour Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM588STS3 | F16XM588BSTS | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Bubble Size Status | F16XM588 Bubble Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM588STS4 | F16XM588LSTS | 2000-F16-PID-PR-10003 | F16-XM-588 Scavenger Flotation Cell 1 Froth Camera Lidar Status | F16XM588 Lidar Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM589STS1 | F16XM589VSTS | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Velocity Status | F16XM589 VelocityStatus | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM589STS2 | F16XM589CSTS | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Colour Status | F16XM589 Colour Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM589STS3 | F16XM589BSTS | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Bubble Size Status | F16XM589 Bubble Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM589STS4 | F16XM589LSTS | 2000-F16-PID-PR-10003 | F16-XM-589 Scavenger Flotation Cell 2 Froth Camera Lidar Status | F16XM589 Lidar Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM590STS1 | F16XM590VSTS | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Velocity Status | F16XM590 VelocityStatus | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM590STS2 | F16XM590CSTS | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Colour Status | F16XM590 Colour Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM590STS3 | F16XM590BSTS | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Bubble Size Status | F16XM590 Bubble Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM590STS4 | F16XM590LSTS | 2000-F16-PID-PR-10003 | F16-XM-590 Scavenger Flotation Cell 3 Froth Camera Lidar Status | F16XM590 Lidar Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM591STS1 | F16XM591VSTS | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Velocity Status | F16XM591 VelocityStatus | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM591STS2 | F16XM591CSTS | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Colour Status | F16XM591 Colour Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM591STS3 | F16XM591BSTS | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Bubble Size Status | F16XM591 Bubble Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F16XM591STS4 | F16XM591LSTS | 2000-F16-PID-PR-10003 | F16-XM-591 Scavenger Flotation Cell 4 Froth Camera Lidar Status | F16XM591 Lidar Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 3
|  |  |  | F18CAM101STS1 | F18CAM101VSTS | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Velocity Status | F18CAM101 VelocityStatus | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 2
|  |  |  | F18CAM101STS2 | F18CAM101CSTS | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Colour Status | F18CAM101 Colour Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 2
|  |  |  | F18CAM101STS3 | F18CAM101BSTS | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Bubble Size Status | F18CAM101 Bubble Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 2
|  |  |  | F18CAM101STS4 | F18CAM101LSTS | 2000-F18-PID-PR-10002 | F18-CAM-101 Cleaner Flotation Cell Froth Camera Lidar Status | F18CAM101 Lidar Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 2
|  |  |  | F18CAM102STS1 | F18CAM102VSTS | 2000-F18-PID-PR-10004 | F18-CAM-102 Cleaner Flotation Cell Froth Camera Velocity Status | F18CAM102 VelocityStatus | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 2
|  |  |  | F18CAM102STS2 | F18CAM102CSTS | 2000-F18-PID-PR-10004 | F18-CAM-102 Cleaner Flotation Cell Froth Camera Colour Status | F18CAM102 Colour Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 2
|  |  |  | F18CAM102STS3 | F18CAM102BSTS | 2000-F18-PID-PR-10004 | F18-CAM-102 Cleaner Flotation Cell Froth Camera Bubble Size Status | F18CAM102 Bubble Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 2
|  |  |  | F18CAM102STS4 | F18CAM102LSTS | 2000-F18-PID-PR-10004 | F18-CAM-102 Cleaner Flotation Cell Froth Camera Lidar Status | F18CAM102 Lidar Status | Alarm | Normal | Alarm | SoftTag | 3 |  | SoftTag From FLS OPC Server | 2
|  |  |  | F17XM572CSALS | F17XM572CSALM | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Cable Too Short | F17XM572 Cable Short | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.CableShortAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572CRALS | F17XM572CRALM | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Setup Data Required | F17XM572 Config Required | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.CfgReqAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572DTALS | F17XM572DTALM | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Dive Time Exceeded | F17XM572 DiveTime Exceed | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.DiveTimeExAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572MSFTS | F17XM572MSFLT | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub HM Switch on during Raise or Home | F17XM572 HeavyMudSwFault | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.HeavyMudSwFlt Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572DRALS | F17XM572DRALM | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Drive Fault | F17XM572 Drive Fault | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.DrvFltAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572OFALS | F17XM572OFALM | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Prox Off Fault | F17XM572 Prox Off Fault | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.ProxOffFltAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572ONALS | F17XM572ONALM | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Prox On Fault | F17XM572 Prox On Fault | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.ProxOnFltAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572ESALS | F17XM572ESALM | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Rake Switch Early | F17XM572 RakeSwitchEarly | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.RakeSwEarlyAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572LSALS | F17XM572LSALM | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Rake Switch Late | F17XM572 RakeSwitchLate | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.RakeSwLateAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572SDALS | F17XM572SDALM | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Sensor Dirty | F17XM572 Sensor Dirty | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.SenDirtyAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572SFALS | F17XM572SFALM | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Sensor Fault | F17XM572 Sensor Fault | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.SenFltAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572SHALS | XA17038 | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Sensor Failed to Return Home | F17XM572 Failed to Home | Normal | Alarm | Alarm | SoftTag | 3 | F17XM572ESTP OR XA17038 OR F17XM572PEF OR XA17012COMF | SoftTag Manta Ref: Manta_Sub.SenHomeFailedAlm Sensor Failed to Return Home. Flotation Tailings Thickener Rakes will trip when alarm active. Manta Sub Documentation: 2000-ME001.5-D02-50002 Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572SJALS | F17XM572SJALM | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Prox On During Dive / Sensor Jammed | F17XM572 Sensor Jammed | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.SenJamAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572SRFAS | F17XM572SRFAL | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Sensor Recovery Failed | F17XM572 Recovery Fail | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.SenRecFailedAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572SRLAS | F17XM572SRLAL | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Prox On During Recovery Lower | F17XM572 Recovery Lower | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.SenRecLowerAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572SOLAS | F17XM572SOLAL | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Rake Switch On Too Long | F17XM572 Rake Sw On Long | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.RakeSwOnLongAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572DIVES | F17XM572DIVE | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Dive In (Rake Detected) | F17XM572 DiveInSta | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.DiveInSta Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572FWDS | F17XM572FWD | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Drive Enable On | F17XM572 Drive Enabled | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.DrvEnSta Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572REVS | F17XM572REV | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Drive Reverse On | F17XM572 Drive Reverse | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.DrvRevSta Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572LSTTS | F17XM572LSTT | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Local Start PB | F17XM572 Local Start | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.PbStSta Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572LSTPS | F17XM572LSTP | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Local Stop PB | F17XM572 Local Stop | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.PbStpSta Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572DOCKS | F17XM572DOCK | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Probe Docked | F17XM572 Probe Docked | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.ProbDckSta Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572PRAOS | F17XM572PRAO | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Dock Prox A On | F17XM572 Prox A | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.ProxASta Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572PRBOS | F17XM572PRBO | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Dock Prox B On | F17XM572 Prox B | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.ProxBSta Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572RSOS | F17XM572RSO | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Rake Switch On | F17XM572 Rake Sw On | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.RakeSwSta Refer to Manta Sub V408 Modbus Tag List (03-REG-371) | [7 empty] | Used to be zs17010
|  |  |  | F17XM572VALS | F17XM572VAL | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Values Updating | F17XM572 ValUpdOk | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.ValUpdOk Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572ESTPS | F17XM572ESTP | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Emergency Stop On | F17XM572 EStop | Alarm | Normal | Alarm | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.EStop Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572HMSS | F17XM572HMS | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Bed Switch On | F17XM572 HeavyMudSwitch | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.HeavyMudSwitch Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572SVOS | F17XM572SVO | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Water Solenoid On | F17XM572 WtrSolSta | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.WtrSolSta Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572WARNS | F17XM572WARN | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Warning | F17XM572 Warning | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub.Warning Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572FLTS | XA17038B | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Fault | F17XM572 Fault | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub.Fault Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572PEFS | F17XM572PEF | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Probe Entangle Fault | F17XM572 Probe Entangle | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Reserve for Future Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572CSFS | F17XM572CSF | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Clarity Sensor Fault | F17XM572 Clarity SensFlt | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub_ClaritySenFltAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572CLFS | F17XM572CLF | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Clarity Low Fault | F17XM572 Clarity Lo Flt | Normal | Alarm | Alarm | SoftTag | 3 |  | SoftTag Manta Ref: Manta_Sub_ClarityLowFltAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572CDNS | F17XM572CDN | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Clarity Depth Negative | F17XM572 Clarity DpthNeg | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub_ClarityDepthNegAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572WPLS | F17XM572WPL | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Water Pressure Low | F17XM572 Water Press Lo | N_Active | Active |  | SoftTag |  |  | SoftTag Manta Ref: Manta_Sub_WaterPressLoAlm Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | XA17012COMFS | XA17012COMF | 2000-F17-PID-PR-10001 |  | F17XM572 Comms Fault | N_Active | Alarm | Alarm | SoftTag | 10 |  | This alarm is to be configured in the Yokogawa DCS
|  |  |  | ZSH17144 | ZSH17144 | 2000-F17-PID-PR-10001 | F17-HU-422 Flotation Tailings Thickener Feed Box Valve HPU Limit Switch High | F17HU422 Valve Limit | Inactive | Active |  | Hardwired to DCS |  |  |  | 3
|  |  |  | PSH17143 | PAH17143 | 2000-F17-PID-PR-10001 | F17-HU-422 Flotation Tailings Thickener Feed Box Valve HPU Return Filter Pressure Switch High | F17HU422 Filter Return | Alarm (see comment) | N_Active | Alarm (see comment) | Hardwired to DCS | 3 |  | Logic: Latch PAH17143 alarm Unlatch if (PSH17143 active and F17HU422 running) for > 10 seconds | 3
|  |  |  | HS17145A | HS17145ALOC | 2000-F17-PID-PR-10001 | F17HU422-CP Flotation Tailings Thickener Feed Box Valve HPU Control Panel Local Selected | F17HU422 Local Mode | N_Active | Local |  | Hardwired to DCS |  |  | 2 selector switch, HS17145A/B Refer to HS17145_LOGIC for logic | 3
|  |  |  | HS17145B | HS17145BREM | 2000-F17-PID-PR-10001 | F17HU422-CP Flotation Tailings Thickener Feed Box Valve HPU Control Panel Remote Selected | F17HU422 Remote Mode | N_Active | Remote |  | Hardwired to DCS |  |  | 2 selector switch, HS17145A/B Refer to HS17145_LOGIC for logic | 3
|  |  |  | HS17146A | HS17146AOP | 2000-F17-PID-PR-10001 | F17HU422-CP Flotation Tailings Thickener Feed Box Valve HPU Control Panel Open Valve Push Button | F17HU422 Open Valve | N_Active | Open |  | Hardwired to DCS |  |  | Refer to HS17145_LOGIC for logic | 3
|  |  |  | HS17146B | HS17146BCL | 2000-F17-PID-PR-10001 | F17HU422-CP Flotation Tailings Thickener Feed Box Valve HPU Control Panel Close Valve Push Button | F17HU422 Close Valve | N_Active | Close |  | Hardwired to DCS |  |  | Refer to HS17145_LOGIC for logic | 3
|  |  |  | TS17039 | TAH17039 | 2000-F17-PID-PR-10001 | F17-PP-459 Flotation Tailings P-DUC Pump Motor Temperature Switch | F17PP459 Motor Temp | Alarm | Normal | Alarm | Hardwired to DCS | 3 |  |  | 3
|  |  |  | FSH16002 | FAH16002 | 2000-F24-PID-PR-10005 | F16-SE-410 FLOTATION AREA SAFETY SHOWER 2 | F16SE410 Alarm | Alarm | Normal | Alarm | Hardwired to DCS | 30 |  |  | 3
|  |  |  | F16TR004WTH | F16TR004_WTH | - | F16-TR-004 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F16TR004 Temp Hi | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3 | 2025-08-19 | CR-034 / MOC-240
|  |  |  | F16TR005WTH | F16TR005_WTH | - | F16-TR-005 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F16TR005 Temp Hi | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3 | 2025-08-19 | CR-034 / MOC-240
|  |  |  | F16TR008WTH | F16TR008_WTH | - | F16-TR-008 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F16TR008 Temp Hi | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 3 | 2025-08-19 | CR-034 / MOC-240
|  |  |  | F16GE104CBTRP | 16GE104CBTRP |  | F16-GE-104 FLOTATION ESSENTIAL SUPPLY 415V GENERATOR CB TRIPPED | F16-GE-104 GEN CB TRP | Alarm | Normal | Alarm | Hardwired to DCS | 0
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 461 | 461

## 4. Digital Output
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - FLOTATION (F16, F17, F18) |  |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)*
2000-F16-LST-PR-10001
DIGITAL INSTRUMENTS (DO)
[16 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date
|  |  |  | YI17117A | YA17117A | 2000-F17-PID-PR-10002 | F17-FN-504 Flotation Tailings Thickener Underflow Tunnel Ventilation Fan Not Running Signal 1 | F17FN504 Not Running 1 | N_Active | Active |  |  |  | Activate when: - F17FN504 Not Running Digital output to activate two beacons located inside the Flotation Tailings Thickener Underflow Tunnel. | 3
|  |  |  | YI17117B | YA17117B | 2000-F17-PID-PR-10002 | F17-FN-504 Flotation Tailings Thickener Underflow Tunnel Ventilation Fan Not Running Signal 2 | F17FN504 Not Running 2 | N_Active | Active |  |  |  | Activate when: - F17FN504 Not Running Digital output to activate two beacons located inside the Flotation Tailings Thickener Underflow Tunnel. | 3
|  |  |  | XY17076 | XC17076 | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel Rake Drive Running Status to LCP Control Signal | F17TH401 Rake Drive Rng | N_Active | Active |  |  |  | Source: 2000-ME001.5-F17-50001. Activate when F17PO408 = RUNNING | 2
|  |  |  | XY17079 | XC17079 | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel 85% Torque Request frrom DCS to LCP Control Signal | F17TH401 85% Torque | N_Active | Active |  |  |  | Activate on NI17030 >= A_HH. Source: 2000-ME001.5-F17-50001. Must activate Torque Cut - Out on LCP - XI17030A. | 2
|  |  |  | XY17083 | XC17083 | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel 50% Torque Request frrom DCS to LCP Control Signal | F17TH401 50% Torque | N_Active | Active |  |  |  | Activate on NI17030 A_Hi. Source: 2000-ME001.5-F17-50001. | 2
|  |  |  | XY17080 | XC17080 | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel 40% Torque Request frrom DCS to LCP Control Signal | F17TH401 40% Torque | N_Active | Active |  |  |  | Activate on NI17030 >= P_Hi. Will activate horn and beacon. Source: 2000-ME001.5-F17-50001. | 2
|  |  |  | XY17084 | XC17084 | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel 30% Torque Request frrom DCS to LCP Control Signal | F17TH401 30% Torque | N_Active | Active |  |  |  | Activate on NI18030 P_Lo. Source: 2000-ME001.5-F17-50001. | 2
|  |  |  | XY17062 | XC17062 | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel Reverse Jog Enable Feedback | F17TH401 Rev Jog Enable | N_Active | Active |  |  |  | Source: 2000-ME001.5-F17-50001. Activate when: Control Room Operator selects button in DCS "Reverse Jog Enable" (F17TH401_REV Active). Clicking this button will activate XC17057. Please refer to 12. Misc for further details on F17TH401 LOCAL mode. | 3 |  |  |  |  | Clickable only when 17HT401 is in local, Clicking this will NOT activate XC17057 | Comments for MISC logic checked - AP 29/07/2026
|  |  |  | XY17057 | XC17057 | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel Local Mode Enable Feedback | F17TH401 Local Mode | Disabled | Enabled |  |  |  | Source: 2000-ME001.5-F17-50001. Activate when: Thickener Faceplate placed into Local mode in DCS. F17TH401 to be constructed as a singular object. Placing into LOCAL mode will place the following equipment into LOCAL (F17TH401_LCL Active): - F17PO408, SV17033, SV17034 - F17PO409, SV17047, SV17048 Please refer to 12. Misc for further details on F17TH401 LOCAL mode. | 2
|  |  |  | XY17082 | XC17082 | 2000-F17-PID-PR-10001 | F17TH401-CP Flotation Tailings Thickener Control Panel Horn Acknowledge Control Signal | F17TH401 Horn Ackwldge | N_Active | Active |  |  |  | Source: 2000-ME001.5-F17-50001. Horn is activated on torque level greater than 50% by XC17080. Horn will continue to sound until physical switch is depressed on local control board or a graphical user-interface button "Horn Acknowledge" is pressed by Control Room Operator. Clicking graphical user-interface button will de-activate horn via activation of this digital output. | 3
|  |  |  | F17XM572CSTTS | HS17038STT | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Communication Start | F17XM572 Remote Start | N_Active | Start |  |  |  | SoftTag Manta Ref: Manta_Sub.CommsStSta Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F17XM572STPS | HS17038STP | 2000-F17-PID-PR-10001 | F17XM572 Manta Sub Exetrnal Stop Request | F17XM572 Remote Stop | N_Active | Stop |  |  |  | SoftTag Manta Ref: Manta_Sub.ExtStopRequest Refer to Manta Sub V408 Modbus Tag List (03-REG-371)
|  |  |  | F16SW011OP1 | F16SW011_OP1 | N/A | Flotation 11kV Switchboard Remote Switching Panel Open Breaker Incomer 1 | Flot 11kV Rem O Break1 | N_Active | Active |  |  |  |  | 2
|  |  |  | F16SW011CL1 | F16SW011_CL1 | N/A | Flotation 11kV Switchboard Remote Switching Panel Close Breaker Incomer 1 | Flot 11kV Rem C Break1 | N_Active | Active |  |  |  |  | 2
|  |  |  | F16SW011OP2 | F16SW011_OP2 | N/A | Flotation 11kV Switchboard Remote Switching Panel Open Breaker Incomer 2 | Flot 11kV Rem O Break2 | N_Active | Active |  |  |  |  | 2
|  |  |  | F16SW011CL2 | F16SW011_CL2 | N/A | Flotation 11kV Switchboard Remote Switching Panel Close Breaker Incomer 2 | Flot 11kV Rem C Break2 | N_Active | Active |  |  |  |  | 2
|  |  |  | XY17147A | XI17147A | 2000-F17-PID-PR-10001 | F17HU422-CP Flotation Tailings Thickener Feed Box Valve HPU Control Panel Valve Opened Indicator Signal | F17HU422 Opened | N_Active | Active |  |  |  | Logic: Activate if XV17009 = open else inactive | 3 |  |  |  |  | Digi out only logic to be checked with vendor
|  |  |  | XY17147B | XI17147B | 2000-F17-PID-PR-10001 | F17HU422-CP Flotation Tailings Thickener Feed Box Valve HPU Control Panel Valve Closed Indicator Signal | F17HU422 Closed | N_Active | Active |  |  |  | Logic: Activate if XV17009 = closed else inactive | 3 |  |  |  |  | Digi out only logic to be checked with vendor
|  |  |  | XY17147C | XI17147C | 2000-F17-PID-PR-10001 | F17HU422-CP Flotation Tailings Thickener Feed Box Valve HPU Control Panel System Healthy Indicator Signal | F17HU422 Healthy | N_Active | Active |  |  |  | Logic: No safety or process interlocks active on F17HU422 | 3 |  |  |  |  | Digi out only logic to be checked with vendor
|  |  |  | XY17147D | XI17147D | 2000-F17-PID-PR-10001 | F17HU422-CP Flotation Tailings Thickener Feed Box Valve HPU Control Panel Oil Temperature High Indicator Signal | F17HU422 Hi Temp | N_Active | Active |  |  |  | Logic: Activate if TI17141 >= A_Hi else inactive | 3 |  |  |  |  | Digi out only logic to be checked with vendor
|  |  |  | XY17147E | XI17147E | 2000-F17-PID-PR-10001 | F17HU422-CP Flotation Tailings Thickener Feed Box Valve HPU Control Panel Oil Level Low Indicator Signal | F17HU422 Oil Lo | N_Active | Active |  |  |  | Logic: Activate if LI17142 <= A_Lo else inactive | 3
|  |  |  | XY17147F | XI17147F | 2000-F17-PID-PR-10001 | F17HU422-CP Flotation Tailings Thickener Feed Box Valve HPU Control Panel Local Control Enable Indicator Signal | F17HU422 Local Enabled | N_Active | Active |  |  |  | Logic: Activate if HS17145ALOC = local else inactive | 3 |  |  |  |  | Digi out only logic to be checked with vendor
|  |  |  | XY17147G | XI17147G | 2000-F17-PID-PR-10001 | F17HU422-CP Flotation Tailings Thickener Feed Box Valve HPU Control Panel HPU Running Indicator Signal | F17HU422 Running | N_Active | Active |  |  |  | Logic: Activate if F17HU422 = running else inactive | 3 |  |  |  |  | Digi out only logic to be checked with vendor
|  |  |  | XY17147H | XI17147H | 2000-F17-PID-PR-10001 | F17HU422-CP Flotation Tailings Thickener Feed Box Valve HPU Control Panel Filter Blocked Indicator Signal | F17HU422 Filter Block | N_Active | Active |  |  |  | Logic: Activate if PAH17143 alarm or PI17140 >= A_Hi else inactive | 3 |  |  |  |  | Digi out only logic to be checked with vendor
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 24 | 24
Operator to get electrician to inspect unit for potential failure

## 5. Totalisers
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION (F16, F17, F18)
2000-F16-LST-PR-10001
TOTALISERS
[11 empty] | Reset Period |  |  |  |  | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | Type | P&ID | Description | Abbreviated Description (Faceplate) | Units | Shift | Day | Cont | Comments | Rev | OK | Date | OK | Date
|  |  |  | WI17121 | WQI17121 | WQI | 2000-F17-PID-PR-10002 | F17-PP-455/456 Flotation Tailings Thickener Underflow Pumps Solids Mass Totaliser | F17TH401 U/F Solids Mass | t | X | X | X | Low cutoff/clamping requirement TBC during commissioning | 3
|  |  |  | WI17130 | WQI17130 | WQI | 2000-F17-PID-PR-10002 | F17-PP-455/456 Flotation Tailings Thickener Underflow to Final Tails Tank Solids Mass Totaliser | F17TH401 UF-Final Tails | t | X | X | X | See 11. Calculation sheet for further information. Low cutoff/clamping requirement TBC during commissioning | 3
|  |  |  | WI18027 | WQI18027 | WQI | 2000-F18-PID-PR-10001 | F18-PP-407/408 Final Concentrate Pumps Discharge Solids Mass Totaliser | F18PP407/8 Solids Mass | t | X | X | X | Low cutoff/clamping requirement TBC during commissioning | 3
|  |  |  | WI18237 | WQI18237 | WQI | 2000-F18-PID-PR-10003 | F18-PP-407/408 Final Concentrate Pumps Discharge Solids Mass Totaliser | F18PP513/4 Solids Mass | t | X | X | X | Low cutoff/clamping requirement TBC during commissioning | 3
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 4 | 4
Operator to get electrician to inspect unit for potential failure

## 6. OnOff Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION (F16, F17, F18)
2000-F16-LST-PR-10001
OPEN-CLOSE VALVES
[14 empty] | Permissives and Trips | [12 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position (Loss of Power) | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (Faceplate) | Delay On | Delay Off | Open Permissive | Close Permissive | Open Interlock | Close Interlock | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date
|  |  |  | XV16025 | 2000-F16-PID-PR-10001 | F16-GA-425 Rougher 1 Concentrate Cleaner Feed Launder Gate Cleaner Flotation Feed Valve | F16GA425 Rgh1 Clnr Con | Detail 3 | FL | X |  | Manually opened by Operator | Manually closed by Operator | [12 empty] | B
|  |  |  | XV16026 | 2000-F16-PID-PR-10001 | F16-GA-426 Rougher 1 Final Concentrate Launder Gate Final Concentrate Feed Valve | F16GA426 Rgh1 Final Con | Detail 3 | FL | X |  | Manually opened by Operator | Manually closed by Operator | [12 empty] | B
|  |  |  | SV16357 | 2000-F24-PID-PR-10003 | F16-PP-515 Flotation Cells Drain Pump Gland Water Solenoid Valve | F16PP515 Gland Supply | Detail 11 | FO | X | X | F16-PP-515 Start | Manually closed by Operator | OT1 | F16PP515 RUNNING | Flotation Cells Drain Pump Rung | 0 |  |  |  | X |  | X |  |  | 3
|  |  |  | XV16152 | 2000-F16-PID-PR-10005 | F16-PP-638 Sample Return Pump 1 Suction Valve | F16PP638 Suction | Detail 3 | FL | X |  | Manually opened by Operator | Manually closed by Operator | [12 empty] | B
|  |  |  | XV16153 | 2000-F16-PID-PR-10005 | F16-PP-638 Sample Return Pump 1 Drain Valve | F16PP638 Suction Drain | Detail 4 | FO | X |  | Manually opened by Operator | Manually closed by Operator | CT1 | F16PP638 RUNNING | Sample Return Pump 1 is Running | 3 |  |  |  |  | X | X |  |  | 3
|  |  |  | SV16155 | 2000-F24-PID-PR-10003 | F16-PP-638 Sample Return Pump 1 Gland Water Solenoid Valve | F16PP638 Gland Supply | Detail 11 | FO | X | X | F16-PP-638 Start | Manually closed by Operator | OT1 | F16PP638 RUNNING | Sample Return Pump 1 is Running | 0 |  |  |  | X |  | X |  |  | 3
|  |  |  | XV16162 | 2000-F16-PID-PR-10005 | F16-PP-639 Sample Return Pump 2 Suction Valve | F16PP639 Suction | Detail 3 | FL | X |  | Manually opened by Operator | Manually closed by Operator | [12 empty] | B
|  |  |  | XV16163 | 2000-F16-PID-PR-10005 | F16-PP-639 Sample Return Pump 2 Suction Drain Valve | F16PP639 Suction Drain | Detail 4 | FO | X |  | Manually opened by Operator | Manually closed by Operator | CT1 | F16PP639 RUNNING | Sample Return Pump 2 is Running | 3 |  |  |  |  | X | X |  |  | 3
|  |  |  | SV16165 | 2000-F24-PID-PR-10003 | F16-PP-639 Sample Return Pump 2 Gland Water Solenoid Valve | F16PP639 Gland Supply | Detail 11 | FO | X | X | F16-PP-639 Start | Manually closed by Operator | OT1 | F16PP639 RUNNING | Sample Return Pump 2 is Running | 0 |  |  |  | X |  | X |  | Shorter than Drive Interlock to maintain operation. | 3
|  |  |  | XV17005 | 2000-F17-PID-PR-10001 | F16-PP-634 Final Tails Sample Pump Suction Valve | F16PP634 Suction | Detail 3 | FL | X |  | Manually opened by Operator | Manually closed by Operator | [12 empty] | B
|  |  |  | XV17006 | 2000-F17-PID-PR-10001 | F16-PP-634 Final Tails Sample Pump Suction Drain Valve | F16PP634 Suction Drain | Detail 7 | FO | X |  | Manually opened by Operator | Manually closed by Operator | CT1 | F16PP634 RUNNING | Final Tails Sample Pump Running | 3 |  |  |  |  | X | X |  |  | 3
|  |  |  | XV17007 | 2000-F17-PID-PR-10001 | F16-PP-634 Final Tails Sample Pump Discharge Drain Valve | F16PP634 Discharge Drain | Detail 7 | FO | X |  | Manually opened by Operator | Manually closed by Operator | [12 empty] | C
|  |  |  | XV17009 | 2000-F17-PID-PR-10001 | F17-BX-410 Flotation Tailings Thickener Recirculation Feed Box Feed Valve | F17BX410 Feed Valve | Detail 5 | FL | X | [15 empty] | 3
|  |  |  | SV17033 | 2000-F17-PID-PR-10001 | F17-HU-406 Flotation Tailings Thickener Rake Drive HPU Rake Forward Solenoid Valve | F17HU406 Rake Forward | Detail 11 | FC |  | X |  |  | OP1 | SV17034 NOT ENERGISED | Rev Solenoid N_Energised | 3 |  | X |  |  |  | X |  | DCS user-interface button "Stop Thickener in Forward Mode" when activated will de-energise SV17033. | 3 |  |  |  |  | VV 05/07/2026; Loop Tested only , Fail position and the rest untested. Techs has no access to test fail position
[14 empty] | CT1 | XA17038 Active | Manta Sub Not in Home Posn | 3 |  |  |  |  | X | X |  | Manta Sub Sensor not returned to home position. Thickener rakes will stop to prevent sensor contacting with rakes. DCS user-interface button "Enable Reverse Jog Mode in LOCAL" will de-energise SV17033 if activated AND start F17TH401_T3. Please see 12. Misc for further information. | 3 |  |  |  |  | jwho 25/08/2026 Manta signal, can't test at the moment
[12 empty] | ('F17TH401_STRT Active AND F17PO408 Running) OR (F17TH401_LCL Active AND HS17061 Start Button Pressed AND F17TH401_REV Not Active) | (F17TH401_LCL Active AND HS17064 Stop Button Active) OR (F17TH401_REV Active) OR (F17TH401_STOP) | CT2 | (SSL17016 does not change state for 20 seconds) AND (F17-PO-408 Running) | F17TH401 Zero Speed Active | 0 |  |  |  |  | X | X |  | If there are no change of state detected from SSL17016 for 20 seconds AND F17-PO-408 is running, then close trip valve. | 3
[14 empty] | OP2 | F17TH401_T3 Not Active | Rake Protection Timer Active | 0 |  | X | [5 empty] | See 12. Misc for further details. | 3
|  |  |  | SV17034 | 2000-F17-PID-PR-10001 | F17-HU-406 Flotation Tailings Thickener Rake Drive HPU Rake Reverse Solenoid Valve | F17HU406 Rake Reverse | Detail 11 | FC |  | X | F17TH401_LCL Active AND HS17063 Reverse Jog Button Active AND F17TH401_REV Active AND F17TH401_T3 Not Active AND F17TH401_T2 Not Active | (F17TH401_T1 Elapsed) OR ( 'F17TH401_LCL Active AND HS17063 Released (Falling Edge)) | OP1 | SV17033 NOT ENERGISED | Fwd Solenoid N_Energised | 3 |  | X |  |  |  | X |  | HS17063 must be depressed (active) for SV17034 to remain energised when in LOCAL mode. When SV17034 is energised, F17TH401_T1 is started. Maximum energised duration applies as per timer. Please refer to 12. Misc for further details. Reverse Enable must be Active to Energise Solenoid. Please refer to 12. Misc - F17TH401_REV for further details. | 3 |  |  |  |  | VV 05/07/2026; Loop Tested only
[14 empty] | OP2 | F17TH401_C1 < 3 | Reverse Jog Hourly Limit | 0 |  | X |  |  |  | X |  | Source: 2000-ME001.5-M02-50001. See 12. Misc for further details. | 3
[14 empty] | OP3 | F17TH401_T2 Not Active | Reverse Lockout Timer Active | 0 |  | X |  |  |  | X |  | Source: 2000-ME001.5-M02-50001. See 12. Misc for further details. | 3
[14 empty] | OP4 | F17TH401_T3 Not Active | Rake Protection Timer Active | 0 |  | X | [5 empty] | See 12. Misc for further details. | 3
|  |  |  | SV17047 | 2000-F17-PID-PR-10001 | F17-HU-414 Flotation Tailings Thickener Rake Lift HPU Lower Rake Solenoid Valve | F17HU414 Rake Lower | Detail 11 | FC |  | X | AUTO MODE (F17-TH-401) Active AND NI17030 < P_Lo AND SV17033 Energised AND F17PO408 Running AND F17TH401_REVC = 0 AND ZAL17015 Not Active AND F17PO409 Running (Runtime > 5 seconds) | AUTO MODE (F17-TH-401) Active AND (F17TH401_RLWR Elapsed OR ZAL17015 Active) | OP1 | SV17048 NOT ACTIVE |  | 3 |  | X |  |  |  | X |  | Start F17TH401_RLWR when SV17047 Energised AND in AUTO MODE (F17-TH-401). To open solenoid in AUTO MODE: - NI17030 must be less than 30% - Thickener must be in FORWARD MODE - Revolution Counter must be equal to zero - Rake Low Limit Switch Not Active Control logic to be continually running when Thickener is in FORWARD MODE. Control logic to de-energise solenoid valve if during lowering in AUTO MODE, ZAL17015 becomes active. | 3 |  |  |  |  | VV 05/07/2026; Loop Tested only
[12 empty] | F17TH401_LCL Active AND HS17065B Active | F17TH401_LCL Active AND HS17065B Released (Falling Edge) | OP2 | AUTO MODE (F17-TH-401): F17-PO-408 RUNNING AND SV17033 ACTIVE | Thickener in Forward Mode | 3 |  | X |  |  |  | X |  | Unable to lower rake if thickener is not in FORWARD mode. | 3
[14 empty] | OP3 | AUTO MODE (F17-TH-401): F17PO409 Running (Runtime > 5 seconds) | F19PO409 Startup Timer | 0 |  | X |  |  |  | X |  | Prevent energising solenoid valve if F17PO409 has been started and runtime < 5 seconds. Permissive to allow hydraulic oil pressure to build to operating point. | 3
[14 empty] | CT1 | ZAL17015 Active |  | 3 |  |  |  |  | X | X |  | True in LOCAL AND AUTO Modes (F17-TH-401). Bypass for faulty switch. | 3
|  |  |  | SV17048 | 2000-F17-PID-PR-10001 | F17-HU-414 Flotation Tailings Thickener Rake Lift HPU Raise Rake Solenoid Valve | F17HU414 Rake Raise | Detail 11 | FC |  | X | AUTO MODE (F17-TH-401) Active AND NI17030 >= P_Hi AND SV17033 Energised AND F17PO408 Running AND ZAH17014 Not Active AND F17PO409 Running (Runtime > 5 seconds) | AUTO MODE (F17-TH-401) Active AND (NI17030 < P_Hi OR ZAH17014 Active) | OP1 | SV17047 NOT ACTIVE |  | 3 |  | X |  |  |  | X |  | Control logic to be continually running when Thickener is in FORWARD MODE. Control logic to de-energise solenoid valve if during raising in AUTO MODE (F17-TH-401), ZAH17014 becomes active. | 3 |  |  |  |  | VV 05/07/2026; Loop Tested only
[12 empty] | F17TH401_LCL Active AND HS17065A Active | F17TH401_LCL Active AND HS17065A Released (Falling Edge) | OP2 | AUTO MODE (F17-TH-401): F17-PO-408 RUNNING AND SV17033 ACTIVE | Thickener in Forward Mode | 3 |  | X |  |  |  | X |  | Unable to raise rake if thickener is not in FORWARD mode. Permissive does not apply in LOCAL. | 3
[14 empty] | OP3 | AUTO MODE (F17-TH-401): F17PO409 Running (Runtime > 5 seconds) | F19PO409 Startup Timer | 0 |  | X |  |  |  | X |  | Prevent energising solenoid valve if F17PO409 has been started and runtime < 5 seconds. Permissive to allow hydraulic oil pressure to build to operating point. | 3
[14 empty] | CT1 | ZAH17014 Active |  | 3 |  |  |  |  | X | X |  | True in LOCAL AND AUTO Modes (F17-TH-401). Bypass for faulty switch. | 3
|  |  |  | XV17091 | 2000-F17-PID-PR-10002 | F17-TH-401 Flotation Tailings Thickener Underflow Discharge Valve 1 - F17-PP-455 Suction | F17PP455 Suction 1 | Detail 4 | FC | X | X | F17-SEQ-0001 | F17-SEQ-0002 | OP1 | XV17095 OPEN AND XV17102 CLOSED | Water Hammer Prevention | 3 |  | X |  |  |  | X |  | To prevent water hammer on underflow pump start when Thickener Cone Valves are opened. Bypass for dumping of thickener. Suction Flush Valve must be Open and Suction Drain must be Closed. | 3 |  |  |  |  | VV 07/07/2026; Valve doesn’t Open/Close; Confirm 24V is received but valve doesn’t move. VV ; confirm valve movement from the field
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV17092 | 2000-F17-PID-PR-10002 | F17-TH-401 Flotation Tailings Thickener Underflow Discharge Valve 2 - F17-PP-456 Suction | F17PP456 Suction 1 | Detail 4 | FC | X | X | F17-SEQ-0001 | F17-SEQ-0002 | OP1 | XV17096 OPEN AND XV17112 CLOSED | Water Hammer Prevention | 3 |  | X |  |  |  | X |  | To prevent water hammer on underflow pump start when Thickener Cone Valves are opened. Bypass for dumping of thickener. Suction Flush Valve must be Open and Suction Drain must be Closed. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV17093 | 2000-F17-PID-PR-10002 | F17-TH-401 Flotation Tailings Thickener Underflow Discharge Valve 3 - F17-PP-455 Suction | F17PP455 Suction 2 | Detail 4 | FC | X | X | F17-SEQ-0001 | F17-SEQ-0002 | OP1 | XV17095 OPEN AND XV17102 CLOSED | Water Hammer Prevention | 3 |  | X |  |  |  | X |  | To prevent water hammer on underflow pump start when Thickener Cone Valves are opened. Bypass for dumping of thickener. Suction Flush Valve must be Open and Suction Drain must be Closed. | 3 |  |  |  |  | VV 07/07/2026; Valve doesn’t Open/Close; Confirm 24V is received but valve doesn’t move. VV ; confirm valve movement from the field
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV17094 | 2000-F17-PID-PR-10002 | F17-TH-401 Flotation Tailings Thickener Underflow Discharge Valve 4 - F17-PP-456 Suction | F17PP456 Suction 2 | Detail 4 | FC | X | X | F17-SEQ-0001 | F17-SEQ-0002 | OP1 | XV17096 OPEN AND XV17112 CLOSED | Water Hammer Prevention | 3 |  | X |  |  |  | X |  | To prevent water hammer on underflow pump start when Thickener Cone Valves are opened. Bypass for dumping of thickener. Suction Flush Valve must be Open and Suction Drain must be Closed. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV17095 | 2000-F17-PID-PR-10002 | F17-TH-401 Flotation Tailings Thickener Underflow Discharge Flushing Valve 1 | F17PP455 Suction Flush | Detail 3 | FL | X | X | F17-SEQ-0001 / F17-SEQ-0002 | F17-SEQ-0001 / F17-SEQ-0002 | [12 empty] | B
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV17096 | 2000-F17-PID-PR-10002 | F17-TH-401 Flotation Tailings Thickener Underflow Discharge Flushing Valve 2 | F17PP456 Suction Flush | Detail 3 | FL | X | X | F17-SEQ-0001 / F17-SEQ-0002 | F17-SEQ-0001 / F17-SEQ-0002 | [12 empty] | B
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV17101 | 2000-F17-PID-PR-10002 | F17-PP-455 Flotation Tailings Thickener Underflow Pump 1 Flushing Water Valve | F17PP455 Discharge Flush | Detail 3 | FL | X | X | F17-SEQ-0002 | F17-SEQ-0001 / F17-SEQ-0002 | [12 empty] | B
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV17102 | 2000-F17-PID-PR-10002 | F17-PP-455 Flotation Tailings Thickener Underflow Pump 1 Drain Valve | F17PP455 Suction Drain | Detail 4 | FO | X | X | F17-SEQ-0002 | F17-SEQ-0001 / F17-SEQ-0002 | CT1 | F17PP455 RUNNING | F17TH401 U/F Pump 1 Running | 3 |  |  |  |  | X | X |  | Flotation Tailings Thickener Underflow Pump 1 is Running. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator | OP1 | XV17091 CLOSED AND XV17093 CLOSED | Thickener D/C Valves Closed | 3 |  | X |  |  |  | X |  | Prevent opening of the suction-drain valve until the thickener cone valves are closed. Bypass for dumping of thickener. | 3
|  |  |  | XV17103 | 2000-F17-PID-PR-10002 | F17-PP-455 Flotation Tailings Thickener Underflow Pump 1 Discharge Valve | F17PP455 Discharge | Detail 3 | FL | X | X | F17-SEQ-0001 | F17-SEQ-0002 | CT1 | F17PP456 RUNNING | F17TH401 U/F Pump 2 Running | 3 |  |  |  |  | X | X |  |  | 3 |  |  |  |  | VV 06/07/20206; Openning only at 85% as per Filed tech. Open limit not receive in DCS. To revisit'
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | SV17104 | 2000-F24-PID-PR-10004 | F17-PP-455 Flotation Tailings Thickener Underflow Pump 1 Gland Water Solenoid Valve | F17PP455 Gland Water | Detail 11 | FO | X | X | F17-SEQ-0001 OR F17-PP-455 Start | F17-SEQ-0002 | OT1 | F17PP455 RUNNING | F17TH401 U/F Pump 1 Running | 0 |  |  |  | X |  | X |  | Prevent closing of solenoid valve if pump is running. Open trip prevents CRO from selecting "close" on solenoid valve, tripping pump and upsetting process. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator | [17 empty] | Faceplate accessible from the SFC Faceplate. Logged in as CCR
|  |  |  | XV17111 | 2000-F17-PID-PR-10002 | F17-PP-456 Flotation Tailings Thickener Underflow Pump 2 Flushing Water Valve | F17PP456 Discharge Flush | Detail 3 | FL | X | X | F17-SEQ-0001 / F17-SEQ-0002 | F17-SEQ-0001 / F17-SEQ-0002 | [12 empty] | B
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV17112 | 2000-F17-PID-PR-10002 | F17-PP-456 Flotation Tailings Thickener Underflow Pump 2 Drain Valve | F17PP456 Suction Drain | Detail 4 | FO | X | X | F17-SEQ-0002 | F17-SEQ-0001 / F17-SEQ-0002 | CT1 | F17PP456 RUNNING | F17TH401 U/F Pump 2 Running | 3 |  |  |  |  | X | X |  | Flotation Tailings Thickener Underflow Pump 2 is Running. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator | OP1 | XV17092 CLOSED AND XV17094 CLOSED | Thickener D/C Valves Closed | 3 |  | X |  |  |  | X |  | Prevent opening of the suction-drain valve until the thickener cone valves are closed. Bypass for dumping of thickener. | 3
|  |  |  | XV17113 | 2000-F17-PID-PR-10002 | F17-PP-456 Flotation Tailings Thickener Underflow Pump 2 Discharge Valve | F17PP456 Discharge | Detail 3 | FL | X | X | F17-SEQ-0001 | F17-SEQ-0002 | CT1 | F17PP455 RUNNING | F17TH401 U/F Pump 1 Running | 3 |  |  |  |  | X | X |  |  | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | SV17114 | 2000-F24-PID-PR-10004 | F17-PP-456 Flotation Tailings Thickener Underflow Pump 2 Gland Water Solenoid Valve | F17PP456 Gland Water | Detail 11 | FO | X | X | F17-SEQ-0001 OR F17-PP-456 Start | F17-SEQ-0002 | OT1 | F17PP456 RUNNING | F17TH401 U/F Pump 2 Running | 0 |  |  |  | X |  | X |  | Prevent closing of solenoid valve if pump is running. Open trip prevents CRO from selecting "close" on solenoid valve, tripping pump and upsetting process. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV17123 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps CIL 2, 3, 4, Tails Feed Valve | F17TH401 U/F Forward | Detail 3 | FL | X | X | F17-SEQ-0001 | F17-SEQ-0001 | [12 empty] | B |  |  |  |  | MTM=100s
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV17124 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps CIL 2, 3, 4, Tails Feed Drain Valve | F17TH401 U/F Fwd Drain | Detail 4 | FO | X | X | F17-SEQ-0002 | F17-SEQ-0001 / F17-SEQ-0002 | CT1 | F17PP455/456 RUNNING | F17TH401 U/F Pump 1/2 Running | 3 |  |  |  |  | X | X |  | Bypass for line clearing. | 3 |  |  |  |  | Losss of Power = FO Air Fail = FL MTM = 16s
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV17125 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps Recirculation Feed Box Valve | F17TH401 U/F Recirc | Detail 3 | FL | X | X | F17-SEQ-0001 | F17-SEQ-0001 | [12 empty] | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator | OT1 | DUTY F17PP455/456 RUNNING AND XV17123 CLOSED | F17PP455/6 Rung & Fwd Closed | 0 |  |  |  | X |  | X |  | Flotation Tailings Thickener Underflow Pump 1/2 is Running and Common Discharge Valve is Closed. Place thickener into recirculation mode before tripping duty underflow pumps. | 3
|  |  |  | XV17126 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps Recirculation Feed Box Drain Valve | F17TH401 U/F RecircDrain | Detail 3 | FL | X | X | Manually opened by Operator | F17-SEQ-0001 | CT1 | F17PP455/456 RUNNING AND XV17125 OPEN | F17PP455/6 Rung & RecircOpn | 3 |  |  |  |  | X | X |  | Flotation Tailings Thickener Underflow Pump 1/2 is Running and U/F Recirculation Valve is Open. | 3
|  |  |  | XV17131 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps CIL 2, 3, 4, Tails Feed Valve | F17TH401 U/F Fwd Flush | Detail 3 | FL | X | X | F17-SEQ-0002 | F17-SEQ-0001 / F17-SEQ-0002 | [12 empty] | B |  |  |  |  | MTM = 24s
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV17132 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps Final Tails Feed Valve | F17TH401 UF to FinTails | Detail 3 | FL | X | X | F17-SEQ-0001 | F17-SEQ-0001 | [12 empty] | C
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18012 | 2000-F18-PID-PR-10001 | F18-HP-414 Final Concentrate Hopper Process Water Valve | F18HP414 Water Isolation | Detail 4 | FC | X | X | F18-SEQ-0001 | F18-SEQ-0002 | CT1 | LIC18001A >= A_HH | F18HP414 Level High High | 30 |  |  |  |  | X | X |  | Close off Mill Water addition to hopper if Level High High | 3 |  |  |  |  | jwho - 16/08/2026 - Removed Justin DM
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18013 | 2000-F18-PID-PR-10001 | F18-HP-501 Cleaner Flotation Cell Feed Hopper Process Water Valve | F18HP501 Water Isolation | Detail 4 | FC | X | X | F18-SEQ-0003 | F18-SEQ-0004 | CT1 | LIC18011A >= A_HH | F18HP501 Level High High | 30 |  |  |  |  | X | X |  | Close off Mill Water addition to hopper if Level High High | 3 |  |  |  |  | jwho - 16/08/2026 - Removed Justin DM
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18021 | 2000-F18-PID-PR-10001 | F18-PP-407 Final Concentrate Pump 1 Suction Valve | F18PP407 Suction | Detail 3 | FL | X | X | F18-SEQ-0001 | F18-SEQ-0002 | [12 empty] | B
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18022 | 2000-F18-PID-PR-10001 | F18-PP-407 Final Concentrate Pump 1 Drain Valve | F18PP407 Suction Drain | Detail 4 | FO | X | X | F18-SEQ-0002 | F18-SEQ-0001 | CT1 | F18PP407 RUNNING | Final Concentrate Pump 1 Running | 3 |  |  |  |  | X | X |  |  | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18023 | 2000-F18-PID-PR-10001 | F18-PP-407 Final Concentrate Pump 1 Discharge Valve | F18PP407 Discharge | Detail 3 | FL | X | X | F18-SEQ-0001 | F18-SEQ-0002 | CT1 | F18PP408 RUNNING | Final Concentrate Pump 2 Running | 3 |  |  |  |  | X | X |  |  | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18024 | 2000-F18-PID-PR-10001 | F18-PP-408 Final Concentrate Pump 2 Suction Valve | F18PP408 Suction | Detail 3 | FL | X | X | F18-SEQ-0001 | F18-SEQ-0002 | [12 empty] | B
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18025 | 2000-F18-PID-PR-10001 | F18-PP-408 Final Concentrate Pump 2 Drain Valve | F18PP408 Suction Drain | Detail 4 | FO | X | X | F18-SEQ-0002 | F18-SEQ-0001 | CT1 | F18PP408 RUNNING | Final Concentrate Pump 2 Running | 3 |  |  |  |  | X | X |  |  | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18026 | 2000-F18-PID-PR-10001 | F18-PP-408 Final Concentrate Sampler Discharge Process Water Valve | F18PP408 Discharge | Detail 3 | FL | X | X | F18-SEQ-0001 | F18-SEQ-0002 | CT1 | F18PP407 RUNNING | Final Concentrate Pump 1 Running | 3 |  |  |  |  | X | X |  |  | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18028 | 2000-F18-PID-PR-10001 | F18-SA-403 Final Concentrate Sampler Discharge Valve | F18SA403 Discharge | Detail 7 | FC | X | X | F18-SEQ-0001 | F18-SEQ-0002 | [12 empty] | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18029 | 2000-F18-PID-PR-10001 | F18-SA-403 Final Concentrate Sampler Discharge Process Water Valve | F18SA403 Sample Flush | Detail 7 | FC | X | X |  | F18-SEQ-0001 | OP1 | XV18028 CLOSED | F18SA403 Discharge Valve Closed. | 3 |  | X |  |  |  | X |  | Bypass for operator discretion & low sample flow. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18031 | 2000-F18-PID-PR-10001 | F18-PP-501 Cleaner Flotation Cell Recirculation Pump 1 Suction Valve | F18PP501 Suction | Detail 3 | FL | X | X | F18-SEQ-0003 | F18-SEQ-0004 | [12 empty] | B
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18032 | 2000-F18-PID-PR-10001 | F18-PP-501 Cleaner Flotation Cell Recirculation Pump 1 Drain Valve | F18PP501 Suction Drain | Detail 4 | FO | X | X | F18-SEQ-0004 | F18-SEQ-0003 | CT1 | F18PP501 RUNNING | Cleaner Recirc Pump 1 Running | 3 |  |  |  |  | X | X |  |  | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18033 | 2000-F18-PID-PR-10001 | F18-PP-501 Cleaner Flotation Cell Recirculation Pump 1 Discharge Valve | F18PP501 Discharge | Detail 3 | FL | X | X | F18-SEQ-0003 | F18-SEQ-0004 | CT1 | F18PP502 RUNNING | Cleaner Recirc Pump 2 Running | 3 |  |  |  |  | X | X |  |  | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18034 | 2000-F18-PID-PR-10001 | F18-PP-502 Cleaner Flotation Cell Recirculation Pump 2 Suction Valve | F18PP502 Suction | Detail 3 | FL | X | X | F18-SEQ-0003 | F18-SEQ-0004 | [12 empty] | B
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18035 | 2000-F18-PID-PR-10001 | F18-PP-502 Cleaner Flotation Cell Recirculation Pump 2 Drain Valve | F18PP502 Suction Drain | Detail 4 | FO | X | X | F18-SEQ-0004 | F18-SEQ-0003 | CT1 | F18PP502 RUNNING | Cleaner Recirc Pump 2 Running | 3 |  |  |  |  | X | X |  |  | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18036 | 2000-F18-PID-PR-10001 | F18-PP-502 Cleaner Flotation Cell Recirculation Pump 2 Discharge Valve | F18PP502 Discharge | Detail 3 | FL | X | X | F18-SEQ-0003 | F18-SEQ-0004 | CT1 | F18PP501 RUNNING | Cleaner Recirc Pump 1 Running | 3 |  |  |  |  | X | X |  |  | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator | [11 empty] | XV18038
|  |  |  | XV18038 | 2000-F18-PID-PR-10001 | F16-SA-405 Cleaner Feed Sampler Discharge Valve | F18SA405 Discharge | Detail 7 | FC | X | X | F18-SEQ-0003 | F18-SEQ-0004 | [12 empty] | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18039 | 2000-F18-PID-PR-10001 | F16-SA-405 Cleaner Feed Discharge Process Water Valve | F18SA405 Sample Flush | Detail 7 | FC | X | X |  | F18-SEQ-0003 | OP1 | XV18038 CLOSED | F18SA405 Discharge Valve Closed. | 3 |  | X |  |  |  | X |  | Bypass for operator discretion & low sample flow. | 3 |  |  |  |  | FC 9/6/26 issue with XV18038. to be tested when available MSH 22/06: tested with working XV18038
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18014 | 2000-F18-PID-PR-10003 | F18-HP-511 Cleaner Scavenger Flotation Cell Feed Hopper Process Water Valve | F18HP511 Water Isolation | Detail 4 | FC | X | X | F18-SEQ-0005 | F18-SEQ-0006 | CT1 | LIC18201A >= A_HH | F18HP511 Level High High | 30 |  |  |  |  | X | X |  | Close off Mill Water addition to hopper if Level High High | 3 |  |  |  |  | jwho 16/08/2026 Removed - Justin DM
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18015 | 2000-F18-PID-PR-10003 | F18-HP-513 Cleaner Scavenger Flotation Cell Tails Hopper Process Water Valve | F18HP513 Water Isolation | Detail 4 | FC | X | X | F18-SEQ-0007 | F18-SEQ-0008 | CT1 | LIC18211A >= A_HH | F18HP513 Level High High | 30 |  |  |  |  | X | X |  | Close off Mill Water addition to hopper if Level High High | 3 |  |  |  |  | jwho 16/08/2026 Removed - Justin DM
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18221 | 2000-F18-PID-PR-10003 | F18-PP-511 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Suction Valve | F18PP511 Suction | Detail 3 | FL | X | X | F18-SEQ-0005 | F18-SEQ-0006 | [12 empty] | B |  |  |  |  | Valve Stroke Test on 17/06/2026
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18222 | 2000-F18-PID-PR-10003 | F18-PP-511 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Drain Valve | F18PP511 Suction Drain | Detail 4 | FO | X | X | F18-SEQ-0006 | F18-SEQ-0005 | CT1 | F18PP511 RUNNING | Cleaner-Scav Recirc Pump 1 Rung | 3 |  |  |  |  | X | X |  |  | 3 |  |  |  |  | Valve Stroke Test on 17/06/2026
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18223 | 2000-F18-PID-PR-10003 | F18-PP-511 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Discharge Valve | F18PP511 Discharge | Detail 3 | FL | X | X | F18-SEQ-0005 | F18-SEQ-0006 | CT1 | F18PP512 RUNNING | Cleaner-Scav Pump 2 Rung. | 3 |  |  |  |  | X | X |  |  | 3 |  |  |  |  | Valve Stroke Test on 17/06/2026
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18224 | 2000-F18-PID-PR-10003 | F18-PP-512 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Suction Valve | F18PP512 Suction | Detail 3 | FL | X | X | F18-SEQ-0005 | F18-SEQ-0006 | [12 empty] | B
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18225 | 2000-F18-PID-PR-10003 | F18-PP-512 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Drain Valve | F18PP512 Suction Drain | Detail 4 | FO | X | X | F18-SEQ-0006 | F18-SEQ-0005 | CT1 | F18PP512 RUNNING | Cleaner-Scav Recirc Pump 2 Rung | 3 |  |  |  |  | X | X |  |  | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18226 | 2000-F18-PID-PR-10003 | F18-PP-512 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Discharge Valve | F18PP512 Discharge | Detail 3 | FL | X | X | F18-SEQ-0005 | F18-SEQ-0006 | CT1 | F18PP511 RUNNING | Cleaner-Scav Recirc Pump 1 Rung. | 3 |  |  |  |  | X | X |  |  | 3 |  |  |  |  | Valve Stroke Test on 17/06/2026
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18231 | 2000-F18-PID-PR-10003 | F18-PP-513 Cleaner Scavenger Flotation Cell Tails Pump 1 Suction Valve | F18PP513 Suction | Detail 3 | FL | X | X | F18-SEQ-0007 | F18-SEQ-0008 | [12 empty] | B |  |  |  |  | Travel time around 50 sec, MTM set to 90
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18232 | 2000-F18-PID-PR-10003 | F18-PP-513 Cleaner Scavenger Flotation Cell Tails Pump 1 Drain Valve | F18PP513 Suction Drain | Detail 4 | FO | X | X | F18-SEQ-0008 | F18-SEQ-0007 | CT1 | F18PP513 RUNNING | Cleaner-Scav Tails Pump 1 Rung | 3 |  |  |  |  | X | X |  |  | 3 |  |  |  |  | Travel Time is 7 sec, MTM ste to 15
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18233 | 2000-F18-PID-PR-10003 | F18-PP-513 Cleaner Scavenger Flotation Cell Tails Pump 1 Discharge Valve | F18PP513 Discharge | Detail 3 | FL | X | X | F18-SEQ-0007 | F18-SEQ-0008 | CT1 | F18PP514 RUNNING | Cleaner-Scav Tails Pump 2 Rung | 3 |  |  |  |  | X | X |  |  | 3 |  |  |  |  | Travel time 30 sec, MTM set to 60
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18234 | 2000-F18-PID-PR-10003 | F18-PP-514 Cleaner Scavenger Flotation Cell Tails Pump 2 Suction Valve | F18PP514 Suction | Detail 3 | FL | X | X | F18-SEQ-0007 | F18-SEQ-0008 | [12 empty] | B |  |  |  |  | Travel Time about 60 sec, MTM set to 90
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18235 | 2000-F18-PID-PR-10003 | F18-PP-514 Cleaner Scavenger Flotation Cell Tails Pump 2 Drain Valve | F18PP514 Suction Drain | Detail 4 | FO | X | X | F18-SEQ-0008 | F18-SEQ-0007 | CT1 | F18PP514 RUNNING | Cleaner-Scav Tails Pump 2 Rung | 3 |  |  |  |  | X | X |  |  | 3 |  |  |  |  | Travel time = 7 sec, MTM set to 15
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18236 | 2000-F18-PID-PR-10003 | F18-PP-514 Cleaner Scavenger Flotation Cell Tails Pump 2 Discharge Valve | F18PP514 Discharge | Detail 3 | FL | X | X | F18-SEQ-0007 | F18-SEQ-0008 | CT1 | F18PP513 RUNNING | Cleaner-Scav Tails Pump 1 Rung. | 3 |  |  |  |  | X | X |  |  | 3 |  |  |  |  | Time to ravel = 30 sec, MTM set to 60 sec
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18239 | 2000-F18-PID-PR-10003 | F18-SA-404 Cleaner-Scavenger Tails Sampler Discharge Valve | F18SA404 Discharge | Detail 7 | FC | X | X | F18-SEQ-0007 | F18-SEQ-0008 | [12 empty] | B
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18229 | 2000-F18-PID-PR-10003 | F18-SA-404 Cleaner-Scavenger Tails Sampler Flush Valve | F18SA404 Discharge Flush | Detail 7 | FC | X | X |  | F18-SEQ-0007 | OP1 | XV18239 CLOSED | F18SA404 Discharge Valve Closed. | 3 |  | X |  |  |  | X |  | Bypass for Operator discretion and low sample flow. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV18241 | 2000-F18-PID-PR-10003 | Cleaner Scavenger Tails Discharge to Flotation Tailings Thickener Valve | ClnrScav Tail to F17TH401 | Detail 3 | FL | X |  | Manually opened by Operator | Manually closed by Operator | CT1 | NI17030 >= A_HH | F17TH401 Torque High High | 3 |  |  |  |  | X | X |  |  | 3 |  |  |  |  | 34 sec to travel, MTM set to 45
[14 empty] | CT2 | SV17033 Not Energised AND F17PO408 Not Running | F17TH401 Not Running | 3 |  |  |  |  | X | X |  |  | 3
|  |  |  | XV18242 | 2000-F18-PID-PR-10003 | Cleaner Scavenger Tails Discharge to Scavenger Flotation Valve | Clnr Scv Tail to Scav C1 | Detail 3 | FL | X |  | Manually opened by Operator | Manually closed by Operator | [12 empty] | B |  |  |  |  | 36 to travel, MTM set to 45
|  |  |  | XV18243 | 2000-F18-PID-PR-10003 | Cleaner Scavenger Tails Discharge to Flotation Tailings Thickener Drain Valve | Clnr Scv Tail Drain 1 | Detail 4 | FO | X |  | Manually opened by Operator | Manually closed by Operator | CT1 | XV18241 OPEN | XV18241 OPEN | 3 |  |  |  |  | X | X |  | Cleaner Scav Tail to Flotation Tailings Thickener Valve Open. Bypass for dumping and flushing at operator discretion. | 3 |  |  |  |  | ~6 sec travel, MTM set to 15
|  |  |  | XV18244 | 2000-F18-PID-PR-10003 | Cleaner Scavenger Tails Discharge to Scavenger Flotation Drain Valve | Clnr Scv Tail Drain 2 | Detail 4 | FO | X |  | Manually opened by Operator | Manually closed by Operator | CT1 | XV18242 OPEN | XV18242 OPEN | 3 |  |  |  |  | X | X |  | Cleaner Scav Tail to Scavenger Flotation Cell 1 Valve Open. Bypass for dumping and flushing at operator discretion. | 3 |  |  |  |  | ~6 sec travel, MTM set to 15
|  |  |  | SV18500 | 2000-F24-PID-PR-10003 | F18-PP-407 Final Concentrate Pump 1 Gland Water Solenoid Valve | F18PP407 Gland Supply | Detail 11 | FO | X | X | F18-SEQ-0001 OR F18-PP-407 Start | F18-SEQ-0002 | OT1 | F18PP407 RUNNING | Final Concentrate Pump 1 Running | 0 |  |  |  | X |  | X |  | Shorter than Drive Interlock to maintain operation. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | SV18504 | 2000-F24-PID-PR-10003 | F18-PP-408 Final Concentrate Pump 2 Gland Water Solenoid Valve | F18PP408 Gland Supply | Detail 11 | FO | X | X | F18-SEQ-0001 OR F18-PP-408 Start | F18-SEQ-0002 | OT1 | F18PP408 RUNNING | Final Concentrate Pump 2 Running | 0 |  |  |  | X |  | X |  | Shorter than Drive Interlock to maintain operation. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | SV18508 | 2000-F24-PID-PR-10003 | F18-PP-501 Cleaner Flotation Cell Recirculation Pump 1 Gland Water Solenoid Valve | F18PP501 Gland Supply | Detail 11 | FO | X | X | F18-SEQ-0003 OR F18-PP-501 Start | F18-SEQ-0004 | OT1 | F18PP501 RUNNING | Cleaner Recirc Pump 1 Rung | 0 |  |  |  | X |  | X |  | Shorter than Drive Interlock to maintain operation. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | SV18512 | 2000-F24-PID-PR-10003 | F18-PP-502 Cleaner Flotation Cell Recirculation Pump 2 Gland Water Solenoid Valve | F18PP502 Gland Supply | Detail 11 | FO | X | X | F18-SEQ-0003 OR F18-PP-502 Start | F18-SEQ-0004 | OT1 | F18PP502 RUNNING | Cleaner Recirc Pump 2 Rung | 0 |  |  |  | X |  | X |  | Shorter than Drive Interlock to maintain operation. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | SV18524 | 2000-F24-PID-PR-10003 | F18-PP-511 Cleaner Scavenger Flotation Cell Recirculation Pump 1 Gland Water Solenoid Valve | F18PP511 Gland Supply | Detail 11 | FO | X | X | F18-SEQ-0005 OR F18-PP-511 Start | F18-SEQ-0006 | OT1 | F18PP511 RUNNING | Cleaner Scav Recirc Pump 1 Rung | 0 |  |  |  | X |  | X |  | Shorter than Drive Interlock to maintain operation. | 3 |  |  |  |  | Manual Stroke of the Valves Only
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | SV18528 | 2000-F24-PID-PR-10003 | F18-PP-512 Cleaner Scavenger Flotation Cell Recirculation Pump 2 Gland Water Solenoid Valve | F18PP512 Gland Supply | Detail 11 | FO | X | X | F18-SEQ-0005 OR F18-PP-512 Start | F18-SEQ-0006 | OT1 | F18PP512 RUNNING | Cleaner Scav Recirc Pump 2 Rung | 0 |  |  |  | X |  | X |  | Shorter than Drive Interlock to maintain operation. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | SV18532 | 2000-F24-PID-PR-10003 | F18-PP-513 Cleaner Scavenger Flotation Cell Tails Pump 1 Gland Water Solenoid Valve | F18PP513 Gland Supply | Detail 11 | FO | X | X | F18-SEQ-0007 OR F18-PP-513 Start | F18-SEQ-0008 | OT1 | F18PP513 RUNNING | Cleaner Scav Tails Pump 1 Rung | 0 |  |  |  | X |  | X |  | Shorter than Drive Interlock to maintain operation. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | SV18536 | 2000-F24-PID-PR-10003 | F18-PP-514 Cleaner Scavenger Flotation Cell Tails Pump 2 Gland Water Solenoid Valve | F18PP514 Gland Supply | Detail 11 | FO | X | X | F18-SEQ-0007 OR F18-PP-514 Start | F18-SEQ-0008 | OT1 | F18PP514 RUNNING | Cleaner Scav Tails Pump 2 Rung | 0 |  |  |  | X |  | X |  | Shorter than Drive Interlock to maintain operation. | 3
[12 empty] | Manually opened by Operator | Manually closed by Operator
|  |  |  | XV16122 | 2000-F16-PID-PR-10003 | F16-PP-515 Flotation Cells Drain Pump Suction Valve | F16PP515 Suction Valve | Detail 3 | FL | X |  | Manually opened by Operator | Manually closed by Operator | [12 empty] | 3 |  |  |  |  | Air Fail = FL Signal Fail - FL
|  |  |  | XV16123 | 2000-F16-PID-PR-10003 | F16-PP-515 Flotation Cells Drain Pump Suction Drain Valve | F16PP515 Suction Drain | Detail 3 | FL | X |  | Manually opened by Operator | Manually closed by Operator | [12 empty] | 3 |  |  |  |  | Air Fail = FL Signal Fail - FL
|  |  |  | XV16080 | 2000-F16-PID-PR-10003 | F16-BX-412 Flotation Discharge Box Drain Valve | F16BX412 Drain Valve | Detail 3 | FL | X | [15 empty] | 4 |  |  |  |  | 25/08/2026 jwho - Cannot test due to the discharge box filled with water
|  |  |  | XV18052 | 2000-F18-PID-PR-10002 | F18-CF-501 Cleaner Flotation Cell Drain Valve | F18CF501 Drain Valve | Detail X | FL | X | X | F18-SEQ-003 | F18-SEQ-004 | [12 empty] | 4 |  |  |  |  | PCR (number pending) - AP 30/08/2026
[12 empty] | F18-PP-501 And 502 Not Running > 300 seconds | [13 empty] | 4
|  |  |  | XV18252 | 2000-F18-PID-PR-10004 | F18-CF-511 Cleaner Scavenger Flotation Cell Drain Valve | F18CF511 Drain Valve | Detail X | FL | X | X | F18-SEQ-0006 | F18-SEQ-0005 | [12 empty] | 4 |  |  |  |  | PCR (number pending) - AP 30/08/2026
[12 empty] | F18-PP-511 And 512 Not Running > 300 seconds | [13 empty] | 4
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
85
Operator to get electrician to inspect unit for potential failure

## 8. PID Cont
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION (F16, F17, F18)
2000-F16-LST-PR-10001
PID Controllers
[10 empty] | Modes |  |  |  | Setpoint |  |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [8 empty] | Controlled/Manipulated Variable | [10 empty] | Comment | Rev | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Controller Description | Abbreviated Description (Faceplate) | Normal Operating Mode | Manual | Auto | Cascade | Process Value Tag | Min | Max | Unit | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Range Min | Range Max | Lower Limit | Upper Limit | Unit | Destination Description | Destination (Output) Tag | Direct / Reverse Acting | P | I | D |  |  | OK | Date | OK | Date | Comments
|  |  |  | FT16011 | FIC16011 | 2000-F16-PID-PR-10001 | F16-CF-411 Rougher Flotation Cell 1 Low Pressure Air Flow Transmitter | F16CF411 Blower Air Ctrl | Auto | X | X |  | FT16011 | 50 | 102 | m3/min | 0 | 97 | m3/min | [14 empty] | 40 | 5 | 80 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-411 Rougher Flotation Cell 1 Low Pressure Air Flow Control Valve | FCV16011 | Reverse |  |  |  | Alarm setpoints based on the design cell superficial gas velocity: Superficial Gas Velocity, Design (Jg) = 1.5 cm/s Air Flow Rate, Design = 71.9 m3/h Superficial Gas Velocity, Max (Jg)= 2 cm/s Air Flow Rate, Max = 95.7 m3/h (Design as per 2000-ME001.4-F13-50002). Flowrate variable on varying temperature and pressure. Design and Max flowrates calculated on: T = 100C P = 100kPa(g) Sources: 2000-ME001.4-F16-50001 & 2000-ME001.4-F13-50002. Alarm setpoints to be confirmed during commissioning. Instrument to be ranged greater than 2000-ME001.4-F16-50002 due to additional blower capacity. | 1 |  |  |  |  | MOC610
|  |  |  | LIT16013 | LIC16013 | 2000-F16-PID-PR-10001 | F16-CF-411 Rougher Flotation Cell 1 Level Transmitter | F16CF411 Level Ctrl | Auto | X | X |  | LIT16013 | 100 | 400 | mm | 0 300 | 6000 1150 | mm | [14 empty] | 50 | 5 | 450 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-412 Rougher Flotation Cell 2 Level Control Valve A | LCV16013A | Reverse |  |  |  | Vendor specified operating philosophy is to maintain Valve B at a static position and Valve A to control the level, reducing variability in PID loop. For fine control, programme actuators such that Valve A moves its full stroke (range) before adjusting Valve B position: MV 0-50% = Valve A 0-100% MV 50-100% = Valve B 0-100% Functional Description: 2000-ME001.4-M02-50001 IO List: 2000-ME001.4-F16-50001. Instrument Range: 0 - 6000 mm. Instrument range to be reversed such that 0mm means no froth depth (20mA) and 500mm is the maximum froth depth (0mA). PID loop control to be confirmed during commissioning. Alarm setpoints to be confirmed during commissioning. | 3 |  |  |  |  | MOC-600 - Change of Level Tx Trange
[41 empty] | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-412 Rougher Flotation Cell 2 Level Control Valve B | LCV16013B | Reverse |  |  |  | As per above comments. | 3
|  |  |  | FT16051 | FIC16051 | 2000-F16-PID-PR-10002 | F16-CF-412 Rougher Flotation Cell 2 Low Pressure Air Flow Transmitter | F16CF412 Blower Air Ctrl | Auto | X | X |  | FT16051 | 50 | 102 | m3/min | 0 | 97 | m3/min | [14 empty] | 40 | 5 | 80 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-412 Rougher Flotation Cell 2 Low Pressure Air Flow Control Valve | FCV16051 | Reverse |  |  |  | Alarm setpoints based on the design cell superficial gas velocity: Superficial Gas Velocity, Design (Jg) = 1.5 cm/s Air Flow Rate, Design = 71.9 m3/h Superficial Gas Velocity, Max (Jg)= 2 cm/s Air Flow Rate, Max = 95.7 m3/h (Design as per 2000-ME001.4-F13-50002). Flowrate variable on varying temperature and pressure. Design and Max flowrates calculated on: T = 100C P = 100kPa(g) Sources: 2000-ME001.4-F16-50001 & 2000-ME001.4-F13-50002. Alarm setpoints to be confirmed during commissioning. Instrument to be ranged greater than 2000-ME001.4-F16-50002 due to additional blower capacity. | 0 |  |  |  |  | MOC610
|  |  |  | LIT16053 | LIC16053 | 2000-F16-PID-PR-10002 | F16-CF-412 Rougher Flotation Cell 2 Level Transmitter | F16CF412 Level Ctrl | Auto | X | X |  | LIT16053 | 100 | 400 | mm | 0 300 | 6000 1160 | mm | [14 empty] | 50 | 5 | 450 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-413 Rougher Flotation Cell 3 Level Control Valve A | LCV16053A | Reverse |  |  |  | Vendor specified operating philosophy is to maintain Valve B at a static position and Valve A to control the level, reducing variability in PID loop. For fine control, programme actuators such that Valve A moves its full stroke (range) before adjusting Valve B position: MV 0-50% = Valve A 0-100% MV 50-100% = Valve B 0-100% Functional Description: 2000-ME001.4-M02-50001 IO List: 2000-ME001.4-F16-50001. Instrument Range: 0 - 6000 mm. Instrument range to be reversed such that 0mm means no froth depth (20mA) and 500mm is the maximum froth depth (0mA). PID loop control to be confirmed during commissioning. Alarm setpoints to be confirmed during commissioning. | 3 |  |  |  |  | MOC-600 - Change of Level Tx Trange
[41 empty] | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-413 Rougher Flotation Cell 3 Level Control Valve B | LCV16053B | Reverse |  |  |  | As per above comments. | 3
|  |  |  | FT16061 | FIC16061 | 2000-F16-PID-PR-10002 | F16-CF-413 Rougher Flotation Cell 3 Low Pressure Air Flow Transmitter | F16CF413 Blower Air Ctrl | Auto | X | X |  | FT16061 | 50 | 102 | m3/min | 0 | 97 | m3/min | [14 empty] | 40 | 5 | 80 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-413 Rougher Flotation Cell 3 Low Pressure Air Flow Control Valve | FCV16061 | Reverse |  |  |  | Alarm setpoints based on the design cell superficial gas velocity: Superficial Gas Velocity, Design (Jg) = 1.5 cm/s Air Flow Rate, Design = 71.9 m3/h Superficial Gas Velocity, Max (Jg)= 2 cm/s Air Flow Rate, Max = 95.7 m3/h (Design as per 2000-ME001.4-F13-50002). Flowrate variable on varying temperature and pressure. Design and Max flowrates calculated on: T = 100C P = 100kPa(g) Sources: 2000-ME001.4-F16-50001 & 2000-ME001.4-F13-50002. Alarm setpoints to be confirmed during commissioning. Instrument to be ranged greater than 2000-ME001.4-F16-50002 due to additional blower capacity. | 0 |  |  |  |  | MOC610
|  |  |  | LIT16063 | LIC16063 | 2000-F16-PID-PR-10002 | F16-CF-413 Rougher Flotation Cell 3 Level Indicating Transmitter | F16CF413 Level Ctrl | Auto | X | X |  | LIT16063 | 100 | 400 | mm | 0 200 300 | 6000 1200 | mm | [14 empty] | 50 | 5 | 450 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-414 Scavenger Flotation Cell 1 Level Control Valve A | LCV16063A | Reverse |  |  |  | Vendor specified operating philosophy is to maintain Valve B at a static position and Valve A to control the level, reducing variability in PID loop. For fine control, programme actuators such that Valve A moves its full stroke (range) before adjusting Valve B position: MV 0-50% = Valve A 0-100% MV 50-100% = Valve B 0-100% Functional Description: 2000-ME001.4-M02-50001 IO List: 2000-ME001.4-F16-50001. Instrument Range: 0 - 6000 mm. Instrument range to be reversed such that 0mm means no froth depth (20mA) and 500mm is the maximum froth depth (0mA). PID loop control to be confirmed during commissioning. Alarm setpoints to be confirmed during commissioning. | 3 |  |  |  |  | MOC-600 - Change of Level Tx Trange
[41 empty] | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-414 Scavenger Flotation Cell 1 Level Control Valve B | LCV16063B | Reverse |  |  |  | As per above comments. | 3
|  |  |  | FT16081 | FIC16081 | 2000-F16-PID-PR-10003 | F16-CF-414 Scavenger Flotation Cell 1 Low Pressure Air Flow Transmitter | F16CF414 Blower Air Ctrl | Auto | X | X |  | FT16081 | 50 | 102 | m3/min | m3/min | 97 | m3/min | [14 empty] | 40 | 5 | 80 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-414 Scavenger Flotation Cell 1 Low Pressure Air Flow Control Valve | FCV16081 | Reverse |  |  |  | Alarm setpoints based on the design cell superficial gas velocity: Superficial Gas Velocity, Design (Jg) = 1.5 cm/s Air Flow Rate, Design = 71.9 m3/h Superficial Gas Velocity, Max (Jg)= 2 cm/s Air Flow Rate, Max = 95.7 m3/h (Design as per 2000-ME001.4-F13-50002). Flowrate variable on varying temperature and pressure. Design and Max flowrates calculated on: T = 100C P = 100kPa(g) Sources: 2000-ME001.4-F16-50001 & 2000-ME001.4-F13-50002. Alarm setpoints to be confirmed during commissioning. Instrument to be ranged greater than 2000-ME001.4-F16-50002 due to additional blower capacity. | 0 |  |  |  |  | MOC610
|  |  |  | LIT16083 | LIC16083 | 2000-F16-PID-PR-10003 | F16-CF-414 Scavenger Flotation Cell 1 Level Indicating Transmitter | F16CF414 Level Ctrl | Auto | X | X |  | LIT16083 | 100 | 400 | mm | 0 200 | 6000 1160 | mm | [14 empty] | 50 | 5 | 450 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-415 Scavenger Flotation Cell 2 Level Control Valve A | LCV16083A | Reverse |  |  |  | Vendor specified operating philosophy is to maintain Valve B at a static position and Valve A to control the level, reducing variability in PID loop. For fine control, programme actuators such that Valve A moves its full stroke (range) before adjusting Valve B position: MV 0-50% = Valve A 0-100% MV 50-100% = Valve B 0-100% Functional Description: 2000-ME001.4-M02-50001 IO List: 2000-ME001.4-F16-50001. Instrument Range: 0 - 6000 mm. Instrument range to be reversed such that 0mm means no froth depth (20mA) and 500mm is the maximum froth depth (0mA). PID loop control to be confirmed during commissioning. Alarm setpoints to be confirmed during commissioning. | 3 |  |  |  |  | MOC-600 - Change of Level Tx Trange
[41 empty] | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-415 Scavenger Flotation Cell 2 Level Control Valve B | LCV16083B | Reverse |  |  |  | As per above comments. | 3
|  |  |  | FT16091 | FIC16091 | 2000-F16-PID-PR-10003 | F16-CF-415 Scavenger Flotation Cell 2 Low Pressure Air Flow Transmitter | F16CF415 Blower Air Ctrl | Auto | X | X |  | FT16091 | 50 | 102 | m3/min | 0 | 97 | m3/min | [14 empty] | 40 | 5 | 80 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-415 Scavenger Flotation Cell 2 Low Pressure Air Flow Control Valve | FCV16091 | Reverse |  |  |  | Alarm setpoints based on the design cell superficial gas velocity: Superficial Gas Velocity, Design (Jg) = 1.5 cm/s Air Flow Rate, Design = 71.9 m3/h Superficial Gas Velocity, Max (Jg)= 2 cm/s Air Flow Rate, Max = 95.7 m3/h (Design as per 2000-ME001.4-F13-50002). Flowrate variable on varying temperature and pressure. Design and Max flowrates calculated on: T = 100C P = 100kPa(g) Sources: 2000-ME001.4-F16-50001 & 2000-ME001.4-F13-50002. Alarm setpoints to be confirmed during commissioning. Instrument to be ranged greater than 2000-ME001.4-F16-50002 due to additional blower capacity. | 0 |  |  |  |  | MOC610
|  |  |  | LIT16093 | LIC16093 | 2000-F16-PID-PR-10003 | F16-CF-415 Scavenger Flotation Cell 2 Level Indicating Transmitter | F16CF415 Level Ctrl | Auto | X | X |  | LIT16093 | 100 | 400 | mm | 0 200 | 6000 1215 | mm | [14 empty] | 50 | 5 | 450 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-416 Scavenger Flotation Cell 3 Level Control Valve A | LCV16093A | Reverse |  |  |  | Vendor specified operating philosophy is to maintain Valve B at a static position and Valve A to control the level, reducing variability in PID loop. For fine control, programme actuators such that Valve A moves its full stroke (range) before adjusting Valve B position: MV 0-50% = Valve A 0-100% MV 50-100% = Valve B 0-100% Functional Description: 2000-ME001.4-M02-50001 IO List: 2000-ME001.4-F16-50001. Instrument Range: 0 - 6000 mm. Instrument range to be reversed such that 0mm means no froth depth (20mA) and 500mm is the maximum froth depth (0mA). PID loop control to be confirmed during commissioning. Alarm setpoints to be confirmed during commissioning. | 3 |  |  |  |  | MOC-600 - Change of Level Tx Trange
[41 empty] | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-416 Scavenger Flotation Cell 3 Level Control Valve B | LCV16093B | Reverse |  |  |  | As per above comments. | 3
|  |  |  | FT16101 | FIC16101 | 2000-F16-PID-PR-10003 | F16-CF-416 Scavenger Flotation Cell 3 Low Pressure Air Flow Transmitter | F16CF416 Blower Air Ctrl | Auto | X | X |  | FT16101 | 50 | 102 | m3/min | 0 | 97 | m3/min | [14 empty] | 40 | 5 | 80 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-416 Scavenger Flotation Cell 3 Low Pressure Air Flow Control Valve | FCV16101 | Reverse |  |  |  | Alarm setpoints based on the design cell superficial gas velocity: Superficial Gas Velocity, Design (Jg) = 1.5 cm/s Air Flow Rate, Design = 71.9 m3/h Superficial Gas Velocity, Max (Jg)= 2 cm/s Air Flow Rate, Max = 95.7 m3/h (Design as per 2000-ME001.4-F13-50002). Flowrate variable on varying temperature and pressure. Design and Max flowrates calculated on: T = 100C P = 100kPa(g) Sources: 2000-ME001.4-F16-50001 & 2000-ME001.4-F13-50002. Alarm setpoints to be confirmed during commissioning. Instrument to be ranged greater than 2000-ME001.4-F16-50002 due to additional blower capacity. | 0 |  |  |  |  | MOC610
|  |  |  | LIT16103 | LIC16103 | 2000-F16-PID-PR-10003 | F16-CF-416 Scavenger Flotation Cell 3 Level Indicating Transmitter | F16CF416 Level Ctrl | Auto | X | X |  | LIT16103 | 100 | 400 | mm | 0 200 | 6000 1155 | mm | [14 empty] | 50 | 5 | 450 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-417 Scavenger Flotation Cell 4 Level Control Valve A | LCV16103A | Reverse |  |  |  | Vendor specified operating philosophy is to maintain Valve B at a static position and Valve A to control the level, reducing variability in PID loop. For fine control, programme actuators such that Valve A moves its full stroke (range) before adjusting Valve B position: MV 0-50% = Valve A 0-100% MV 50-100% = Valve B 0-100% Functional Description: 2000-ME001.4-M02-50001 IO List: 2000-ME001.4-F16-50001. Instrument Range: 0 - 6000 mm. Instrument range to be reversed such that 0mm means no froth depth (20mA) and 500mm is the maximum froth depth (0mA). PID loop control to be confirmed during commissioning. Alarm setpoints to be confirmed during commissioning. | 3 |  |  |  |  | MOC-600 - Change of Level Tx Trange
[41 empty] | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-417 Scavenger Flotation Cell 4 Level Control Valve B | LCV16103B | Reverse |  |  |  | As per above comments. | 3
|  |  |  | FT16111 | FIC16111 | 2000-F16-PID-PR-10003 | F16-CF-417 Scavenger Flotation Cell 4 Low Pressure Air Flow Transmitter | F16CF417 Blower Air Ctrl | Auto | X | X |  | FT16111 | 50 | 102 | m3/min | 0 | 97 | m3/min | [14 empty] | 40 | 5 | 80 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-CF-417 Scavenger Flotation Cell 4 Low Pressure Air Flow Control Valve | FCV16111 | Reverse |  |  |  | Alarm setpoints based on the design cell superficial gas velocity: Superficial Gas Velocity, Design (Jg) = 1.5 cm/s Air Flow Rate, Design = 71.9 m3/h Superficial Gas Velocity, Max (Jg)= 2 cm/s Air Flow Rate, Max = 95.7 m3/h (Design as per 2000-ME001.4-F13-50002). Flowrate variable on varying temperature and pressure. Design and Max flowrates calculated on: T = 100C P = 100kPa(g) Sources: 2000-ME001.4-F16-50001 & 2000-ME001.4-F13-50002. Alarm setpoints to be confirmed during commissioning. Instrument to be ranged greater than 2000-ME001.4-F16-50002 due to additional blower capacity. | 0 |  |  |  |  | MOC610 range change
|  |  |  | LIT16113 | LIC16113 | 2000-F16-PID-PR-10003 | F16-CF-417 Scavenger Flotation Cell 4 Level Indicating Transmitter | F16CF417 Level Ctrl | Auto | X | X |  | LIT16113 | 100 | 400 | mm | 0 200 | 6000 1160 | mm | [14 empty] | 50 | 5 | 450 | 5 |  |  |  | 0 | 100 | 0 | 100 | % Open (valve) | F16-BX-412 Flotation Discharge Box Level Control Valve A | LCV16113A | Reverse |  |  |  | Vendor specified operating philosophy is to maintain Valve B at a static position and Valve A to control the level, reducing variability in PID loop. For fine control, programme actuators such that Valve A moves its full stroke (range) before adjusting Valve B position: MV 0-50% = Valve A 0-100% MV 50-100% = Valve B 0-100% Functional Description: 2000-ME001.4-M02-50001 IO List: 2000-ME001.4-F16-50001. Instrument Range: 0 - 6000 mm. Instrument range to be reversed such that 0mm means no froth depth (20mA) and 500mm is the maximum froth depth (0mA). PID loop control to be confirmed during commissioning. Alarm setpoints to be confirmed during commissioning. | 3 |  |  |  |  | MOC-600 - Change of Level Tx Trange
[41 empty] | 0 | 100 | 0 | 100 | % Open (valve) | F16-BX-412 Flotation Discharge Box Level Control Valve B | LCV16113B | Reverse |  |  |  | As per above comments. | 3
|  |  |  | LT16161 | LIC16161 | 2000-F16-PID-PR-10005 | F16-HP-452 Sample Return Hopper 2 Level Indicating Transmitter | F16HP452 Level Ctrl | Auto | X | X |  | LT16161 | 25 | 80 | % | 0 | 100 | % | [12 empty] | 20 | 5 | 30 | 5 | 85 | 5 |  |  |  | 0 | 100 | 40 | 100 | % Speed VSD | Sample Return Pump 2 VSD | F16-PP-639 VSD | Direct |  |  |  | A_LL = Trip F16-PP-639 Setpoint ranges and alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | LT16151 | LIC16151 | 2000-F16-PID-PR-10005 | F16-HP-451 Sample Return Hopper 1 Level Indicating Transmitter | F16HP451 Level Ctrl | Auto | X | X |  | LT16151 | 25 | 80 | % | 0 | 100 | % |  |  |  | 40 | 5 | [7 empty] | 20 | 5 | 30 | 5 | 85 | 5 |  |  |  | 0 | 100 | 40 | 100 | % Speed VSD | Sample Return Pump 1 VSD | F16-PP-638 VSD | Direct |  |  |  | A_LL = Trip F16-PP-638 Setpoint ranges and alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | PT16199 | PIC16199 | 2000-F16-PID-PR-10006 | F16-BW-401 Flotation Blower 1 Outlet Pressure Indicating Transmitter | F16BW401 Pressure Ctrl | Auto | X | X |  | PT16199 | 50 | 115 | kPa(g) | -100 | 300 | kPa(g) | [16 empty] | 120 | 5 | 125 | 5 |  | 0 | 100 | 40 | 100 | % Speed VSD | Flotation Blower 1 VSD | F16-BW-401 | Reverse |  |  |  | Source: Vendor document 2000-ME001.4-M02-50001. Nominal pressure: 8,688m3/h @ 102.5 kPa per blower (4 blowers). Maximum pressure: 8,688m3/h @ 119.7 kPa per blower (3 blowers). Design intent - three duty blowers, one standby. A_Hi = Alarm A_HH = Trip F16-BW-401 Setpoing range to be confirmed during commissioning. Alarm setpoints to be confirmed during commissioning. | 1 |  |  |  |  | MSH: PIC functionaity to be checked
|  |  |  | PT16209 | PIC16209 | 2000-F16-PID-PR-10006 | F16-BW-402 Flotation Blower 2 Outlet Pressure Indicating Transmitter | F16BW402 Pressure Ctrl | Auto | X | X |  | PT16209 | 50 | 115 | kPa(g) | -100 | 300 | kPa(g) | [16 empty] | 120 | 5 | 125 | 5 |  | 0 | 100 | 40 | 100 | % Speed VSD | Flotation Blower 2 VSD | F16-BW-402 | Reverse |  |  |  | Source: Vendor document 2000-ME001.4-M02-50001. Nominal pressure: 8,688m3/h @ 102.5 kPa per blower (4 blowers). Maximum pressure: 8,688m3/h @ 119.7 kPa per blower (3 blowers). Design intent - three duty blowers, one standby. A_Hi = Alarm A_HH = Trip F16-BW-402 Setpoing range to be confirmed during commissioning. Alarm setpoints to be confirmed during commissioning. | 1 |  |  |  |  | MSH: PIC functionaity to be checked
|  |  |  | PT16219 | PIC16219 | 2000-F16-PID-PR-10006 | F16-BW-403 Flotation Blower 3 Outlet Pressure Indicating Transmitter | F16BW403 Pressure Ctrl | Auto | X | X |  | PT16219 | 50 | 115 | kPa(g) | -100 | 300 | kPa(g) | [16 empty] | 120 | 5 | 125 | 5 |  | 0 | 100 | 40 | 100 | % Speed VSD | Flotation Blower 3 VSD | F16-BW-403 | Reverse |  |  |  | Source: Vendor document 2000-ME001.4-M02-50001. Nominal pressure: 8,688m3/h @ 102.5 kPa per blower (4 blowers). Maximum pressure: 8,688m3/h @ 119.7 kPa per blower (3 blowers). Design intent - three duty blowers, one standby. A_Hi = Alarm A_HH = Trip F16-BW-403 Setpoing range to be confirmed during commissioning. Alarm setpoints to be confirmed during commissioning. | 1 |  |  |  |  | MSH: PIC functionaity to be checked
|  |  |  | PT16229 | PIC16229 | 2000-F16-PID-PR-10006 | F16-BW-404 Flotation Blower 4 Outlet Pressure Indicating Transmitter | F16BW404 Pressure Ctrl | Auto | X | X |  | PT16229 | 50 | 115 | kPa(g) | -100 | 300 | kPa(g) | [16 empty] | 120 | 5 | 125 | 5 |  | 0 | 100 | 40 | 100 | % Speed VSD | Flotation Blower 4 VSD | F16-BW-404 | Reverse |  |  |  | Source: Vendor document 2000-ME001.4-M02-50001. Nominal pressure: 8,688m3/h @ 102.5 kPa per blower (4 blowers). Maximum pressure: 8,688m3/h @ 119.7 kPa per blower (3 blowers). Design intent - three duty blowers, one standby. A_Hi = Alarm A_HH = Trip F16-BW-404 Setpoint range to be confirmed during commissioning. Alarm setpoints to be confirmed during commissioning. | 1 |  |  |  |  | MSH: PIC functionaity to be checked
|  |  |  | FIT17001 | FIC17001 | 2000-F17-PID-PR-10001 | F17-XM-413 Pre-Leach Thickener Flocculant In-Line Mixer Process Water Flow Indicating Transmitter | F17TH401 Flocc Diln Ctrl | Cascade | X | X | X | FIT17001 | 0 | 500 | m3/hr | 0 | 500 | m3/hr | [20 empty] | Mask A_Lo when F72PP691 AND 692 are Not Running | 0 | 100 | 0 | 100 | % Open (valve) | F17-XM-413 Pre-Leach Thickener Flocculant In-Line Mixer Process Water Flow Control Valve | FCV17001 | Reverse |  |  |  | 28.35 Mtpa Case 4: 45.5 m3/h Nominal. In CASCADE: F17CALC0001 provides the SP for FIC17001. Alarm setpoints to be confirmed during commissioning. Set deviation alarm of 25m3/h (calculated as ~5% of nom SV). | 3 |  |  |  |  | Dynamic Alarm HI/LO setpoint details. DCS Hi = 132m3/h; DCS Lo = 108 m3/h
|  |  |  | PIT17011 | PIC17011 | 2000-F17-PID-PR-10001 | F17-TH-401 Flotation Tailings Thickener Bed Mass Pressure Indicating Transmitter | F17TH401 Bed Ctrl | Auto | X | X |  | PIT17011 | 0 | 200 | kPa(g) | 0 | 200 | kPa(g) | [14 empty] | 94.01 | 5 | 95.91 | 5 | 97.31 | 5 |  | 0 | 6000 | 0 | 4000 | m3/hr | Flotation Tailings Thickener Underflow Pumps Discharge Flow Indicating Controller | FIC17121 | Direct |  |  |  | Analogue input over comms. Cascade to provide SP for flow controller FIC17121. Range based on 20/18 AH pump curve. Remove hysteresis else reduce to 0.25% | 3 |  |  |  |  | Loop Check Only
|  |  |  | LT17004 | LIC17004 | 2000-F17-PID-PR-10001 | F16-HP-456 Final Tails Sample Hopper Level Indicating Transmitter | F16HP456 Level Ctrl | Auto | X | X |  | LT17004 | 20 | 100 | % | 0 | 100 | % | [12 empty] | 20 | 5 | 30 | 5 | 80 | 5 |  |  |  | 0 | 100 | 40 | 100 | % Speed VSD | F16-PP-634 Final Tails Sample Pump | F16-PP-634 VSD | Direct |  |  |  | Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | F17CALC0007 | DNIC17121 | 2000-F17-PID-PR-10002 | F17-PP-455/456 Discharge Density Indicating Transmitter | F17PP455/6 Density Ctrl | Auto | X | X |  | F17CALC0007 | 0 | 100 | %w/w | 0 | 100 | %w/w | [6 empty] | 58 | 5 |  |  |  |  | 40 | 5 | 42 | 5 | 60 | 5 | 62 | 5 | F17-PP-455/456 NOT RUNNING Alarm enabled delay of 10 seconds during F17PP455 OR 456 start-up. | 0 | 6000 | 0 | 4000 | m3/hr | FIC17121 Flotation Tailings Thickener Underflow Pump 1/2 Flow Indicator Controller | FIC17121 | Direct |  |  |  | Alarm setpoints to be confirmed during commissioning. | 3
|  |  |  | FIT17121 | FIC17121 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps Discharge Flow Indicating Transmitter | F17PP455/6 Flow Ctrl | Cascade | X | X | X | FIT17121 | 0 | 4000 | m3/hr | 0 | 6000 | m3/hr | [12 empty] | 200 | 5 | [6 empty] | F17-PP-455/456 NOT RUNNING Alarm enabled delay of 10 seconds during F17PP455 OR 456 start-up. | 0 | 100 | 40 | 100 | % Speed VSD | F17-PP-455/456 Flotation Tailings Thickener Underflow Pump 1/2 | Duty F17-PP-455/456 VSD | Reverse |  |  |  | Controller normally slave controller for DIC17121 or PIC17011 (as per HS17011 ). Set deviation alarm of 150m3/h (calculated as ~5% of nom SV). Alarm setpoints to be confirmed during commissioning. | 3 |  |  |  |  | Loop Check Only
|  |  |  | FIT17127 | FIC17127 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps CIL2 Feed Valve Flow Indicating Transmitter | F17TH401 UF to CIL2 | Auto | X | X |  | FIT17127 | 0 | 3000 | m3/hr | 0 | 5000 | m3/hr | [12 empty] | 400 | 5 | 700 | 5 |  |  |  |  | F17-PP-455/456 NOT RUNNING | 0 | 100 | 0 | 100 | % Open (valve) | Flotation Tailings Thickener Underflow Pumps CIL2 Feed Flow Control Valve | FCV17127 | Reverse |  |  |  | Alarm setpoints to be confirmed during commissioning. Nominal (Case 1): 1924 m3/h for CIL2 & 3 feed. | B |  |  |  |  | Loop Check Only
|  |  |  | FIT17128 | FIC17128 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps CIL3 Feed Valve Flow Indicating Transmitter | F17TH401 UF to CIL3 | Auto | X | X |  | FIT17128 | 0 | 3000 | m3/hr | 0 | 5000 | m3/hr | [12 empty] | 400 | 5 | 700 | 5 |  |  |  |  | F17-PP-455/456 NOT RUNNING | 0 | 100 | 0 | 100 | % Open (valve) | Flotation Tailings Thickener Underflow Pumps CIL3 Feed Flow Control Valve | FCV17128 | Reverse |  |  |  | Alarm setpoints to be confirmed during commissioning. Nominal (Case 1): 1924 m3/h for CIL2 & 3 feed. | B |  |  |  |  | Loop Check Only
|  |  |  | LT18001 | LIC18001A | 2000-F18-PID-PR-10001 | F18-HP-414 Final Concentrate Hopper Level Indicating Transmitter | F18HP414 Water Ctrl | Auto | X | X |  | LT18001 | 30 | 90 | % | 0 | 100 | % |  |  |  | 50 | 5 | [7 empty] | 20 | 5 | 30 | 5 | 80 | 5 | 90 | 5 |  | 0 | 100 | 0 | 100 | % Open (valve) | F18-HP-414 Final Concentrate Hopper Process Water Feed Level Control Valve | LCV18001 | Reverse |  |  |  | Dual hopper control. See 2000-F00-REP-PR-10001 for further information. Operator to ensure Level Controller A setpoint is less than Level Controller B setpoint. Alarm setpoints to be confirmed during commissioning. | 3
|  |  |  | LT18001 | LIC18001B | 2000-F18-PID-PR-10001 | F18-HP-414 Final Concentrate Hopper Level Indicating Transmitter | F18HP414 Pump Ctrl | Auto | X | X |  | LT18001 | 30 | 90 | % | 0 | 100 | % | [21 empty] | 0 | 100 | 40 | 100 | % Speed VSD | F18-PP-407/408 Duty Final Concentrate Pump 1/2 | Duty F18PP407/408 VSD via HS18027 | Direct |  |  |  | Dual hopper control. See 2000-F00-REP-PR-10001 for further information. Operator to ensure Level Controller A setpoint is less than Level Controller B setpoint. | 3
|  |  |  | LT18011 | LIC18011A | 2000-F18-PID-PR-10001 | F18-HP-501 Cleaner Flotation Cell Feed Hopper Level Indicating Transmitter | F18HP501 Water Ctrl | Auto | X | X |  | LT18011 | 30 | 90 | % | 0 | 100 | % |  |  |  | 60 | 5 | [7 empty] | 20 | 5 | 30 | 5 | 80 | 5 | 90 | 5 |  | 0 | 100 | 0 | 100 | % Open (valve) | F18-HP-501 Cleaner Flotation Cell Feed Hopper Process Water Feed Level Control Valve | LCV18011A | Reverse |  |  |  | Dual hopper control. See 2000-F00-REP-PR-10001 for further information. Operator to ensure Level Controller A setpoint is less than Level Controller B setpoint. Alarm setpoints to be confirmed during commissioning. | 3
|  |  |  | LT18011 | LIC18011B | 2000-F18-PID-PR-10001 | F18-HP-501 Cleaner Flotation Cell Feed Hopper Level Indicating Transmitter | F18CF501 Recycle Ctrl | Auto | X | X |  | LT18011 | 30 | 90 | % | 0 | 100 | % | [21 empty] | 0 | 100 | 0 | 100 | % Open (valve) | F18-BX-501 Cleaner Flotation ERM Recycle Level Control Valve | LCV18011B | Reverse |  |  |  | Dual hopper control. See 2000-F00-REP-PR-10001 for further information. Operator to ensure Level Controller A setpoint is less than Level Controller B setpoint. | 3
|  |  |  | FIT18037 | FIC18037 | 2000-F18-PID-PR-10001 | F18-PP-501/502 Cleaner Flotation Cell Recirculation Pumps Discharge Flow Indicating Transmitter | F18PP501/2 Ctrl | Auto | X | X |  | FIT18037 | 0 | 2500 | m3/hr | 0 | 2500 | m3/hr | [12 empty] | 400 | 5 | 1950 | 5 | 2050 | 5 |  |  | DUTY F18PP501/502 NOT RUNNING Alarm enabled delay of 60 seconds on F18PP501 OR 502 start-up. | 0 | 100 | 40 | 100 | % Speed VSD | Cleaner Flotation Cell Recirculation Pump 1/2 | Duty F18PP501/502 VSD via Handswitch HS18037 | Reverse |  |  |  | Nominal and maximum 1993 m3/hr. Alarm setpoints to be confirmed during commissioning. | 3
|  |  |  | FIT18057 | FIC18057 | 2000-F18-PID-PR-10002 | F18-CF-501 Cleaner Flotation Cell Wash Water Flow Indicating Transmitter | F18CF501 Conc Water Ctrl | Cascade | X | X | X | FIT18057 | 0 | 650 | m3/hr | 0 | 650 | m3/hr | [12 empty] | 5 | 5 | 106 | 5 | 350 | 5 |  |  | A_LL: DUTY F18PP501/502 NOT RUNNING A_Lo: DUTY F18PP501/502 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP501/502 Start-Up. | 0 | 100 | 0 | 100 | % Open (valve) | F18-CF-501 Cleaner Flotation Cell Wash Water Flow Flow Control Valve | FCV18057 | Reverse |  |  |  | In CASCADE Mode, the setpoint for FIC18057 is provided by F18CALC0001. Alarms to be confirmed during commissioning. Source: 2000-ME073-M01-10002. | 3 |  |  |  |  | MSH: Mode switching to be verified to be bumpless?
|  |  |  | FIT18056 | FIC18056 | 2000-F18-PID-PR-10002 | F18-CF-501 Cleaner Flotation Cell Air Flow Indicating Transmitter | F18CF501 Air Ctrl | Auto | X | X |  | FIT18056 | 800 | 1600 | Sm3/hr | 0 | 2000 | Sm3/hr | [12 empty] | 200 | 5 | [6 empty] | A_LL: DUTY F18PP501/502 NOT RUNNING Alarm enabled delay of 60 seconds during F18PP501/502 Start-Up. | 0 | 100 | 0 | 100 | % Open (valve) | F18-CF-501 Cleaner Flotation Cell Air Flow Control Valve | FCV18056 | Reverse |  |  |  | Alarm setpoints to be confirmed during commissioning. Source: 2000-ME073-M01-10002. | 3
|  |  |  | LNI18051 | LIC18051 | 2000-F18-PID-PR-10002 | F18-CF-501 Cleaner Flotation Cell Tank Slurry Level Indicating Transmitter | F18CF501 Froth | Auto | X | X |  | LNI18051 | 0 | 680 | mm | 0 | 1900 | mm | [6 empty] | 1000 | 5 | [10 empty] | 700 | 5 |  | 0 | 100 | 0 | 100 | % Open (valve) | F18-CF-501 Cleaner Flotation Cell Tank Slurry Level Control Valve | LCV18051 | Reverse |  |  |  | Please refer to 2000-ME073-M01-10001 Page 8 and 11. Calculation for dual level transmitter setup. Bottom-range is zero for manual shutdown sequence. Alarm setpoints to be confirmed during commissioning. Source: 2000-ME073-M01-10002. | 3 |  |  |  |  | drive LCV using the PID loop
|  |  |  | LT18201 | LIC18201A | 2000-F18-PID-PR-10003 | F18-HP-511 Cleaner Scavenger Flotation Cell Feed Hopper Level Indicating Transmitter | F18HP511 Water Ctrl | Auto | X | X |  | LT18201 | 30 | 90 | % | 0 | 100 | % |  |  |  | 60 | 5 | [7 empty] | 20 | 5 | 30 | 5 | 80 | 5 | 90 | 5 |  | 0 | 100 | 0 | 100 | % Open (valve) | F18-HP-511 Cleaner Scavenger Flotation Cell Feed Hopper Level Control Valve | LCV18201A | Reverse |  |  |  | Dual hopper control. See 2000-F00-REP-PR-10001 for further information. Operator to ensure Level Controller A setpoint is less than Level Controller B setpoint. Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | LT18201 | LIC18201B | 2000-F18-PID-PR-10003 | F18-HP-511 Cleaner Scavenger Flotation Cell Feed Hopper Level Indicating Transmitter | F18CF511 Recycle Ctrl | Auto | X | X |  | LT18201 | 30 | 90 | % | 0 | 100 | % | [21 empty] | 0 | 100 | 0 | 100 | % Open (valve) | F18-BX-511 Cleaner Scavenger Flotation ERM Recycle Level Control Valve | LCV18201B | Reverse |  |  |  | Dual hopper control. See 2000-F00-REP-PR-10001 for further information. Operator to ensure Level Controller A setpoint is less than Level Controller B setpoint. | 1
|  |  |  | FIT18227 | FIC18227 | 2000-F18-PID-PR-10003 | F18-PP-511/512 Cleaner Scavenger Flotation Cell Recirculation Pumps Discharge Flow Indicating Transmitter | F18PP511/2 Ctrl | Auto | X | X |  | FIT18227 | 0 | 2200 | m3/hr | 0 | 2500 | m3/hr | [12 empty] | 400 | 5 | 1990 | 5 | 2050 | 5 |  |  | DUTY F18PP511/512 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP511 OR 512 start-up. | 0 | 100 | 40 | 100 | % Speed VSD | Cleaner Flotation Cell Recirculation Pump 1/2 via Handswitch 18227 | Duty F18PP511/512 VSD via HS18227 | Reverse |  |  |  | Maximum 2018 m3/hr. Pumps designed to 2242 m3/hr. Alarm setpoints to be confirmed during commissioning. | 3 |  |  |  |  | flow instrument tested, PID action test outstanding -PH 15/06/2026
|  |  |  | LT18211 | LIC18211A | 2000-F18-PID-PR-10003 | F18-HP-513 Cleaner Scavenger Flotation Cell Tails Hopper Level Indicating Transmitter | F18HP513 Water Ctrl | Auto | X | X |  | LT18211 | 30 | 90 | % | 0 | 100 | % |  |  |  | 60 | 5 | [7 empty] | 20 | 5 | 30 | 5 | 80 | 5 | 90 | 5 |  | 0 | 100 | 0 | 100 | % Open (valve) | F18-HP-513 Cleaner Scavenger Flotation Cell Tails Hopper Level Control Valve | LCV18211 | Reverse |  |  |  | Dual hopper control. See 2000-F00-REP-PR-10001 for further information. Operator to ensure Level Controller A setpoint is less than Level Controller B setpoint. Alarms to be confirmed during commissioning. | 1
|  |  |  | LT18211 | LIC18211B | 2000-F18-PID-PR-10003 | F18-HP-513 Cleaner Scavenger Flotation Cell Tails Hopper Level Indicating Transmitter | F18HP511 Pump Ctrl | Auto | X | X |  | LT18211 | 30 | 90 | % | 0 | 100 | % | [21 empty] | 0 | 100 | 40 | 100 | % Speed VSD | Cleaner Scavenger Flotation Cell Tails Pump 1/2 via Handswitch 18237 | Duty F18PP513/514 VSD via HS18237 | Direct |  |  |  | Dual hopper control. See 2000-F00-REP-PR-10001 for further information. Operator to ensure Level Controller A setpoint is less than Level Controller B setpoint. | 1
|  |  |  | FIT18257 | FIC18257 | 2000-F18-PID-PR-10004 | F26-CF-511 Cleaner-Scavenger Flotation Cell Wash Water Flow Flow Indicating Transmitter | F18CF511 Conc Water Ctrl | Cascade | X | X | X | FIT18257 | 0 | 200 | m3/hr | 0 | 200 | m3/hr | [12 empty] | 5 | 5 | 19 | 5 | 64 | 5 |  |  | A_LL: DUTY F18PP511/512 NOT RUNNING A_Lo: DUTY F18PP511/512 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP511 OR 512 start-up. | 0 | 100 | 0 | 100 | % Open (valve) | F18-CF-511 Cleaner-Scavenger Flotation Cell Wash Water Flow Flow Control Valve | FCV18257 | Reverse |  |  |  | In CASCADE Mode, the setpoint for FIC18257 is provided by F18CALC0006. Alarms to be confirmed during commissioning. Source: 2000-ME073-M01-10001. | 3 |  |  |  |  | MSH: Mode switching to be verified to be bumpless?
|  |  |  | FIT18256 | FIC18256 | 2000-F18-PID-PR-10004 | F26-CF-511 Cleaner-Scavenger Flotation Cell Air Flow Indicating Transmitter | F18CF511 Air Ctrl | Auto | X | X |  | FIT18256 | 800 | 1650 | Sm3/hr | 0 | 2000 | Sm3/hr | [12 empty] | 200 | 5 | [6 empty] | A_LL: DUTY F18PP511/512 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP511 OR 512 start-up. | 0 | 100 | 0 | 100 | % Open (valve) | F18-CF-511 Cleaner-Scavenger Flotation Cell Air Flow Control Valve | FCV18256 | Reverse |  |  |  | Alarm setpoints to be confirmed during commissioning. Source: 2000-ME073-M01-10001. | 3 |  |  |  |  | Instument tested, not PID action 23/06/2026
|  |  |  | LNI18251 | LIC18251 | 2000-F18-PID-PR-10004 | F18-CF-511 Cleaner-Scavenger Flotation Cell Tank Slurry Level Indicating Transmitter | F18CF511 Froth | Auto | X | X |  | LNI18251 | 0 | 680 | mm | 0 | 1900 | mm | [6 empty] | 800 | 5 | [10 empty] | 700 | 5 |  | 0 | 100 | 0 | 100 | % Open (valve) | F18-CF-511 Cleaner-Scavenger Flotation Cell Tank Slurry Level Control Valve | LCV18251 | Reverse |  |  |  | Please refer to 2000-ME073-M01-10001 Page 8 and 11. Calculation for dual level transmitter setup. Bottom-range is zero for manual shutdown sequence. Alarm setpoints to be confirmed during commissioning. Source: 2000-ME073-M01-10001. | 3
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 43 | 43
Operator to get electrician to inspect unit for potential failure

## 7. Control Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION (F16, F17, F18)
2000-F16-LST-PR-10001
CONTROL VALVES
[14 empty] | Permissive and Trips | [12 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (Faceplate) | Delay On | Delay Off | Open Permissive | Close Permissive | Open Interlock | Close Interlock | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date
|  |  |  | FCV16011 | 2000-F16-PID-PR-10001 | F16-CF-411 Rougher Flotation Cell 1 Low Pressure Air Flow Control Valve | F16CF11 Blower Air | Detail 1 | FL | X | X | FIC16011 | FIC16011 | [12 empty] | 3 |  |  |  |  | Loss of Signal = Fail Close / Loss Of Air = Fail Last
|  |  |  | FCV16051 | 2000-F16-PID-PR-10002 | F16-CF-412 Rougher Flotation Cell 2 Low Pressure Air Flow Control Valve | F16CF412 Blower Air | Detail 1 | FL | X | X | FIC16051 | FIC16051 | [12 empty] | 3 |  |  |  |  | Loss of Signal = Fail Close / Loss Of Air = Fail Last
|  |  |  | LCV16013A | 2000-F16-PID-PR-10002 | F16-CF-412 Rougher Flotation Cell 2 Level Control Valve A | F16CF412 Dart Valve A | Detail 1 | FO | X | X | LIC16013A | LIC16013A | [11 empty] | Vendor specified operating range: 50 - 80% stroke. To be primary valve adjusting level when in Auto. To be confirmed during commissioning. Source: 2000-ME001.4-M02-50001. | 3 |  |  |  |  | Loss of Signal = Fail Open / Loss Of Air = Fail Last
|  |  |  | LCV16013B | 2000-F16-PID-PR-10002 | F16-CF-412 Rougher Flotation Cell 2 Level Control Valve B | F16CF412 Dart Valve B | Detail 1 | FO | X | X | LIC16013B | LIC16013B | [11 empty] | To be confirmed during commissioning. Source: 2000-ME001.4-M02-50001. | 3 |  |  |  |  | Loss of Signal = Fail Open / Loss Of Air = Fail Last
|  |  |  | FCV16061 | 2000-F16-PID-PR-10002 | F16-CF-413 Rougher Flotation Cell 3 Low Pressure Air Flow Control Valve | F16CF413 Blower Air | Detail 1 | FL | X | X | FIC16061 | FIC16061 | [11 empty] | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | LCV16053A | 2000-F16-PID-PR-10002 | F16-CF-413 Rougher Flotation Cell 3 Level Control Valve A | F16CF413 Dart Valve A | Detail 1 | FO | X | X | LIC16053A | LIC16053A | [11 empty] | Vendor specified operating range: 50 - 80% stroke. To be primary valve adjusting level when in Auto. To be confirmed during commissioning. Source: 2000-ME001.4-M02-50001. | 3 |  |  |  |  | Loss of Signal = Fail Open / Loss Of Air = Fail Last
|  |  |  | LCV16053B | 2000-F16-PID-PR-10002 | F16-CF-413 Rougher Flotation Cell 3 Level Control Valve B | F16CF413 Dart Valve B | Detail 1 | FO | X | X | LIC16053B | LIC16053B | [11 empty] | To be confirmed during commissioning. Source: 2000-ME001.4-M02-50001. | 3 |  |  |  |  | Loss of Signal = Fail Open / Loss Of Air = Fail Last
|  |  |  | FCV16081 | 2000-F16-PID-PR-10003 | F16-CF-414 Scavenger Flotation Cell 1 Low Pressure Air Flow Control Valve | F16CF414 Blower Air | Detail 1 | FL | X | X | FIC16081 | FIC16081 | [11 empty] | Source: 2000-ME001.4-M02-50001. | 3 |  |  |  |  | Loss of Signal = Fail Close / Loss Of Air = Fail Last
|  |  |  | LCV16063A | 2000-F16-PID-PR-10003 | F16-CF-414 Scavenger Flotation Cell 1 Level Control Valve A | F16CF414 Dart Valve A | Detail 1 | FO | X | X | LIC16063A | LIC16063A | [11 empty] | Vendor specified operating range: 50 - 80% stroke. To be primary valve adjusting level when in Auto. To be confirmed during commissioning. Source: 2000-ME001.4-M02-50001. | 3 |  |  |  |  | Loss of Signal = Fail Open / Loss Of Air = Fail Last
|  |  |  | LCV16063B | 2000-F16-PID-PR-10003 | F16-CF-414 Scavenger Flotation Cell 1 Level Control Valve B | F16CF414 Dart Valve B | Detail 1 | FO | X | X | LIC16063B | LIC16063B | [11 empty] | To be confirmed during commissioning. Source: 2000-ME001.4-M02-50001. | 3 |  |  |  |  | Loss of Signal = Fail Open / Loss Of Air = Fail Last
|  |  |  | FCV16091 | 2000-F16-PID-PR-10003 | F16-CF-415 Scavenger Flotation Cell 2 Low Pressure Air Flow Control Valve | F16CF415 Blower Air | Detail 1 | FL | X | X | FIC16091 | FIC16091 | [11 empty] | Source: 2000-ME001.4-M02-50001. | 3 |  |  |  |  | SC -Stroked valve only, valve failed closed
|  |  |  | LCV16083A | 2000-F16-PID-PR-10003 | F16-CF-415 Scavenger Flotation Cell 2 Level Control Valve A | F16CF415 Dart Valve A | Detail 1 | FO | X | X | LIC16083A | LIC16083A | [11 empty] | Vendor specified operating range: 50 - 80% stroke. To be primary valve adjusting level when in Auto. To be confirmed during commissioning. Source: 2000-ME001.4-M02-50001. | 3 |  |  |  |  | Loss of Signal = Fail Open / Loss Of Air = Fail Last
|  |  |  | LCV16083B | 2000-F16-PID-PR-10003 | F16-CF-415 Scavenger Flotation Cell 2 Level Control Valve B | F16CF415 Dart Valve B | Detail 1 | FO | X | X | LIC16083B | LIC16083B | [11 empty] | To be confirmed during commissioning. Source: 2000-ME001.4-M02-50001. | 3 |  |  |  |  | Loss of Signal = Fail Open / Loss Of Air = Fail Last
|  |  |  | FCV16101 | 2000-F16-PID-PR-10003 | F16-CF-416 Scavenger Flotation Cell 3 Low Pressure Air Flow Control Valve | F16CF416 Blower Air | Detail 1 | FL | X | X | FIC16101 | FIC16101 | [11 empty] | Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | LCV16093A | 2000-F16-PID-PR-10003 | F16-CF-416 Scavenger Flotation Cell 3 Level Control Valve A | F16CF416 Dart Valve A | Detail 1 | FO | X | X | LIC16093A | LIC16093A | [11 empty] | Vendor specified operating range: 50 - 80% stroke. To be primary valve adjusting level when in Auto. To be confirmed during commissioning. Source: 2000-ME001.4-M02-50001. | 3 |  |  |  |  | Loss of Signal = Fail Open / Loss Of Air = Fail Last
|  |  |  | LCV16093B | 2000-F16-PID-PR-10003 | F16-CF-416 Scavenger Flotation Cell 3 Level Control Valve B | F16CF416 Dart Valve B | Detail 1 | FO | X | X | LIC16093B | LIC16093B | [11 empty] | To be confirmed during commissioning. Source: 2000-ME001.4-M02-50001. | 3 |  |  |  |  | Loss of Signal = Fail Open / Loss Of Air = Fail Last
|  |  |  | FCV16111 | 2000-F16-PID-PR-10003 | F16-CF-417 Scavenger Flotation Cell 4 Low Pressure Air Flow Control Valve | F16CF417 Blower Air | Detail 1 | FL | X | X | FIC16111 | FIC16111 | [11 empty] | Source: 2000-ME001.4-M02-50001. | 3 |  |  |  |  | Loss of Signal = Fail Close / Loss Of Air = Fail Last
|  |  |  | LCV16103A | 2000-F16-PID-PR-10003 | F16-CF-417 Scavenger Flotation Cell 4 Level Control Valve A | F16CF417 Dart Valve A | Detail 1 | FO | X | X | LIC16103A | LIC16103A | [11 empty] | Vendor specified operating range: 50 - 80% stroke. To be primary valve adjusting level when in Auto. To be confirmed during commissioning. Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | LCV16103B | 2000-F16-PID-PR-10003 | F16-CF-417 Scavenger Flotation Cell 4 Level Control Valve B | F16CF417 Dart Valve B | Detail 1 | FO | X | X | LIC16103B | LIC16103B | [11 empty] | To be confirmed during commissioning. Source: 2000-ME001.4-M02-50001. | 3
|  |  |  | LCV16113A | 2000-F16-PID-PR-10003 | F16-BX-412 Flotation Discharge Box Level Control Valve A | F16BX412 Discharge Box A | Detail 1 | FL | X | X | LIC16113A | LIC16113A | [12 empty] | 3 |  |  |  |  | Loss of Signal = Fail Open / Loss Of Air = Fail Last
|  |  |  | LCV16113B | 2000-F16-PID-PR-10003 | F16-BX-412 Flotation Discharge Box Level Control Valve B | F16BX412 Discharge Box B | Detail 1 | FL | X | X | LIC16113B | LIC16113B | [12 empty] | 3 |  |  |  |  | Loss of Signal = Fail Close / Loss Of Air = Fail Last
|  |  |  | FCV17001 | 2000-F17-PID-PR-10001 | F17-XM-413 Pre-Leach Thickener Flocculant In-Line Mixer Process Water Flow Control Valve | F17XM413 Flocc PW Diln | Detail 1 | FC | X | X | FIC17001 | FIC17001 | [12 empty] | C
|  |  |  | FCV17127 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps CIL2 Feed Flow Control Valve | F17TH401 UF to CIL2 | Detail 2 | FL | X | X | FIC17127 | FIC17127 | [11 empty] | Manual control only | 3 |  |  |  |  | AIR FAIL = FL LOSS OF SIGNAL = FL
|  |  |  | FCV17128 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps CIL3 Feed Flow Control Valve | F17TH401 UF to CIL3 | Detail 2 | FL | X | X | FIC17128 | FIC17128 | [11 empty] | Manual control only | 3 |  |  |  |  | AIR FAIL = FL LOSS OF SIGNAL = FL
|  |  |  | FCV17130 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps Final Tails Tank Flow Control Valve | F17TH401 UF to FinTails | Detail 2 | FL | X | [14 empty] | Manual control only | 3 |  |  |  |  | AIR FAIL = FL LOSS OF SIGNAL = FL
|  |  |  | LCV18001 | 2000-F18-PID-PR-10001 | F18-HP-414 Final Concentrate Hopper Process Water Feed Level Control Valve | F18HP414 Water Addition | Detail 1 | FC | X | X | LIC18001A | LIC18001A | [12 empty] | 1
|  |  |  | LCV18011A | 2000-F18-PID-PR-10001 | F18-HP-501 Cleaner Flotation Cell Feed Hopper Process Water Feed Level Control Valve | F18HP501 Water Addition | Detail 1 | FC | X | X | LIC18011A | LIC18011A | [12 empty] | 1
|  |  |  | LCV18051 | 2000-F18-PID-PR-10002 | F18-CF-501 Cleaner Flotation Cell Tank Slurry Level Control Valve | F18CF501 Froth Depth | Detail 1 | FL | X | X | F18-SEQ-0009 | Manually closed by Operator | [12 empty] | 3
[12 empty] | LIC18051 | LIC18051 | [12 empty] | x
|  |  |  | FCV18056 | 2000-F18-PID-PR-10002 | F18-CF-501 Cleaner Flotation Cell Air Flow Control Valve | F18CF501 Air | Detail 1 | FL | X | X | F18-SEQ-0009 | Manually closed by Operator | [12 empty] | 3
[12 empty] | FIC18056 | FIC18056 | [12 empty] | x
|  |  |  | FCV18057 | 2000-F18-PID-PR-10002 | F18-CF-501 Cleaner Flotation Cell Wash Water Flow Flow Control Valve | F18CF501 Con Wash Water | Detail 1 | FL | X | X | F18-SEQ-0009 | Manually closed by Operator | [12 empty] | 3
[12 empty] | FIC18057 | FIC18057 | [12 empty] | x
|  |  |  | LCV18011B | 2000-F18-PID-PR-10002 | F18-BX-501 Cleaner Flotation ERM Recycle Level Control Valve | F18CF501 Recycle | Detail 2 | FL | X | X | F18-SEQ-0009 | Manually closed by Operator | [12 empty] | 3
[12 empty] | LIC18011B | LIC18011B | [12 empty] | x
|  |  |  | LCV18201A | 2000-F18-PID-PR-10003 | F18-HP-511 Cleaner Scavenger Flotation Cell Feed Hopper Level Control Valve | F18HP511 Process Water | Detail 1 | FC | X | X | LIC18201A | LIC18201A | [12 empty] | 1 |  |  |  |  | OOP has been change to "LOW" alarm priority from "Reference Alarm" CAMS
|  |  |  | LCV18211 | 2000-F18-PID-PR-10003 | F18-HP-513 Cleaner Scavenger Flotation Cell Tails Hopper Level Control Valve | F18HP513 Process Water | Detail 1 | FC | X | X | LIC18211A | LIC18211A | [12 empty] | 1 |  |  |  |  | OOP has been change to "LOW" alarm priority from "Reference Alarm" CAMS
|  |  |  | LCV18251 | 2000-F18-PID-PR-10004 | F18-CF-511 Cleaner-Scavenger Flotation Cell Tank Slurry Level Control Valve | F18CF511 Froth Depth | Detail 1 | FL | X | X | F18-SEQ-0010 | Manually closed by Operator | [12 empty] | 3
[12 empty] | LIC18251 | LIC18251 | [12 empty] | x
|  |  |  | FCV18256 | 2000-F18-PID-PR-10004 | F18-CF-511 Cleaner-Scavenger Flotation Cell Air Flow Control Valve | F18CF511 Air | Detail 1 | FL | X | X | F18-SEQ-0010 | Manually closed by Operator | [12 empty] | 3
[12 empty] | FIC18256 | FIC18256 | [12 empty] | x
|  |  |  | FCV18257 | 2000-F18-PID-PR-10004 | F18-CF-511 Cleaner-Scavenger Flotation Cell Wash Water Flow Flow Control Valve | F18CF511 Con Wash Water | Detail 1 | FL | X | X | F18-SEQ-0010 | Manually closed by Operator | [12 empty] | 3
[12 empty] | FIC18257 | FIC18257 | [12 empty] | x
|  |  |  | LCV18201B | 2000-F18-PID-PR-10004 | F18-CF-511 Cleaner-Scavenger Flotation Cell Recycle Valve | F18CF511 Recycle | Detail 2 | FL | X | X | F18-SEQ-0010 | Manually closed by Operator | [11 empty] | ZI18201B not functioning at time of testing, but Output to valve and valve itself functioning ok. LR 25/06/26 | B
[12 empty] | LIC18201B | LIC18201B
|  |  |  | FCV16001 | 2000-F16-PID-PR-10001 | F16-CF-411 Rougher Flotation Cell 1 Process Water Flow Control Valve Position Control | F16CF411 PW FCV | Detail 1 | FC | X | [14 empty] | Manual control only | 3
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
38

## 9. Drives
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION (F16, F17, F18)
2000-F16-LST-PR-10001
DRIVE INTERLOCKS AND CONTROL
[19 empty] | Interlocks | [6 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Name | Drive Type | Speed Min | Speed Max | Speed Units | SP Lower Limit | SP Upper Limit | Current Max | Manual | Auto | Start Condition (Auto Mode) | Stop Condition (Auto Mode) | # | Description (Unhealthy Interlocks and Healthy Permissives) | Delay On | Delay Off | Start Permissive | Process | Critical | Hardwired to Drive | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date | Comments
F16-AG-421 | 2000-F16-PID-PR-10001 | ROUGHER FLOTATION CELL 1 AGITATOR | VSD | 0 | 100 | % | 80 | 100 | 104 | X |  | Manually started by CRO | Manually stopped by CRO
[14 empty] | 1 | F16-AG-421 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-AG-421 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-AG-421 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-AG-421 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-AG-421 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-AG-421 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-AG-421 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16014 >= A_HH | 5 |  |  |  | X |  |  |  | Protection for gear unit. | B
[14 empty] | 9 | PI16015 <= A_LL AND (F16-AG-421 Running > 10 seconds) | 5 |  |  |  | X |  |  |  | Protection for gear unit. | 3
[14 empty] | 10 | VI16019 >= A_HH | 5 |  |  | X |  |  | X |  | Gearbox Vibration Alarm High High | 0
[14 empty] | 11 | VI16020 >= A_HH | 5 |  |  | X |  |  | X |  | Motor Vibration Alarm High High | 0
F16-AG-422 | 2000-F16-PID-PR-10002 | ROUGHER FLOTATION CELL 2 AGITATOR | VSD | 0 | 100 | % | 80 | 100 | 104 | X |  | Manually started by CRO | Manually stopped by CRO
[14 empty] | 1 | F16-AG-422 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-AG-422 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-AG-422 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-AG-422 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-AG-422 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-AG-422 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-AG-422 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16054 >= A_HH | 5 |  |  |  | X |  |  |  | Protection for gear unit. | B
[14 empty] | 9 | PI16055 <= A_LL AND (F16-AG-422 Running > 10 seconds) | 5 |  |  |  | X |  |  |  | Protection for gear unit. | 3
[14 empty] | 10 | VI16059 >= A_HH | 5 |  |  | X |  |  | X |  | Gearbox Vibration Alarm High High | 0
[14 empty] | 11 | VI16060 >= A_HH | 5 |  |  | X |  |  | X |  | Motor Vibration Alarm High High | 0
F16-AG-423 | 2000-F16-PID-PR-10002 | ROUGHER FLOTATION CELL 3 AGITATOR | VSD | 0 | 100 | % | 80 | 100 | 104 | X |  | Manually started by CRO | Manually stopped by CRO
[14 empty] | 1 | F16-AG-423 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-AG-423 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-AG-423 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-AG-423 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-AG-423 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-AG-423 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-AG-423 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16064 >= A_HH | 5 |  |  |  | X |  |  |  | Protection for gear unit. | B
[14 empty] | 9 | PI16065 <= A_LL AND (F16-AG-423 Running > 10 seconds) | 5 |  |  |  | X |  |  |  | Protection for gear unit. | 3
[14 empty] | 10 | VI16069 >= A_HH | 5 |  |  | X |  |  | X |  | Gearbox Vibration Alarm High High | 0
[14 empty] | 11 | VI16070 >= A_HH | 5 |  |  | X |  |  | X |  | Motor Vibration Alarm High High | 0
F16-FN-497 | 2000-F16-PID-PR-10001 | ROUGHER FLOTATION CELL 1 GEARBOX COOLING FAN | DOL | [5 empty] | 1.66 |  | X | TI16014 > P_HH | TI16014 < P_Hi | [11 empty] | 1
[14 empty] | 1 | F16-FN-497 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-497 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-497 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-497 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-HT-562 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-497 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-497 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-HT-562X | 2000-F16-PID-PR-10001 | ROUGHER FLOTATION CELL 1 GEARBOX HEATER 1 & 2 | DOL | [5 empty] | 5.5648 |  | X | TI16014 < P_LL | TI16014 > P_Lo | [10 empty] | F16-HT-562 & F16-HT-563 controlled by a common DOL starter. | 3
[14 empty] | 1 | F16-HT-562X Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-HT-562X Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-HT-562X Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-HT-562X E-Stop | 0 |  |  |  | X | X |  |  | N/A | 2 |  |  |  |  | VV 10/06/2026; NA
[14 empty] | 5 | F16-HT-562X MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | VV 10/06/2026; NA
[14 empty] | 6 | F16-HT-562X Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-HT-562X Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16014 >= A_Hi | 5 |  |  |  | X |  |  |  | Protection for gear unit. | C
F16-FN-498 | 2000-F16-PID-PR-10002 | ROUGHER FLOTATION CELL 2 GEARBOX COOLING FAN | DOL | [5 empty] | 1.66 |  | X | TI16054 > P_HH | TI16054 < P_Hi | [11 empty] | 1
[14 empty] | 1 | F16-FN-498 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-498 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-498 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-498 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-498 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-498 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-498 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-HT-564X | 2000-F16-PID-PR-10002 | ROUGHER FLOTATION CELL 2 GEARBOX HEATER 1 & 2 | DOL | [5 empty] | 5.5648 | X | X | TI16054 < P_LL | TI16054 > P_Lo | [10 empty] | F16-HT-564 & F16-HT-565 controlled by a common DOL starter. | 3
[14 empty] | 1 | F16-HT-564X Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-HT-564X Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-HT-564X Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-HT-564X E-Stop | 0 |  |  |  | X | X |  |  | N/A | 2 |  |  |  |  | VV 10/06/2026; NA
[14 empty] | 5 | F16-HT-564X MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | VV 10/06/2026; NA
[14 empty] | 6 | F16-HT-564X Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-HT-564X Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16054 >= A_Hi | 5 |  |  |  | X |  |  |  | Protection for gear unit. | C
F16-FN-499 | 2000-F16-PID-PR-10002 | ROUGHER FLOTATION CELL 3 GEARBOX COOLING FAN | DOL | [5 empty] | 1.66 |  | X | TI16064 > P_HH | TI16064 < P_Hi | [11 empty] | 1
[14 empty] | 1 | F16-FN-499 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-499 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-499 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-499 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-499 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-499 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-499 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-HT-566X | 2000-F16-PID-PR-10002 | ROUGHER FLOTATION CELL 3 GEARBOX HEATER 1 & 2 | DOL | [5 empty] | 5.5648 |  | X | TI16064 < P_LL | TI16064 > P_Lo | [10 empty] | F16-HT-566 & F16-HT-567 controlled by a common DOL starter. | 3
[14 empty] | 1 | F16-HT-566X Comms Failure | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 2 | F16-HT-566X Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-HT-566X Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-HT-566X E-Stop | 0 |  |  |  | X | X |  |  | N/A | 2 |  |  |  |  | VV 10/06/2026; NA
[14 empty] | 5 | F16-HT-566X MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 1 |  |  |  |  | VV 10/06/2026; NA
[14 empty] | 6 | F16-HT-566X Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 7 | F16-HT-566X Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16064 >= A_Hi | 5 |  |  |  | X |  |  |  | Protection for gear unit. | 1
F16-AG-424 | 2000-F16-PID-PR-10003 | SCAVENGER FLOTATION CELL 1 AGITATOR | VSD | 0 | 100 | % | 80 | 100 | 104 | X |  | Manually started by CRO | Manually stopped by CRO
[14 empty] | 1 | F16-AG-424 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-AG-424 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-AG-424 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-AG-424 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-AG-424 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-AG-424 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-AG-424 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16084 >= A_HH | 5 |  |  |  | X |  |  |  | Protection for gear unit. | C
[14 empty] | 9 | PI16085 <= A_LL AND (F16-AG-424 Running > 10 seconds) | 20 |  |  |  | X |  |  |  | Protection for gear unit. | 3
[14 empty] | 10 | VI16089 >= A_HH | 5 |  |  | X |  |  | X |  | Gearbox Vibration Alarm High High | 0
[14 empty] | 11 | VI16090 >= A_HH | 5 |  |  | X |  |  | X |  | Motor Vibration Alarm High High | 0
F16-AG-425 | 2000-F16-PID-PR-10003 | SCAVENGER FLOTATION CELL 2 AGITATOR | VSD | 0 | 100 | % | 80 | 100 | 104 | X |  | Manually started by CRO | Manually stopped by CRO
[14 empty] | 1 | F16-AG-425 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-AG-425 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-AG-425 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-AG-425 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-AG-425 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-AG-425 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-AG-425 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16094 >= A_HH | 5 |  |  |  | X |  |  |  | Protection for gear unit. | B
[14 empty] | 9 | PI16095 <= A_LL AND (F16-AG-425 Running > 10 seconds) | 20 |  |  |  | X |  |  |  | Protection for gear unit. | 3
[14 empty] | 10 | VI16099 >= A_HH | 5 |  |  | X |  |  | X |  | Gearbox Vibration Alarm High High | 0
[14 empty] | 11 | VI16100 >= A_HH | 5 |  |  | X |  |  | X |  | Motor Vibration Alarm High High | 0
F16-AG-426 | 2000-F16-PID-PR-10003 | SCAVENGER FLOTATION CELL 3 AGITATOR | VSD | 0 | 100 | % | 80 | 100 | 104 | X |  | Manually started by CRO | Manually stopped by CRO
[14 empty] | 1 | F16-AG-426 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-AG-426 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-AG-426 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-AG-426 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-AG-426 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-AG-426 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-AG-426 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16104 >= A_HH | 5 |  |  |  | X |  |  |  | Protection for gear unit. | B
[14 empty] | 9 | PI16105 <= A_LL AND (F16-AG-426 Running > 10 seconds) | 20 |  |  |  | X |  |  |  | Protection for gear unit. | 3
[14 empty] | 10 | VI16109 >= A_HH | 5 |  |  | X |  |  | X |  | Gearbox Vibration Alarm High High | 0
[14 empty] | 11 | VI16110 >= A_HH | 5 |  |  | X |  |  | X |  | Motor Vibration Alarm High High | 0
F16-FN-500 | 2000-F16-PID-PR-10003 | SCAVENGER FLOTATION CELL 1 GEARBOX COOLING FAN | DOL | [5 empty] | 1.66 |  | X | TI16084 > P_HH | TI16084 < P_Hi | [11 empty] | 1
[14 empty] | 1 | F16-FN-500 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-500 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-500 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-500 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-500 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-500 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-500 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-HT-568X | 2000-F16-PID-PR-10003 | SCAVENGER FLOTATION CELL 1 GEARBOX HEATER 1 & 2 | DOL | [5 empty] | 5.5648 |  | X | TI16084 < P_LL | TI16084 > P_Lo | [10 empty] | F16-HT-568 & F16-HT-569 controlled by a common DOL starter. | 3
[14 empty] | 1 | F16-HT-568X Comms Failure | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 2 | F16-HT-568X Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-HT-568X Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-HT-568X E-Stop | 0 |  |  |  | X | X |  |  | N/A | 2
[14 empty] | 5 | F16-HT-568X MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 6 | F16-HT-568X Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 7 | F16-HT-568X Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16084 >= A_Hi | 5 |  |  |  | X |  |  |  | Protection for gear unit. | 1
F16-FN-501 | 2000-F16-PID-PR-10003 | SCAVENGER FLOTATION CELL 2 GEARBOX COOLING FAN | DOL | [5 empty] | 1.66 |  | X | TI16094 > P_HH | TI16094 < P_Hi | [11 empty] | 3
[14 empty] | 1 | F16-FN-501 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-501 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-501 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-501 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-501 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-501 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-501 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-HT-570X | 2000-F16-PID-PR-10003 | SCAVENGER FLOTATION CELL 2 GEARBOX HEATER 1 & 2 | DOL | [5 empty] | 5.5648 |  | X | TI16094 < P_LL | TI16094 > P_Lo | [10 empty] | F16-HT-570 & F16-HT-571 controlled by a common DOL starter. | 3
[14 empty] | 1 | F16-HT-570X Comms Failure | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 2 | F16-HT-570X Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-HT-570X Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-HT-570X E-Stop | 0 |  |  |  | X | X |  |  | N/A | 2
[14 empty] | 5 | F16-HT-570X MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 6 | F16-HT-570X Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 7 | F16-HT-570X Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16094 >= A_Hi | 5 |  |  |  | X |  |  |  | Protection for gear unit. | 1
F16-FN-502 | 2000-F16-PID-PR-10003 | SCAVENGER FLOTATION CELL 3 GEARBOX COOLING FAN | DOL | [5 empty] | 1.66 |  | X | TI16104 P_HH | TI16104 P_Hi | [11 empty] | 1
[14 empty] | 1 | F16-FN-502 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-502 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-502 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-502 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-502 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-502 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-502 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-HT-572X | 2000-F16-PID-PR-10003 | SCAVENGER FLOTATION CELL 3 GEARBOX HEATER 1 & 2 | DOL | [5 empty] | 5.5648 |  | X | TI16104 < P_LL | TI16104 > P_Lo | [10 empty] | F16-HT-572 & F16-HT-573 controlled by a common DOL starter. | 3
[14 empty] | 1 | F16-HT-572X Comms Failure | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 2 | F16-HT-572X Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-HT-572X Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-HT-572X E-Stop | 0 |  |  |  | X | X |  |  | N/A | 2
[14 empty] | 5 | F16-HT-572X MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 6 | F16-HT-572X Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 7 | F16-HT-572X Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16104 >= A_Hi | 5 |  |  |  | X |  |  |  | Protection for gear unit. | 1
F16-AG-427 | 2000-F16-PID-PR-10003 | SCAVENGER FLOTATION CELL 4 AGITATOR | VSD | 0 | 100 | % | 80 | 100 | 104 | X |  | Manually started by CRO | Manually stopped by CRO
[14 empty] | 1 | F16-AG-427 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-AG-427 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-AG-427 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-AG-427 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[12 empty] | 1 |  | 5 | F16-AG-427 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-AG-427 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-AG-427 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16114 >= A_HH | 5 |  |  |  | X |  |  |  | Protection for gear unit. | B
[14 empty] | 9 | PI16115 <= A_LL AND (F16-AG-427 Running > 10 seconds) | 5 |  |  |  | X |  |  |  | Protection for gear unit. | 3
[14 empty] | 10 | VI16119 >= A_HH | 5 |  |  | X |  |  | X |  | Gearbox Vibration Alarm High High | 0
[14 empty] | 11 | VI16120 >= A_HH | 5 |  |  | X |  |  | X |  | Motor Vibration Alarm High High | 0
F16-FN-503 | 2000-F16-PID-PR-10003 | SCAVENGER FLOTATION CELL 4 GEARBOX COOLING FAN | DOL | [5 empty] | 1.66 |  | X | TI16114 > P_HH | TI16114 < P_Hi | [11 empty] | 3
[14 empty] | 1 | F16-FN-503 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-503 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-503 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-503 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-503 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-503 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-503 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-HT-574X | 2000-F16-PID-PR-10003 | SCAVENGER FLOTATION CELL 4 GEARBOX HEATER 1 & 2 | DOL | [5 empty] | 5.5648 |  | X | TI16114 < P_LL | TI16114 > P_Lo | [10 empty] | F16-HT-574 & F16-HT-575 controlled by a common DOL starter. | 3
[14 empty] | 1 | F16-HT-574X Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-HT-574X Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-HT-574X Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-HT-574X E-Stop | 0 |  |  |  | X | X |  |  | N/A | 2 |  |  |  |  | VV 10/06/2026; NA
[14 empty] | 5 | F16-HT-574X MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | VV 10/06/2026; NA
[14 empty] | 6 | F16-HT-574X Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-HT-574X Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | TI16114 >= A_Hi | 5 |  |  |  | X |  |  |  | Protection for gear unit. | C
F16-BW-401 | 2000-F16-PID-PR-10006 | FLOTATION AIR BLOWER 1 | VSD | 0 | 100 | % | 40 | 100 | 520 | X | X | Manually started by CRO | Manually stopped by CRO
[14 empty] | 1 | F16-BW-401 Comms Failure | 0 |  |  |  | X |  |  |  | VSD ramp up from standstill to minimum speed must be greater than 5-6 seconds. VSD ramping up or down during normal operation < 1Hz/s. Source: 2000-ME001.4-M02-50001 | C
[14 empty] | 2 | F16-BW-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-BW-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-BW-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-BW-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-BW-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-BW-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | PI16261 <= A_LL | 5 |  |  | X |  |  | X |  | Inlet air pressure low low | B
[14 empty] | 9 | PIC16199 >= A_HH | 5 |  |  | X |  |  | X |  | Outlet air pressure high high | B
[14 empty] | 10 | TI16265 >= A_HH | 5 |  |  | X |  |  | X |  | Blower enclosure temperature | B
[14 empty] | 11 | TI16263 >= A_HH | 5 |  |  | X |  |  | X |  | Blower outlet temperature | B
[14 empty] | 12 | TI16264 >= A_HH | 5 |  |  | X |  |  | X |  | Blower gearbox oil temperature (drive end) | B
[14 empty] | 13 | TI16198A >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase U. Resistance Thermocouple Detector to trip drive on temperature high high. | B
[14 empty] | 14 | TI16198B >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase V. Resistance Thermocouple Detector to trip drive on temperature high high. | B
[14 empty] | 15 | TI16198C >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase W. Resistance Thermocouple Detector to trip drive on temperature high high. | B
[14 empty] | 16 | TI16198D >= A_HH | 5 |  |  |  | X |  |  |  | DE Bearing. Drive-End bearing temperature high high | B
[14 empty] | 17 | TI16198E >= A_HH | 5 |  |  |  | X |  |  |  | NDE Bearing. Non-Drive End bearing temperature high high. | B
[14 empty] | 18 | F16-FN-487 in Auto | 0 |  | X |  |  |  | X |  |  | 3
[14 empty] | 19 | F16-FN-493 in Auto | 0 |  | X |  |  |  | X |  |  | 3
F16-FN-487 | 2000-F16-PID-PR-10006 | FLOTATION AIR BLOWER 1 MOTOR COOLING FAN | DOL | [5 empty] | 2.18 |  | X | STARTS WHEN F16-BW-401 RUNNING | 15 MINUTE TIMER ELAPSED SINCE F16-BW-401 STOPPED RUNNING | [11 empty] | 1
[14 empty] | 1 | F16-FN-487 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-487 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-487 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-487 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-487 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-487 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-487 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-FN-493 | 2000-F16-PID-PR-10006 | FLOTATION AIR BLOWER 1 VENTILATION FAN | DOL | [5 empty] | 4.74 |  | X | STARTS WHEN F16-BW-401 RUNNING | 15 MINUTE TIMER ELAPSED SINCE F16-BW-401 STOPPED RUNNING | [11 empty] | 1 |  |  |  |  | WORD swap required in WW
[14 empty] | 1 | F16-FN-493 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-493 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-493 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-493 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-493 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-493 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-493 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-BW-402 | 2000-F16-PID-PR-10006 | FLOTATION AIR BLOWER 2 | VSD | 0 | 100 | % | 40 | 100 | 520 | X | X | Manually started by CRO | Manually stopped by CRO
[14 empty] | 1 | F16-BW-402 Comms Failure | 0 |  |  |  | X |  |  |  | VSD ramp up from standstill to minimum speed must be greater than 5-6 seconds. VSD ramping up or down during normal operation < 1Hz/s. Source: 2000-ME001.4-M02-50001 | C
[14 empty] | 2 | F16-BW-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-BW-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-BW-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-BW-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-BW-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-BW-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | PI16271 <= A_LL | 5 |  |  | X |  |  | X |  | Inlet air pressure low low | B
[14 empty] | 9 | PIC16209 >= A_HH | 5 |  |  | X |  |  | X |  | Outlet air pressure high high | B
[14 empty] | 10 | TI16275 >= A_HH | 5 |  |  | X |  |  | X |  | Blower enclosure temperature | B
[14 empty] | 11 | TI16273 >= A_HH | 5 |  |  | X |  |  | X |  | Blower outlet temperature | B
[14 empty] | 12 | TI16274 >= A_HH | 5 |  |  | X |  |  | X |  | Blower gearbox oil temperature (drive end) | B
[14 empty] | 13 | TI16208A >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase U. Resistance Thermocouple Detector to trip drive on temperature high high. | B
[14 empty] | 14 | TI16208B >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase V. Resistance Thermocouple Detector to trip drive on temperature high high. | B
[14 empty] | 15 | TI16208C >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase W. Resistance Thermocouple Detector to trip drive on temperature high high. | B
[14 empty] | 16 | TI16208D >= A_HH | 5 |  |  |  | X |  |  |  | DE Bearing. Drive-End bearing temperature high high | B
[14 empty] | 17 | TI16208E >= A_HH | 5 |  |  |  | X |  |  |  | NDE Bearing. Non-Drive End bearing temperature high high. | B
[14 empty] | 18 | F16-FN-488 in Auto | 0 |  | X |  |  |  | X |  |  | 3
[14 empty] | 19 | F16-FN-494 in Auto | 0 |  | X |  |  |  | X |  |  | 3
F16-FN-488 | 2000-F16-PID-PR-10006 | FLOTATION AIR BLOWER 2 MOTOR COOLING FAN | DOL | [5 empty] | 2.18 |  | X | STARTS WHEN F16-BW-402 RUNNING | 15 MINUTE TIMER ELAPSED SINCE F16-BW-402 STOPPED RUNNING | [11 empty] | 1
[14 empty] | 1 | F16-FN-488 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-488 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-488 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-488 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-488 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-488 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-488 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-FN-494 | 2000-F16-PID-PR-10006 | FLOTATION AIR BLOWER 2 VENTILATION FAN | DOL | [5 empty] | 4.74 |  | X | STARTS WHEN F16-BW-402 RUNNING | 15 MINUTE TIMER ELAPSED SINCE F16-BW-402 STOPPED RUNNING | [11 empty] | 1
[14 empty] | 1 | F16-FN-494 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-494 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-494 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-494 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-494 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-494 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-494 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-BW-403 | 2000-F16-PID-PR-10006 | FLOTATION AIR BLOWER 3 | VSD | 0 | 100 | % | 40 | 100 | 520 | X | X | Manually started by CRO | Manually stopped by CRO
[14 empty] | 1 | F16-BW-403 Comms Failure | 0 |  |  |  | X |  |  |  | VSD ramp up from standstill to minimum speed must be greater than 5-6 seconds. VSD ramping up or down during normal operation < 1Hz/s. Source: 2000-ME001.4-M02-50001 | C
[14 empty] | 2 | F16-BW-403 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-BW-403 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-BW-403 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-BW-403 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-BW-403 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-BW-403 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | PI16281 <= A_LL | 5 |  |  | X |  |  | X |  | Inlet air pressure low low | B
[14 empty] | 9 | PIC16219 >= A_HH | 5 |  |  | X |  |  | X |  | Outlet air pressure high high | C
[14 empty] | 10 | TI16285 >= A_HH | 5 |  |  | X |  |  | X |  | Blower enclosure temperature | B
[14 empty] | 11 | TI16283 >= A_HH | 5 |  |  | X |  |  | X |  | Blower outlet temperature | B
[14 empty] | 12 | TI16284 >= A_HH | 5 |  |  | X |  |  | X |  | Blower gearbox oil temperature (drive end) | B
[14 empty] | 13 | TI16218A >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase U. Resistance Thermocouple Detector to trip drive on temperature high high. | B
[14 empty] | 14 | TI16218B >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase V. Resistance Thermocouple Detector to trip drive on temperature high high. | B
[14 empty] | 15 | TI16218C >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase W. Resistance Thermocouple Detector to trip drive on temperature high high. | B
[14 empty] | 16 | TI16218D >= A_HH | 5 |  |  |  | X |  |  |  | DE Bearing. Drive-End bearing temperature high high | B
[14 empty] | 17 | TI16218E >= A_HH | 5 |  |  |  | X |  |  |  | NDE Bearing. Non-Drive End bearing temperature high high. | B
[14 empty] | 18 | F16-FN-489 in Auto | 0 |  | X |  |  |  | X |  |  | 3
[14 empty] | 19 | F16-FN-495 in Auto | 0 |  | X |  |  |  | X |  |  | 3
F16-FN-489 | 2000-F16-PID-PR-10006 | FLOTATION AIR BLOWER 3 MOTOR COOLING FAN | DOL | [5 empty] | 2.18 |  | X | STARTS WHEN F16-BW-403 RUNNING | 15 MINUTE TIMER ELAPSED SINCE F16-BW-403 STOPPED RUNNING | [11 empty] | 1
[14 empty] | 1 | F16-FN-489 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-489 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-489 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-489 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-489 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-489 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-489 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-FN-495 | 2000-F16-PID-PR-10006 | FLOTATION AIR BLOWER 3 VENTILATION FAN | DOL | [5 empty] | 4.74 |  | X | STARTS WHEN F16-BW-403 RUNNING | 15 MINUTE TIMER ELAPSED SINCE F16-BW-403 STOPPED RUNNING | [11 empty] | 1
[14 empty] | 1 | F16-FN-495 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-495 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-495 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-495 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-495 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-495 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-495 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-BW-404 | 2000-F16-PID-PR-10006 | FLOTATION AIR BLOWER 4 | VSD | 0 | 100 | % | 40 | 100 | 520 | X | X | Manually started by CRO | Manually stopped by CRO | [16 empty] | Need to actually confirm max current of these drives - AP
[14 empty] | 1 | F16-BW-404 Comms Failure | 0 |  |  |  | X |  |  |  | VSD ramp up from standstill to minimum speed must be greater than 5-6 seconds. VSD ramping up or down during normal operation < 1Hz/s. Source: 2000-ME001.4-M02-50001 | C
[14 empty] | 2 | F16-BW-404 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-BW-404 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-BW-404 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-BW-404 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-BW-404 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-BW-404 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | PI16291 <= A_LL | 5 |  |  | X |  |  | X |  | Inlet air pressure low low | B
[14 empty] | 9 | PIC16229 >= A_HH | 5 |  |  | X |  |  | X |  | Outlet air pressure high high | B
[14 empty] | 10 | TI16295 >= A_HH | 5 |  |  | X |  |  | X |  | Blower enclosure temperature | B
[14 empty] | 11 | TI16293 >= A_HH | 5 |  |  | X |  |  | X |  | Blower outlet temperature | B
[14 empty] | 12 | TI16294 >= A_HH | 5 |  |  | X |  |  | X |  | Blower gearbox oil temperature (drive end) | B
[14 empty] | 13 | TI16228A >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase U. Resistance Thermocouple Detector to trip drive on temperature high high. | B
[14 empty] | 14 | TI16228B >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase V. Resistance Thermocouple Detector to trip drive on temperature high high. | B
[14 empty] | 15 | TI16228C >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase W. Resistance Thermocouple Detector to trip drive on temperature high high. | B
[14 empty] | 16 | TI16228D >= A_HH | 5 |  |  |  | X |  |  |  | DE Bearing. Drive-End bearing temperature high high | B
[14 empty] | 17 | TI16228E >= A_HH | 5 |  |  |  | X |  |  |  | NDE Bearing. Non-Drive End bearing temperature high high. | B
[14 empty] | 18 | F16-FN-490 in Auto | 0 |  | X |  |  |  | X |  |  | 3
[14 empty] | 19 | F16-FN-496 in Auto | 0 |  | X |  |  |  | X |  |  | 3
F16-FN-490 | 2000-F16-PID-PR-10006 | FLOTATION AIR BLOWER 4 MOTOR COOLING FAN | DOL | [5 empty] | 2.18 |  | X | STARTS WHEN F16-BW-404 RUNNING | 15 MINUTE TIMER ELAPSED SINCE F16-BW-404 STOPPED RUNNING | [11 empty] | 1
[14 empty] | 1 | F16-FN-490 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-490 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-490 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-490 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-490 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-490 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-490 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-FN-496 | 2000-F16-PID-PR-10006 | FLOTATION AIR BLOWER 4 VENTILATION FAN | DOL | [5 empty] | 4.74 |  | X | STARTS WHEN F16-BW-404 RUNNING | 15 MINUTE TIMER ELAPSED SINCE F16-BW-404 STOPPED RUNNING | [11 empty] | 1
[14 empty] | 1 | F16-FN-496 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-FN-496 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-FN-496 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-FN-496 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-FN-496 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-FN-496 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-FN-496 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F17-PP-459 | 2000-ME001.5-E02-50001 | FLOTATION TAILINGS THICKENER P-DUC PUMP | VSD | 0 | 100 | % | 40 | 100 | 67 | X | X | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1 |  |  |  |  | VV; 28/07/2026 Bump Test Complete/Successful, 1-Hr ran at 40% speed
[12 empty] | F17PP459_ES |  | 1 | F17-PP-459 Comms Failure | 0 |  |  |  | X |  |  |  |  | 3
[14 empty] | 2 | F17-PP-459 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F17-PP-459 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F17-PP-459 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F17-PP-459 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F17-PP-459 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F17-PP-459 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | XA17060 Inactive | 0 |  |  |  | X | X |  | X | Flotation Tailings Thickener E-Stop Active | 3
[14 empty] | 9 | F17PP459_I <= 14 Amps AND F17-PP-459 Running | 5 |  |  | X |  |  | X |  | P-Duc no load current. Setpoint TBC during commissioning | 3
[14 empty] | 10 | TS17039 Active | 3 |  |  | X |  |  | X |  | P-Duc motor temperature | 3
F17-XM-572 | 2000-ME001.5-E02-50002 | FLOTATION TAILINGS THICKENER MANTA SUB | FE | [5 empty] | - | X | X | Manually started by CRO | Manually stopped by CRO
[14 empty] | 1 | F17-XM-572 Comms Failure | 0 |  |  |  | X
[14 empty] | 2 | F17-XM-572 Fail to Start / Stop | 0 |  |  |  | X
[14 empty] | 3 | F17-XM-572 Drive Fault | 0 |  |  |  | X
[14 empty] | 4 | F17-XM-572 E-Stop | 0 |  |  |  | X | X
[14 empty] | 5 | F17-XM-572 MCC Unhealthy | 0 |  |  |  | X
[14 empty] | 6 | F17-XM-572 Drive Out of Service | 0 |  |  |  | X
[14 empty] | 7 | F17-XM-572 Drive Ready | 0 |  |  |  | X
F17-TH-401 | 2000-ME001.5-E02-50002 | FLOTATION TAILINGS THICKENER | SOFT DRIVE | [5 empty] | - | X | X | [12 empty] | Manual - to indicate when not in local Local - this is attached to F17TH401_LCL soft signal Forward - this is attached to F17TH401_STRT soft signal Stop - this is attached to F17TH401_STOP soft signal Show forward feedback when F17-PO-408 is running AND SV17033 is open Show reverse feedback when F17-PO-408 is running AND SV17034 is open. | 3
[14 empty] | 1 | F17-PO-408 Not Available | 0 |  |  |  | X |  |  |  |  | 3
[14 empty] | 2 | F17-PO-408 Auto | 0 |  | X |  |  |  | X |  |  | 3
[14 empty] | 3 | F17-PO-409 Available | 0 |  | X |  |  |  | X |  |  | 3
[14 empty] | 4 | F17-PO-409 Auto | 0 |  | X |  |  |  | X |  |  | 3
[14 empty] | 5 | SV17033 Not Available | 0 |  |  |  | X |  |  |  |  | 3
[14 empty] | 6 | SV17033 Not in Auto | 0 |  |  |  | X |  |  |  |  | 3
[14 empty] | 7 | SV17034 Not Available | 0 |  |  |  | X |  |  |  |  | 3
[14 empty] | 8 | SV17034 Not in Auto | 0 |  |  |  | X |  |  |  |  | 3
[14 empty] | 9 | SV17047 Available | 0 |  | X |  |  |  | X |  |  | 3
[14 empty] | 10 | SV17047 Auto | 0 |  | X |  |  |  | X |  |  | 3
[14 empty] | 11 | SV17048 Available | 0 |  | X |  |  |  | X |  |  | 3
[14 empty] | 12 | SV17048 Auto | 0 |  | X |  |  |  | X |  |  | 3
F17-FN-492 | 2000-ME001.5-E02-50002 | FLOTATION TAILINGS THICKENER RAKE DRIVE OIL COOLING FAN | DOL | [5 empty] | 2.6 | X | X | TSH17025 ACTIVE | TSH17025 INACTIVE And 300 second timer elapsed | [11 empty] | 3 |  |  |  |  | VV 06/07/2026; 1 Hr Uncoupled Run started/completed
[14 empty] | 1 | F17-FN-492 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F17-FN-492 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F17-FN-492 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F17-FN-492 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F17-FN-492 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | VV 06/07/2026; N/A. ap 29/07/2026 - Still interlcoks as per design functionality
[14 empty] | 6 | F17-FN-492 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F17-FN-492 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | XA17060 Inactive | 0 |  |  |  | X | X |  | X | Flotation Tailings Thickener E-Stop Active | 3
F17-PO-408 | 2000-ME001.5-E02-50002 | FLOTATION TAILINGS THICKENER RAKE DRIVE PUMP | DOL | [5 empty] | 55 | X | X | Thickener Rake Run Request 'F17TH401OUT Active | Thickener Rake Run Request 'F17TH401OUT Inactive | [11 empty] | 1 |  |  |  |  | VV 06/07/2026; 1 Hr Uncoupled Run started/completed
[12 empty] | F17TH401_LCL Active AND HS17061 Forward Field Start Button Active | F17TH401_LCL Active AND HS17064 Stop Button Active | 1 | F17-PO-408 Comms Failure | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | AP for auto start conditions - 29/07/2026
[12 empty] | F17TH401_LCL Active AND HS17063 Reverse Jog Button Active AND F17TH401_REV Active | F17PO408_RT1 Elapsed | 2 | F17-PO-408 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[12 empty] | Started manually by the operator | Stopped manually by the operator | 3 | F17-PO-408 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F17-PO-408 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F17-PO-408 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | VV 06/07/2026; N/A. ap 29/07/2026 - Still interlcoks as per design functionality
[14 empty] | 6 | F17-PO-408 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F17-PO-408 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | XA17060 Inactive | 0 |  |  |  | X | X |  | X | Flotation Tailings Thickener E-Stop Active | 3
[14 empty] | 9 | NI17030 >= A_HH | 5 |  |  |  | X |  |  |  | Flotation Tailings Thickener HPU Rake Torque 85%. | B
[14 empty] | 10 | ZSO17026 INACTIVE | 3 |  |  |  | X |  |  |  | Rake Drive Pump Suction/Inlet valve not open. | 3
[14 empty] | 11 | LSLL17023 Inactive | 3 |  |  |  | X |  |  | X | Hydraulic tank level low low. | 3
[14 empty] | 12 | TSHH17024 Inactive | 3 |  |  |  | X |  |  |  | Hydraulic oil tank temperature high high | 3
[14 empty] | 13 | Reverse Jog Cooldown Active | 3 |  |  |  | X |  |  |  | Logic: SV17034 ENERGISED AND F17TH401_T2 ACTIVE Prevent reverse jog being activated before Reverse Jog Cooldown Timer has elapsed. | 3
[14 empty] | 14 | Reverse Jog 30 Min Limit | 3 |  |  |  | X |  |  |  | Logic: SV17034 ENERGISED AND (F17TH401_C1 >= 3) Prevent reverse jog being activated if Reverse Jog Action Counter is equal to 3 in a half hour. | 3
[14 empty] | 15 | XA17038 Inactive | 3 |  |  |  | X |  |  |  | Manta Sub: Sensor Failed To Return Home. Critical fault of Manta Sub. Source: 2000-ME001.5-D02-50002 | 3
[14 empty] | 16 | (SSL17016 INACTIVE FOR >20 SECONDS) AND (F17-PO-408 Running) | 0 |  |  |  | X |  |  |  | Speed sensor not detecting pulses from rotating rake drive for > 20 seconds whilst the rake pump is running | 3
[14 empty] | 17 | PSL24651 InActive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated. 3-second damper applied to prevent trip due to thermal expansion Refer to 2000-F24-LST-PR-10001 for fire alarm system details | 3
F17-HU-422 | 2000-F17-PID-PR-10001 | FLOTATION TAILINGS THICKENER FEED BOX VALVE HYDRAULIC POWER UNIT | N/A | [5 empty] | 14.1 | X | X | XV17009_OP or XV17009_CL | XV17009 Opened for 5 seconds OR | [10 empty] | see Misc tab for XV17009_OP and XV17009_CL (valve open / close logic) | 3 |  |  |  |  | VV 08/07/2026; 1 Hr uncoupled Run started/completed with Remote Start =Success; Local Start = Failed; Sparkys will have a look at it
[13 empty] | XV17009 Closed for 5 seconds | 1 | F17-HU-422 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F17-HU-422 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F17-HU-422 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F17-HU-422 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F17-HU-422 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | VV - 07/07/2026 ; N/A Interlock still functions as per design - AP 29/07/2026
[14 empty] | 6 | F17-HU-422 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F17-HU-422 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | PI17140 ≥ A_HH | 5 |  |  | X |  |  | X |  | Hydraulic supply pressure | 3
[14 empty] | 9 | TI17141 ≥ A_HH | 5 |  |  | X |  |  | X |  | Hydraulic reservoir temperature | 3
[14 empty] | 10 | LI17142 ≤ A_LL | 5 |  |  | X |  |  | X |  | Hydraulic reservoir level | 3
[14 empty] | 11 | ZSH17144 Inactive | 5 |  |  | X |  |  | X |  | Suction valve limit switch | 3
[14 empty] | 12 | PSL24651 InActive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated. 3-second damper applied to prevent trip due to thermal expansion Refer to 2000-F24-LST-PR-10001 for fire alarm system details | 3
F17-PO-409 | 2000-ME001.5-E02-50002 | FLOTATION TAILINGS THICKENER RAKE LIFT PUMP | DOL | [5 empty] | 4.8 | X | X | Started manually by the operator | Stopped manually by the operator | [10 empty] | F17PO409 to be Running 5 seconds prior to energising SV17047 OR SV17048 to ensure adequate hydraulic pressure in hydraulic pack. | 1 |  |  |  |  | VV 07/07/2026; 1 Hr uncoupled Run started/completed
[12 empty] | F17TH401_LCL Active AND (HS17065A Active OR HS17065B Active) | F17TH401_LCL Active AND (HS17065A Released (Falling Edge) OR HS17065B Released (Falling Edge)) AND F17PO409_RT1 Elapsed | 1 | F17-PO-409 Comms Failure | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | 04080104LC2 is HS17065A missed?
[12 empty] | AUTO MODE (F17-TH-401) Active AND (NI17030 < P_Lo OR NI17030 >= P_Hi) AND F17PO408 Running AND SV17033 Energised | AUTO MODE (F17-TH-401) Active AND F17PO409_RT1 Elapsed AND NI17030<P_LO AND ZSL17015 triggered AND 'F17TH401_LCL NOT Active | 2 | F17-PO-409 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 3
[14 empty] | 3 | F17-PO-409 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F17-PO-409 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F17-PO-409 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | VV - 05/07/2026 ; N/A Interlock still works as per design - AP 29/07/2026
[14 empty] | 6 | F17-PO-409 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F17-PO-409 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | XA17060 Inactive | 0 |  |  |  | X |  |  | X | Flotation Tailings Thickener E-Stop Active | 3
[14 empty] | 9 | LSLL17043 Inactive | 3 |  |  |  | X |  |  |  | Hydraulic oil tank level low low switch. | 3
[14 empty] | 10 | TSHH17044 Inactive | 3 |  |  |  | X |  |  |  | Hydraulic oil tank temperature high high switch. | 3
[14 empty] | 11 | F17TH401 Not in Forward Mode | 3 |  |  | X |  |  | X |  | Logic: F17PO408 NOT RUNNING AND SV17033 DE-ENERGISED Disable ability to lower/raise rakes if thickener is not in FORWARD mode and rakes are turning. | 2
[14 empty] | 12 | PSL24651 InActive | 3 |  |  |  | X |  |  |  | Fire check valve alarm activated. 3-second damper applied to prevent trip due to thermal expansion Refer to 2000-F24-LST-PR-10001 for fire alarm system details | 3
[14 empty] | 13 | ZSH17014 Inactive AND SV17048 OPEN AND F17-PO-409 RUNNING | 3 |  |  | X |  |  | X |  |  | 3
[14 empty] | 14 | ZSL17015 Inactive AND SV17047 OPEN AND F17-PO-409 RUNNING | 3 |  |  | X |  |  | X |  |  | 3
F16-PS-411 | 2000-F16-PID-PR-10001 | FLOTATION AREA SUMP PUMP 1 | DOL SP | [5 empty] | 93.7 | X | X | LSH16041 ACTIVE | LSH16041 INACTIVE for 600 seconds | [11 empty] | 3 |  |  |  |  | is 600 seconds too long?
[12 empty] | Manually started by Operator | Manually stopped by Operator | 1 | F16-PS-411 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-PS-411 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-PS-411 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-PS-411 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-PS-411 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-PS-411 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-PS-411 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | F16-AG-421 NOT RUNNING | 5 |  |  | X |  |  | X |  | Rougher Flotation Cell 1 Not Running. Bypass if not intended destination. | B
[14 empty] | 9 | F17TH401 NOT RUNNING | 5 |  |  | X |  |  | X |  | Logic: F17PO408 Not Running AND SV17033 Not Energised Bypass if not intended destination. | C
[14 empty] | 10 | NI17030 >= A_HH | 5 |  |  | X |  |  | X |  | F17TH401 Torque High High Bypass if not intended destination. | C
F16-PS-412 | 2000-F16-PID-PR-10003 | FLOTATION AREA SUMP PUMP 2 | DOL SP | [5 empty] | 93.7 | X | X | LSH16121 ACTIVE | LSH16121 INACTIVE for 420 seconds | [11 empty] | 3 |  |  |  |  | FC 7/7/26 : run on timer changed to match field requirement. Was 600 ,Now set to 420
[14 empty] | 1 | F16-PS-412 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-PS-412 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-PS-412 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-PS-412 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-PS-412 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-PS-412 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-PS-412 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | F16-AG-421 Not Running | 5 |  |  | X |  |  | X |  | Rougher Flotation Cell 1 Not Running. Bypass if not intended destination. | C
[14 empty] | 9 | F17TH401 Not Running | 5 |  |  | X |  |  | X |  | Logic: F17PO408 Not Running AND SV17033 Not Energised Bypass if not intended destination. | C
[14 empty] | 10 | NI17030 >= A_HH | 5 |  |  | X |  |  | X |  | F17TH401 Torque High High Bypass if not intended destination. | C
F16-PS-413 | 2000-F16-PID-PR-10004 | FLOTATION AREA SUMP PUMP 3 | DOL SP | [5 empty] | 93.7 | X | X | LSH16141 ACTIVE | LSH16141 INACTIVE for 420 seconds | [11 empty] | 3
[14 empty] | 1 | F16-PS-413 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-PS-413 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-PS-413 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-PS-413 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-PS-413 MCC Unhealthy | 0 |  |  |  | X |  |  |  | N/A | C |  |  |  |  | VV-10/06/2026 ; NA
[14 empty] | 6 | F16-PS-413 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-PS-413 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | F16-AG-421 Not Running | 5 |  |  | X |  |  | X |  | Rougher Flotation Cell 1 Not Running. Bypass if not intended destination. | C
[14 empty] | 9 | F17TH401 Not Running | 5 |  |  | X |  |  | X |  | Logic: F17PO408 Not Running AND SV17033 Not Energised Bypass if not intended destination. | C
[14 empty] | 10 | NI17030 >= A_HH | 5 |  |  | X |  |  | X |  | F17TH401 Torque High High Bypass if not intended destination. | C
F17-PS-427 | 2000-F17-PID-PR-10001 | FLOTATION TAILINGS THICKENER AREA SUMP PUMP | DOL SP | [5 empty] | 128 | X | X | LSH17081 ACTIVE | LSH17081 INACTIVE for 60 seconds | [11 empty] | 3 |  |  |  |  | is 600 seconds too long?
[14 empty] | 1 | F17-PS-427 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F17-PS-427 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F17-PS-427 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F17-PS-427 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F17-PS-427 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | VV-10/06/2026 ; NA
[14 empty] | 6 | F17-PS-427 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F17-PS-427 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | F17TH401 Not Running | 5 |  |  | X |  |  | X |  | Logic: F17PO408 Not Running AND SV17033 Not Energised Bypass at discretion of Operator. | C
[14 empty] | 9 | NI17030 >= A_HH | 5 |  |  | X |  |  | X |  | F17TH401 Torque High High Bypass at discretion of Operator. | C
F18-PS-501 | 2000-F18-PID-PR-10001 | CLEANER AREA SUMP PUMP | DOL SP | [5 empty] | 51.6 | X | X | LSH18041 ACTIVE | LSH18041 INACTIVE for 20 seconds | [11 empty] | 3
[14 empty] | 1 | F18-PS-501 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F18-PS-501 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F18-PS-501 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F18-PS-501 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F18-PS-501 MCC Unhealthy | 0 |  |  |  | X |  |  |  | N/A | C
[14 empty] | 6 | F18-PS-501 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F18-PS-501 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-PP-629 | 2000-F16-PID-PR-10001 | ROUGHER 1 CONCENTRATE CLEANER FEED SAMPLE PUMP | VSD | 0 | 100 | % | 40 | 100 | 9.83 | X |  | Manually started by CRO | Manually stopped by CRO
[14 empty] | 1 | F16-PP-629 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-PP-629 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-PP-629 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-PP-629 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-PP-629 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | Undervoltage for MCC unhealthy, check when isolated. AP 29/07/2026
[14 empty] | 6 | F16-PP-629 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-PP-629 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | XSH16042 Inactive | 3 |  |  | X |  |  | X |  | Burst hose detection. | 3
[14 empty] | 9 | XV16025 Closed | 5 |  |  | X |  |  | X |  | Rougher 1 Final Concentrate Launder Gate Closed | 3
F16-PP-630 | 2000-F16-PID-PR-10001 | ROUGHER 1 FINAL CONCENTRATE SAMPLE PUMP | VSD | 0 | 100 | % | 40 | 100 | 9.83 | X |  | Manually started by CRO | Manually stopped by CRO | [16 empty] | Has this drive been run?
[14 empty] | 1 | F16-PP-630 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-PP-630 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-PP-630 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-PP-630 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-PP-630 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | Undervoltage for MCC unhealthy, check when isolated. AP 29/07/2026
[14 empty] | 6 | F16-PP-630 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-PP-630 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | XSH16043 Inactive | 3 |  |  | X |  |  | X |  | Burst hose detection. | 3
[14 empty] | 9 | XV16026 Closed | 5 |  |  | X |  |  | X |  | Rougher 1 Final Concentrate Launder Gate Closed | 3
F16-PP-631 | 2000-F16-PID-PR-10002 | ROUGHER 2 & 3 CONCENTRATE SAMPLE PUMP | VSD | 0 | 100 | % | 40 | 100 | 9.83 | X |  | Manually started by CRO | Manually stopped by CRO | [16 empty] | Has this drive been run?
[14 empty] | 1 | F16-PP-631 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-PP-631 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-PP-631 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-PP-631 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-PP-631 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-PP-631 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-PP-631 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | XSH16044 Inactive | 3 |  |  | X |  |  | X |  | Burst hose detection. | 3
F16-PP-515 | 2000-F16-PID-PR-10003 | FLOTATION CELLS DRAIN PUMP | DOL | [5 empty] | 128 | X |  | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1
[14 empty] | 1 | F16-PP-515 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-PP-515 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-PP-515 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-PP-515 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-PP-515 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-PP-515 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-PP-515 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SV16357 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve in auto | 3
[14 empty] | 9 | FSL16358 Inactive AND F16-PP-515 RUNNING | 25 |  |  | X |  |  | X |  | Gland water flow low switch active. | 3
[14 empty] | 10 | F17TH401 Not Running | 5 |  |  | X |  |  | X |  | Logic: F17PO408 Not Running AND SV17033 Not Energised Bypass at discretion of Operator. | C
[14 empty] | 11 | NI17030 >= A_HH | 5 |  |  | X |  |  | X |  | F17TH401 Torque High High Bypass at discretion of Operator. | C
[14 empty] | 12 | XV16123 Open | 3 |  |  | X |  |  | X |  | F16-PP-515 Suction Drain Valve open | 3
[14 empty] | 13 | XV16122 Closed | 3 |  |  | X |  |  | X |  | F16-PP-515 Suction Valve closed | 3
F16-PP-632 | 2000-F16-PID-PR-10004 | SCAVENGER CONCENTRATE SAMPLE PUMP | VSD | 0 | 100 | % | 40 | 100 | 9.83 | X |  | Manually started by CRO | Manually stopped by CRO | [16 empty] | Has this drive been run?
[14 empty] | 1 | F16-PP-632 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-PP-632 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-PP-632 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-PP-632 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-PP-632 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-PP-632 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-PP-632 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | XSH16045 Inactive | 3 |  |  | X |  |  | X |  | Burst hose detection. | 3
F16-PP-633 | 2000-F16-PID-PR-10004 | SCAVENGER TAILS SAMPLE PUMP | VSD | 0 | 100 | % | 40 | 100 | 9.83 | X |  | Manually started by CRO | Manually stopped by CRO | [16 empty] | Confitm motor nameplate current, has this drive been run?
[14 empty] | 1 | F16-PP-633 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-PP-633 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-PP-633 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-PP-633 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-PP-633 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-PP-633 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-PP-633 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | XSH16046 Inactive | 3 |  |  | X |  |  | X |  | Burst hose detection. | 3
F16-PP-638 | 2000-F16-PID-PR-10005 | SAMPLE RETURN PUMP 1 | VSD | 0 | 100 | % | 40 | 100 | 51.4 | X | X | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1 |  |  |  |  | Confitm motor nameplate current, has this drive been run?
[14 empty] | 1 | F16-PP-638 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-PP-638 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-PP-638 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-PP-638 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-PP-638 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | looking at undervoltage? Needs to be checked when drive is isolated - AP 29/07/2026
[14 empty] | 6 | F16-PP-638 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-PP-638 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SV16155 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve in auto | 3
[14 empty] | 9 | FSL16156 Inactive AND F16-PP-638 RUNNING | 25 |  |  | X |  |  | X |  | Gland water flow low switch active. | 3
[14 empty] | 10 | XV16152 Closed | 3 |  |  | X |  |  | X |  | Suction valve closed | 2
[14 empty] | 11 | XV16153 Open | 3 |  |  | X |  |  | X |  | Suction-drain open | 2
[14 empty] | 12 | LIC16151 <= A_LL | 5 |  |  | X |  |  | X |  | Sample Return Hopper 1 Level Low Low | 2
[14 empty] | 13 | F16PP638_II >= A_HH | 10 |  |  | X |  |  | X |  | High current trip HAZOP Action Node F16-03.1.8 Alarm setpoint estimated as 150% FLC. TBC with operating data | 4
F16-PP-639 | 2000-F16-PID-PR-10005 | SAMPLE RETURN PUMP 2 | VSD | 0 | 100 | % | 40 | 100 | 51.4 | X | X | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1 |  |  |  |  | Confitm motor nameplate current, has this drive been run?
[14 empty] | 1 | F16-PP-639 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-PP-639 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-PP-639 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-PP-639 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-PP-639 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C |  |  |  |  | looking at undervoltage? Needs to be checked when drive is isolated - AP 29/07/2026
[14 empty] | 6 | F16-PP-639 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-PP-639 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SV16165 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve in auto | 3
[14 empty] | 9 | FSL16166 Inactive AND F16-PP-639 RUNNING | 25 |  |  | X |  |  | X |  | Gland water flow low switch active. | 3
[14 empty] | 10 | XV16162 Closed | 3 |  |  | X |  |  | X |  | Suction valve closed | 2
[14 empty] | 11 | XV16163 Open | 3 |  |  | X |  |  | X |  | Suction-drain open | 2
[14 empty] | 12 | LIC16161 <= A_LL | 5 |  |  | X |  |  | X |  | Sample Return Hopper 2 Level Low Low | 2
[14 empty] | 13 | F16PP639_II >= A_HH | 10 |  |  | X |  |  | X |  | High current trip HAZOP Action Node F16-03.1.8 Alarm setpoint estimated as 150% FLC. TBC with operating data | 4
F16-AN-403 | 2000-F16-PID-PR-10005 | ONSTREAM ANALYSER | FE | [5 empty] | - |  | X | Vendor PLC | Vendor PLC | [11 empty] | 1
[14 empty] | 1 | F16-AN-403 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-AN-403 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-AN-403 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-AN-403 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-AN-403 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-AN-403 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-AN-403 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-AN-402 | 2000-F16-PID-PR-10005 | FLOTATION PARTICLE SIZE ANALYSER | FE | [5 empty] | - |  | X | Vendor PLC | Vendor PLC | [11 empty] | 1
[14 empty] | 1 | F16-AN-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-AN-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-AN-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-AN-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-AN-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-AN-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-AN-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F16-PP-634 | 2000-F17-PID-PR-10001 | FINAL TAILS SAMPLE PUMP | VSD | 0 | 100 | % | 40 | 100 | 9.83 | X |  | Manually started by CRO | Manually stopped by CRO | [16 empty] | Confitm motor nameplate current, has this drive been run?
[14 empty] | 1 | F16-PP-634 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F16-PP-634 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F16-PP-634 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F16-PP-634 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F16-PP-634 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F16-PP-634 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F16-PP-634 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | XSH17008 Inactive | 3 |  |  | X |  |  | X |  | Burst hose detection. | 3
[14 empty] | 9 | XV17005 Closed | 3 |  |  | X |  |  | X |  | Suction Valve Closed | 3
[14 empty] | 10 | XV17006 Open | 3 |  |  | X |  |  | X |  | Suction Drain Valve Open | 2
F17-FN-504 | 2000-F17-PID-PR-10002 | FLOTATION TAILINGS THICKENER UNDERFLOW TUNNEL VENTILATION FAN | DOL | [5 empty] | 4.27 | X |  | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1
[14 empty] | 1 | F17-FN-504 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F17-FN-504 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F17-FN-504 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F17-FN-504 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F17-FN-504 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F17-FN-504 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F17-FN-504 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F17-PP-455 | 2000-F17-PID-PR-10002 | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 1 | VSD | 0 | 100 | % | 40 | 100 | 165 | X | X | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1
[12 empty] | F17-SEQ-0001 | F17-SEQ-0002 | 1 | F17-PP-455 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F17-PP-455 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F17-PP-455 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F17-PP-455 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F17-PP-455 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F17-PP-455 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F17-PP-455 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SV17104 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve in auto | 3
[14 empty] | 9 | FI17105 <= A_LL AND F17-PP-455 RUNNING | 25 |  |  | X |  |  | X |  | Gland water flow low low alarm. | 3
[14 empty] | 10 | [(XV17091 Closed OR XV17093 Closed) AND XV17095 Closed] OR [(F24-PW-417 Not Running AND F24-PW-418 Not Running AND XV17095 Open AND (XV17091 Closed OR XV17093 Closed)] | 3 |  |  | X |  |  | X |  | Suction valve closed U/F Suction Path Closed | 3
[14 empty] | 11 | XV17102 Open | 3 |  |  | X |  |  | X |  | Suction-drain open | 3
[14 empty] | 12 | XV17103 Closed | 3 |  |  | X |  |  | X |  | Discharge valve closed | 3
[14 empty] | 13 | XV17123 Closed & XV17125 Closed | 3 |  |  | X |  |  | X |  | Common discharge and Recirculation discharge valves closed | 3
[14 empty] | 14 | U/F Destination Valves Closed | 3 |  |  | X |  |  | X |  | Logic (SP1): XV17125 Closed AND FCV17127 Closed AND FCV17128 Closed AND FCV17130 Closed AND XV17132 Closed Logic (SP2): XV17125 Closed All destination valves closed. | 4
[14 empty] | 15 | PI17122 >= A_HH | 5 |  |  | X |  |  | X |  | Discharge manifold pressure high high alarm. | 2
[14 empty] | 16 | FIC17121 <= A_LL AND F17-PP-455 RUNNING | 60 |  |  | X |  |  | X |  | Discharge manifold flow low low alarm. | 3 |  |  |  |  | VV 08/07/2026 with 10S timer for pump running prior to tripping
[14 empty] | 17 | F17-PP-456 Running | 3 |  |  | X |  |  | X |  | Prevent start-up or interlock pump if standby is running. | 3
[14 empty] | 18 | XV17113 Open | 3 |  |  | X |  |  | X |  | Prevent start-up or interlock pump if standby discharge valve is open. | 2
[14 empty] | 19 | TI17100 >=A_HH | 5 |  |  | X |  |  | X |  | Gear Box Termperature Transmitter Hi-Hi Alarm | 4
F17-PP-456 | 2000-F17-PID-PR-10002 | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 2 | VSD | 0 | 100 | % | 40 | 100 | 165 | X | X | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1
[12 empty] | F17-SEQ-0001 | F17-SEQ-0002 | 1 | F17-PP-456 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F17-PP-456 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F17-PP-456 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F17-PP-456 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F17-PP-456 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F17-PP-456 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F17-PP-456 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SV17114 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve in auto | 3
[14 empty] | 9 | FI17115 <= A_LL AND F17-PP-456 RUNNING | 25 |  |  | X |  |  | X |  | Gland water flow low low alarm | 3
[14 empty] | 10 | [(XV17092 Closed OR XV17094 Closed) AND XV17096 Closed] OR [(F24-PW-417 Not Running AND F24-PW-418 Not Running AND XV17096 Open AND (XV17092 Closed OR XV17094 Closed)] | 3 |  |  | X |  |  | X |  | Suction valve closed U/F Suction Path Closed | 2
[14 empty] | 11 | XV17112 Open | 3 |  |  | X |  |  | X |  | Suction-drain open | 2
[14 empty] | 12 | XV17113 Closed | 3 |  |  | X |  |  | X |  | Discharge valve closed | 2
[14 empty] | 13 | XV17123 Closed & XV17125 Closed | 3 |  |  | X |  |  | X |  | Logic: XV17123 Closed AND XV17125 Closed Common discharge and Recirculation discharge valves closed | 2
[14 empty] | 14 | U/F Destination Valves Closed | 3 |  |  | X |  |  | X |  | Logic (SP1): XV17125 Closed AND FCV17127 Closed AND FCV17128 Closed AND FCV17130 Closed AND XV17132 Closed Logic (SP2): XV17125 Closed All destination valves closed. | 4
[14 empty] | 15 | PI17122 >= A_HH | 5 |  |  | X |  |  | X |  | Discharge manifold pressure high high alarm. | 2
[14 empty] | 16 | FIC17121 <= A_LL AND F17-PP-456 RUNNING | 60 |  |  | X |  |  | X |  | Discharge manifold flow low low alarm. | 3
[14 empty] | 17 | F17-PP-455 Running | 3 |  |  | X |  |  | X |  | Prevent start-up or interlock pump if standby is running. | 2
[14 empty] | 18 | XV17103 Open | 3 |  |  | X |  |  | X |  | Prevent start-up or interlock pump if standby discharge valve is open. | 2
[14 empty] | 19 | TI17110 >= A_HH | 5 |  |  | X |  |  | X |  | Gear Box Termperature Transmitter Hi-Hi Alarm | 4
F18-PP-407 | 2000-F18-PID-PR-10001 | FINAL CONCENTRATE PUMP 1 | VSD | 0 | 100 | % | 40 | 100 | 218 | X | X | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1
[12 empty] | F18-SEQ-0001 | F18-SEQ-0002 | 1 | F18-PP-407 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F18-PP-407 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F18-PP-407 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F18-PP-407 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F18-PP-407 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F18-PP-407 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F18-PP-407 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SV18500 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve in auto | 3
[14 empty] | 9 | FSL18501 Inactive AND F18-PP-407 RUNNING | 25 |  |  | X |  |  | X |  | Gland water flow low switch active. | 3
[14 empty] | 10 | XV18021 Closed | 3 |  |  | X |  |  | X |  | Suction valve closed | 2
[14 empty] | 11 | XV18022 Open | 3 |  |  | X |  |  | X |  | Suction-drain open | 2
[14 empty] | 12 | XV18023 Closed | 3 |  |  | X |  |  | X |  | Discharge valve closed | 2
[14 empty] | 13 | LIC18001A <= A_LL | 5 |  |  | X |  |  | X |  | Hopper level low low | 3
[14 empty] | 14 | F30TH61 Bypass and Feed Tanks HH | 300 |  |  | X |  |  | X |  | Logic: ZSO30444 ACTIVE AND LI3502 >= A_HH AND LI3503 >= A_HH Concentrate Thickener bypass valve open and Filter Feed Tank A Level High High and Filter Feed Tank B Level High-High. | 3
[14 empty] | 15 | F30TH61 Torque HH | 120 |  |  | X |  |  | X |  | Logic: NAHH30602 Active AND ZIO30443 Active Trip Final Concentrate Pump if Concentrate Thickener F30-TH-61 torque High-High is active. NAHH30602 and ZIO30443 is repurposed (brownfields). | 3
[14 empty] | 16 | FI18027 <= A_LL AND F18-PP-407 RUNNING | 60 |  |  | X |  |  | X |  | Final Concentrate Discharge Flow Low Low | 3
F18-PP-408 | 2000-F18-PID-PR-10001 | FINAL CONCENTRATE PUMP 2 | VSD | 0 | 100 | % | 40 | 100 | 218 | X | X | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1
[12 empty] | F18-SEQ-0001 | F18-SEQ-0002 | 1 | F18-PP-408 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F18-PP-408 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F18-PP-408 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F18-PP-408 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F18-PP-408 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F18-PP-408 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F18-PP-408 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SV18504 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve in auto | 3
[14 empty] | 9 | FSL18505 Inactive AND F18-PP-408 RUNNING | 25 |  |  | X |  |  | X |  | Gland water flow low switch active. | 3
[14 empty] | 10 | XV18024 Closed | 3 |  |  | X |  |  | X |  | Suction valve closed | 2
[14 empty] | 11 | XV18025 Open | 3 |  |  | X |  |  | X |  | Suction-drain open | 2
[14 empty] | 12 | XV18026 Closed | 3 |  |  | X |  |  | X |  | Discharge valve closed | 2
[14 empty] | 13 | LIC18001A <= A_LL | 5 |  |  | X |  |  | X |  | Hopper level low low | 3
[14 empty] | 14 | F30TH61 Bypass and Feed Tanks HH | 300 |  |  | X |  |  | X |  | Logic: ZIO30444 ACTIVE AND LI3502 >= A_HH AND LI3503 >= A_HH Concentrate Thickener bypass valve open and Filter Feed Tank A Level High High and Filter Feed Tank B Level High-High. | 3
[14 empty] | 15 | F30TH61 Torque HH | 120 |  |  | X |  |  | X |  | Logic: NAHH30602 Active AND ZIO30443 Active Trip Final Concentrate Pump if Concentrate Thickener F30-TH-61 torque High-High is active. NAHH30602 and ZIO30443 is repurposed (brownfields). | 3
[14 empty] | 16 | FI18027 <= A_LL AND F18-PP-408 RUNNING | 60 |  |  | X |  |  | X |  | Final Concentrate Discharge Flow Low Low | 3
F18-PP-501 | 2000-F18-PID-PR-10001 | CLEANER FLOTATION CELL RECIRCULATION PUMP 1 | VSD | 0 | 100 | % | 40 | 100 | 776 | X | X | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1 |  |  |  |  | Confirm current on motor nameplate - AP
[12 empty] | F18-SEQ-0003 | F18-SEQ-0004 | 1 | F18-PP-501 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F18-PP-501 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F18-PP-501 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F18-PP-501 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F18-PP-501 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F18-PP-501 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F18-PP-501 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SV18508 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve in auto | 3
[14 empty] | 9 | FSL18509 Inactive AND F18-PP-501 RUNNING | 25 |  |  | X |  |  | X |  | Gland water flow low switch active. | 3
[14 empty] | 10 | XV18031 Closed | 3 |  |  | X |  |  | X |  | Suction valve closed | 2
[14 empty] | 11 | XV18032 Open | 3 |  |  | X |  |  | X |  | Suction-drain open | 2
[14 empty] | 12 | XV18033 Closed | 3 |  |  | X |  |  | X |  | Discharge valve closed | 2
[14 empty] | 13 | LIC18011A <= A_LL | 5 |  |  | X |  |  | X |  | Hopper level low low | 3
[14 empty] | 14 | PI18054 <= A_LL AND F18-PP-501 RUNNING | 60 |  |  | X |  |  | X |  | Cleaner Flotation Cell Slurry Distributor Pressure Low-Low (indicating the feed line prior to distributor is blocked) | 3 |  |  |  |  | jwho 16/08/2026 - Removed - Justin DM
[14 empty] | 15 | PI18054 >= A_HH | 5 |  |  | X |  |  | X |  | Cleaner Flotation Cell Slurry Distributor Pressure High-High (indicating distributor is blocked) | C
[14 empty] | 16 | FIC18037 <= A_LL AND F18-PP-501 RUNNING | 60 |  |  | X |  |  | X |  | Cleaner Flotation Cell Recirculation Pump Discharge Flow Low Low | 3
[14 empty] | 17 | LIC18051 >= A_HH | 10 |  |  | X |  |  | X |  | Cleaner Flotation Cell Level High High | C |  |  |  |  | MOC 658
[14 empty] | 18 | TI18542A >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase U. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 19 | TI18542B >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase V. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 20 | TI18542C >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase W. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 21 | TI18542D >= A_HH | 5 |  |  |  | X |  |  |  | DE Bearing. Drive-End bearing temperature high high | C
[14 empty] | 22 | TI18542E >= A_HH | 5 |  |  |  | X |  |  |  | NDE Bearing. Non-Drive End bearing temperature high high. | C
[14 empty] | 23 | XV18052 Not Closed | 3 |  |  | X |  |  | X |  | Cleaner Flotation Cell Drain Valve Open | 5 |  |  |  |  | PCR (number pending) - AP 30/08/2026
F18-PP-502 | 2000-F18-PID-PR-10001 | CLEANER FLOTATION CELL RECIRCULATION PUMP 2 | VSD | 0 | 100 | % | 40 | 100 | 776 | X | X | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1 |  |  |  |  | Confirm current on motor nameplate - AP
[12 empty] | F18-SEQ-0003 | F18-SEQ-0004 | 1 | F18-PP-502 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F18-PP-502 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F18-PP-502 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F18-PP-502 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F18-PP-502 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F18-PP-502 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F18-PP-502 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SV18512 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve in auto | 3
[14 empty] | 9 | FSL18513 Inactive AND F18-PP-502 RUNNING | 25 |  |  | X |  |  | X |  | Gland water flow low switch active. | 3
[14 empty] | 10 | XV18034 Closed | 3 |  |  | X |  |  | X |  | Suction valve closed | 2
[14 empty] | 11 | XV18035 Open | 3 |  |  | X |  |  | X |  | Suction-drain open | 2
[14 empty] | 12 | XV18036 Closed | 3 |  |  | X |  |  | X |  | Discharge valve closed | 2
[14 empty] | 13 | LIC18011A <= A_LL | 5 |  |  | X |  |  | X |  | Hopper level low low | 3
[14 empty] | 14 | PI18054 <= A_LL AND F18-PP-502 RUNNING | 60 |  |  | X |  |  | X |  | Cleaner Flotation Cell Slurry Distributor Pressure Low-Low (indicating the feed line prior to distributor is blocked) | 3 |  |  |  |  | jwho - 16/08/2026 Removed - Justin DM
[14 empty] | 15 | PI18054 >= A_HH | 5 |  |  | X |  |  | X |  | Cleaner Flotation Cell Slurry Distributor Pressure High-High (indicating distributor is blocked) | C
[14 empty] | 16 | FIC18037 <= A_LL AND F18-PP-502 RUNNING | 60 |  |  | X |  |  | X |  | Cleaner Flotation Cell Recirculation Pump Discharge Flow Low Low | 3
[14 empty] | 17 | LIC18051 >= A_HH | 10 |  |  | X |  |  | X |  | Cleaner Flotation Cell Level High High | C |  |  |  |  | MOC 658
[14 empty] | 18 | TI18543A >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase U. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 19 | TI18543B >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase V. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 20 | TI18543C >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase W. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 21 | TI18543D >= A_HH | 5 |  |  |  | X |  |  |  | DE Bearing. Drive-End bearing temperature high high | C
[14 empty] | 22 | TI18543E >= A_HH | 5 |  |  |  | X |  |  |  | NDE Bearing. Non-Drive End bearing temperature high high. | C
[14 empty] | 23 | XV18052 Not Closed | 3 |  |  | X |  |  | X |  | Cleaner Flotation Cell Drain Valve Open | 5 |  |  |  |  | PCR (number pending) - AP 30/08/2026
F18-PP-511 | 2000-F18-PID-PR-10003 | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 1 | VSD | 0 | 100 | % | 40 | 100 | 776 | X | X | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1 |  |  |  |  | Confirm current on motor nameplate - AP
[12 empty] | F18-SEQ-0005 | F18-SEQ-0006 | 1 | F18-PP-511 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F18-PP-511 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F18-PP-511 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F18-PP-511 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F18-PP-511 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F18-PP-511 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F18-PP-511 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SV18524 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve in auto | 3
[14 empty] | 9 | FSL18525 Inactive AND F18-PP-511 RUNNING | 25 |  |  | X |  |  | X |  | Gland water flow low switch active. | 3
[14 empty] | 10 | XV18221 Closed | 3 |  |  | X |  |  | X |  | Suction valve closed | 2
[14 empty] | 11 | XV18222 Open | 3 |  |  | X |  |  | X |  | Suction-drain open | 2
[14 empty] | 12 | XV18223 Closed | 3 |  |  | X |  |  | X |  | Discharge valve closed | 2
[14 empty] | 13 | LIC18201A <= A_LL | 5 |  |  | X |  |  | X |  | Hopper level low low | 3
[14 empty] | 14 | FIC18227 <= A_LL AND F18-PP-511 RUNNING | 60 |  |  | X |  |  | X |  | Flow alarm low low | 3
[14 empty] | 15 | PI18254 <= A_LL AND F18-PP-511 RUNNING | 60 |  |  | X |  |  | X |  | Cleaner-Scavenger Flotation Cell Slurry Distributor Pressure Low-Low (indicating the feed line prior to distributor is blocked) | 3 | [5 empty] | jwho - removed 16/08/2026
[14 empty] | 16 | PI18254 >= A_HH | 5 |  |  | X |  |  | X |  | Cleaner-Scavenger Flotation Cell Slurry Distributor Pressure High-High (indicating distributor is blocked) | C
[14 empty] | 17 | TI18546A >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase U. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 18 | TI18546B >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase V. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 19 | TI18546C >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase W. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 20 | TI18546D >= A_HH | 5 |  |  |  | X |  |  |  | DE Bearing. Drive-End bearing temperature high high | C
[14 empty] | 21 | TI18546E >= A_HH | 5 |  |  |  | X |  |  |  | NDE Bearing. Non-Drive End bearing temperature high high. | C
[14 empty] | 23 | XV18252 Not Closed | 3 |  |  | X |  |  | X |  | Cleaner Scavenger Flotation Cell Drain Valve Open | 5 |  |  |  |  | PCR (number pending) - AP 30/08/2026
F18-PP-512 | 2000-F18-PID-PR-10003 | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 2 | VSD | 0 | 100 | % | 40 | 100 | 776 | X | X | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1 |  |  |  |  | Confirm current on motor nameplate - AP
[12 empty] | F18-SEQ-0005 | F18-SEQ-0006 | 1 | F18-PP-512 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F18-PP-512 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F18-PP-512 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F18-PP-512 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F18-PP-512 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F18-PP-512 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F18-PP-512 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SV18528 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve in auto | 3
[14 empty] | 9 | FSL18529 Inactive AND F18-PP-512 RUNNING | 25 |  |  | X |  |  | X |  | Gland water flow low switch active. | 3
[14 empty] | 10 | XV18224 Closed | 3 |  |  | X |  |  | X |  | Suction valve closed | 2
[14 empty] | 11 | XV18225 Open | 3 |  |  | X |  |  | X |  | Suction-drain open | 2
[14 empty] | 12 | XV18226 Closed | 3 |  |  | X |  |  | X |  | Discharge valve closed | 2
[14 empty] | 13 | LIC18201A <= A_LL | 5 |  |  | X |  |  | X |  | Hopper level low low | 3
[14 empty] | 14 | FIC18227 <= A_LL AND F18-PP-512 RUNNING | 60 |  |  | X |  |  | X |  | Flow alarm low low | 3
[14 empty] | 15 | PI18254 <= A_LL AND F18-PP-512 RUNNING | 60 |  |  | X |  |  | X |  | Cleaner-Scavenger Flotation Cell Slurry Distributor Pressure Low-Low (indicating the feed line prior to distributor is blocked) | 3 | [5 empty] | jwho - 16/08/2026 Removed
[14 empty] | 16 | PI18254 >= A_HH | 5 |  |  | X |  |  | X |  | Cleaner-Scavenger Flotation Cell Slurry Distributor Pressure High-High (indicating distributor is blocked) | C
[14 empty] | 17 | TI18547A >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase U. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 18 | TI18547B >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase V. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 19 | TI18547C >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase W. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 20 | TI18547D >= A_HH | 5 |  |  |  | X |  |  |  | DE Bearing. Drive-End bearing temperature high high | C
[14 empty] | 21 | TI18547E >= A_HH | 5 |  |  |  | X |  |  |  | NDE Bearing. Non-Drive End bearing temperature high high. | C
[14 empty] | 23 | XV18252 Not Closed | 3 |  |  | X |  |  | X |  | Cleaner Scavenger Flotation Cell Drain Valve Open | 5 |  |  |  |  | PCR (number pending) - AP 30/08/2026
F18-PP-513 | 2000-F18-PID-PR-10003 | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 1 | VSD | 0 | 100 | % | 66 | 100 | 523 | X | X | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1 |  |  |  |  | Confirm current on motor nameplate - AP
[12 empty] | F18-SEQ-0007 | F18-SEQ-0008 | 1 | F18-PP-513 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F18-PP-513 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F18-PP-513 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F18-PP-513 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F18-PP-513 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F18-PP-513 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F18-PP-513 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SV18532 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve in auto | 3
[14 empty] | 9 | FSL18533 Inactive AND F18-PP-513 RUNNING | 25 |  |  | X |  |  | X |  | Gland water flow low switch active. | 3
[14 empty] | 10 | XV18231 Closed | 3 |  |  | X |  |  | X |  | Suction valve closed | 2
[14 empty] | 11 | XV18232 Open | 3 |  |  | X |  |  | X |  | Suction-drain open | 2
[14 empty] | 12 | XV18233 Closed | 3 |  |  | X |  |  | X |  | Discharge valve closed | 2
[14 empty] | 13 | LIC18211A <= A_LL | 5 |  |  | X |  |  | X |  | Hopper level low low | 2
[14 empty] | 14 | Discharge Locations Closed | 5 |  |  | X |  |  | X |  | Logic: XV18241 Closed AND XV18242 Closed Discharge valve destinations closed. | 2
[14 empty] | 15 | FI18237 <= A_LL AND F18-PP-513 RUNNING | 60 |  |  | X |  |  | X |  | Flow alarm low low | 3
[14 empty] | 16 | LIC18251 >= A_HH | 10 |  |  | X |  |  | X |  | Cleaner-Scavenger Flotation Cell Level High High | C | [5 empty] | jwho 16/08/2026 Removed - Justin DM
[14 empty] | 17 | TI18550A >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase U. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 18 | TI18550B >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase V. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 19 | TI18550C >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase W. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 20 | TI18550D >= A_HH | 5 |  |  |  | X |  |  |  | DE Bearing. Drive-End bearing temperature high high | C
[14 empty] | 21 | TI18550E >= A_HH | 5 |  |  |  | X |  |  |  | NDE Bearing. Non-Drive End bearing temperature high high. | C
F18-PP-514 | 2000-F18-PID-PR-10003 | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 2 | VSD | 0 | 100 | % | 66 | 100 | 523 | X | X | Manually started by CRO | Manually stopped by CRO | [11 empty] | 1 |  |  |  |  | Confirm current on motor nameplate - AP
[12 empty] | F18-SEQ-0007 | F18-SEQ-0008 | 1 | F18-PP-514 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F18-PP-514 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F18-PP-514 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F18-PP-514 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F18-PP-514 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F18-PP-514 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F18-PP-514 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SV18536 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve in auto | 3
[14 empty] | 9 | FSL18537 Inactive AND F18-PP-514 RUNNING | 25 |  |  | X |  |  | X |  | Gland water flow low switch active. | 3
[14 empty] | 10 | XV18234 Closed | 3 |  |  | X |  |  | X |  | Suction valve closed | 2
[14 empty] | 11 | XV18235 Open | 3 |  |  | X |  |  | X |  | Suction-drain open | 2
[14 empty] | 12 | XV18236 Closed | 3 |  |  | X |  |  | X |  | Discharge valve closed | 2
[14 empty] | 13 | LIC18211A <= A_LL | 5 |  |  | X |  |  | X |  | Hopper level low low | 2
[14 empty] | 14 | Discharge Locations Closed | 5 |  |  | X |  |  | X |  | Logic: XV18241 Closed AND XV18242 Closed Discharge valve destinations closed. | 3
[14 empty] | 15 | FI18237 <= A_LL AND F18-PP-514 RUNNING | 60 |  |  | X |  |  | X |  | Flow alarm low low | 3
[14 empty] | 16 | LIC18251 >= A_HH | 10 |  |  | X |  |  | X |  | Cleaner-Scavenger Flotation Cell Level High High | C | [5 empty] | jwho 16/08/2026 Removed - Justin DM
[14 empty] | 17 | TI18551A >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase U. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 18 | TI18551B >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase V. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 19 | TI18551C >= A_HH | 5 |  |  |  | X |  |  |  | RTD Phase W. Resistance Thermocouple Detector to trip drive on temperature high high. | C
[14 empty] | 20 | TI18551D >= A_HH | 5 |  |  |  | X |  |  |  | DE Bearing. Drive-End bearing temperature high high | C
[14 empty] | 21 | TI18551E >= A_HH | 5 |  |  |  | X |  |  |  | NDE Bearing. Non-Drive End bearing temperature high high. | C
67

## 10. Sequence
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION (F16, F17, F18)
2000-F16-LST-PR-10001
SEQUENCES
Seq No. | Seq Description | Step | Action | Tag / Item | Description | Next Step Delay (s) | Step Advance Condition | Comments | Rev | Equipment Permissives | Recovery Seq. No if Step Faults
PLEASE REFER TO SEQUENCE FLOWCHART DOCUMENT (2000-F16-LST-PR-10002)
Operator to get electrician to inspect unit for potential failure

## 11. Calculation
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION (F16, F17, F18)
2000-F16-LST-PR-10001
CALCULATIONS
|  |  | Unit | Inputs |  |  |  | Operator Input | Calc. Value | Manual Input | [5 empty] | C1 Sign Off |  | C2 Sign Off |  | Comments
Tag Name | P&ID | Description (Software Tag Only) |  | # | Tag | Unit | Description |  |  | Nom | Min | Max | Calculation | Comments | Rev | OK | Date | OK | Date
F17CALC0001 | 2000-F17-PID-PR-10001 | F17TH401 Flocc Dilution Ratio | m3/h | 1 | F17XM413_R1 | - | Flocculant Dilution Ratio - User Input | X |  | 10 | 0 | 15 | FIC17001_SP_CALC = (F17XM413_R1 * FI17003_PV) - (FI17003_PV) | Operator input. | 3
|  |  |  | 2 | FI17003_PV | m3/h | Flocculant Flowrate | [7 empty] | 3
|  |  |  | 3 | FIC17001_SP_CALC | m3/h | Mill Water Flowrate Setpoint |  | X | [5 empty] | B
F17CALC0002 | 2000-F17-PID-PR-10002 | F17TH401 UF Dry Solids | t/h | 1 | DNI17121 | %w/w solids | Flotation Tailings Thickener Underflow Density | [5 empty] | WI17121 = FI17121_PV / ((1 / F17TH401_P1) + ( 1 / (DNI17121 / 100) - F17TH401_P2)) | See F17CALC0007 | 2
|  |  |  | 2 | FI17121_PV | m3/h | Flotation Tailings Thickener Underflow Flow Rate | [7 empty] | B
|  |  |  | 3 | F17TH401_P1 | t/m3 | Dry Solids SG (Engineer Input) | X |  | 2.89 | 2 | 3 |  | Engineer input to be input to other calculations around the Flotation Tailings Thickener Underflow, where F17TH401_P1 is specified. | B
|  |  |  | 4 | F17TH401_P2 | t/m3 | Liquid SG (Engineer Input) | X |  | 1.07 | 0.9 | 1.2 |  | Engineer input to be input to other calculations around the Flotation Tailings Thickener Underflow, where F17TH401_P2 is specified. | B
|  |  |  | 5 | WI17121 | t/h | Flotation Tailings Thickener Underflow Dry Solids Mass Flow |  | X | [5 empty] | B
F17CALC0003 | 2000-F17-PID-PR-10002 | F17TH401 UF - CIL2 Dry Solids | t/h | 1 | DNI17121 | %w/w solids | Flotation Tailings Thickener Underflow Density | [5 empty] | WI17127 = FI17127_PV / ((1 / F17TH401_P1) + ( 1 / (DNI17121 / 100) - F17TH401_P2)) | Use same User Input variables from F17CALC0002 above for consistency in mass balance. | 2
|  |  |  | 2 | FI17127_PV | m3/h | Flotation Tailings Thickener Underflow CIL2 Feed Flow rate | [7 empty] | B
|  |  |  | 3 | WI17127 | t/h | Flotation Tailings Thickener Underflow CIL2 Dry Solids Mass Flow |  | X | [5 empty] | B
F17CALC0004 | 2000-F17-PID-PR-10002 | F17TH401 UF - CIL3 Dry Solids | t/h | 1 | DNI17121 | %w/w solids | Flotation Tailings Thickener Underflow Density | [5 empty] | WI17128 = FI17128_PV / ((1 / F17TH401_P1) + ( 1 / (DNI17121 / 100) - F17TH401_P2)) | Use same User Input variables from F17CALC0002 above for consistency in mass balance. | 2
|  |  |  | 2 | FI17128_PV | m3/h | Flotation Tailings Thickener Underflow CIL3 Feed Flow Rate | [7 empty] | B
|  |  |  | 3 | WI17128 | t/h | Flotation Tailings Thickener Underflow CIL3 Dry Solids Mass Flow |  | X | [5 empty] | B
F17CALC0005 | 2000-F17-PID-PR-10002 | F17TH401 UF - Final Tails | m3/h | 1 | FI17130_PV | m3/h | Final Tails Slurry Feed Flow Rate |  | X |  |  |  | FI17130_PV = FI17121_PV - (FI17127_PV + FI17128_PV) |  | 2
|  |  |  | 2 | FI17121_PV | m3/h | Flotation Tailings Thickener Underflow Flow Rate | [7 empty] | B
|  |  |  | 3 | FI17127_PV | m3/h | Flotation Tailings Thickener Underflow CIL2 Feed Flow Rate | [7 empty] | B
|  |  |  | 4 | FI17128_PV | m3/h | Flotation Tailings Thickener Underflow CIL3 Feed Flow Rate | [7 empty] | B
F17CALC0006 | 2000-F17-PID-PR-10002 | F17TH401 UF Dry Solids | t/h | 1 | DNI17121 | %w/w solids | Flotation Tailings Thickener Underflow Density | [5 empty] | WI17130 = FI17130_PV / ((1 / F17TH401_P1) + ( 1 / (DNI17121 / 100) - F17TH401_P2)) | Use same User Input variables from F17CALC0002 above for consistency in mass balance. | 2
|  |  |  | 2 | FI17130_PV | m3/h | Final Tails Feed Flow rate | [7 empty] | B
|  |  |  | 3 | WI17130 | t/h | Final Tails Dry Solids Mass Flow |  | X | [5 empty] | B
F17CALC0007 | 2000-F17-PID-PR-10002 | F17TH401 UF Solids | %w/w solids | 1 | DI17121 | t/m3 | Flotation Tailings Thickener Underflow Feed Slurry SG | [5 empty] | DNI17121 = [(F17TH401_P1 * F17TH401_P2) - (DIT17121 * F17TH401_P1)] / [(DIT17121 * (F17TH401_P2 - F17TH401_P1)]*100 | F17TH401_P1 to be a single input specified within F17 Area for input into other calculations within this sheet. Please see F17CALC0002 for specification. | 3
|  |  |  | 2 | DNI17121 | %w/w solids | Flotation Tailings Thickener Underflow %w/w solids |  | X |  |  |  |  | F17TH401_P2 to be a single input specified within F17 Area for input into other calculations within this sheet. Please see F17CALC0002 for specification. | 2
F18CALC0001 | 2000-F18-PID-PR-10002 | F18CF501 Wash Water Ctrl | m3/h | 1 | FIC18057_SP1 | m3/h | F18CF501 Wash Water Ctrl |  | X |  |  |  | FIC18057_SP1 = F18CF501_Ratio * FI18027_PV | In CASCADE Mode, the setpoint for FIC18057 is provided by this calculation. | 2
|  |  |  | 2 | FI18027_PV | m3/h | Final Concentrate Slurry Flow | [7 empty] | B
|  |  |  | 3 | F18CF501_Ratio | - | Ratio Setpoint | X |  | 0.5 | 0 | 1 |  |  | 3
F18CALC0002 | 2000-F18-PID-PR-10001 | F18PP407/408 Solids | %w/w solids | 1 | DI18027 | t/m3 | Final Concentrate Feed Slurry SG | [5 empty] | DNI18027 = [(F18PP407_Parameter_1 * F18PP407_Parameter_2) - (DIT18027 * F18PP407_Parameter_1)] / [(DIT18027 * (F18PP407_Parameter_2 - F18PP407_Parameter_1)]*100 |  | 3
|  |  |  | 2 | F18PP407_Parameter 1 | t/m3 | Dry Solids SG for that stream (Engineer Input) | X |  | 3.99 | 2 | 4.5 |  | Nominal SG 2.89 | C
|  |  |  | 3 | F18PP407_Parameter 2 | t/m3 | Liquid SG (Engineer Input) | X |  | 1.07 | 0.9 | 1.2 |  |  | C
|  |  |  | 4 | DNI18027 | %w/w solids | Final Concentrate %w/w solids |  | X | [5 empty] | 1
F18CALC0003 | 2000-F18-PID-PR-10003 | F18PP513/514 Solids | %w/w solids | 1 | DI18237 | t/m3 | Cleaner Scavenger Tails Feed Slurry SG | [5 empty] | DNI18237 = [(F18PP513_Parameter_1 * F18PP513_Parameter_2) - (DIT18237 * F18PP513_Parameter_1)] / [(DIT18237 * (F18PP513_Parameter_2 - F18PP513_Parameter_1)]*100 |  | 3
|  |  |  | 2 | F18PP513_Parameter 1 | t/m3 | Dry Solids SG for that stream (Engineer Input) | X |  | 2.87 | 2 | 4 |  |  | B
|  |  |  | 3 | F18PP513_Parameter 2 | t/m3 | Liquid SG (Engineer Input) | X |  | 1.07 | 0.9 | 1.2 |  |  | C
|  |  |  | 4 | DNI18237 | %w/w solids | Cleaner Scavenger Tails %w/w solids |  | X | [5 empty] | B
F18CALC0004 | 2000-F18-PID-PR-10003 | F18PP513/514 Dry Solids tph | t/h | 1 | DNI18237 | %w/w solids | Cleaner Scavenger Tails Density | [5 empty] | WI18237= FI18237_PV / ((1 / F18PP513_Parameter 1) + ( 1 / (DNI18237 / 100) - F18PP513_Parameter 2)) |  | 2
|  |  |  | 2 | FI18237_PV | m3/h | Cleaner Scavenger Tails Feed Flow rate | [7 empty] | B
|  |  |  | 3 | F18PP513_Parameter 1 | t/m3 | Dry Solids SG for that stream (Engineer Input) | X |  | 2.89 | 2 | 3 |  | Nominal SG 2.89 | B
|  |  |  | 4 | F18PP513_Parameter 2 | t/m3 | Liquid SG (Engineer Input) | X |  | 1.07 | 0.9 | 1.2 |  |  | C
|  |  |  | 5 | WI18237 | t/h | Cleaner Scavenger Tails Dry Solids Mass Flow |  | X | [5 empty] | B
F18CALC0005 | 2000-F18-PID-PR-10001 | F18PP407/408 Dry Solids tph | t/h | 1 | DNI18027 | %w/w solids | Final Concentrate Density | [5 empty] | WI18027= FI18027_PV / ((1 / F18PP407_Parameter 1) + ( 1 / (DNI18027 / 100) - F18PP407_Parameter 2)) |  | 2
|  |  |  | 2 | FI18027_PV | m3/h | Final Concentrate Feed Flow rate | [7 empty] | B
|  |  |  | 3 | F18PP407_Parameter 1 | t/m3 | Dry Solids SG for that stream (Engineer Input) | X |  | 3.99 | 2 | 4.5 |  | Nominal SG 3.99 | B
|  |  |  | 4 | F18PP407_Parameter 2 | t/m3 | Liquid SG (Engineer Input) | X |  | 1.07 | 0.9 | 1.2 |  |  | C
|  |  |  | 5 | WI18027 | t/h | Final Concentrate Dry Solids Mass Flow |  | X | [5 empty] | B
F18CALC0006 | 2000-F18-PID-PR-10004 | F18CF511 Wash Water Ctrl | m3/h | 1 | FIC18257_SP1 | m3/h | F18CF501 Wash Water Ctrl |  | X |  |  |  | FIC18257_SP1 = F18CF511_Ratio * (FIC18227_PV - FI18237_PV) | In CASCADE Mode, the setpoint for FIC18257 is provided by this calculation. | 2
|  |  |  | 2 | FIC18227_PV | m3/h | Cleaner-Scavenger Feed Slurry Flow | [7 empty] | C
|  |  |  | 2 | FI18237_PV | m3/h | Cleaner-Scavenger Tails Slurry Flow | [7 empty] | B
|  |  |  | 3 | F18CF511_Ratio | - | Ratio Setpoint | X |  | 0.5 | 0 | 1 |  |  | 3
F18CALC0007 | 2000-F18-PID-PR-10002 | F18CF501 Level | mm | [9 empty] | RV = LIT18051A_PV RV1 = LIT18051B_PV P01 = Compensated Density P01 = (RV - RV1) / 700 if (P01 =< 0.5) then P02 = 0.5 else P02 = P01 end if P03 = RV / P02 if (P03 => 1900) then P04 = 1900 else P04 = P03 end if LNI18051 = 1900 - P04 | Refer to 2000-ME073-M01-10002 for description on calculation. | 2
|  |  |  | 1 | LIT18051A_PV | mm | Cleaner Froth Depth Transmitter A | [7 empty] | B
|  |  |  | 2 | LIT18051B_PV | mm | Cleaner Froth Depth Transmitter B | [7 empty] | B
|  |  |  | 3 | LNI18051 | mm | Froth/Level depth. |  | X | [5 empty] | 1
F18CALC0008 | 2000-F18-PID-PR-10004 | F18CF511 Level | mm | [9 empty] | RV = LIT18251A_PV RV1 = LIT18251B_PV P01 = Compensated Density P01 = (RV - RV1) / 700 if (P01 =< 0.5) then P02 = 0.5 else P02 = P01 end if P03 = RV / PO2 if (P03 => 1900) then P04 = 1900 else P04 = P03 end if LNI18251 = 1900 - P04 | Refer to 2000-ME073-M01-10001 for description on calculation. | 2
|  |  |  | 1 | LIT18251A_PV | mm | Cleaner Froth Depth Transmitter A | [7 empty] | B
|  |  |  | 2 | LIT18251B_PV | mm | Cleaner Froth Depth Transmitter B | [7 empty] | B
|  |  |  | 3 | LNI18251 | mm | Froth/Level depth. |  | X | [5 empty] | 1
F16CALC0009 | 2000-F16-PID-PR-10005 | F16AN403 OSA Sulphur | % | 1 | F16AN403S1Fe | % | F16AN403 S1 Fe | [5 empty] | Define formula in a single location so that updating it once applies the change to all 10 calculation outputs. 1.3678 * F16AN403S#Fe - 10.147 = F16AN403S#SU Where # = 1, 2, 3, 4, 5, 6, 7, 8, 9, 10 |  | 3
|  |  |  | 2 | F16AN403S2Fe | % | F16AN403 S2 Fe | [7 empty] | 3
|  |  |  | 3 | F16AN403S3Fe | % | F16AN403 S3 Fe | [7 empty] | 3
|  |  |  | 4 | F16AN403S4Fe | % | F16AN403 S4 Fe | [7 empty] | 3
|  |  |  | 5 | F16AN403S5Fe | % | F16AN403 S5 Fe | [7 empty] | 3
|  |  |  | 6 | F16AN403S6Fe | % | F16AN403 S6 Fe | [7 empty] | 3
|  |  |  | 7 | F16AN403S7Fe | % | F16AN403 S7 Fe | [7 empty] | 3
|  |  |  | 8 | F16AN403S8Fe | % | F16AN403 S8 Fe | [7 empty] | 3
|  |  |  | 9 | F16AN403S9Fe | % | F16AN403 S9 Fe | [7 empty] | 3
|  |  |  | 10 | F16AN403S10Fe | % | F16AN403 S10 Fe | [7 empty] | 3
|  |  |  | 11 | F16AN403S1SU | % | F16AN403 S1 S |  | X |  |  |  |  | Fe–S relationship to be refined with operational data | 3
|  |  |  | 12 | F16AN403S2SU | % | F16AN403 S2 S |  | X | [5 empty] | 3
|  |  |  | 13 | F16AN403S3SU | % | F16AN403 S3 S |  | X | [5 empty] | 3
|  |  |  | 14 | F16AN403S4SU | % | F16AN403 S4 S |  | X | [5 empty] | 3
|  |  |  | 15 | F16AN403S5SU | % | F16AN403 S5 S |  | X | [5 empty] | 3
|  |  |  | 16 | F16AN403S6SU | % | F16AN403 S6 S |  | X | [5 empty] | 3
|  |  |  | 17 | F16AN403S7SU | % | F16AN403 S7 S |  | X | [5 empty] | 3
|  |  |  | 18 | F16AN403S8SU | % | F16AN403 S8 S |  | X | [5 empty] | 3
|  |  |  | 19 | F16AN403S9SU | % | F16AN403 S9 S |  | X | [5 empty] | 3
|  |  |  | 20 | F16AN403S10SU | % | F16AN403 S10 S |  | X | [5 empty] | 3
16 | 16
Operator to get electrician to inspect unit for potential failure

## 13. Alarm Database
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION (F16, F17, F18)
2000-F16-LST-PR-10001
ALARM DATABASE
[14 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Abbreviated Description (Faceplate) | Type | Alarm State | Alarm Value | Alarm Units | On Delay (sec) | Alarm Masking Condition | Impact | Urgency | Priority | Operator Response | Rev | OK | Date | OK | Date
F18PP5134_IV | 2000-F18-PID-PR-10003 | F18PP513/4 Invld Circuit | Misc | Alarm |  |  | 3 | Mask when F18PP513 OR 514 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate if Cleaner-Scavenger Flotation Cell Tails Pump discharge locations both open is intentional. | 2
FI16001 | 2000-F16-PID-PR-10001 | Flotation HP Prcss Water | Analogue Input | A_Lo | 200 | m3/h | 5 | DUTY F24PW417/418 NOT RUNNING Alarm enabled delay of 20 seconds on HP Process Water Pump start-up (duration to be confirmed during commissioning). | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review process requirements for water addition. | B
FI16001 | 2000-F16-PID-PR-10001 | Flotation HP Prcss Water | Analogue Input | A_Hi | 500 | m3/h | 5 | DUTY F24PW417/418 NOT RUNNING Alarm enabled delay of 20 seconds on HP Process Water Pump start-up (duration to be confirmed during commissioning). | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review process requirements for water addition. | B
F16SW004_PS | N/A | F16SW004 ACBShunt 24V OK | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | 2025-10-23
F16SW004_AF | N/A | F16SW004 Arc Flash | Digital Input | Alarm |  |  | 0 |  | Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness. | Prompt (>15 to <30 minutes) | High | Electrician to investigate | 2
F16SW004_TRP | N/A | F16SW004 Breaker Trip | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Switchroom tripped. Electrician to investigate | 2
F16SW004_SD | N/A | F16 MCC Incomer Healthy | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | 2
F16SW005_PS | N/A | F16SW005 ACBShunt 24V OK | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | 2025-10-23
F16SW005_AF | N/A | F16SW005 Arc Flash | Digital Input | Alarm |  |  | 0 |  | Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness. | Prompt (>15 to <30 minutes) | High | Electrician to investigate | 2
F16SW005_TRP | N/A | F16SW005 Breaker Trip | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Switchroom tripped. Electrician to investigate | 2
F16SW005_SD | N/A | F16SW005 Incomer Div OK | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | 2
F16SW008_PS | N/A | F16SW008ACB Shunt24VDCOK | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | 2025-10-23
F16SW008_AF | N/A | F16SW008 Arc Flash | Digital Input | Alarm |  |  | 0 |  | Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness. | Prompt (>15 to <30 minutes) | High | Electrician to investigate | 2
F16SW008_TRP | N/A | F16SW008 Breaker Trip | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Switchroom tripped. Electrician to investigate | 2
F16SW008_SD | N/A | F16SW008 Inc SurgeDivert | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | 2
FIC16011 | 2000-F16-PID-PR-10001 | F16CF411 Blower Air Ctrl | Analogue PID | A_Lo | 40 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review process requirements for blower air consumption flow rate. | 0
FIC16011 | 2000-F16-PID-PR-10001 | F16CF411 Blower Air Ctrl | Analogue PID | A_Hi | 80 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review process requirements for blower air consumption flow rate. | 0
F16SW004_PS1 | N/A | F16SW004 PS1 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
F16SW004_PS2 | N/A | F16SW004 PS2 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
F16SW005_PS1 | N/A | F16SW005 PS1 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
F16SW005_PS2 | N/A | F16SW005 PS2 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
UI16031 | N/A | F16SR002 415V SR Temp | Analogue Input | A_Hi | 30 | °C | 60 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
UI16032 | N/A | F16SR002 415V SR TF1 | Analogue Input | A_Hi | 30 | °C | 60 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
UI16033 | N/A | F16SR002 415V SR TF2 | Analogue Input | A_Hi | 30 | °C | 60 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
UI16034 | N/A | F16SR002 415V SR TF3 | Analogue Input | A_Hi | 30 | °C | 60 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
UI16030 | N/A | F16SR001 11kV SR Temp | Analogue Input | A_Hi | 30 | °C | 60 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
PI16012 | 2000-F16-PID-PR-10001 | F16CF411 Blower Air | Analogue Input | A_Lo | 90 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of low blower pressure. | 0
PI16012 | 2000-F16-PID-PR-10001 | F16CF411 Blower Air | Analogue Input | A_Hi | 130 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of high blower pressure. | 0
LIC16013 | 2000-F16-PID-PR-10001 | F16CF411 Level Ctrl | Analogue PID | A_Lo | 50 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
LIC16013 | 2000-F16-PID-PR-10001 | F16CF411 Level Ctrl | Analogue PID | A_Hi | 450 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
TI16014 | 2000-F16-PID-PR-10001 | F16CF411 G/Box Oil | Analogue Input | A_Hi | 80 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect oil supply system before agitator shutdown. | C
TI16014 | 2000-F16-PID-PR-10001 | F16CF411 G/Box Oil | Analogue Input | A_HH | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Agitator stopped. Operator to investigate. | C
PI16015 | 2000-F16-PID-PR-10001 | F16CF411 G/Box Oil | Analogue Input | A_LL | 50 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-421 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Agitator stopped. Operator to investigate. | B
PI16015 | 2000-F16-PID-PR-10001 | F16CF411 G/Box Oil | Analogue Input | A_Lo | 70 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-421 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit before agitator shutdown. | C
PI16015 | 2000-F16-PID-PR-10001 | F16CF411 G/Box Oil | Analogue Input | A_Hi | 800 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-421 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review causes of high gearbox oil pressure. | C
PDI16018 | 2000-F16-PID-PR-10001 | F16CF411 G/Box Fltr Dlta | Analogue Input | A_Hi | 200 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-421 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to isolate and change filter. Note: Cold ambient temperatures during start-up periods may result in alarm indicating. | 0
VI16019 | 2000-F16-PID-PR-10001 | F16CF411 G/Box | Analogue Input | A_Hi | 8 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-421 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect gearbox in-field. | 0
VI16019 | 2000-F16-PID-PR-10001 | F16CF411 G/Box | Analogue Input | A_HH | 12 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-421 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect gearbox in-field. | 0
VI16020 | 2000-F16-PID-PR-10001 | F16CF411 Motor | Analogue Input | A_Hi | 4 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-421 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect motor in-field. | 0
VI16020 | 2000-F16-PID-PR-10001 | F16CF411 Motor | Analogue Input | A_HH | 7.1 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-421 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect motor in-field. | 0
LAH16041 | 2000-F16-PID-PR-10001 | F16PS411 Flot Sump 1 | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Plant spillage into bunded area. Operator to review cause of spillage and operation of sump pump. | 2
XAH16042 | 2000-F16-PID-PR-10001 | F16PP629 Hose Leak | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate condition of peristaltic hose and isolate pump if necessary. | 2
XAH16043 | 2000-F16-PID-PR-10001 | F16PP630 Hose Leak | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate condition of peristaltic hose and isolate pump if necessary. | 2
XAH16044 | 2000-F16-PID-PR-10002 | F16PP631 Hose Leak | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate condition of peristaltic hose and isolate pump if necessary. | 2
XAH16045 | 2000-F16-PID-PR-10004 | F16PP632 Hose Leak | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate condition of peristaltic hose and isolate pump if necessary. | 2
XAH16046 | 2000-F16-PID-PR-10004 | F16PP633 Hose Leak | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate condition of peristaltic hose and isolate pump if necessary. | 2
FIC16051 | 2000-F16-PID-PR-10002 | F16CF412 Blower Air Ctrl | Analogue PID | A_Lo | 40 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review process requirements for blower air consumption flow rate. | 0
FIC16051 | 2000-F16-PID-PR-10002 | F16CF412 Blower Air Ctrl | Analogue PID | A_Hi | 80 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review process requirements for blower air consumption flow rate. | 0
PI16052 | 2000-F16-PID-PR-10002 | F16CF412 Blower Air | Analogue Input | A_Lo | 90 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of low blower pressure. | 0
PI16052 | 2000-F16-PID-PR-10002 | F16CF412 Blower Air | Analogue Input | A_Hi | 130 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of high blower pressure. | 0
LIC16053 | 2000-F16-PID-PR-10002 | F16CF412 Level Ctrl | Analogue PID | A_Lo | 50 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
LIC16053 | 2000-F16-PID-PR-10002 | F16CF412 Level Ctrl | Analogue PID | A_Hi | 450 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
TI16054 | 2000-F16-PID-PR-10001 | F16CF412 G/Box Oil | Analogue Input | A_Hi | 80 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect oil supply system. | B
TI16054 | 2000-F16-PID-PR-10002 | F16CF412 G/Box Oil | Analogue Input | A_HH | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect oil supply system. | B
PI16055 | 2000-F16-PID-PR-10002 | F16CF412 G/Box Oil | Analogue Input | A_LL | 50 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-422 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Agitator stopped. Operator to investigate. | B
PI16055 | 2000-F16-PID-PR-10002 | F16CF412 G/Box Oil | Analogue Input | A_Lo | 70 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-422 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit before shutdown. | B
PI16055 | 2000-F16-PID-PR-10002 | F16CF412 G/Box Oil | Analogue Input | A_Hi | 800 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-422 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review causes of high gearbox oil pressure. | C
PDI16058 | 2000-F16-PID-PR-10002 | F16CF412 G/Box Fltr Dlta | Analogue Input | A_Hi | 200 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-422 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to isolate and change filter. Note: Cold ambient temperatures during start-up periods may result in alarm indicating. | 0
VI16059 | 2000-F16-PID-PR-10002 | F16CF412 G/Box | Analogue Input | A_Hi | 8 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-422 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect gearbox in-field. | 0
VI16059 | 2000-F16-PID-PR-10002 | F16CF412 G/Box | Analogue Input | A_HH | 12 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-422 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect gearbox in-field. | 0
VI16060 | 2000-F16-PID-PR-10002 | F16CF412 Motor | Analogue Input | A_Hi | 4 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-422 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect motor in-field. | 0
VI16060 | 2000-F16-PID-PR-10002 | F16CF412 Motor | Analogue Input | A_HH | 7.1 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-422 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect motor in-field. | 0
FIC16061 | 2000-F16-PID-PR-10002 | F16CF413 Blower Air Ctrl | Analogue PID | A_Lo | 40 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review process requirements for blower air consumption flow rate. | 0
FIC16061 | 2000-F16-PID-PR-10002 | F16CF413 Blower Air Ctrl | Analogue PID | A_Hi | 80 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review process requirements for blower air consumption flow rate. | 0
PI16062 | 2000-F16-PID-PR-10002 | F16CF413 Blower Air | Analogue Input | A_Lo | 90 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of low blower pressure. | 0
PI16062 | 2000-F16-PID-PR-10002 | F16CF413 Blower Air | Analogue Input | A_Hi | 130 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of high blower pressure. | 0
LIC16063 | 2000-F16-PID-PR-10002 | F16CF413 Level Ctrl | Analogue PID | A_Lo | 50 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
LIC16063 | 2000-F16-PID-PR-10002 | AN402 | Analogue PID | A_Hi | 450 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
TI16064 | 2000-F16-PID-PR-10001 | F16CF413 G/Box Oil | Analogue Input | A_Hi | 80 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect oil supply system. | B
TI16064 | 2000-F16-PID-PR-10002 | F16CF413 G/Box Oil | Analogue Input | A_HH | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect oil supply system. | B
PI16065 | 2000-F16-PID-PR-10002 | F16CF413 G/Box Oil | Analogue Input | A_LL | 50 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-423 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Agitator stopped. Operator to investigate. | B
PI16065 | 2000-F16-PID-PR-10002 | F16CF413 G/Box Oil | Analogue Input | A_Lo | 70 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-423 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit before shutdown. | B
PI16065 | 2000-F16-PID-PR-10002 | F16CF413 G/Box Oil | Analogue Input | A_Hi | 800 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-423 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review causes of high gearbox oil pressure. | C
PDI16068 | 2000-F16-PID-PR-10002 | F16CF413 G/Box Fltr Dlta | Analogue Input | A_Hi | 200 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-423 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to isolate and change filter. Note: Cold ambient temperatures during start-up periods may result in alarm indicating. | 0
VI16069 | 2000-F16-PID-PR-10002 | F16CF413 G/Box | Analogue Input | A_Hi | 8 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-423 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect gearbox in-field. | 0
VI16069 | 2000-F16-PID-PR-10002 | F16CF413 G/Box | Analogue Input | A_HH | 12 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-423 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect gearbox in-field. | 0
VI16070 | 2000-F16-PID-PR-10002 | F16CF413 Motor | Analogue Input | A_Hi | 4 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-423 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect motor in-field. | 0
VI16070 | 2000-F16-PID-PR-10002 | F16CF413 Motor | Analogue Input | A_HH | 7.1 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-423 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect motor in-field. | 0
FIC16081 | 2000-F16-PID-PR-10003 | F16CF414 Blower Air Ctrl | Analogue PID | A_Lo | 40 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review process requirements for blower air consumption flow rate. | 0
FIC16081 | 2000-F16-PID-PR-10003 | F16CF414 Blower Air Ctrl | Analogue PID | A_Hi | 80 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review process requirements for blower air consumption flow rate. | 0
PI16082 | 2000-F16-PID-PR-10003 | F16CF414 Blower Air | Analogue Input | A_Lo | 90 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of low blower pressure. | 0
PI16082 | 2000-F16-PID-PR-10003 | F16CF414 Blower Air | Analogue Input | A_Hi | 130 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of high blower pressure. | 0
LIC16083 | 2000-F16-PID-PR-10003 | F16CF414 Level Ctrl | Analogue PID | A_Lo | 50 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
LIC16083 | 2000-F16-PID-PR-10003 | F16CF414 Level Ctrl | Analogue PID | A_Hi | 450 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
TI16084 | 2000-F16-PID-PR-10003 | F16CF414 G/Box Oil | Analogue Input | A_Hi | 80 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect oil supply system. | B
TI16084 | 2000-F16-PID-PR-10003 | F16CF414 G/Box Oil | Analogue Input | A_HH | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect oil supply system. | B
PI16085 | 2000-F16-PID-PR-10003 | F16CF414 G/Box Oil | Analogue Input | A_LL | 50 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-424 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Agitator stopped. Operator to investigate. | B
PI16085 | 2000-F16-PID-PR-10003 | F16CF414 G/Box Oil | Analogue Input | A_Lo | 70 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-424 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit before shutdown. | B
PI16085 | 2000-F16-PID-PR-10003 | F16CF414 G/Box Oil | Analogue Input | A_Hi | 800 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-424 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review causes of high gearbox oil pressure. | C
PDI16088 | 2000-F16-PID-PR-10003 | F16CF414 G/Box Fltr Dlta | Analogue Input | A_Hi | 200 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-424 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to isolate and change filter. Note: Cold ambient temperatures during start-up periods may result in alarm indicating. | 0
VI16089 | 2000-F16-PID-PR-10003 | F16CF414 G/Box | Analogue Input | A_Hi | 8 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-424 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect gearbox in-field. | 0
VI16089 | 2000-F16-PID-PR-10003 | F16CF414 G/Box | Analogue Input | A_HH | 12 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-424 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect gearbox in-field. | 0
VI16090 | 2000-F16-PID-PR-10003 | F16CF414 Motor | Analogue Input | A_Hi | 4 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-424 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect motor in-field. | 0
VI16090 | 2000-F16-PID-PR-10003 | F16CF414 Motor | Analogue Input | A_HH | 7.1 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-424 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect motor in-field. | 0
FIC16091 | 2000-F16-PID-PR-10003 | F16CF415 Blower Air Ctrl | Analogue PID | A_Lo | 40 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review process requirements for blower air consumption flow rate. | 0
FIC16091 | 2000-F16-PID-PR-10003 | F16CF415 Blower Air Ctrl | Analogue PID | A_Hi | 80 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review process requirements for blower air consumption flow rate. | 0
PI16092 | 2000-F16-PID-PR-10003 | F16CF415 Blower Air | Analogue Input | A_Lo | 90 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of low blower pressure. | 0
PI16092 | 2000-F16-PID-PR-10003 | F16CF415 Blower Air | Analogue Input | A_Hi | 130 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of high blower pressure. | 0
LIC16093 | 2000-F16-PID-PR-10003 | F16CF415 Level Ctrl | Analogue PID | A_Lo | 50 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
LIC16093 | 2000-F16-PID-PR-10003 | F16CF415 Level Ctrl | Analogue PID | A_Hi | 450 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
TI16094 | 2000-F16-PID-PR-10001 | F16CF415 G/Box Oil | Analogue Input | A_Hi | 80 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect oil supply system. | B
TI16094 | 2000-F16-PID-PR-10003 | F16CF415 G/Box Oil | Analogue Input | A_HH | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect oil supply system. | B
PI16095 | 2000-F16-PID-PR-10003 | F16CF415 G/Box Oil | Analogue Input | A_LL | 50 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-425 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Agitator stopped. Operator to investigate. | B
PI16095 | 2000-F16-PID-PR-10003 | F16CF415 G/Box Oil | Analogue Input | A_Lo | 70 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-425 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit before shutdown. | B
PI16095 | 2000-F16-PID-PR-10003 | F16CF415 G/Box Oil | Analogue Input | A_Hi | 800 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-425 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review causes of high gearbox oil pressure. | C
PDI16098 | 2000-F16-PID-PR-10003 | F16CF415 G/Box Fltr Dlta | Analogue Input | A_Hi | 200 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-425 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to isolate and change filter. Note: Cold ambient temperatures during start-up periods may result in alarm indicating. | 0
VI16099 | 2000-F16-PID-PR-10003 | F16CF415 G/Box | Analogue Input | A_Hi | 8 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-425 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect gearbox in-field. | 0
VI16099 | 2000-F16-PID-PR-10003 | F16CF415 G/Box | Analogue Input | A_HH | 12 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-425 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect gearbox in-field. | 0
VI16100 | 2000-F16-PID-PR-10003 | F16CF415 Motor | Analogue Input | A_Hi | 4 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-425 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect motor in-field. | 0
VI16100 | 2000-F16-PID-PR-10003 | F16CF415 Motor | Analogue Input | A_HH | 7.1 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-425 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect motor in-field. | 0
F16SW008_PS1 | N/A | F16SW008 PS1 24VDC OK | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Electrician to investigate | 2
FIC16101 | 2000-F16-PID-PR-10003 | F16CF416 Blower Air Ctrl | Analogue PID | A_Lo | 40 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review process requirements for blower air consumption flow rate. | 0
FIC16101 | 2000-F16-PID-PR-10003 | F16CF416 Blower Air Ctrl | Analogue PID | A_Hi | 80 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review process requirements for blower air consumption flow rate. | 0
PI16102 | 2000-F16-PID-PR-10003 | F16CF416 Blower Air | Analogue Input | A_Lo | 90 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of low blower pressure. | 0
PI16102 | 2000-F16-PID-PR-10003 | F16CF416 Blower Air | Analogue Input | A_Hi | 130 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of high blower pressure. | 0
LIC16103 | 2000-F16-PID-PR-10003 | F16CF416 Level Ctrl | Analogue PID | A_Lo | 50 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
LIC16103 | 2000-F16-PID-PR-10003 | F16CF416 Level Ctrl | Analogue PID | A_Hi | 450 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
TI16104 | 2000-F16-PID-PR-10001 | F16CF416 G/Box Oil | Analogue Input | A_Hi | 80 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect oil supply system. | B
TI16104 | 2000-F16-PID-PR-10003 | F16CF416 G/Box Oil | Analogue Input | A_HH | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect oil supply system. | B
PI16105 | 2000-F16-PID-PR-10003 | F16CF416 G/Box Oil | Analogue Input | A_LL | 50 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-426 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Agitator stopped. Operator to investigate. | B
PI16105 | 2000-F16-PID-PR-10003 | F16CF416 G/Box Oil | Analogue Input | A_Lo | 70 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-426 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit before shutdown. | B
PI16105 | 2000-F16-PID-PR-10003 | F16CF416 G/Box Oil | Analogue Input | A_Hi | 800 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-426 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review causes of high gearbox oil pressure. | C
PDI16108 | 2000-F16-PID-PR-10003 | F16CF416 G/Box Fltr Dlta | Analogue Input | A_Hi | 200 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-426 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to isolate and change filter. Note: Cold ambient temperatures during start-up periods may result in alarm indicating. | 0
VI16109 | 2000-F16-PID-PR-10003 | F16CF416 G/Box | Analogue Input | A_Hi | 8 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-426 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect gearbox in-field. | 0
VI16109 | 2000-F16-PID-PR-10003 | F16CF416 G/Box | Analogue Input | A_HH | 12 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-426 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect gearbox in-field. | 0
VI16110 | 2000-F16-PID-PR-10003 | F16CF416 Motor | Analogue Input | A_Hi | 4 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-426 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect motor in-field. | 0
VI16110 | 2000-F16-PID-PR-10003 | F16CF416 Motor | Analogue Input | A_HH | 7.1 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-426 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect motor in-field. | 0
FIC16111 | 2000-F16-PID-PR-10003 | F16CF417 Blower Air Ctrl | Analogue PID | A_Lo | 40 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review process requirements for blower air consumption flow rate. | 0
FIC16111 | 2000-F16-PID-PR-10003 | F16CF417 Blower Air Ctrl | Analogue PID | A_Hi | 103 | m3/min | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review process requirements for blower air consumption flow rate. | 0
PI16112 | 2000-F16-PID-PR-10003 | F16CF417 Blower Air | Analogue Input | A_Lo | 90 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of low blower pressure. | 0
PI16112 | 2000-F16-PID-PR-10003 | F16CF417 Blower Air | Analogue Input | A_Hi | 130 | kPa | 5 | Duty F16BW401 AND 402 AND 403 AND 404 NOT RUNNING Alarm enabled delay of 10 seconds during blower (F16BW401 OR 402 OR 403 OR 404 NOT RUNNING) start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of high blower pressure. | 0
LIC16113 | 2000-F16-PID-PR-10003 | F16CF417 Level Ctrl | Analogue PID | A_Lo | 50 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
LIC16113 | 2000-F16-PID-PR-10003 | F16CF417 Level Ctrl | Analogue PID | A_Hi | 450 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review if cell level controller in Automatic mode, valves in correct position and feed is on. | B
TI16114 | 2000-F16-PID-PR-10001 | F16CF417 G/Box Oil | Analogue Input | A_Hi | 80 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect oil supply system. | B
TI16114 | 2000-F16-PID-PR-10003 | F16CF417 G/Box Oil | Analogue Input | A_HH | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect oil supply system. | B
PI16115 | 2000-F16-PID-PR-10003 | F16CF417 G/Box Oil | Analogue Input | A_LL | 50 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-427 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Agitator stopped. Operator to investigate. | B
PI16115 | 2000-F16-PID-PR-10003 | F16CF417 G/Box Oil | Analogue Input | A_Lo | 70 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-427 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit before shutdown. | B
PI16115 | 2000-F16-PID-PR-10003 | F16CF417 G/Box Oil | Analogue Input | A_Hi | 800 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-427 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review causes of high gearbox oil pressure. | C
PDI16118 | 2000-F16-PID-PR-10003 | F16CF417 G/Box Fltr Dlta | Analogue Input | A_Hi | 200 | kPa | 5 | Alarm enabled delay of 10 seconds on F16-AG-427 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to isolate and change filter. Note: Cold ambient temperatures during start-up periods may result in alarm indicating. | 0
VI16119 | 2000-F16-PID-PR-10003 | F16CF417 G/Box | Analogue Input | A_Hi | 8 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-427 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect gearbox in-field. | 0
VI16119 | 2000-F16-PID-PR-10003 | F16CF417 G/Box | Analogue Input | A_HH | 12 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-427 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect gearbox in-field. | 0
VI16120 | 2000-F16-PID-PR-10003 | F16CF417 Motor | Analogue Input | A_Hi | 4 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-427 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect motor in-field. | 0
VI16120 | 2000-F16-PID-PR-10003 | F16CF417 Motor | Analogue Input | A_HH | 7.1 | mm/s | 5 | Alarm enabled delay of 10 seconds on F16-AG-427 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect motor in-field. | 0
LAH16121 | 2000-F16-PID-PR-10003 | F16PS412 Flot Sump 2 | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Plant spillage into bunded area. Operator to review cause of spillage and operation of sump pump. | 2
LAH16141 | 2000-F16-PID-PR-10004 | F16PS413 Flot Sump 3 | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Plant spillage into bunded area. Operator to review cause of spillage and operation of sump pump. | 2
LIC16151 | 2000-F16-PID-PR-10005 | F16HP451 Level Ctrl | Analogue PID | A_LL | 20 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to verify if cause of hopper low-low is expected in relation to sample collection. | B
LIC16151 | 2000-F16-PID-PR-10005 | F16HP451 Level Ctrl | Analogue PID | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to verify if cause of hopper low is expected in relation to sample collection. | B
LIC16151 | 2000-F16-PID-PR-10005 | F16HP451 Level Ctrl | Analogue PID | A_Hi | 85 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate pump operation and sampling arrangement as a sub-system. | 0
FAL16156 | 2000-F24-PID-PR-10003 | F16PP638 Gland | Digital Input | Alarm |  |  | 3 | F16PP638 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Gland flow low. Operator to review gland delivery and utilise standby pump if available. | 3
LIC16161 | 2000-F16-PID-PR-10005 | F16HP452 Level Ctrl | Analogue PID | A_LL | 20 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to verify if cause of hopper low-low is expected in relation to sample collection. | B
LIC16161 | 2000-F16-PID-PR-10005 | F16HP452 Level Ctrl | Analogue PID | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to verify if cause of hopper low is expected in relation to sample collection. | B
LIC16161 | 2000-F16-PID-PR-10005 | F16HP452 Level Ctrl | Analogue PID | A_Hi | 85 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate pump operation and sampling arrangement as a sub-system. | 0
FAL16166 | 2000-F24-PID-PR-10003 | F16PP639 Gland | Digital Input | Alarm |  |  | 3 | F16PP639 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Gland flow low. Operator to review gland delivery and utilise standby pump if available. | 3
PI16182 | 2000-F24-PID-PR-10008 | F16RA402 Discharge | Analogue Input | A_Lo | 600 | kPa | 5 | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are stopped Mask A_Lo for 30 seconds during F24-CM-401, 402 OR 403 start up Duration to be confirmed during commissioning. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate cause of low air receiver pressure. | 3
PI16182 | 2000-F24-PID-PR-10008 | F16RA402 Discharge | Analogue Input | A_Hi | 1000 | kPa | 5 | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are stopped Mask A_Lo for 30 seconds during F24-CM-401, 402 OR 403 start up Duration to be confirmed during commissioning. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate cause of high air receiver pressure. | 3
TI16198A | 2000-F16-PID-PR-10006 | F16BW401 Motor P.U RTD | Analogue Input | A_Hi | 130 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | B
TI16198A | 2000-F16-PID-PR-10006 | F16BW401 Motor P.U RTD | Analogue Input | A_HH | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16198B | 2000-F16-PID-PR-10006 | F16BW401 Motor P.V RTD | Analogue Input | A_Hi | 130 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | B
TI16198B | 2000-F16-PID-PR-10006 | F16BW401 Motor P.V RTD | Analogue Input | A_HH | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16198C | 2000-F16-PID-PR-10006 | F16BW401 Motor P.W RTD | Analogue Input | A_Hi | 130 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | B
TI16198C | 2000-F16-PID-PR-10006 | F16BW401 Motor P.W RTD | Analogue Input | A_HH | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16198D | 2000-F16-PID-PR-10006 | F16BW401 Mtr DE Brg RTD | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | B
TI16198D | 2000-F16-PID-PR-10006 | F16BW401 Mtr DE Brg RTD | Analogue Input | A_HH | 110 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16198E | 2000-F16-PID-PR-10006 | F16BW401 Mtr NDE Brg RTD | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | B
TI16198E | 2000-F16-PID-PR-10006 | F16BW401 Mtr NDE Brg RTD | Analogue Input | A_HH | 110 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
PIC16199 | 2000-F16-PID-PR-10006 | F16BW401 Pressure Ctrl | Analogue PID | A_Hi | 120 | kPa(g) | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review if pressure controller is in Automatic mode. | B
PIC16199 | 2000-F16-PID-PR-10006 | F16BW401 Pressure Ctrl | Analogue PID | A_HH | 125 | kPa(g) | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
TI16208A | 2000-F16-PID-PR-10006 | F16BW402 Motor P.U RTD | Analogue Input | A_Hi | 130 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | B
TI16208A | 2000-F16-PID-PR-10006 | F16BW402 Motor P.U RTD | Analogue Input | A_HH | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16208B | 2000-F16-PID-PR-10006 | F16BW402 Motor P.V RTD | Analogue Input | A_Hi | 130 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | B
TI16208B | 2000-F16-PID-PR-10006 | F16BW402 Motor P.V RTD | Analogue Input | A_HH | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16208C | 2000-F16-PID-PR-10006 | F16BW402 Motor P.W RTD | Analogue Input | A_Hi | 130 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | B
TI16208C | 2000-F16-PID-PR-10006 | F16BW402 Motor P.W RTD | Analogue Input | A_HH | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16208D | 2000-F16-PID-PR-10006 | F16BW402 DE Bearing RTD | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | B
TI16208D | 2000-F16-PID-PR-10006 | F16BW402 DE Bearing RTD | Analogue Input | A_HH | 110 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16208E | 2000-F16-PID-PR-10006 | F16BW402 NDE Bearing RTD | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | B
TI16208E | 2000-F16-PID-PR-10006 | F16BW402 NDE Bearing RTD | Analogue Input | A_HH | 110 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
PIC16209 | 2000-F16-PID-PR-10006 | F16BW402 Pressure Ctrl | Analogue PID | A_Hi | 120 | kPa(g) | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review if pressure controller is in Automatic mode. | B
PIC16209 | 2000-F16-PID-PR-10006 | F16BW402 Pressure Ctrl | Analogue PID | A_HH | 125 | kPa(g) | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
TI16218A | 2000-F16-PID-PR-10006 | F16BW403 Motor P.U RTD | Analogue Input | A_Hi | 130 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | B
TI16218A | 2000-F16-PID-PR-10006 | F16BW403 Motor P.U RTD | Analogue Input | A_HH | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16218B | 2000-F16-PID-PR-10006 | F16BW403 Motor P.V RTD | Analogue Input | A_Hi | 130 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | B
TI16218B | 2000-F16-PID-PR-10006 | F16BW403 Motor P.V RTD | Analogue Input | A_HH | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16218C | 2000-F16-PID-PR-10006 | F16BW403 Motor P.W RTD | Analogue Input | A_Hi | 130 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | B
TI16218C | 2000-F16-PID-PR-10006 | F16BW403 Motor P.W RTD | Analogue Input | A_HH | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16218D | 2000-F16-PID-PR-10006 | F16BW403 DE Bearing RTD | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | B
TI16218D | 2000-F16-PID-PR-10006 | F16BW403 DE Bearing RTD | Analogue Input | A_HH | 110 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16218E | 2000-F16-PID-PR-10006 | F16BW403 NDE Bearing RTD | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | B
TI16218E | 2000-F16-PID-PR-10006 | F16BW403 NDE Bearing RTD | Analogue Input | A_HH | 110 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
PIC16219 | 2000-F16-PID-PR-10006 | F16BW403 Pressure Ctrl | Analogue PID | A_Hi | 120 | kPa(g) | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review if pressure controller is in Automatic mode. | B
PIC16219 | 2000-F16-PID-PR-10006 | F16BW403 Pressure Ctrl | Analogue PID | A_HH | 125 | kPa(g) | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
TI16228B | 2000-F16-PID-PR-10006 | F16BW404 Motor P.V RTD | Analogue Input | A_Hi | 130 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | B
TI16228B | 2000-F16-PID-PR-10006 | F16BW404 Motor P.V RTD | Analogue Input | A_HH | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16228C | 2000-F16-PID-PR-10006 | F16BW404 Motor P.W RTD | Analogue Input | A_Hi | 130 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | B
TI16228C | 2000-F16-PID-PR-10006 | F16BW404 Motor P.W RTD | Analogue Input | A_HH | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16228D | 2000-F16-PID-PR-10006 | F16BW404 Mtr DE Brg RTD | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | B
TI16228D | 2000-F16-PID-PR-10006 | F16BW404 Mtr DE Brg RTD | Analogue Input | A_HH | 110 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16228E | 2000-F16-PID-PR-10006 | F16BW404 Mtr NDE Brg RTD | Analogue Input | A_Hi | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | B
TI16228E | 2000-F16-PID-PR-10006 | F16BW404 Mtr NDE Brg RTD | Analogue Input | A_HH | 110 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | B
TI16228A | 2000-F16-PID-PR-10006 | F16BW404 Motor P.U RTD | Analogue Input | A_Hi | 130 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | 3
TI16228A | 2000-F16-PID-PR-10006 | F16BW404 Motor P.U RTD | Analogue Input | A_HH | 155 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 3
PIC16229 | 2000-F16-PID-PR-10006 | F16BW404 Pressure Ctrl | Analogue PID | A_Hi | 120 | kPa(g) | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review if pressure controller is in Automatic mode. | B
PIC16229 | 2000-F16-PID-PR-10006 | F16BW404 Pressure Ctrl | Analogue PID | A_HH | 125 | kPa(g) | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
PI16261 | 2000-F16-PID-PR-10006 | F16BW401 Blower 1 Inlet | Analogue Input | A_LL | -8 | kPa | 5 | F16BW401 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit for blocked inlet filter or foreign material. | B
PI16261 | 2000-F16-PID-PR-10006 | F16BW401 Blower 1 Inlet | Analogue Input | A_Lo | -6 | kPa | 5 | F16BW401 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit for blocked inlet filter or foreign material. | B
TI16263 | 2000-F16-PID-PR-10006 | F16BW401 Blower 1 Outlet | Analogue Input | A_Hi | 172 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to inspect unit. | B
TI16263 | 2000-F16-PID-PR-10006 | F16BW401 Blower 1 Outlet | Analogue Input | A_HH | 177 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
TI16264 | 2000-F16-PID-PR-10006 | F16BW401 Blower 1 G/Box | Analogue Input | A_HH | 118 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
TI16264 | 2000-F16-PID-PR-10006 | F16BW401 Blower 1 G/Box | Analogue Input | A_Hi | 113 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit. | B
TI16265 | 2000-F16-PID-PR-10006 | F16BW401 Blower 1 | Analogue Input | A_Hi | 50 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit. | B
TI16265 | 2000-F16-PID-PR-10006 | F16BW401 Blower 1 | Analogue Input | A_HH | 52 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
PI16271 | 2000-F16-PID-PR-10006 | F16BW402 Blower 2 Inlet | Analogue Input | A_LL | -8 | kPa | 5 | F16BW402 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit for blocked inlet filter or foreign material. | B
PI16271 | 2000-F16-PID-PR-10006 | F16BW402 Blower 2 Inlet | Analogue Input | A_Lo | -6 | kPa | 5 | F16BW402 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit for blocked inlet filter or foreign material. | B
TI16273 | 2000-F16-PID-PR-10006 | F16BW402 Blower 2 Outlet | Analogue Input | A_Hi | 172 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to inspect unit. | B
TI16273 | 2000-F16-PID-PR-10006 | F16BW402 Blower 2 Outlet | Analogue Input | A_HH | 177 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
TI16274 | 2000-F16-PID-PR-10006 | F16BW402 Blower 2 G/Box | Analogue Input | A_HH | 118 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
TI16274 | 2000-F16-PID-PR-10006 | F16BW402 Blower 2 G/Box | Analogue Input | A_Hi | 113 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit. | B
TI16275 | 2000-F16-PID-PR-10006 | F16BW402 Blower 2 | Analogue Input | A_Hi | 50 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit. | B
TI16275 | 2000-F16-PID-PR-10006 | F16BW402 Blower 2 | Analogue Input | A_HH | 52 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
PI16281 | 2000-F16-PID-PR-10006 | F16BW403 Blower 3 Inlet | Analogue Input | A_LL | -8 | kPa | 5 | F16BW403 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit for blocked inlet filter or foreign material. | B
PI16281 | 2000-F16-PID-PR-10006 | F16BW403 Blower 3 Inlet | Analogue Input | A_Lo | -6 | kPa | 5 | F16BW403 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit for blocked inlet filter or foreign material. | B
TI16283 | 2000-F16-PID-PR-10006 | F16BW403 Blower 3 Outlet | Analogue Input | A_Hi | 172 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to inspect unit. | B
TI16283 | 2000-F16-PID-PR-10006 | F16BW403 Blower 3 Outlet | Analogue Input | A_HH | 177 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
TI16284 | 2000-F16-PID-PR-10006 | F16BW403 Blower 3 G/Box | Analogue Input | A_HH | 118 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
TI16284 | 2000-F16-PID-PR-10006 | F16BW403 Blower 3 G/Box | Analogue Input | A_Hi | 113 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit. | B
TI16285 | 2000-F16-PID-PR-10006 | F16BW403 Blower 3 | Analogue Input | A_Hi | 50 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit. | B
TI16285 | 2000-F16-PID-PR-10006 | F16BW403 Blower 3 | Analogue Input | A_HH | 52 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
PI16291 | 2000-F16-PID-PR-10006 | F16BW404 Blower 4 Inlet | Analogue Input | A_LL | -8 | kPa | 5 | F16BW404 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit for blocked inlet filter or foreign material. | B
PI16291 | 2000-F16-PID-PR-10006 | F16BW404 Blower 4 Inlet | Analogue Input | A_Lo | -6 | kPa | 5 | F16BW404 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit for blocked inlet filter or foreign material. | B
TI16293 | 2000-F16-PID-PR-10006 | F16BW404 Blower 4 Outlet | Analogue Input | A_Hi | 172 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to inspect unit. | B
TI16293 | 2000-F16-PID-PR-10006 | F16BW404 Blower 4 Outlet | Analogue Input | A_HH | 177 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
TI16294 | 2000-F16-PID-PR-10006 | F16BW404 Blower 4 G/Box | Analogue Input | A_HH | 118 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
TI16294 | 2000-F16-PID-PR-10006 | F16BW404 Blower 4 G/Box | Analogue Input | A_Hi | 113 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit. | B
TI16295 | 2000-F16-PID-PR-10006 | F16BW404 Blower 4 | Analogue Input | A_Hi | 50 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to inspect unit. | B
TI16295 | 2000-F16-PID-PR-10006 | F16BW404 Blower 4 | Analogue Input | A_HH | 52 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to inspect unit. | B
FAL16358 | 2000-F24-PID-PR-10003 | F16PP515 Gland | Digital Input | Alarm |  |  | 3 | F16PP515 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Gland flow low. Operator to review gland delivery and utilise standby pump if available. | 3
FIC17001 | 2000-F17-PID-PR-10001 | F17TH401 Flocc Diln Ctrl | Analogue PID | DV+/- | 25 | m3/hr | - | Mask A_Lo when F72PP691 AND 692 are Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate cause of high/low flocculant dilution water. | 3 | [5 empty] | Alarm setpoints/masking to be checked, incosistent details. Refer PID Control Tab
LIC17004 | 2000-F17-PID-PR-10001 | F16HP456 Level Ctrl | Analogue PID | A_LL | 20 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to verify if cause of hopper low-low is expected in relation to sample collection. | B
LIC17004 | 2000-F17-PID-PR-10001 | F16HP456 Level Ctrl | Analogue PID | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to verify if cause of hopper low is expected in relation to sample collection. | B
LIC17004 | 2000-F17-PID-PR-10001 | F16HP456 Level Ctrl | Analogue PID | A_Hi | 80 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate pump operation and sampling arrangement as a sub-system. | B
XAH17008 | 2000-F17-PID-PR-10001 | F16PP634 Hose Leak | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate condition of peristaltic hose and isolate pump if necessary. | 2
PIC17011 | 2000-F17-PID-PR-10001 | F17TH401 Bed Ctrl | Analogue PID | A_Lo | 94.01 | kPa(g) | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review underflow pump speed or control mode. | B
PIC17011 | 2000-F17-PID-PR-10001 | F17TH401 Bed Ctrl | Analogue PID | A_Hi | 95.91 | kPa(g) | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review underflow pump speed or control mode. | B
PIC17011 | 2000-F17-PID-PR-10001 | F17TH401 Bed Ctrl | Analogue PID | A_HH | 97.31 | kPa(g) | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review thickener torque, thickener feed rate and/or underflow pump speed. | B
ZAH17014 | 2000-F17-PID-PR-10001 | F17TH401 Rake Hi Limit | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to ensure rake high is expected given existing process conditions. | 2
ZAL17015 | 2000-F17-PID-PR-10001 | F17TH401 Rake Lo Limit | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Operator to ensure rake low is expected given existing process conditions. | 2
SAL17016 | 2000-F17-PID-PR-10001 | F17TH401 Rake Speed | Digital Input | Alarm |  |  | 20 | Mask if F17PO408 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of rake stoppage. | 2
LAL17017 | 2000-F17-PID-PR-10001 | F17TH401 Gear Redcr Oil1 | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to manually check and top off oil level. | 2
LAL17018 | 2000-F17-PID-PR-10001 | F17TH401 Gear Redcr Oil2 | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to manually check and top off oil level. | 2
AI17019 | 2000-F17-PID-PR-10001 | F17TH401 O/F Turbidity | Analogue Input | A_Hi | 180 | NTU | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review thickener operation & flocculant dosing rate. | B
AI17019 | 2000-F17-PID-PR-10001 | F17TH401 O/F Turbidity | Analogue Input | A_HH | 200 | NTU | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review thickener operation & flocculant dosing rate. | B
LAL17021 | 2000-F17-PID-PR-10001 | F17HU406 Rake Drive HPU | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to manually check and top off oil level. | 2
TAH17022 | 2000-F17-PID-PR-10001 | F17HU406 Rake Drive HPU | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high oil temperature. | 2
LALL17023 | 2000-F17-PID-PR-10001 | F17HU406 Rake Drive HPU | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Plant tripped. Operator to investigate cause of low oil level and manually check and top off oil level. | 2
TAHH17024 | 2000-F17-PID-PR-10001 | F17HU406 Rake Drive HPU | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Plant tripped. Operator to investigate cause of high oil temperature. | 2
ZAO17026 | 2000-F17-PID-PR-10001 | F17PO408 Inlet Valve Opn | Digital Input | N_Open |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | F17TH401 Rake Drive HPU Pump Inlet Valve Not Open. Operator to inspect for correct operation. | 3
PDAH17028 | 2000-F17-PID-PR-10001 | F17PO408 D/C Fltr Dlta | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to clean/replace oil filter. | 2
NI17030 | 2000-F17-PID-PR-10001 | F17TH401 Rake Torque | Analogue Input | P_Hi | 40 (8163) | % (kPa) | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Rake Raise. Logging. | [5 empty] | Shouldnt this be removed? AP
NI17030 | 2000-F17-PID-PR-10001 | F17TH401 Rake Torque | Analogue Input | A_Hi | 50 (10204) | % (kPa) | 5 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Operator to increase underflow pump VSD, lower or halt plant feed, evaluate flocculant dosing control. | B
NI17030 | 2000-F17-PID-PR-10001 | F17TH401 Rake Torque | Analogue Input | A_HH | 85 (17347) | % (kPa) | 5 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Plant Tripped | Logging | Operator to increase underflow pump VSD, lower or halt plant feed, evaluate flocculant dosing control. Thickener tripped. | B
PDAH17031 | 2000-F17-PID-PR-10001 | F17HU406 Outlet Delta | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to clean/replace oil filter. | 2
PDAH17036 | 2000-F17-PID-PR-10001 | F17HU406 Rtrn Fltr Dlta | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to clean/replace oil filter. | 2
PDAH17037 | 2000-F17-PID-PR-10001 | F17HU406 Rtrn Fltr Dlta | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to clean/replace oil filter. | 2
LAL17041 | 2000-F17-PID-PR-10001 | F17HU414 Rake Lift HPU | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to manually check and top off oil level. | 2
TAH17042 | 2000-F17-PID-PR-10001 | F17HU414 Rake Lift HPU | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high oil temperature. | 2
LALL17043 | 2000-F17-PID-PR-10001 | F17HU414 Rake Lift HPU | Digital Input | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Plant tripped. Operator to investigate cause of low oil level and manually check and top off oil level. | 2
TAHH17044 | 2000-F17-PID-PR-10001 | F17HU414 Rake Lift HPU | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to clean/replace oil filter. | 2
PDAH17051 | 2000-F17-PID-PR-10001 | F17HU414 Rtrn Fltr Dlta | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to clean/replace oil filter. | 2
XA17060 | 2000-F17-PID-PR-10001 | F17TH401 EStop | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Operator to promptly investigate cause of activation of Emergency Stop. | C
HS17063STT | 2000-F17-PID-PR-10001 | F17TH401 Reverse Jog | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Flotation Tailings Thickener in Reverse. Logging only. | 2
HS17064STT | 2000-F17-PID-PR-10001 | F17TH401 Local Stop | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Flotation Tailings Thickener stopped in LOCAL. Logging. | 2
LAH17081 | 2000-F17-PID-PR-10001 | F17PS427 Thicknr Sump | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Plant spillage into bunded area. Operator to review cause of spillage and operation of sump pump. | 2
FI17105 | 2000-F24-PID-PR-10003 | F17PP455 Gland | Analogue Input | A_LL | 1 | m3/hr | 5 | F17PP455 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to engage standby pump if available and inspect system in field. | 3
FI17105 | 2000-F24-PID-PR-10003 | F17PP455 Gland | Analogue Input | A_Lo | 1.4 | m3/hr | 5 | F17PP455 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate cause of low gland flow. | 3
FI17115 | 2000-F24-PID-PR-10003 | F17PP456 Gland | Analogue Input | A_LL | 1 | m3/hr | 5 | F17PP456 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to engage standby pump if available and inspect system in field. | 3
FI17115 | 2000-F24-PID-PR-10003 | F17PP456 Gland | Analogue Input | A_Lo | 1.4 | m3/hr | 5 | F17PP456 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate cause of low gland flow. | 3
DNIC17121 | 2000-F17-PID-PR-10002 | F17PP455/6 Density Ctrl | Analogue PID | A_LL | 40 | %w/w | 5 | F17-PP-455/456 NOT RUNNING Alarm enabled delay of 10 seconds during F17PP455 OR 456 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to evaluate process. | 3
DNIC17121 | 2000-F17-PID-PR-10002 | F17PP455/6 Density Ctrl | Analogue PID | A_Lo | 42 | %w/w | 5 | F17-PP-455/456 NOT RUNNING Alarm enabled delay of 10 seconds during F17PP455 OR 456 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to evaluate process. | 3
DNIC17121 | 2000-F17-PID-PR-10002 | F17PP455/6 Density Ctrl | Analogue PID | A_Hi | 60 | %w/w | 5 | F17-PP-455/456 NOT RUNNING Alarm enabled delay of 10 seconds during F17PP455 OR 456 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to take action to reduce discharge density to prevent line sanding. | 3
DNIC17121 | 2000-F17-PID-PR-10002 | F17PP455/6 Density Ctrl | Analogue PID | A_HH | 62 | %w/w | 5 | F17-PP-455/456 NOT RUNNING Alarm enabled delay of 10 seconds during F17PP455 OR 456 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to take action to reduce discharge density to prevent line sanding. | 3
FIC17121 | 2000-F17-PID-PR-10002 | F17PP455/6 Flow Ctrl | Analogue PID | A_LL | 200 | m3/hr | 5 | F17-PP-455/456 NOT RUNNING Alarm enabled delay of 10 seconds during F17PP455 OR 456 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to evaluate discharge line for blockages, closed discharge valves | B
FIC17121 | 2000-F17-PID-PR-10002 | F17PP455/6 Flow Ctrl | Analogue PID | DV+/- | 150 | m3/hr | - | F17-PP-455/456 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review discharge flow, pump control method, | 3 | [5 empty] | ALARM priority set to medium in DCS as Yellow High = Medium in DCS = Yellow
PI17122 | 2000-F17-PID-PR-10002 | F17PP455/456 Discharge | Analogue Input | A_Hi | 330 | kPa | 5 | F17PP455 AND 456 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F17-PP-455 OR 456 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to evaluate process for invalid conditions. | B
PI17122 | 2000-F17-PID-PR-10002 | F17PP455/456 Discharge | Analogue Input | A_HH | 350 | kPa | 5 | F17PP455 AND 456 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F17-PP-455 OR 456 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Plant tripped to protect pump. Operator to investigate cause and engage standby pump if available. | B
WI17127 | 2000-F17-PID-PR-10002 | F17TH401 UF CIL2 Solids | Analogue Input | A_LL | 200 | t/h | 5 | F17PP455 AND 456 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F17-PP-455 OR 456 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review open/close position of destination valves on Flotation Tailings Thickener Underflow Pump discharge. | B
WI17127 | 2000-F17-PID-PR-10002 | F17TH401 UF CIL2 Solids | Analogue Input | A_Lo | 400 | t/h | 5 | F17PP455 AND 456 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F17-PP-455 OR 456 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review open/close position of destination valves on Flotation Tailings Thickener Underflow Pump discharge. | B
FIC17127 | 2000-F17-PID-PR-10002 | F17TH401 UF to CIL2 | Analogue PID | A_LL | 400 | m3/hr | 5 | F17-PP-455/456 NOT RUNNING | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to review valve position. | B
FIC17127 | 2000-F17-PID-PR-10002 | F17TH401 UF to CIL2 | Analogue PID | A_Lo | 700 | m3/hr | 5 | F17-PP-455/456 NOT RUNNING | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to review valve position. | B
FIC17128 | 2000-F17-PID-PR-10002 | F17TH401 UF to CIL3 | Analogue PID | A_LL | 400 | m3/hr | 5 | F17-PP-455/456 NOT RUNNING | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate cause of low-low flow to CIL3. | B
FIC17128 | 2000-F17-PID-PR-10002 | F17TH401 UF to CIL3 | Analogue PID | A_Lo | 700 | m3/hr | 5 | F17-PP-455/456 NOT RUNNING | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of low flow to CIL3. | B
WI17128 | 2000-F17-PID-PR-10002 | F17TH401 UF CIL3 Solids | Analogue Input | A_LL | 200 | t/h | 5 | F17PP455 AND 456 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F17-PP-455 OR 456 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review open/close position of destination valves on Flotation Tailings Thickener Underflow Pump discharge. | B
WI17128 | 2000-F17-PID-PR-10002 | F17TH401 UF CIL3 Solids | Analogue Input | A_Lo | 400 | t/h | 5 | F17PP455 AND 456 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F17-PP-455 OR 456 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review open/close position of destination valves on Flotation Tailings Thickener Underflow Pump discharge. | B
FI17130 | 2000-F17-PID-PR-10002 | F17TH401 UF Final Tails | Analogue Input | A_LL | 800 | m3/h | 5 | F17PP455 AND 456 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F17-PP-455 OR 456 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review plant feed rate and flotation tailings mass flow destinations. | B
FI17130 | 2000-F17-PID-PR-10002 | F17TH401 UF Final Tails | Analogue Input | A_Lo | 1200 | m3/h | 5 | F17PP455 AND 456 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F17-PP-455 OR 456 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review plant feed rate and flotation tailings mass flow destinations. | B
WI17130 | 2000-F17-PID-PR-10002 | F17TH401 UF Final Tails | Analogue Input | A_LL | 200 | t/h | 5 | F17PP455 AND 456 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review open/close position of destination valves on Flotation Tailings Thickener Underflow Pump discharge. | B
WI17130 | 2000-F17-PID-PR-10002 | F17TH401 UF Final Tails | Analogue Input | A_Lo | 500 | t/h | 5 | F17PP455 AND 456 NOT RUNNING | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review open/close position of destination valves on Flotation Tailings Thickener Underflow Pump discharge. | B
LIC18001A | 2000-F18-PID-PR-10001 | F18HP414 Water Ctrl | Analogue PID | A_LL | 20 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate cause of final concentrate hopper low-low. | 3
LIC18001A | 2000-F18-PID-PR-10001 | F18HP414 Water Ctrl | Analogue PID | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review flotation system to ascertain cause of dropping final concentrate hopper level. | 3
LIC18001A | 2000-F18-PID-PR-10001 | F18HP414 Water Ctrl | Analogue PID | A_Hi | 80 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to review flotation system to ascertain cause of rising final concentrate hopper level. | 3
LIC18001A | 2000-F18-PID-PR-10001 | F18HP414 Water Ctrl | Analogue PID | A_HH | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to review flotation system to ascertain cause of rising final concentrate hopper level. | 3
LIC18011A | 2000-F18-PID-PR-10001 | F18HP501 Water Ctrl | Analogue PID | A_LL | 20 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of Cleaner Flotation feed hopper low-low. | 3
LIC18011A | 2000-F18-PID-PR-10001 | F18HP501 Water Ctrl | Analogue PID | A_Lo | 30 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to review flotation system to ascertain cause of dropping Cleaner Flotation feed hopper level. | 3
LIC18011A | 2000-F18-PID-PR-10001 | F18HP501 Water Ctrl | Analogue PID | A_Hi | 80 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to review flotation system to ascertain cause of rising Cleaner Flotation feed hopper level. | 3
LIC18011A | 2000-F18-PID-PR-10001 | F18HP501 Water Ctrl | Analogue PID | A_HH | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to review flotation system to ascertain cause of rising Cleaner Flotation feed hopper level. | 3
FI18027 | 2000-F18-PID-PR-10001 | F18PP407/8 Final Con D/C | Analogue Input | A_LL | 50 | m3/h | 5 | F18PP407 AND 408 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-407 OR 408 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Plant tripped to protect pump. Operator to investigate cause and engage standby pump if available. | B
FI18027 | 2000-F18-PID-PR-10001 | F18PP407/8 Final Con D/C | Analogue Input | A_Lo | 90 | m3/h | 5 | F18PP407 AND 408 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-407 OR 408 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to review process. | B
FI18027 | 2000-F18-PID-PR-10001 | F18PP407/8 Final Con D/C | Analogue Input | A_Hi | 380 | m3/h | 5 | F18PP407 AND 408 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-407 OR 408 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review process. | B
DNI18027 | 2000-F18-PID-PR-10001 | F18PP407/408 D/C Solids | Analogue Input | A_HH | 40 | %w/w | 5 | F17PP407 AND 408 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-407 OR 408 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to take action to reduce pipeline density to prevent line sanding. | 3
DNI18027 | 2000-F18-PID-PR-10001 | F18PP407/408 D/C Solids | Analogue Input | A_Hi | 35 | %w/w | 5 | F17PP407 AND 408 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-407 OR 408 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to take action to reduce pipeline density to prevent line sanding. | 3
FIC18037 | 2000-F18-PID-PR-10001 | F18PP501/2 Ctrl | Analogue PID | A_LL | 400 | m3/hr | 5 | DUTY F18PP501/502 NOT RUNNING Alarm enabled delay of 10 seconds on F18PP501 OR 502 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Plant tripped to protect pump. Operator to investigate cause and engage standby pump if available. | B
FIC18037 | 2000-F18-PID-PR-10001 | F18PP501/2 Ctrl | Analogue PID | A_Lo | 1950 | m3/hr | 5 | DUTY F18PP501/502 NOT RUNNING Alarm enabled delay of 10 seconds on F18PP501 OR 502 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to review process. | 0
FIC18037 | 2000-F18-PID-PR-10001 | F18PP501/2 Ctrl | Analogue PID | A_Hi | 2050 | m3/hr | 5 | DUTY F18PP501/502 NOT RUNNING Alarm enabled delay of 10 seconds on F18PP501 OR 502 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review process. | 0
LAH18041 | 2000-F18-PID-PR-10001 | F18PS501 Cleaner Sump | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Plant spillage into bunded area. Operator to review cause of spillage and operation of sump pump. | 2
LIC18051 | 2000-F18-PID-PR-10002 | F18CF501 Froth | Analogue PID | A_HH | 700 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to promptly review and bring level down to ensure Jameson cell performance is optimal. | B
PI18054 | 2000-F18-PID-PR-10002 | F18CF501 Cleaner Feed | Analogue Input | A_Lo | 80 | kPa | 5 | F18PP501 AND 502 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-501 OR 502 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to review process. | B
PI18054 | 2000-F18-PID-PR-10002 | F18CF501 Cleaner Feed | Analogue Input | A_Hi | 200 | kPa | 5 | F18PP501 AND 502 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-501 OR 502 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review process. | B
PI18054 | 2000-F18-PID-PR-10002 | F18CF501 Cleaner Feed | Analogue Input | A_HH | 249 | kPa | 5 | F18PP501 AND 502 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-501 OR 502 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate Jameson Cell for downcomer blockage, closed downcomer valves. Consult Vendor IOM and/or Functional Description. | B
PI18054 | 2000-F18-PID-PR-10002 | F18CF501 Cleaner Feed | Analogue Input | A_LL | 50 | kPa | 5 | F18PP501 AND 502 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-501 OR 502 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of low pressure at Jameson Cell Slurry Distributor. | B
PI18055 | 2000-F18-PID-PR-10002 | F18CF501 Feed Air | Analogue Input | A_Lo | -30 | kPa | 5 | F18PP501 AND 502 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-501 OR 502 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator Configurable Alarm. Default Listed. Operator to investigate cause of low feed air pressure. | C
PI18055 | 2000-F18-PID-PR-10002 | F18CF501 Feed Air | Analogue Input | A_Hi | -10 | kPa | 5 | F18PP501 AND 502 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-501 OR 502 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator Configurable Alarm. Default Listed. Operator to investigate cause of high feed air pressure. | C
FIC18056 | 2000-F18-PID-PR-10002 | F18CF501 Air Ctrl | Analogue PID | A_LL | 200 | Sm3/hr | 5 | A_LL: DUTY F18PP501/502 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP501/502 Start-Up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate. Jameson Cell operation outside Vendor recommended operation parameters. | 0
FIC18057 | 2000-F18-PID-PR-10002 | F18CF501 Conc Water Ctrl | Analogue PID | A_LL | 5 | m3/hr | 5 | A_LL: DUTY F18PP501/502 NOT RUNNING A_Lo: DUTY F18PP501/502 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP501/502 Start-Up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate operation of High Pressure Process Water Pumps. | C
FIC18057 | 2000-F18-PID-PR-10002 | F18CF501 Conc Water Ctrl | Analogue PID | A_Lo | 106 | m3/hr | 5 | A_LL: DUTY F18PP501/502 NOT RUNNING A_Lo: DUTY F18PP501/502 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP501/502 Start-Up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate operation of High Pressure Process Water Pumps and flow of high pressure process water to Jameson Cell. | C
FIC18057 | 2000-F18-PID-PR-10002 | F18CF501 Conc Water Ctrl | Analogue PID | A_Hi | 350 | m3/hr | 5 | A_LL: DUTY F18PP501/502 NOT RUNNING A_Lo: DUTY F18PP501/502 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP501/502 Start-Up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate control method of Jameson Cell wash water. | C
LIC18201A | 2000-F18-PID-PR-10003 | F18HP511 Water Ctrl | Analogue PID | A_LL | 20 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of Cleaner Scavenger Feed hopper low-low. | 1
LIC18201A | 2000-F18-PID-PR-10003 | F18HP511 Water Ctrl | Analogue PID | A_Lo | 30 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to review flotation system to ascertain cause of dropping Cleaner Scavenger Feed hopper level. | 1
LIC18201A | 2000-F18-PID-PR-10003 | F18HP511 Water Ctrl | Analogue PID | A_Hi | 80 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to review flotation system to ascertain cause of rising Cleaner Scavenger Feed hopper level. | 1
LIC18201A | 2000-F18-PID-PR-10003 | F18HP511 Water Ctrl | Analogue PID | A_HH | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to review flotation system to ascertain cause of rising Cleaner Scavenger Feed hopper level. | 1
LIC18211A | 2000-F18-PID-PR-10003 | F18HP513 Water Ctrl | Analogue PID | A_LL | 20 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of Cleaner Scavenger Tails hopper low-low. | 1
LIC18211A | 2000-F18-PID-PR-10003 | F18HP513 Water Ctrl | Analogue PID | A_Lo | 30 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to review flotation system to ascertain cause of dropping Cleaner Scavenger Tails hopper level. | 1
LIC18211A | 2000-F18-PID-PR-10003 | F18HP513 Water Ctrl | Analogue PID | A_Hi | 80 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to review flotation system to ascertain cause of rising Cleaner Scavenger Tails hopper level. | 1
LIC18211A | 2000-F18-PID-PR-10003 | F18HP513 Water Ctrl | Analogue PID | A_HH | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to review flotation system to ascertain cause of rising Cleaner Scavenger Tails hopper level. | 1
FIC18227 | 2000-F18-PID-PR-10003 | F18PP511/2 Ctrl | Analogue PID | A_LL | 400 | m3/hr | 5 | DUTY F18PP511/512 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP511 OR 512 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Plant tripped to protect pump. Operator to investigate cause and engage standby pump is available. | B
FIC18227 | 2000-F18-PID-PR-10003 | F18PP511/2 Ctrl | Analogue PID | A_Lo | 1990 | m3/hr | 5 | DUTY F18PP511/512 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP511 OR 512 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to review cause of low flow and respond appropriately. | B
FIC18227 | 2000-F18-PID-PR-10003 | F18PP511/2 Ctrl | Analogue PID | A_Hi | 2050 | m3/hr | 5 | DUTY F18PP511/512 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP511 OR 512 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of high flow and respond appropriately. | B
FI18237 | 2000-F18-PID-PR-10003 | F18PP513/514 Discharge | Analogue Input | A_LL | 300 | m3/h | 5 | F18PP513 AND 514 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-513 OR 514 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Plant tripped to protect pump. Operator to investigate cause and engage standby pump if available. | B
FI18237 | 2000-F18-PID-PR-10003 | F18PP513/514 Discharge | Analogue Input | A_Lo | 400 | m3/h | 5 | F18PP513 AND 514 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-513 OR 514 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to review process. | B
FI18237 | 2000-F18-PID-PR-10003 | F18PP513/514 Discharge | Analogue Input | A_Hi | 1400 | m3/h | 5 | F18PP513 AND 514 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-513 OR 514 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review process. | B
DNI18237 | 2000-F18-PID-PR-10003 | F18PP513/514 D/C Solids | Analogue Input | A_Lo | 5 | %w/w | 5 | F18PP513 AND 514 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-513 OR 514 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review process. | 1
DNI18237 | 2000-F18-PID-PR-10003 | F18PP513/514 D/C Solids | Analogue Input | A_Hi | 30 | %w/w | 5 | F18PP513 AND 514 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-513 OR 514 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review process to prevent line sanding. | 1
LIC18251 | 2000-F18-PID-PR-10002 | F18CF511 Froth | Analogue PID | A_HH | 700 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate control method of Jameson Cell Froth Level Controller and/or alternate causes of high high level. | C
PI18254 | 2000-F18-PID-PR-10004 | F18CF511 Clnr-Scav Feed | Analogue Input | A_Lo | 80 | kPa | 5 | F18PP511 AND 512 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-511 OR 512 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to review process. | B
PI18254 | 2000-F18-PID-PR-10004 | F18CF511 Clnr-Scav Feed | Analogue Input | A_Hi | 200 | kPa | 5 | F18PP511 AND 512 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-511 OR 512 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review process. | B
PI18254 | 2000-F18-PID-PR-10004 | F18CF511 Clnr-Scav Feed | Analogue Input | A_HH | 249 | kPa | 5 | F18PP511 AND 512 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-511 OR 512 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate Jameson Cell for downcomer blockage, closed downcomer valves. Consult Vendor IOM and/or Functional Description. | B
PI18254 | 2000-F18-PID-PR-10004 | F18CF511 Clnr-Scav Feed | Analogue Input | A_LL | 50 | kPa | 5 | F18PP511 AND 512 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-511 OR 512 start-up. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of low pressure at Jameson Cell Slurry Distributor. | B
PI18255 | 2000-F18-PID-PR-10004 | F18CF511 Feed Air | Analogue Input | A_Lo | -30 | kPa | 5 | F18PP511 AND 512 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-511 OR 512 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator Configurable Alarm. Default Listed. Operator to investigate cause of low feed air pressure. | 0
PI18255 | 2000-F18-PID-PR-10004 | F18CF511 Feed Air | Analogue Input | A_Hi | -10 | kPa | 5 | F18PP511 AND 512 NOT RUNNING Alarm enabled delay of 10 seconds (to be confirmed during commissioning) on F18-PP-511 OR 512 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator Configurable Alarm. Default Listed. Operator to investigate cause of high feed air pressure. | 0
FIC18256 | 2000-F18-PID-PR-10004 | F18CF511 Air Ctrl | Analogue PID | A_LL | 200 | Sm3/hr | 5 | A_LL: DUTY F18PP511/512 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP511 OR 512 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate. Jameson Cell operation outside Vendor recommended operation parameters. | B
FIC18257 | 2000-F18-PID-PR-10004 | F18CF511 Conc Water Ctrl | Analogue PID | A_LL | 5 | m3/hr | 5 | A_LL: DUTY F18PP511/512 NOT RUNNING A_Lo: DUTY F18PP511/512 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP511 OR 512 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Concentrate wash water low-low. Operator to review and remediate. | B
FIC18257 | 2000-F18-PID-PR-10004 | F18CF511 Conc Water Ctrl | Analogue PID | A_Lo | 19 | m3/hr | 5 | A_LL: DUTY F18PP511/512 NOT RUNNING A_Lo: DUTY F18PP511/512 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP511 OR 512 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Concentrate wash water low. Operator to review and remediate. | B
FIC18257 | 2000-F18-PID-PR-10004 | F18CF511 Conc Water Ctrl | Analogue PID | A_Hi | 64 | m3/hr | 5 | A_LL: DUTY F18PP511/512 NOT RUNNING A_Lo: DUTY F18PP511/512 NOT RUNNING Alarm enabled delay of 10 seconds during F18PP511 OR 512 start-up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Concentrate wash water high. Operator to review and remediate. | B
FAL18501 | 2000-F24-PID-PR-10003 | F18PP407 Gland | Digital Input | Alarm |  |  | 3 | F18PP407 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Gland flow low. Operator to review gland delivery and utilise standby pump if available. | 3
FAL18505 | 2000-F24-PID-PR-10003 | F18PP408 Gland | Digital Input | Alarm |  |  | 3 | F18PP408 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Gland flow low. Operator to review gland delivery and utilise standby pump if available. | 3
FAL18509 | 2000-F24-PID-PR-10003 | F18PP501 Gland | Digital Input | Alarm |  |  | 3 | F18PP501 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Gland flow low. Operator to review gland delivery and utilise standby pump if available. | 3
FAL18513 | 2000-F24-PID-PR-10003 | F18PP502 Gland | Digital Input | Alarm |  |  | 3 | F18PP502 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Gland flow low. Operator to review gland delivery and utilise standby pump if available. | 3
FAL18525 | 2000-F24-PID-PR-10003 | F18PP511 Gland | Digital Input | Alarm |  |  | 3 | F18PP511 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Gland flow low. Operator to review gland delivery and utilise standby pump if available. | 3
FAL18529 | 2000-F24-PID-PR-10003 | F18PP512 Gland | Digital Input | Alarm |  |  | 3 | F18PP512 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Gland flow low. Operator to review gland delivery and utilise standby pump if available. | 3
FAL18533 | 2000-F24-PID-PR-10003 | F18PP513 Gland | Digital Input | Alarm |  |  | 3 | F18PP513 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Gland flow low. Operator to review gland delivery and utilise standby pump if available. | 3
FAL18537 | 2000-F24-PID-PR-10003 | F18PP514 Gland | Digital Input | Alarm |  |  | 3 | F18PP514 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Gland flow low. Operator to review gland delivery and utilise standby pump if available. | 3
TI18542A | 2000-F18-PID-PR-10001 | F18PP501 Motor P.U RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18542A | 2000-F18-PID-PR-10001 | F18PP501 Motor P.U RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18542B | 2000-F18-PID-PR-10001 | F18PP501 Motor P.V RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18542B | 2000-F18-PID-PR-10001 | F18PP501 Motor P.V RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18542C | 2000-F18-PID-PR-10001 | F18PP501 Motor P.W RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18542C | 2000-F18-PID-PR-10001 | F18PP501 Motor P.W RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18542D | 2000-F18-PID-PR-10001 | F18PP501 DE Bearing | Analogue Input | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | C
TI18542D | 2000-F18-PID-PR-10001 | F18PP501 DE Bearing | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | C
TI18542E | 2000-F18-PID-PR-10001 | F18PP501 NDE Bearing | Analogue Input | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | C
TI18542E | 2000-F18-PID-PR-10001 | F18PP501 NDE Bearing | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | C
TI18543A | 2000-F18-PID-PR-10001 | F18PP502 Motor P.U RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18543A | 2000-F18-PID-PR-10001 | F18PP502 Motor P.U RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18543B | 2000-F18-PID-PR-10001 | F18PP502 Motor P.V RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18543B | 2000-F18-PID-PR-10001 | F18PP502 Motor P.V RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18543C | 2000-F18-PID-PR-10001 | F18PP502 Motor P.W RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18543C | 2000-F18-PID-PR-10001 | F18PP502 Motor P.W RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18543D | 2000-F18-PID-PR-10001 | F18PP502 DE Bearing | Analogue Input | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | C
TI18543D | 2000-F18-PID-PR-10001 | F18PP502 DE Bearing | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | C
TI18543E | 2000-F18-PID-PR-10001 | F18PP502 NDE Bearing | Analogue Input | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | C
TI18543E | 2000-F18-PID-PR-10001 | F18PP502 NDE Bearing | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | C
TI18546A | 2000-F18-PID-PR-10001 | F18PP511 Motor P.U RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18546A | 2000-F18-PID-PR-10001 | F18PP511 Motor P.U RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18546B | 2000-F18-PID-PR-10001 | F18PP511 Motor P.V RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18546B | 2000-F18-PID-PR-10001 | F18PP511 Motor P.V RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18546C | 2000-F18-PID-PR-10001 | F18PP511 Motor P.W RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18546C | 2000-F18-PID-PR-10001 | F18PP511 Motor P.W RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18546D | 2000-F18-PID-PR-10001 | F18PP511 DE Bearing | Analogue Input | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | C
TI18546D | 2000-F18-PID-PR-10001 | F18PP511 DE Bearing | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | C
TI18546E | 2000-F18-PID-PR-10001 | F18PP511 NDE Bearing | Analogue Input | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | C
TI18546E | 2000-F18-PID-PR-10001 | F18PP511 NDE Bearing | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | C
TI18547A | 2000-F18-PID-PR-10001 | F18PP512 Motor P.U RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18547A | 2000-F18-PID-PR-10001 | F18PP512 Motor P.U RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18547B | 2000-F18-PID-PR-10001 | F18PP512 Motor P.V RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18547B | 2000-F18-PID-PR-10001 | F18PP512 Motor P.V RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18547C | 2000-F18-PID-PR-10001 | F18PP512 Motor P.W RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18547C | 2000-F18-PID-PR-10001 | F18PP512 Motor P.W RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18547D | 2000-F18-PID-PR-10001 | F18PP512 DE Bearing | Analogue Input | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | C
TI18547D | 2000-F18-PID-PR-10001 | F18PP512 DE Bearing | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | C
TI18547E | 2000-F18-PID-PR-10001 | F18PP512 NDE Bearing | Analogue Input | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | C
TI18547E | 2000-F18-PID-PR-10001 | F18PP512 NDE Bearing | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | C
TI18550A | 2000-F18-PID-PR-10001 | F18PP513 Motor P.U RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18550A | 2000-F18-PID-PR-10001 | F18PP513 Motor P.U RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18550B | 2000-F18-PID-PR-10001 | F18PP513 Motor P.V RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18550B | 2000-F18-PID-PR-10001 | F18PP513 Motor P.V RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18550C | 2000-F18-PID-PR-10001 | F18PP513 Motor P.W RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18550C | 2000-F18-PID-PR-10001 | F18PP513 Motor P.W RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18550D | 2000-F18-PID-PR-10001 | F18PP513 DE Bearing | Analogue Input | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | C
TI18550D | 2000-F18-PID-PR-10001 | F18PP513 DE Bearing | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | C
TI18550E | 2000-F18-PID-PR-10001 | F18PP513 NDE Bearing | Analogue Input | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | C
TI18550E | 2000-F18-PID-PR-10001 | F18PP513 NDE Bearing | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | C
TI18551A | 2000-F18-PID-PR-10001 | F18PP514 Motor P.U RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18551A | 2000-F18-PID-PR-10001 | F18PP514 Motor P.U RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18551B | 2000-F18-PID-PR-10001 | F18PP514 Motor P.V RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18551B | 2000-F18-PID-PR-10001 | F18PP514 Motor P.V RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18551C | 2000-F18-PID-PR-10001 | F18PP514 Motor P.W RTD | Analogue Input | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 1
TI18551C | 2000-F18-PID-PR-10001 | F18PP514 Motor P.W RTD | Analogue Input | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 1
TI18551D | 2000-F18-PID-PR-10001 | F18PP514 DE Bearing | Analogue Input | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | C
TI18551D | 2000-F18-PID-PR-10001 | F18PP514 DE Bearing | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | C
TI18551E | 2000-F18-PID-PR-10001 | F18PP514 NDE Bearing | Analogue Input | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to consider shutting unit down and inspecting in field. | C
TI18551E | 2000-F18-PID-PR-10001 | F18PP514 NDE Bearing | Analogue Input | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | C
F16FIP002_ISL | N/A | F16FIP002 Isolate | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 2
F16SW104_SD | N/A | F16SW104 Surge Diverter | Digital Input | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Electrician to investigate | 2
F16DCS408_PS1 | N/A | F16DCS408 PS1 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 1
F16DCS408_PS2 | N/A | F16DCS408 PS2 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F16SR002_ESTP | N/A | F16SR002 Estop | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Switchroom tripped. Electrician to investigate | 2
LAHH16035 | N/A | F16GE001 Fuel Level | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to cease re-fuelling immediately, likely diesel spillage. Operator to investigat in-field and respond in-line with company combustible material spillage protocol. | 2
LAH16035 | N/A | F16GE001 Fuel Level | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | High fuel level in generator fuel reservoir. Operator to radio local field operator to cease re-fuelling. | 2
LAL16035 | N/A | F16GE001 Fuel Level | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operational risk for backup power. Operator to organise re-fuelling. | 2
LAHH16036 | N/A | F16GE104 Fuel Level | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to cease re-fuelling immediately, likely diesel spillage. Operator to investigat in-field and respond in-line with company combustible material spillage protocol. | 2
LAH16036 | N/A | F16GE104 Fuel Level | Digital Input | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | High fuel level in generator fuel reservoir. Operator to radio local field operator to cease re-fuelling. | 2
LAL16036 | N/A | F16GE104 Fuel Level | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operational risk for backup power. Operator to organise re-fuelling. | 2
F16BC001_FL1 | N/A | F16BC001 Charger Mains | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
F16BC001_FL2 | N/A | F16BC001 Charger Battery | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
F16FIP001_ISL | N/A | F16FIP001 Isolate | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 2
F16FIP002_ALM | N/A | F16FIP002 Alarm | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 2
F16FIP002_FLT | N/A | F16FIP002 Fault | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 2
F16SW011A02FH | N/A | F16SW011 A02 Fuse | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder tripped. Electrician to investigate | 2
F16SW011A03FH | N/A | F16SW011 A03 Fuse | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder tripped. Electrician to investigate | 2
F16SW011A04FH | N/A | F16SW011 A04 Fuse | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder tripped. Electrician to investigate | 2
F16SW011A05FH | N/A | F16SW011 A05 Fuse | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder tripped. Electrician to investigate | 2
F16SW011A06FH | N/A | F16SW011 A06 Fuse | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder tripped. Electrician to investigate | 2
F16SW011A07FH | N/A | F16SW011 A07 Fuse | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder tripped. Electrician to investigate | 2
F16SW011A08FH | N/A | F16SW011 A08 Fuse | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder tripped. Electrician to investigate | 2
F16SW011A10FH | N/A | F16SW011 A10 Fuse | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder tripped. Electrician to investigate | 2
F16SW011A11FH | N/A | F16SW011 A11 Fuse | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder tripped. Electrician to investigate | 2
F16SW011A16FH | N/A | F16SW011 A16 Fuse | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder tripped. Electrician to investigate | 2
F16SW011A17FH | N/A | F16SW011 A17 Fuse | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder tripped. Electrician to investigate | 2
F16SW011A18FH | N/A | F16SW011 A18 Fuse | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder tripped. Electrician to investigate | 2
F16SW011A19FH | N/A | F16SW011 A19 Fuse | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Feeder tripped. Electrician to investigate | 2
F16FIP001_ALM | N/A | Flot 11kV SR Fire Alarm | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire alarm. Follow site specific Fire Emergency Plan. | 2
F16FIP001_FLT | N/A | Flot 11kV SR Fire Fault | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire alarm fault. Follow site specific Fire Emergency Plan. | 2
F16SR001_ESTP | N/A | Flot 11kV SR E Shut | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Switchroom tripped. Electrician to investigate | 2
F17RIO001_PS1 | N/A | F17RIO001 PS1 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F17RIO001_PS2 | N/A | F17RIO001 PS2 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F16RIO001_PS1 | N/A | F16RIO001 PS1 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F16RIO001_PS2 | N/A | F16RIO001 PS2 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F16RIO002_PS1 | N/A | F16RIO002 PS1 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F16RIO002_PS2 | N/A | F16RIO002 PS2 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F17RIO002_PS1 | N/A | F17RIO002 PS1 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F17RIO002_PS2 | N/A | F17RIO002 PS2 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F18RIO001_PS1 | N/A | F18RIO001 PS1 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F18RIO001_PS2 | N/A | F18RIO001 PS2 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F18RIO002_PS1 | N/A | F18RIO002 PS1 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F18RIO002_PS2 | N/A | F18RIO002 PS2 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F16RIO100_PS1 | N/A | F16RIO100 PS1 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
F16RIO100_PS2 | N/A | F16RIO100 PS2 24VDC | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to get electrician to inspect unit for potential failure | 2
XA16168 | N/A | F16AN402 General Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Particle Size Analyser - General Alarm | 2
F16AN402_FL1 | N/A | F16AN402 Assy1 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Particle Size Analyser - Assay 1 Invalid | 2
F16AN402_FL2 | N/A | F16AN402 Assy2 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Particle Size Analyser - Assay 2 Invalid | 2
F16AN402_FL3 | N/A | F16AN402 Assy3 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Particle Size Analyser - Assay 3 Invalid | 2
F16AN402_FL4 | N/A | F16AN402 Assy4 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Particle Size Analyser - Assay 4 Invalid | 2
F16AN402_FL5 | N/A | F16AN402 Assy5 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Particle Size Analyser - Assay 5 Invalid | 2
F16AN402_FL6 | N/A | F16AN402 Assy6 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Particle Size Analyser - Assay 6 Invalid | 2
F16AN402_FL7 | N/A | F16AN402 Assy7 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Particle Size Analyser - Assay 7 Invalid | 2 |  |  |  |  | Operator to get electrician to inspect unit for potential failure
F16AN402_FL8 | N/A | F16AN402 Assy8 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Particle Size Analyser - Assay 8 Invalid | 2
F16AN402_FL9 | N/A | F16AN402 Assy9 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Particle Size Analyser - Assay 9 Invalid | 2
F16AN402_FL10 | N/A | F16AN402 Assy10 Alarm | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Particle Size Analyser - Assay 10 Invalid | 2
XA16176 | N/A | F16AN403 Analyser Warn | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Generic Analyser Warning. Onstream Analyser. | 2
XA16177 | N/A | F16AN403 Analyser Alarm | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Generic Analyser Alarm. Onstream Analyser. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S1W | 2000-F16-PID-PR-10005 | F16AN403 S1 Warning | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Warning. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S2W | 2000-F16-PID-PR-10006 | F16AN403 S2 Warning | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Warning. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S3W | 2000-F16-PID-PR-10007 | F16AN403 S3 Warning | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Warning. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S4W | 2000-F16-PID-PR-10008 | F16AN403 S4 Warning | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Warning. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S5W | 2000-F16-PID-PR-10009 | F16AN403 S5 Warning | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Warning. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S6W | 2000-F16-PID-PR-10010 | F16AN403 S6 Warning | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Warning. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S7W | 2000-F16-PID-PR-10011 | F16AN403 S7 Warning | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Warning. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S8W | 2000-F16-PID-PR-10012 | F16AN403 S8 Warning | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Warning. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S9W | 2000-F16-PID-PR-10013 | F16AN403 S9 Warning | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Warning. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S10W | 2000-F16-PID-PR-10014 | F16AN403 S10 Warning | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Warning. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S11W | 2000-F16-PID-PR-10015 | F16AN403 S11 Warning | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Warning. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S12W | 2000-F16-PID-PR-10016 | F16AN403 S12 Warning | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Warning. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S1AL | 2000-F16-PID-PR-10005 | F16AN403 S1 Alarm | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Alarm. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S2AL | 2000-F16-PID-PR-10006 | F16AN403 S2 Alarm | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Alarm. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S3AL | 2000-F16-PID-PR-10007 | F16AN403 S3 Alarm | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Alarm. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S4AL | 2000-F16-PID-PR-10008 | F16AN403 S4 Alarm | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Alarm. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S5AL | 2000-F16-PID-PR-10009 | F16AN403 S5 Alarm | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Alarm. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S6AL | 2000-F16-PID-PR-10010 | F16AN403 S6 Alarm | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Alarm. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S7AL | 2000-F16-PID-PR-10011 | F16AN403 S7 Alarm | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Alarm. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S8AL | 2000-F16-PID-PR-10012 | F16AN403 S8 Alarm | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Alarm. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S9AL | 2000-F16-PID-PR-10013 | F16AN403 S9 Alarm | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Alarm. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S10A | 2000-F16-PID-PR-10014 | F16AN403 S10 Alarm | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Alarm. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S11A | 2000-F16-PID-PR-10015 | F16AN403 S11 Alarm | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Alarm. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S12A | 2000-F16-PID-PR-10016 | F16AN403 S12 Alarm | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Alarm. Operator to consult local OSA HMI for diagnosis. | 2
F16AN403S1NE | 2000-F16-PID-PR-10005 | F16AN403 S1 Not Exec | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not executable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S2NE | 2000-F16-PID-PR-10006 | F16AN403 S2 Not Exec | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not executable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S3NE | 2000-F16-PID-PR-10007 | F16AN403 S3 Not Exec | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not executable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S4NE | 2000-F16-PID-PR-10008 | F16AN403 S4 Not Exec | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not executable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S5NE | 2000-F16-PID-PR-10009 | F16AN403 S5 Not Exec | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not executable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S6NE | 2000-F16-PID-PR-10010 | F16AN403 S6 Not Exec | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not executable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S7NE | 2000-F16-PID-PR-10011 | F16AN403 S7 Not Exec | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not executable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S8NE | 2000-F16-PID-PR-10012 | F16AN403 S8 Not Exec | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not executable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S9NE | 2000-F16-PID-PR-10013 | F16AN403 S9 Not Exec | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not executable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S10E | 2000-F16-PID-PR-10014 | F16AN403 S10 Not Exec | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not executable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S11E | 2000-F16-PID-PR-10015 | F16AN403 S11 Not Exec | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not executable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S12E | 2000-F16-PID-PR-10016 | F16AN403 S12 Not Exec | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not executable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S1NM | 2000-F16-PID-PR-10005 | F16AN403 S1 Not Meas | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not Measureable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S2NM | 2000-F16-PID-PR-10006 | F16AN403 S2 Not Meas | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not Measureable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S3NM | 2000-F16-PID-PR-10007 | F16AN403 S3 Not Meas | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not Measureable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S4NM | 2000-F16-PID-PR-10008 | F16AN403 S4 Not Meas | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not Measureable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S5NM | 2000-F16-PID-PR-10009 | F16AN403 S5 Not Meas | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not Measureable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S6NM | 2000-F16-PID-PR-10010 | F16AN403 S6 Not Meas | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not Measureable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S7NM | 2000-F16-PID-PR-10011 | F16AN403 S7 Not Meas | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not Measureable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S8NM | 2000-F16-PID-PR-10012 | F16AN403 S8 Not Meas | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not Measureable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S9NM | 2000-F16-PID-PR-10013 | F16AN403 S9 Not Meas | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not Measureable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S10NM | 2000-F16-PID-PR-10014 | F16AN403 S10 Not Meas | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not Measureable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S11NM | 2000-F16-PID-PR-10015 | F16AN403 S11 Not Meas | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not Measureable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S12NM | 2000-F16-PID-PR-10016 | F16AN403 S12 Not Meas | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Sample No. "n" Not Measureable. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S1MR | 2000-F16-PID-PR-10005 | F16AN403 S1 Results Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Results Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S2MR | 2000-F16-PID-PR-10006 | F16AN403 S2 Results Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Results Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S3MR | 2000-F16-PID-PR-10007 | F16AN403 S3 Results Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Results Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S4MR | 2000-F16-PID-PR-10008 | F16AN403 S4 Results Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Results Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S5MR | 2000-F16-PID-PR-10009 | F16AN403 S5 Results Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Results Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S6MR | 2000-F16-PID-PR-10010 | F16AN403 S6 Results Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Results Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S7MR | 2000-F16-PID-PR-10011 | F16AN403 S7 Results Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Results Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S8MR | 2000-F16-PID-PR-10012 | F16AN403 S8 Results Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Results Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S9MR | 2000-F16-PID-PR-10013 | F16AN403 S9 Results Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Results Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S10MR | 2000-F16-PID-PR-10014 | F16AN403 S10 Results Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Results Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S11MR | 2000-F16-PID-PR-10015 | F16AN403 S11 Results Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Results Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S12MR | 2000-F16-PID-PR-10016 | F16AN403 S12 Results Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Results Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S1AV | 2000-F16-PID-PR-10005 | F16AN403 S1 Analysis Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Analysis Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S2AV | 2000-F16-PID-PR-10006 | F16AN403 S2 Analysis Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Analysis Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S3AV | 2000-F16-PID-PR-10007 | F16AN403 S3 Analysis Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Analysis Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S4AV | 2000-F16-PID-PR-10008 | F16AN403 S4 Analysis Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Analysis Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S5AV | 2000-F16-PID-PR-10009 | F16AN403 S5 Analysis Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Analysis Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S6AV | 2000-F16-PID-PR-10010 | F16AN403 S6 Analysis Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Analysis Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S7AV | 2000-F16-PID-PR-10011 | F16AN403 S7 Analysis Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Analysis Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S8AV | 2000-F16-PID-PR-10012 | F16AN403 S8 Analysis Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Analysis Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S9AV | 2000-F16-PID-PR-10013 | F16AN403 S9 Analysis Flt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Analysis Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S10AV | 2000-F16-PID-PR-10014 | F16AN403 S10 AnalysisFlt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Analysis Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S11AV | 2000-F16-PID-PR-10015 | F16AN403 S11 AnalysisFlt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Analysis Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
F16AN403S12AV | 2000-F16-PID-PR-10016 | F16AN403 S12 AnalysisFlt | Digital Input | Active |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Sample No. "n" Analysis Fault. Operator to consult local OSA HMI and vendor IOM for diagnosis. | 2
ZAC16037 | N/A | F16TR004 415VMCC Door | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Restricted work area potential safety breach/issue | 2
ZAC16039 | N/A | F16TR008 415VMCC Door | Digital Input | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Restricted work area potential safety breach/issue | 2
F16SW011_HTY | N/A | F16SW011 Fuse Healthy | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | Urgent | Electrician to investigate | 2
F16XM411VSTS | 2000-F16-PID-PR-10001 | F16XM411 VelocityStatus | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM411CSTS | 2000-F16-PID-PR-10001 | F16XM411 Colour Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM411BSTS | 2000-F16-PID-PR-10001 | F16XM411 Bubble Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM411LSTS | 2000-F16-PID-PR-10001 | F16XM411 Lidar Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM586VSTS | 2000-F16-PID-PR-10002 | F16XM586 VelocityStatus | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM586CSTS | 2000-F16-PID-PR-10002 | F16XM586 Colour Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM586BSTS | 2000-F16-PID-PR-10002 | F16XM586 Bubble Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM586LSTS | 2000-F16-PID-PR-10002 | F16XM586 Lidar Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM587VSTS | 2000-F16-PID-PR-10002 | F16XM587 VelocityStatus | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM587CSTS | 2000-F16-PID-PR-10002 | F16XM587 Colour Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM587BSTS | 2000-F16-PID-PR-10002 | F16XM587 Bubble Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM587LSTS | 2000-F16-PID-PR-10002 | F16XM587 Lidar Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM588VSTS | 2000-F16-PID-PR-10003 | F16XM588 VelocityStatus | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM588CSTS | 2000-F16-PID-PR-10003 | F16XM588 Colour Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM588BSTS | 2000-F16-PID-PR-10003 | F16XM588 Bubble Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM588LSTS | 2000-F16-PID-PR-10003 | F16XM588 Lidar Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM589VSTS | 2000-F16-PID-PR-10003 | F16XM589 VelocityStatus | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM589CSTS | 2000-F16-PID-PR-10003 | F16XM589 Colour Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM589BSTS | 2000-F16-PID-PR-10003 | F16XM589 Bubble Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM589LSTS | 2000-F16-PID-PR-10003 | F16XM589 Lidar Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM590VSTS | 2000-F16-PID-PR-10003 | F16XM590 VelocityStatus | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM590CSTS | 2000-F16-PID-PR-10003 | F16XM590 Colour Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM590BSTS | 2000-F16-PID-PR-10003 | F16XM590 Bubble Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM590LSTS | 2000-F16-PID-PR-10003 | F16XM590 Lidar Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM591VSTS | 2000-F16-PID-PR-10003 | F16XM591 VelocityStatus | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM591CSTS | 2000-F16-PID-PR-10003 | F16XM591 Colour Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM591BSTS | 2000-F16-PID-PR-10003 | F16XM591 Bubble Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F16XM591LSTS | 2000-F16-PID-PR-10003 | F16XM591 Lidar Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
F18CAM101VSTS | 2000-F18-PID-PR-10002 | F18CAM101 VelocityStatus | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
F18CAM101CSTS | 2000-F18-PID-PR-10002 | F18CAM101 Colour Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
F18CAM101BSTS | 2000-F18-PID-PR-10002 | F18CAM101 Bubble Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
F18CAM101LSTS | 2000-F18-PID-PR-10002 | F18CAM101 Lidar Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
F18CAM102VSTS | 2000-F18-PID-PR-10004 | F18CAM102 VelocityStatus | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
F18CAM102CSTS | 2000-F18-PID-PR-10004 | F18CAM102 Colour Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
F18CAM102BSTS | 2000-F18-PID-PR-10004 | F18CAM102 Bubble Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
F18CAM102LSTS | 2000-F18-PID-PR-10004 | F18CAM102 Lidar Status | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
XA17038B | 2000-F17-PID-PR-10001 | F17XM572 Fault | Digital Input | Alarm |  |  | 3 |  | Financial3: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Investigate - determine what faults are present via the Manta Sub diagnostics page or by having the field operator check the Manta Sub panel HMI.
F17XM572ESTP | 2000-F17-PID-PR-10001 | F17XM572 EStop | Digital Input | Alarm |  |  | 0 |  | Personnel1: First Aid Injury, Reversible health effects | Immediate (<5 minutes) | High | Contact the area to determine if anyone requires assistance.
XA17038 | 2000-F17-PID-PR-10001 | F17XM572 Failed to Home | Digital Input | Alarm |  |  | 3 | F17XM572ESTP OR XA17038 OR F17XM572PEF OR XA17012COMF | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Send field operator to determine why the sensor is not in the wash bay.
F17XM572PEF | 2000-F17-PID-PR-10001 | F17XM572 Probe Entangle | Digital Input | Alarm |  |  | 3 |  | Financial3: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Send field operator to determine why the sensor is not in the wash bay. Consider stopping the rake if probe is about to become caught by the rake.
XA17012COMF | 2000-F17-PID-PR-10001 | F17XM572 Comms Fault | Digital Input | Alarm |  |  | 10 |  | Financial3: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Escalate to the Process Control Team.
F17XM572SJALM | 2000-F17-PID-PR-10001 | F17XM572 Sensor Jammed | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Arrange for Maintenance to investigate - wash bay rollers binding, scale on the probe.
F17XM572DRALM | 2000-F17-PID-PR-10001 | F17XM572 Drive Fault | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Arrange for Maintenance to investigate - winch drum jammed, motor failed, encoder failed or loose connection, drive shaft failed.
F17XM572SRFAL | 2000-F17-PID-PR-10001 | F17XM572 Recovery Fail | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Arrange for an Electrician to check the wash bay proximity sensors and adjust.
F17XM572SRLAL | 2000-F17-PID-PR-10001 | F17XM572 Recovery Lower | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Arrange for Maintenance to investigate - wash bay rollers binding, scale on the probe.
F17XM572SOLAL | 2000-F17-PID-PR-10001 | F17XM572 Rake Sw On Long | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Send field operator to investigate - check the operation of the rake switch.
F17XM572ESALM | 2000-F17-PID-PR-10001 | F17XM572 RakeSwitchEarly | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Send field operator to investigate - check the operation of the rake switch, check rake rotation time.
F17XM572LSALM | 2000-F17-PID-PR-10001 | F17XM572 RakeSwitchLate | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Send field operator to investigate - check the operation of the rake switch, check rake rotation time.
F17XM572DTALM | 2000-F17-PID-PR-10001 | F17XM572 DiveTime Exceed | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Arrange for Maintenance to check causes of restricted movement of the winch drum and operation of the motor.
F17XM572SFALM | 2000-F17-PID-PR-10001 | F17XM572 Sensor Fault | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Arrange for an Electrician to obtain the transmitter fault code and clean the probe.
F17XM572SDALM | 2000-F17-PID-PR-10001 | F17XM572 Sensor Dirty | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Arrange for the probe to be cleaned.
F17XM572CSF | 2000-F17-PID-PR-10001 | F17XM572 Clarity SensFlt | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Arrange for the probe to be cleaned. Arrange for an Electrician to check the sensor raw reading and to check slip rings and patch cables.
F17XM572MSFLT | 2000-F17-PID-PR-10001 | F17XM572 HeavyMudSwFault | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Arrange for maintenance to check the movement of the switch assembly and clean if necessary.
F17XM572CLF | 2000-F17-PID-PR-10001 | F17XM572 Clarity Lo Flt | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Arrange for an Electrician to check the sensor raw reading, perform a health check and zero the sensor.
F17XM572OFALM | 2000-F17-PID-PR-10001 | F17XM572 Prox Off Fault | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Arrange for an Electrician to check the wash bay proximity sensors and adjust.
F17XM572ONALM | 2000-F17-PID-PR-10001 | F17XM572 Prox On Fault | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Arrange for Maintenance to investigate - wash bay rollers binding, scale on the probe.
XI17066 | 2000-F17-PID-PR-10001 | F17TH401 Pwr Healthy | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
F16BC001_FL3 | 2000-F16-PID-PR-10001 | F16BC001 Charger Status | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
ZAC16038 | N/A | F16TR005 415VMCC Door | Digital Input | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 3
TAH17039 | 2000-F17-PID-PR-10001 | F17PP459 Motor Temp | Digital Input | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | P-Duc trip. Operator / Maintenance to investigate high motor temperature | 3
16SW011_V_LO | N/A | F16SW011 Voltage Low Alarm | Misc | Alarm |  |  | 300 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Confirm power outage event and initiate the Mains to 11kV Generator changeover sequence | 3
16SW011_V_OK | N/A | F16SW011 Voltage OK Alarm | Misc | Alarm |  |  | 600 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Confirm power supply is healthy and stable, and initiate the 11kV Generator to Mains changeover sequence | 3
FAH16002 | 2000-F24-PID-PR-10005 | F16SE410 Alarm | Digital Input | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 3
PI17140 | 2000-F17-PID-PR-10001 | F17HU422 Hyd Supply | Analogue Input | A_Hi | 15000 | kPa | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise Maintenance or Field Operator to check F17HU422 hydraulic oil filter and/or investigate hydraulic skid for other issues. | 3
PI17140 | 2000-F17-PID-PR-10001 | F17HU422 Hyd Supply | Analogue Input | A_HH | 16000 | kPa | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Maintenance or Field Operator to check F17HU422 hydraulic oil filter and/or investigate hydraulic skid for other issues. | 3
TI17141 | 2000-F17-PID-PR-10001 | F17HU422 Hyd Reservoir | Analogue Input | A_Hi | 65 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise Maintenance or Field Operator to check F17HU422 hydraulic oil filter and/or investigate hydraulic skid for other issues. | 3
TI17141 | 2000-F17-PID-PR-10001 | F17HU422 Hyd Reservoir | Analogue Input | A_HH | 70 | °C | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Maintenance or Field Operator to check F17HU422 hydraulic oil filter and/or investigate hydraulic skid for other issues. | 3
LI17142 | 2000-F17-PID-PR-10001 | F17HU422 Hyd Reservoir | Analogue Input | A_LL | 50 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Advise Maintenance or Field Operator to check F17HU422 hydraulic oil level and/or investigate hydraulic skid for other issues. | 3
LI17142 | 2000-F17-PID-PR-10001 | F17HU422 Hyd Reservoir | Analogue Input | A_Lo | 60 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise Maintenance or Field Operator to check F17HU422 hydraulic oil level and/or investigate hydraulic skid for other issues. | 3
PAH17143 | 2000-F17-PID-PR-10001 | F17HU422 Filter Return | Digital Input | Alarm (see comment) |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Advise Maintenance or Field Operator to check F17HU422 hydraulic oil filter and/or investigate hydraulic skid for other issues. | 3
F16TR004_WTH | - | F16TR004 Temp Hi | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrican to investigate high transformer winding temperature alarm | 3
F16TR005_WTH | - | F16TR005 Temp Hi | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrican to investigate high transformer winding temperature alarm | 3
F16TR008_WTH | - | F16TR008 Temp Hi | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrican to investigate high transformer winding temperature alarm | 3
TI17100 |  | F17PP455 GearBox Temp | Analogue Input | A_Hi | 85 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 4
TI17100 |  | F17PP455 GearBox Temp | Analogue Input | A_HH | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 4
TI17110 |  | F17PP456 GearBox Temp | Analogue Input | A_Hi | 85 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect unit in field. | 4
TI17110 |  | F17PP456 GearBox Temp | Analogue Input | A_HH | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to inspect unit in field. | 4
F16PP638_II | 2000-F16-PID-PR-10005 | F16PP638 Current | Analogue Input | A_HH | 77 | Amps | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | The sample return pump has tripped. Investigate potential pump faults or blockages in the line. If no issues are identified, review and revise the allarm setpoint to prevent spurious alarms or trips. | 4
F16PP638_II | 2000-F16-PID-PR-10005 | F16PP638 Current | Analogue Input | A_Hi | 62 | Amps | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Investigate pump issues / blockages in line. If no issues are identified, revise alarm setpoint if spurious alarms and/or trips are occurring. | 4
F16PP639_II | 2000-F16-PID-PR-10005 | F16PP639 Current | Analogue Input | A_HH | 77 | Amps | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | The sample return pump has tripped. Investigate potential pump faults or blockages in the line. If no issues are identified, review and revise the allarm setpoint to prevent spurious alarms or trips. | 4
F16PP639_II | 2000-F16-PID-PR-10005 | F16PP639 Current | Analogue Input | A_Hi | 62 | Amps | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Investigate pump issues / blockages in line. If no issues are identified, revise alarm setpoint if spurious alarms and/or trips are occurring. | 4
F16GE104CBTRP | - | F16-GE-104 GEN CB TRP | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to manually change over generator | 1

## 12. Misc
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION (F16, F17, F18)
2000-F16-LST-PR-10001
MISC. INSTRUMENTS AND CONTROLLERS
[10 empty] | C1 Sign Off |  | C2 Sign Off |  | Comments
Tag Name | P&ID | Description | Normal State | Alarm State | Hardwired (y/n) | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date
F17PO408_RT1 | 2000-ME001.5-E02-50002 | F17PO408 Shutdown Timer | INACTIVE | ACTIVE | N |  |  | Timer Duration: 1200 seconds. Engineer Configurable Range: 0 - 2400 seconds. Timer to count-down from nominated duration. Timer to count-down when: - SV17033 De-Energised AND SV17034 De-Energised AND F17PO408 Running Timer will reset and stop if: - SV17033 OR SV17034 are energised during count-down. - SV17033 De-Energised AND SV17034 De-Energised AND F17PO408 Not Running | C |  |  |  |  | Timer not resetting when its meant to 13/06/26
F17PO409_RT1 | 2000-ME001.5-E02-50003 | F17PO409 Shutdown Timer | INACTIVE | ACTIVE | N |  |  | Timer Duration: 300 seconds. Engineer Configurable Range: 0 - 600 seconds. Timer to count-down from nominated duration. Timer to start count-down when: - SV17047 De-Energised AND SV17048 De-Energised AND F17PO409 Running Timer will reset and stop if: - SV17048 OR SV17047 are energised during count-down. - SV17047 De-Energised AND SV17048 De-Energised AND F17PO409 Not Running | C
F17TH401_C1 | 2000-F17-PID-PR-10001 | F17TH401 Reverse Jog Action Counter | INACTIVE | ACTIVE | N |  |  | Increase counter by one when F17TH401_T1 = STARTED F17TH401_C1 to prevent further reverse jog activations if counter equals three (3) (Prevent Reverse Jog from being active (SV17034 from being Active)). No more than 3x attempts of reverse jog per 30 minute periods. Counter to reset after 30 minutes from elapse of F17TH401_T1. Display counter on DCS graphic. | 0
F17TH401_LCL | 2000-F17-PID-PR-10001 | F17TH401 Local Mode | INACTIVE | ACTIVE | N |  |  | LOCAL mode for the Flotation Tailings Thickener F17TH401. When active, allows the following equipment to be controlled from the field push buttons: - F17PO408, SV17033, SV17034 (F17HU406) - F17PO409, SV17047, SV17048 (F17HU414) Local mode applies to list above to activate appropriate Thickener Control Panel buttons. Please see Digital Inputs, OnOff Valves and Drives for further information. | 3
F17TH401_REV | 2000-F17-PID-PR-10001 | F17TH401 Reverse Enable | INACTIVE | ACTIVE | N |  |  | Reverse Enable Active. DCS user-interface button "Enable Reverse Jog Mode in LOCAL" to be placed alongside F17TH401. When activated/clicked by operator, de-energise SV17033 if activated (see OnOff tab)Can only be activated if F17-TH-401 is in Local Mode (F17TH401_LCL) XC17062 will be activated when "Reverse Enable" is activated by Control Room Operator. See Digital Outputs sheet. | 3
F17TH401_REVC | 2000-F17-PID-PR-10001 | F17TH401 Rake Rotation Counter | INACTIVE | ACTIVE | N |  |  | Counter to count down from 1 revolution of F17TH401 rake. Adjustable Count Down Timer. Default Timer: 925 seconds (1 rake revolution) OR SSL17016 = 120 pulses per revolution (whichever comes first). Engineer Configurable Range: (Timer) 700 - 1200 (Pulses) 80 - 200 pulses Counter to begin counting down from configured value (equivalent to 1 rake revolution) when: - AUTO MODE (F17-TH-401) Active AND F17TH401_RLWR Elapsed Counter resets when: - SV17047 in AUTO MODE AND Energised AND F17TH401_RLWR Elapsed Confirm timer during commissioning. 1 rake revolution will be equal to 120 pulses of SSL17016. | 3
F17TH401_RLWR | 2000-F17-PID-PR-10001 | F17TH401 Rake Lower Timer | INACTIVE | ACTIVE | N |  |  | Timer Duration: 30 seconds. Engineer Configurable Range: 0 - 180 seconds. Timer to start when: F17PO409 Running AND SV17047 Energised. F17TH401 must be in AUTO MODE (F17-TH-401). In LOCAL MODE (F17TH401_LCL), the rake may be lowered via local control panel until lower rake position switch is activated (ZSL17015) as detailed in 9. Drives for F17PO409. Timer does not apply in LOCAL MODE. Reset timer upon elapse. Timer duration source: 2000-ME001.5-M02-50001. Timer must be confirmed during commissioning. | 3 |  |  |  |  | Timer TBC.
F17TH401_STOP | 2000-F17-PID-PR-10001 | F17TH401 Stop Forward Mode | INACTIVE | ACTIVE | N |  |  | DCS user-interface button "Stop Thickener in Forward Mode" when activated will de-energise SV17033 and stop F17PO408. | 3
F17TH401_STRT | 2000-F17-PID-PR-10001 | F17TH401 Start Forward Mode | INACTIVE | ACTIVE | N |  |  | DCS User-Interface button "Start Thickener In Forward Mode" to reside next to F17TH401 object in DCS. When activated will energise SV17033 and start F17PO408. See 9. Drives for further information. Grey-out button if interlocks are active. | C
F17TH401_T1 | 2000-F17-PID-PR-10001 | F17TH401 Reverse Jog Active Timer | INACTIVE | ACTIVE | N |  |  | Timer duration: 0 - 10 seconds. Default value: 3 seconds. Adjustable by Engineer login only. Timer starts if: SV17034 = ENERGISED AND F17PO408 = RUNNING . On timer elapse: Timer to CLOSE SV17034 AND issue DCS Prompt: "Reverse Jog Exceeds Allowable Time." AND Start F17TH401_T2. Timer to stop if: SV17034 De-Energised Timer applicable in ALL modes of operation of F17PO408: Auto, Manual and Local. | 0
F17TH401_T2 | 2000-F17-PID-PR-10001 | F17TH401 Reverse Jog Lockout Timer | INACTIVE | ACTIVE | N |  |  | Timer duration: 60 seconds. Configurable Range: 30 - 180 seconds. Adjustable by Engineer login only. If F17TH401_T1 is STARTED AND (STOPPED OR ELAPSES), then: Start F17TH401_T2. If F17TH401_T2 = Active / Running then: Prevent SV17034 being energised until timer expired AND Issue DCS Prompt if Reverse Jog attempted to be activated: "Reverse Jog Cooldown Timer still active for << XX >> seconds." Timer applicable in ALL modes of operation of F17PO408: Auto, Manual and Local. Display timer in DCS graphic. | 3 |  |  |  |  | DCS prompt to confirm if required.
F17TH401_T3 | 2000-F17-PID-PR-10001 | F17TH401 Rake Protection Timer | INACTIVE | ACTIVE | N |  |  | Timer duration: 20 seconds. Engineer Configurable Range: 5 - 30 seconds. Timer to start when: 1. F17PO408 Running AND SV17033 De-Energised (from Energised state). Timer will lock out and prevent SV17034 being Energised until Timer elapsed. 2. F17PO408 Running AND SV17034 De-Energised (from Energised State). Timer will lock out and prevent SV17033 being Energised until Timer elapsed. Timer intended to prevent damage to rakes when switching from forward to reverse jogging operation (or vice-versa). Timer duration must be confirmed during commissioning and set by Engineer-level login within DCS. | C
F17TH401_UFFL | 2000-F17-PID-PR-10001 | F17PP455/6 Suction Flush Timer | INACTIVE | ACTIVE | N |  |  | Timer Duration: 120 seconds (Default) Operator Configurable Range: 0 - 600 seconds. Timer to start during F17-SEQ-0001. Please refer to Sequences for further details. Configurable range to be confirmed during commissioning. | 2
F17TH401_UFPR | 2000-F17-PID-PR-10001 | F17PP455/6 Suction Prime Timer | INACTIVE | ACTIVE | N |  |  | Timer Duration: 20 seconds (Default) Operator Configurable Range: 0 - 600 seconds. Timer to start during F17-SEQ-0001. Please refer to Sequences for further details. Configurable range to be confirmed during commissioning. | 2
F18PP4078_T1 | 2000-F18-PID-PR-10001 | F18PP407/8 Startup Timer | INACTIVE | ACTIVE | N |  |  | Timer Duration: 30 seconds. Operator Configurable Range: 0 - 120 seconds. Timer to count-down from nominated duration. Used in F18-SEQ-0001. | 2 |  |  |  |  | Refer to parameters tab on 18SEW0001 faceplate
F18PP4078STT | 2000-F18-PID-PR-10001 | F18PP407/8 Startup | Setpoint |  | N |  |  | Operator-adjustable start-up VSD speed for the Final Concentrate Pumps. F18PP4078STT [=] % Speed (Engineering Units). Configurable Range: 40 - 100% Used in F18-SEQ-0001 START. This will set the MV of LIC18001B when it is changed to manual. Value and configurable range to be confirmed during commissioning. | 3 |  |  |  |  | Refer to parameters tab on 18SEQ0001 faceplate
F18PP5134_IV | 2000-F18-PID-PR-10003 | F18PP513/514 Invalid Circuit | Normal State | Alarm State | N | 5 |  | Alarm when: - XV18242 Open AND XV18241 Open On-Delay: 5 seconds. | 3
F18PP5134_T1 | 2000-F18-PID-PR-10003 | F18PP513/4 Startup Timer | INACTIVE | ACTIVE | N |  |  | Timer Duration: 30 seconds. Operator Configurable Range: 0 - 120 seconds. Timer to count-down from nominated duration. Used in F18-SEQ-0007. | 2 |  |  |  |  | Refer to parameters tab on 18SEQ0007 faceplate
F18PP5134STT | 2000-F18-PID-PR-10003 | F18PP513/4 Startup | Setpoint |  | N |  |  | Operator-adjustable start-up VSD speed for the Cleaner-Scavenger Tails Pumps. F18PP5134STT [=] % Speed (Engineering Units). Configurable Range: 40 - 100% Used in F18-SEQ-0007 START. This will set the MV of LIC18211B when it is changed to manual. Value and configurable range to be confirmed during commissioning. | 3 |  |  |  |  | Refer to parameters tab on 18SEQ0007 faceplate
FIC17121_STP | 2000-F17-PID-PR-10001 | F17PP455/6 Shutdown | INACTIVE | ACTIVE | N |  |  | Operator-adjustable shut-up setpoint variable for Flotation Tailings Thickener Underflow Pumps. FIC17121_STP [=] m3/h (Engineering Units). Configurable Range: 2000 - 3000 m3/h. Setpoint used in F17-SEQ-0002 STOP. Range to be confirmed during commissioning. | 2 |  |  |  |  | Refer to parameters tab on 18SEQ0002 faceplate
FIC17121_STT | 2000-F17-PID-PR-10001 | F17PP455/6 Startup | Setpoint |  | N |  |  | Operator-adjustable start-up VSD speed for the Flotation Tailings Thickener Underflow Pumps. FIC17121_STT [=] % Speed (Engineering Units). Configurable Range: 40 - 100% Used in F17-SEQ-0001 START. This will set the MV of FIC17121 when it is changed to manual. Value and configurable range to be confirmed during commissioning. | 3 |  |  |  |  | Refer to parameters tab on 18SEQ0001 faceplate
FIC18037_OPP | 2000-F18-PID-PR-10001 | F18PP501/2 Operating Point | INACTIVE | ACTIVE | N |  |  | Operator-adjustable desired running setpoint variable for Cleaner Flotation Cell Recirculation Pumps. FIC18037_OPP [=] m3/h (Engineering Units). Configurable Range: 1800 - 2400 m3/h. Setpoint used in F18-SEQ-0003. Range to be confirmed during commissioning. | C |  |  |  |  | Doesn't look like this functionality has been configures in the sequence
FIC18037_STT | 2000-F18-PID-PR-10001 | F18PP501/2 Startup | Setpoint |  | N |  |  | Operator-adjustable start-up VSD speed for the Cleaner Flotation Cell Recirculation Pumps. FIC18037_STT [=] % Speed (Engineering Units). Configurable Range: 40 - 100% Used in F18-SEQ-0003 START. This will set the MV of FIC18037 when it is changed to manual. Value and configurable range to be confirmed during commissioning. | 3 |  |  |  |  | Refer to parameters tab on 18SEQ0003 faceplate
FIC18037_T1 | 2000-F18-PID-PR-10001 | F18PP501/2 Startup Timer | INACTIVE | ACTIVE | N |  |  | Timer Duration: 30 seconds. Operator Configurable Range: 0 - 120 seconds. Timer to count-down from nominated duration. Used in F18-SEQ-0003. | 2 |  |  |  |  | Refer to parameters tab on 18SEQ0003 faceplate
FIC18227_OPP | 2000-F18-PID-PR-10003 | F18PP511/2 Operating Point | INACTIVE | ACTIVE | N |  |  | Operator-adjustable desired running setpoint variable for Cleaner-Scavenger Flotation Cell Recirculation Pumps. FIC18227_OPP [=] m3/h (Engineering Units). Configurable Range: 1800 - 2400 m3/h. Setpoint used in F18-SEQ-0005. Range to be confirmed during commissioning. | C |  |  |  |  | Doesn't look like this functionality has been configures in the sequence
FIC18227_STT | 2000-F18-PID-PR-10003 | F18PP511/2 Startup | Setpoint |  | N |  |  | Operator-adjustable start-up VSD speed for the Cleaner-Scavenger Flotation Cell Recirculation Pumps. FIC18227_STT [=] % Speed (Engineering Units). Configurable Range: 40 - 100% Used in F18-SEQ-0005 START. This will set the MV of FIC18227 when it is changed to manual. Value and configurable range to be confirmed during commissioning. | 3 |  |  |  |  | Refer to parameters tab on 18SEQ0005 faceplate
FIC18227_T1 | 2000-F18-PID-PR-10003 | F18PP511/2 Startup Timer | INACTIVE | ACTIVE | N |  |  | Timer Duration: 30 seconds. Operator Configurable Range: 0 - 120 seconds. Timer to count-down from nominated duration. Used in F18-SEQ-0005. | 2 |  |  |  |  | Refer to parameters tab on 18SEQ0005 faceplate
HS17011 | 2000-F17-PID-PR-10002 | F17TH401 Control Method Switch | PIC17011 | DIC17121 | N |  |  | DCS Faceplate to select between Density Control or Thickener Bed Pressure Control to manipulate Flotation Tailings Thickener Underflow Pump 1/2 (F17-PP-455/456) VSD via slave controller FIC17121. | 0
HS17121 | 2000-F17-PID-PR-10002 | F17PP455/6 Duty Selection | CRO Selection |  | N |  |  | DCS Graphic Faceplate to select between duty Flotation Tailings Thickener Underflow Pump 1 or 2. | 0
HS18027 | 2000-F18-PID-PR-10001 | Duty F18PP407/408 | INACTIVE | ACTIVE | N |  |  | Handswitch to switch between duty pump F18-PP-407 and 408. To be achieved on faceplate within DCS. | C
HS18037 | 2000-F18-PID-PR-10001 | Duty F18PP501/502 | INACTIVE | ACTIVE | N |  |  | Handswitch to switch between duty pump F18-PP-501 and 502. To be achieved on faceplate within DCS. | C
HS18227 | 2000-F18-PID-PR-10003 | Duty F18PP511/512 | INACTIVE | ACTIVE | N |  |  | Handswitch to switch between duty pump F18-PP-511 and 512. To be achieved on faceplate within DCS. | C
HS18237 | 2000-F18-PID-PR-10003 | Duty F18PP513/514 | INACTIVE | ACTIVE | N |  |  | Handswitch to switch between duty pump F18-PP-513 and 514. To be achieved on faceplate within DCS. | C
LIC18051_OPP | 2000-F18-PID-PR-10002 | F18CF501 Level Setpoint | INACTIVE | ACTIVE | N |  |  | Operator-adjustable desired level setpoint variable for Cleaner Flotation Cell . LIC18051_OPP [=] MM (Engineering Units). Configurable Range: 50 - 700MM Setpoint used in F18-SEQ-0009. Range to be confirmed during commissioning. | C
LIC18251_OPP | 2000-F18-PID-PR-10004 | F18CF511 Level Setpoint | INACTIVE | ACTIVE | N |  |  | Operator-adjustable desired level setpoint variable for Cleaner-Scavenger Flotation Cell . LIC18051_OPP [=] MM (Engineering Units). Configurable Range: 50 - 700MM Setpoint used in F18-SEQ-0010. Range to be confirmed during commissioning. | C
PSA_BYP1 | 2000-F16-PID-PR-10006 | PSA Bypass 1 (Flotation Feed) | INACTIVE | ACTIVE | N |  |  | IF((401207.03 == 1 AND 401279.00 == 1) Unlatch Modbus Address 00027 == 0 (Bypass) IF((401207.01 == 1 AND 401279.00 == 1) Latch Modbus Address 00027 == 1 (Line ON) | 3
PSA_BYP2 | 2000-F16-PID-PR-10006 | PSA Bypass 2 (Flotation Tails) | INACTIVE | ACTIVE | N |  |  | IF((401207.03 == 1 AND 401278.00 == 1) Unlatch Modbus Address 00028 == 0 (Bypass) IF((401207.01 == 1 AND 401278.00 == 1) Latch Modbus Address 00028 == 1 (Line ON) | 3
16SW011_V_LO | - | F16SW011 Voltage Low Alarm | Normal | Alarm | N | 300 |  | If F16SW011A09-BCF1 Vab, Vbc OR Vca <= 1100V: Alarm 16SW011_V_LO Op Guide: Confirm and initiate the Mains to 11kV Generator changeover sequence | 3
16SW011_V_OK | - | F16SW011 Voltage OK Alarm | Normal | Alarm | N | 600 |  | If F16SW011A09-BCF1 Vab, Vbc AND Vca >= 11000V AND F16SW011A15-BCF1 Generator CB = CLOSED: Alarm 16SW011_V_OK Op Guide: Confirm and initiate the 11kV Generator to Mains changeover sequence | 3
16SW011_BTCB | - | F16SW011 Bus Tie Close OK | Logic |  | N |  |  | If F16SW011A15 Generator CB = Closed: Set F16SW011A15 Generator CB = Bus Tie CB Close Blocking active Else F16SW011A15 Generator CB = Bus Tie CB Close Blocking inactive See Modbus Map 2000-SPC-CS-11001 | 3
XV17009_OP | 2000-F17-PID-PR-10001 | XV17009 Open | Logic |  | N |  |  | If XV17009 open is requested: - Start F17HU422 - After F17HU422 running 10 seconds, energise SVO17009 to open XV17009 If ZSO17009 = active then deenergise SVO17009 Refer to 2000-PP007-M01-10001 | 3
XV17009_CL | 2000-F17-PID-PR-10001 | XV17009 Close | Logic |  | N |  |  | If XV17009 close is requested: - Start F17HU422 - After F17HU422 running 10 seconds, energise SVC17009 to close XV17009 If ZSC17009 = active then deenergise SVC17009 Refer to 2000-PP007-M01-10001 | 3
HS17145_LOGIC | 2000-F17-PID-PR-10001 | HS17145 Local/Remote | Logic |  | N |  |  | If HS17145ALOC = active, force XV17009 = MAN if HS17145BREM rising edge, one shot XV17009 = AUT If HS17145ALOC = active and HS13544AOP = active then open XV17009 If HS17145ALOC = active and HS13544ACL = active then close XV17009 | 3 |  |  |  |  | VV 02/08/2026 ; ALOC is catered in logic as AUT function to OPEN/CLOSE the valve in LOCAL Panel. BREM as pulse to MAN for DCS Operation is missing.
RECIRC_SPEED | 2000-F17-PID-PR-10002 | F17PP455/6 Recirc Speed | Logic |  | N |  |  | if XV17125 = opened and XV17123 = closed: set F17-PP-455 and F17-PP-456 speed SV to SV lower limit | 3 |  |  |  |  | RECIRC_SPEED toggles as desired, have not confirmed it actually changes pump speed -PH 17/06/2026
WQI17121_PAU | 2000-F17-PID-PR-10002 | WQI17121 Pause | Logic |  | N |  |  | if XV17125 = opened: pause totalising WQI17121 else resume totalising WQI17121 | 3
F17PP459_ES | 2000-F17-PID-PR-10001 | F17PP459 Emergency Start | Logic |  | N |  |  | if F16-GE-001 = running and F16SW011A15-R01 generator CB = closed pulse F17PP459 to auto and pulse start F17PP459 | 3 |  |  |  |  | VV 26/07/2026; desktop checked on logic. 17PP459 not yet tested / run VV 28/07/2026; 17PP459 tested / run
46

## RiskMatrix
Consequence | None | Personnel1: First Aid Injury, Reversible health effects | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Environmental2: Minor on-site environmental impact, reportable to regulators. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness. | Environmental3: Moderate environmental impacts, extends beyond site boundary or regulatory violations with fines. | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k
Not Urgent (>30 minutes) | No Alarm | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Low \ Review the alarm for urgency | Low \ Review the alarm for urgency | Low \ Review the alarm for urgency | High \ Review the alarm for urgency | High \ Review the alarm for urgency | High \ Review the alarm for urgency
Prompt (>15 to <30 minutes) | No Alarm | Low | Low | Low | Low | Low | Low | High | High | High
Rapid (>5 to <15 minutes) | No Alarm | Low | Low | Low | High | High | High | Urgent | Urgent | Urgent
Immediate (<5 minutes) | No Alarm | High | High | High | Urgent | Urgent | Urgent | Invalid | Invalid | Invalid
Plant Tripped | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Logging | Logging | Logging | Logging | Logging | Logging | Logging | Logging | Logging
|  | Priority | Description
|  | Low | Indicates that the process in no longer within nominal operational limits and a prompt operator intervention is required before the process becomes unrecoverable, resulting in minor safety, environmental or financial impacts.
|  | High | Indicates that the process is no longer within nominal operational limits and a rapid operator intervention is required before the process becomes unrecoverable resulting in serious safety, environmental or financial impacts.
|  | Urgent | Indicates that the process is no longer within nominal operational limits and a immediate operator intervention is required before the process becomes unrecoverable resulting in catastrophic safety, environmental or financial impacts.
|  | Logging | Indicates that the process or equipment has reached a unrecoverable or inoperable state and has been stopped. Logging alarms are for post event investigation and are not to enunciate to the operator.
|  | No Alarm | This condition does not meet the minimum requirements required under ISA 18.2 for a alarm to be generated. Including being a abnormal event\condition, requiring an operator response, undertaking a defined action within a defined time limit and having a defined consequences of no action is taken.
|  | Invalid | This senario is likely to be already unrecovreable and as such is unacceptable. Additional solutions such as automated repsonses, re-engeering or modifications the the process \ equipment is required.

## ReferenceList
Consequences
None
Personnel1: First Aid Injury, Reversible health effects
Environmental1: Localised environmental impact, contained, with no regulatory reporting
Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000
Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment.
Environmental2: Minor on-site environmental impact, reportable to regulators.
Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k.
Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness.
Environmental3: Moderate environmental impacts, extends beyond site boundary or regulatory violations with fines.
Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k
Type
Analogue
Digital
Alarm State
High-High
High
Low
Low-Low
Active