## Revisions
PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21)
REVISION HISTORY
KCGM GROWTH PROJECT
2000-F21-LST-PR-10101
NORTHERN STAR RESOURCES LIMITED
Revision | Document Changes | Date
A - Issued for Internal Review | - Vendor data TBC highlighted or red text | 2024-07-24
B - Issued for Tender | - Vendor data TBC highlighted or red text | 2024-07-24
C - Issued for Client Review | - Additional Vendor data inputted | 2024-11-18
- Vendor data TBC highlighted or red text
0 - Issued for Design | - Additional Vendor data inputted | 2025-02-04
- Vendor data TBC highlighted or red text
1 - Post FAT Updates | - Revision 1 changes highlighted in orange | 2026-09-01
- Strikethrough indicates removal from design

## 1. Analogue Input
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21) | [39 empty] | Urgent (Critical Failure) | #REF!
|  |  |  | 2000-F21-LST-PR-10101 | [39 empty] | High (Fault/Error) | #REF!
|  |  |  | ANALOGUE INSTRUMENTS | [39 empty] | Low (Warning) | #REF!
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [11 empty] | C1 Sign Off |  | C2 Sign Off |  |  |  |  | Information/Event (Journal) | #REF!
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Controller (Y/N) | Comments | Rev | OK | Date | OK | Date | Comments - Don't put comments in C2 column | Change Date | Change Reference | - | #REF!
|  |  |  | FIT21002 | FI21002 | 2000-F21-PID-PR-10001 | F21-FD-431 CIL4 FEED DISTRIBUTION BOX CYANIDE FEED FLOW INDICATING TRANSMITTER | F21FD431 CN Addn | 1 | 0 |  | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3 | 5 | - | - | - | - | F72PP675 is NOT RUNNING AND F72PP676 is NOT RUNNING | Y |  | C | [6 empty] | Declared in PID
|  |  |  | FIT21003 | FI21003 | 2000-F21-PID-PR-10001 | F21-TK-411 CIL4 TANK 1 CYANIDE FEED FLOW INDICATING TRANSMITTER | F21TK411 CN Addn | 1 | 0 |  | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5 | - | - | - | - | F72PP675 is NOT RUNNING AND F72PP676 is NOT RUNNING | Y |  | C | [6 empty] | Declared in PID
|  |  |  | FIT21004 | FI21004 | 2000-F21-PID-PR-10001 | F21-TK-412 CIL4 TANK 2 CYANIDE FEED FLOW INDICATING TRANSMITTER | F21TK412 CN Addn | 1 | 0 |  | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5 | - | - | - | - | F72PP675 is NOT RUNNING AND F72PP676 is NOT RUNNING | Y |  | C | [6 empty] | Declared in PID
|  |  |  | PIT21071 | PI21071 | 2000-F21-PID-PR-10001 | F21-TK-411 CIL4 Tank 1 Oxygen Side Lance Branch 1 Pressure Indicating Transmitter | F21TK411 Lance 1 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21072 | PI21072 | 2000-F21-PID-PR-10001 | F21-TK-411 CIL4 Tank 1 Oxygen Side Lance Branch 2 Pressure Indicating Transmitter | F21TK411 Lance 2 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21073 | PI21073 | 2000-F21-PID-PR-10001 | F21-TK-411 CIL4 Tank 1 Oxygen Side Lance Branch 3 Pressure Indicating Transmitter | F21TK411 Lance 3 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21074 | PI21074 | 2000-F21-PID-PR-10001 | F21-TK-411 CIL4 Tank 1 Oxygen Side Lance Branch 4 Pressure Indicating Transmitter | F21TK411 Lance 4 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21054 | PI21054 | 2000-F21-PID-PR-10001 | F21-TK-411 CIL4 TANK 1 OXYGEN RETURN PRESSURE INDICATING TRANSMITTER | F21PP478 Press 1 | 1 | 0 | 700 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 5 | - | - | 500 | 5 | 550 | 5 | F21-PP-478 is NOT RUNNING (Applies to A_LL only) Ensure 10s delay mask for pump start-up | N |  | 1 | [5 empty] | 2025-05-01 | Updated as per KAN-1599
|  |  |  | PIT21055 | PI21055 | 2000-F21-PID-PR-10001 | F21-PP-478 CIL4 TANK 1 OXYGEN INJECTION PUMP DISCHARGE PRESSURE INDICATING TRANSMITTER | F21PP478 Press 2 | 1 | 0 | 700 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 5 | - | - | 500 | 5 | 550 | 5 | F21-PP-478 is NOT RUNNING (Applies to A_LL only) Ensure 10s delay mask for pump start-up | N |  | 1 | [5 empty] | 2025-05-01 | Updated as per KAN-1599
|  |  |  | PIT21032 | PI21032 | 2000-F21-PID-PR-10001 | CIL4 Tank 1 Oxygen Injection Pressure Indicating Transmitter | F21TK411 Injector Header | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | C
|  |  |  | FIT21033 | FI21033 | 2000-F21-PID-PR-10001 | CIL4 Tank 1 Oxygen Injection Flow Indicating Transmitter | F21TK411 Injector Head | 1 | 0 |  | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 5 | 200 | 5 | - | - | - | Y | Series 150 Oxygen Injector has nominal flowrate of 75 m3/h. | C
|  |  |  | PIT21340 | PI21340 | 2000-F72-PID-PR-10011 | F72-PK-405 OXYGEN PLANT DISCHARGE PRESSURE INDICATING TRANSMITTER | CIL4 O2 Pressure | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | C
|  |  |  | FIT21341 | FI21341 | 2000-F72-PID-PR-10011 | F72-PK-405 OXYGEN PLANT DISCHARGE FLOW INDICATING TRANSMITTER | CIL4 O2 Flowrate | 1 | 0 | 700 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Series 150 Oxygen Injector has nominal flowrate of 75 m3/h. | C
|  |  |  | FIT21057 | FI21057 | 2000-F21-PID-PR-10001 | F21-TK-411 CIL4 Tank 1 Oxygen Feed Flow Indicating Transmitter | F21TK411 Lance Header | 1 | 0 |  | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | C
|  |  |  | PIT21021 | PI21021 | 2000-F21-PID-PR-10001 | CIL4 Oxygen Distribution Pressure Indicating Transmitter 1 | CIL4 Oxy Injector Header | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | C
|  |  |  | PIT21022 | PI21022 | 2000-F21-PID-PR-10001 | F21-TK-412 CIL4 TANK 2 OXYGEN FEED PRESSURE INDICATING TRANSMITTER | CIL4 Oxy Lance Header | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | C
|  |  |  | PIT21111 | PI21111 | 2000-F21-PID-PR-10001 | F21-TK-412 CIL4 Tank 2 Oxygen Side Lance Branch 1 Pressure Indicating Transmitter | F21TK412 Lance 1 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21112 | PI21112 | 2000-F21-PID-PR-10001 | F21-TK-412 CIL4 Tank 2 Oxygen Side Lance Branch 2 Pressure Indicating Transmitter | F21TK412 Lance 2 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21113 | PI21113 | 2000-F21-PID-PR-10001 | F21-TK-412 CIL4 Tank 2 Oxygen Side Lance Branch 3 Pressure Indicating Transmitter | F21TK412 Lance 3 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21114 | PI21114 | 2000-F21-PID-PR-10001 | F21-TK-412 CIL4 Tank 2 Oxygen Side Lance Branch 4 Pressure Indicating Transmitter | F21TK412 Lance 4 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21094 | PI21094 | 2000-F21-PID-PR-10001 | F21-TK-412 CIL4 TANK 2 OXYGEN RETURN PRESSURE INDICATING TRANSMITTER | F21PP491 Press 1 | 1 | 0 | 700 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 5 | - | - | 500 | 5 | 550 | 5 | F21-PP-491 is NOT RUNNING (Applies to A_LL only) Ensure 10s delay mask for pump start-up | N |  | 0
|  |  |  | PIT21095 | PI21095 | 2000-F21-PID-PR-10001 | F21-PP-491 CIL4 TANK 2 OXYGEN INJECTION PUMP DISCHARGE PRESSURE INDICATING TRANSMITTER | F21PP491 Press 2 | 1 | 0 | 700 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 5 | - | - | 500 | 5 | 550 | 5 | F21-PP-491 is NOT RUNNING (Applies to A_LL only) Ensure 10s delay mask for pump start-up | N |  | 0
|  |  |  | AIT21061 | AI21061 | 2000-F21-PID-PR-10001 | F21-TK-411 CIL4 TANK 1 DISSOLVED OXYGEN TRANSMITTER | F21TK411 DO | 1 | 0 | 25 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10 | 5 | - | - | - | - | - | N |  | A
|  |  |  | AIT21062 | AI21062 | 2000-F21-PID-PR-10001 | F21-TK-411 CIL4 TANK 1 PH TRANSMITTER | F21TK411 pH | 1 | 0 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | - | 8 | 5 | 8.5 | 5 | - | - | - | - | - | Y |  | C | [6 empty] | declared in PID
|  |  |  | AIT21211 | AI21211 | 2000-F21-PID-PR-10001 | CIL4 TANKS 1 AND 2 HCN GAS ANALYSER INDICATING TRANSMITTER | CIL4 HCN Conc. 1 | 1 | 0 | 30 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
|  |  |  | AIT21101 | AI21101 | 2000-F21-PID-PR-10001 | F21-TK-412 CIL4 TANK 2 DISSOLVED OXYGEN TRANSMITTER | F21TK412 DO | 1 | 0 | 25 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10 | 5 | - | - | - | - | - | N |  | A
|  |  |  | AIT21102 | #N/A | 2000-F21-PID-PR-10001 | F21-TK-412 CIL4 TANK 2 PH TRANSMITTER | F21TK412 pH | 1 | 0 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | - | 8 | 5 | 8.5 | 5 | - | - | - | - | - | Y |  | C | [6 empty] | declared in PID
|  |  |  | PIT21348 | PI21348 | 2000-F72-PID-PR-10011 | F21-TK-411 CIL4 TANK 1 OXYGEN INJECTION 1 PRESSURE INDICATING TRANSMITTER | F21TK411 Injct 1 | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 400 | 5 | 720 | 5 | 750 | 5 | A_Lo: 'F21-PP-478 is NOT RUNNING Ensure 10s delay mask for pump start-up | N |  | 1 | [5 empty] | 2025-04-09 | Design change - HAZID 4/04/2025
|  |  |  | PIT21350 | PI21350 | 2000-F72-PID-PR-10011 | F21-TK-411 CIL4 TANK 1 OXYGEN INJECTION 2 PRESSURE INDICATING TRANSMITTER | F21TK411 Injct 2 | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 400 | 5 | 720 | 5 | 750 | 5 | A_Lo: 'F21-PP-478 is NOT RUNNING Ensure 10s delay mask for pump start-up | N |  | 1 | [5 empty] | 2025-04-09 | Design change - HAZID 4/04/2025
|  |  |  | FIT21005 | FI21005 | 2000-F21-PID-PR-10002 | F21-TK-413 CIL4 TANK 3 CYANIDE FEED FLOW TRANSMITTER | F21TK413 CN Addn | 1 | 0 |  | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5 | - | - | - | - | F72PP675 is NOT RUNNING AND F72PP676 is NOT RUNNING | Y |  | C | [6 empty] | declared in PID
|  |  |  | PIT21151 | PI21151 | 2000-F21-PID-PR-10002 | F21-TK-413 CIL4 Tank 3 Oxygen Side Lance Branch 1 Pressure Indicating Transmitter | F21TK413 Lance 1 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21152 | PI21152 | 2000-F21-PID-PR-10002 | F21-TK-413 CIL4 Tank 3 Oxygen Side Lance Branch 2 Pressure Indicating Transmitter | F21TK413 Lance 2 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21153 | PI21153 | 2000-F21-PID-PR-10002 | F21-TK-413 CIL4 Tank 3 Oxygen Side Lance Branch 3 Pressure Indicating Transmitter | F21TK413 Lance 3 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21154 | PI21154 | 2000-F21-PID-PR-10002 | F21-TK-413 CIL4 Tank 3 Oxygen Side Lance Branch 4 Pressure Indicating Transmitter | F21TK413 Lance 4 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | FIT21163 | FI21163 | 2000-F21-PID-PR-10002 | F21-TK-413 CIL4 Tank 3 Oxygen Feed Flow Indicating Transmitter | F21TK413 Lance Header | 1 | 0 |  | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | C
|  |  |  | PIT21191 | PI21191 | 2000-F21-PID-PR-10002 | F21-TK-414 CIL4 Tank 4 Oxygen Side Lance Branch 1 Pressure Indicating Transmitter | F21TK414 Lance 1 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21192 | PI21192 | 2000-F21-PID-PR-10002 | F21-TK-414 CIL4 Tank 4 Oxygen Side Lance Branch 2 Pressure Indicating Transmitter | F21TK414 Lance 2 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21193 | PI21193 | 2000-F21-PID-PR-10002 | F21-TK-414 CIL4 Tank 4 Oxygen Side Lance Branch 3 Pressure Indicating Transmitter | F21TK414 Lance 3 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | PIT21194 | PI21194 | 2000-F21-PID-PR-10002 | F21-TK-414 CIL4 Tank 4 Oxygen Side Lance Branch 4 Pressure Indicating Transmitter | F21TK414 Lance 4 | 1 | 0 |  | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 360 | 5 | - | - | - | - | - | N | Low Pressure Alarm set to CIL4 Tank Static Head at 55 %w/w. Lance pressure has to exceed static head to prevent lance sanding/blcoking | C
|  |  |  | FIT21183 | FI21183 | 2000-F21-PID-PR-10002 | F21-TK-414 CIL4 Tank 4 Oxygen Feed Flow Indicating Transmitter | F21TK414 Lance Header | 1 | 0 |  | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | C
|  |  |  | AI21140AS | AI21140A | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DISSOLVED OXYGEN TRANSMITTER | F21TK411 DO | 1 | 0 | 25 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21141AS | AI21141A | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DISSOLVED OXYGEN TRANSMITTER | F21TK412 DO | 1 | 0 | 25 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21142AS | AI21142A | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DISSOLVED OXYGEN TRANSMITTER | F21TK413 DO | 1 | 0 | 25 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21143AS | AI21143A | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DISSOLVED OXYGEN TRANSMITTER | F21TK414 DO | 1 | 0 | 25 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21144AS | AI21144A | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DISSOLVED OXYGEN TRANSMITTER | F21TK415 DO | 1 | 0 | 25 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21145AS | AI21145A | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DISSOLVED OXYGEN TRANSMITTER | F21TK416 DO | 1 | 0 | 25 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21146AS | AI21146A | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DISSOLVED OXYGEN TRANSMITTER | F21TK417 DO | 1 | 0 | 25 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21147AS | AI21147A | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DISSOLVED OXYGEN TRANSMITTER | F21TK418 DO | 1 | 0 | 25 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21140BS | AI21140B | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT PH TRANSMITTER | F21TK411 pH | 1 | 0 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21141BS | AI21141B | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT PH TRANSMITTER | F21TK412 pH | 1 | 0 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21142BS | AI21142B | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT PH TRANSMITTER | F21TK413 pH | 1 | 0 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21143BS | AI21143B | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT PH TRANSMITTER | F21TK414 pH | 1 | 0 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21144BS | AI21144B | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT PH TRANSMITTER | F21TK415 pH | 1 | 0 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21145BS | AI21145B | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT PH TRANSMITTER | F21TK416 pH | 1 | 0 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21146BS | AI21146B | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT PH TRANSMITTER | F21TK417 pH | 1 | 0 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21147BS | AI21147B | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT PH TRANSMITTER | F21TK418 pH | 1 | 0 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21140CS | AI21140C | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DENSITY TRANSMITTER | F21TK411 C Conc. | 1 | 0 | 20 | g/L | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21141CS | AI21141C | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DENSITY TRANSMITTER | F21TK412 C Conc. | 1 | 0 | 20 | g/L | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21142CS | AI21142C | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DENSITY TRANSMITTER | F21TK413 C Conc. | 1 | 0 | 20 | g/L | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21143CS | AI21143C | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DENSITY TRANSMITTER | F21TK414 C Conc. | 1 | 0 | 20 | g/L | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21144CS | AI21144C | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DENSITY TRANSMITTER | F21TK415 C Conc. | 1 | 0 | 20 | g/L | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21145CS | AI21145C | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DENSITY TRANSMITTER | F21TK416 C Conc. | 1 | 0 | 20 | g/L | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21146CS | AI21146C | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DENSITY TRANSMITTER | F21TK417 C Conc. | 1 | 0 | 20 | g/L | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21147CS | AI21147C | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT DENSITY TRANSMITTER | F21TK418 C Conc. | 1 | 0 | 20 | g/L | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21140DS | AI21140D | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT GOLD PPM | F21TK411 Au Conc | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21141DS | AI21141D | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT GOLD PPM | F21TK412 Au Conc | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21142DS | AI21142D | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT GOLD PPM | F21TK413 Au Conc | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21143DS | AI21143D | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT GOLD PPM | F21TK414 Au Conc | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21144DS | AI21144D | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT GOLD PPM | F21TK415 Au Conc | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21145DS | AI21145D | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT GOLD PPM | F21TK416 Au Conc | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21146DS | AI21146D | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT GOLD PPM | F21TK417 Au Conc | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AI21147DS | AI21147D | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT GOLD PPM | F21TK418 Au Conc | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-07-28 | KAN-2149
|  |  |  | AIT21212 | AI21212 | 2000-F21-PID-PR-10002 | CIL4 MID TANK SECTION HCN GAS ANALYSER INDICATING TRANSMITTER | CIL4 HCN Conc. 2 | 1 | 0 | 30 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
|  |  |  | PIT21357 | PI21357 | 2000-F72-PID-PR-10011 | F21-TK-412 CIL4 TANK 2 OXYGEN INJECTION 1 PRESSURE INDICATING TRANSMITTER | F21TK412 Injct 1 | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 400 | 5 | 720 | 5 | 750 | 5 | A_Lo: 'F21-PP-491 is NOT RUNNING Ensure 10s delay mask for pump start-up | N |  | 1 | [5 empty] | 2025-04-09 | Design change - HAZID 4/04/2025
|  |  |  | PIT21359 | PI21359 | 2000-F72-PID-PR-10011 | F21-TK-412 CIL4 TANK 2 OXYGEN INJECTION 2 PRESSURE INDICATING TRANSMITTER | F21TK412 Injct 2 | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 400 | 5 | 720 | 5 | 750 | 5 | A_Lo: 'F21-PP-491 is NOT RUNNING Ensure 10s delay mask for pump start-up | N |  | 1 | [5 empty] | 2025-04-09 | Design change - HAZID 4/04/2025
|  |  |  | AI21243S | AI21243 | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS CYANIDE CONCENTRATION 1 | F21TK411 Free CN | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Y | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-08-04 | KAN-2149
|  |  |  | AI21249S | AI21249 | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS WAD CYANIDE CONCENTRATION 1 | F21TK411 WAD CN | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-08-04 | KAN-2149
|  |  |  | AI21244S | AI21244 | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS CYANIDE CONCENTRATION 2 | F21TK412 Free CN | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Y | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-08-04 | KAN-2149
|  |  |  | AI21250S | AI21250 | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS WAD CYANIDE CONCENTRATION 2 | F21TK412 WAD CN | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-08-04 | KAN-2149
|  |  |  | AI21245S | AI21245 | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS CYANIDE CONCENTRATION 3 | F21TK413 Free CN | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-08-04 | KAN-2149
|  |  |  | AI21251S | AI21251 | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS WAD CYANIDE CONCENTRATION 3 | F21TK413 WAD CN | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-08-04 | KAN-2149
|  |  |  | AI21246S | AI21246 | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS CYANIDE CONCENTRATION 4 | F21TK416 Free CN | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-08-04 | KAN-2149
|  |  |  | AI21252S | AI21252 | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS WAD CYANIDE CONCENTRATION 4 | F21TK416 WAD CN | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-08-04 | KAN-2149
|  |  |  | AI21247S | AI21247 | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS CYANIDE CONCENTRATION 5 | F21TK418 Free CN | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-08-04 | KAN-2149
|  |  |  | AI21253S | AI21253 | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS WAD CYANIDE CONCENTRATION 5 | F21TK418 Free CN | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-08-04 | KAN-2149
|  |  |  | AI21248S | AI21248 | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS CYANIDE CONCENTRATION 6 | F23TK404 Free CN | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-08-04 | KAN-2149
|  |  |  | AI21254S | AI21254 | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS WAD CYANIDE CONCENTRATION 6 | F23TK404 WAD CN | 1 | 0 | 800 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | Soft Tag. Signal over modbus. | 1 | [5 empty] | 2025-08-04 | KAN-2149
|  |  |  | AIT21213 | AI21213 | 2000-F21-PID-PR-10003 | CIL4 TANKS 7 AND 8 HCN GAS ANALYSER INDICATING TRANSMITTER | CIL4 HCN Conc. 3 | 1 | 0 | 30 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N |  | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
|  |  |  | AI21007S | AI21007 | 2000-F21-PID-PR-10001 | F21-AN-409 CARBON DETECTION ANALYSER 2 CARBON CONCENTRATION | F21AN409 C Conc. | 1 | 0 | 20 | g/L | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N | SoftTag (ref 2000-SPC-CS-11001) | 1 | [5 empty] | 4/08/2025 18/08/2025 | KAN-2107 CR-043
|  |  |  | AI21319S | AI21319 | 2000-F21-PID-PR-10005 | F21-AN-405 CIL 4 CARBON DETECTION ANALYSER CARBON CONCENTRATION | F21AN405 C Conc. | 1 | 0 | 20 | g/L | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | 5 | 5 | 5 | - | N | SoftTag (ref 2000-SPC-CS-11001) Alarms to be determined during commissioning | 1 | [5 empty] | 4/08/2025 18/08/2025 | KAN-2107 CR-043
|  |  |  | TT21016 |  | - | F21-SR-001 CIL4 415V SWITCHROOM TEMPERATURE TRANSMITTER | F21SR001 SW Temp | 1 | -5 | 80 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 30 | 5 | - | - | - | N | A_Hi = Alarm. Nominal 24C. Alarm setpoint to be confirmed during commissioning. | C
|  |  |  | TT21017 |  | - | F21-SR-001 CIL4 415V SWITCHROOM TEMPERATURE TRANSMITTER | F21SR001 SW Temp | 1 | -5 | 80 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 30 | 5 | - | - | - | N | A_Hi = Alarm. Nominal 24C. Alarm setpoint to be confirmed during commissioning. | C
|  |  |  | TT21018 |  | - | F21-SR-001 CIL4 415V SWITCHROOM TEMPERATURE TRANSMITTER | F21SR001 SW Temp | 1 | -5 | 80 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 30 | 5 | - | - | - | N | A_Hi = Alarm. Nominal 24C. Alarm setpoint to be confirmed during commissioning. | C
|  |  |  | PIT21332 | PI21332 | 2000-F24-PID-PR-10016 | F21-RA-409 CIL4/ELUTION AIR RECEIVER DISCHARGE PRESSURE INDICATING TRANSMITTER | F21RA409 Press. | 1 | 0 | 1400 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 900 | 5 | 1300 | 5 | - | - | - | N |  | C
|  |  |  | PIT21335 | PI21335 | 2000-F24-PID-PR-10016 | F21-RA-410 CIL4 REAGENTS AIR RECEIVER DISCHARGE PRESSURE INDICATING TRANSMITTER | F21RA410 Press. | 1 | 0 | 1400 | kPa(g) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 900 | 5 | 1300 | 5 | - | - | - | N |  | C
|  |  |  | TE21023A | TI21023A | - | F21-AG-411 CIL4 TANK 1 AGITATOR MOTOR PHASE U RTD | F21AG411 U RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | 1 | [5 empty] | 2025-05-01 | Updated as per KAN-1600
|  |  |  | TE21023B | TI21023B | - | F21-AG-411 CIL4 TANK 1 AGITATOR MOTOR PHASE V RTD | F21AG411 V RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21023C | TI21023C | - | F21-AG-411 CIL4 TANK 1 AGITATOR MOTOR PHASE W RTD | F21AG411 W RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21023D | TI21023D | - | F21-AG-411 CIL4 TANK 1 AGITATOR MOTOR DE BEARING RTD | F21AG411 DE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21023E | TI21023E | - | F21-AG-411 CIL4 TANK 1 AGITATOR MOTOR NDE BEARING RTD | F21AG411 NDE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21031A | TI21031A | - | F21-PP-478 CIL4 TANK 1 OXYGEN INJECTION PUMP MOTOR PHASE U RTD | F21PP478 U RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 180 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 180degC. Motor is Class H insulation. | 0
|  |  |  | TE21031B | TI21031B | - | F21-PP-478 CIL4 TANK 1 OXYGEN INJECTION PUMP MOTOR PHASE V RTD | F21PP478 V RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 180 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 180degC. Motor is Class H insulation. | 0
|  |  |  | TE21031C | TI21031C | - | F21-PP-478 CIL4 TANK 1 OXYGEN INJECTION PUMP MOTOR PHASE W RTD | F21PP478 W RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 180 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 180degC. Motor is Class H insulation. | 0
|  |  |  | TE21031D | TI21031D | - | F21-PP-478 CIL4 TANK 1 OXYGEN INJECTION PUMP MOTOR DE BEARING RTD | F21PP478 DE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95 | 5 | 105 | 5 | - | N |  | 0
|  |  |  | TE21031E | TI21031E | - | F21-PP-478 CIL4 TANK 1 OXYGEN INJECTION PUMP MOTOR NDE BEARING RTD | F21PP478 NDE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95 | 5 | 105 | 5 | - | N |  | 0
|  |  |  | TE21024A | TI21024A | - | F21-AG-412 CIL4 TANK 2 AGITATOR MOTOR PHASE U RTD | F21AG412 U RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21024B | TI21024B | - | F21-AG-412 CIL4 TANK 2 AGITATOR MOTOR PHASE V RTD | F21AG412 V RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21024C | TI21024C | - | F21-AG-412 CIL4 TANK 2 AGITATOR MOTOR PHASE W RTD | F21AG412 W RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21024D | TI21024D | - | F21-AG-412 CIL4 TANK 2 AGITATOR MOTOR DE BEARING RTD | F21AG412 DE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21024E | TI21024E | - | F21-AG-412 CIL4 TANK 2 AGITATOR MOTOR NDE BEARING RTD | F21AG412 NDE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21034A | TI21034A | - | F21-PP-491 CIL4 TANK 2 OXYGEN INJECTION PUMP MOTOR PHASE U RTD | F21PP491 U RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 180 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 180degC. Motor is Class H insulation. | 0
|  |  |  | TE21034B | TI21034B | - | F21-PP-491 CIL4 TANK 2 OXYGEN INJECTION PUMP MOTOR PHASE V RTD | F21PP491 V RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 180 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 180degC. Motor is Class H insulation. | 0
|  |  |  | TE21034C | TI21034C | - | F21-PP-491 CIL4 TANK 2 OXYGEN INJECTION PUMP MOTOR PHASE W RTD | F21PP491 W RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 180 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 180degC. Motor is Class H insulation. | 0
|  |  |  | TE21034D | TI21034D | - | F21-PP-491 CIL4 TANK 2 OXYGEN INJECTION PUMP MOTOR DE BEARING RTD | F21PP491 DE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95 | 5 | 105 | 5 | - | N |  | 0
|  |  |  | TE21034E | TI21034E | - | F21-PP-491 CIL4 TANK 2 OXYGEN INJECTION PUMP MOTOR NDE BEARING RTD | F21PP491 NDE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95 | 5 | 105 | 5 | - | N |  | 0
|  |  |  | TE21025A | TI21025A | - | F21-AG-413 CIL4 TANK 3 AGITATOR MOTOR PHASE U RTD | F21AG413 U RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21025B | TI21025B | - | F21-AG-413 CIL4 TANK 3 AGITATOR MOTOR PHASE V RTD | F21AG413 V RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21025C | TI21025C | - | F21-AG-413 CIL4 TANK 3 AGITATOR MOTOR PHASE W RTD | F21AG413 W RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21025D | TI21025D | - | F21-AG-413 CIL4 TANK 3 AGITATOR MOTOR DE BEARING RTD | F21AG413 DE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21025E | TI21025E | - | F21-AG-413 CIL4 TANK 3 AGITATOR MOTOR NDE BEARING RTD | F21AG413 NDE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21026A | TI21026A | - | F21-AG-414 CIL4 TANK 4 AGITATOR MOTOR PHASE U RTD | F21AG414 U RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21026B | TI21026B | - | F21-AG-414 CIL4 TANK 4 AGITATOR MOTOR PHASE V RTD | F21AG414 V RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21026C | TI21026C | - | F21-AG-414 CIL4 TANK 4 AGITATOR MOTOR PHASE W RTD | F21AG414 W RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21026D | TI21026D | - | F21-AG-414 CIL4 TANK 4 AGITATOR MOTOR DE BEARING RTD | F21AG414 DE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21026E | TI21026E | - | F21-AG-414 CIL4 TANK 4 AGITATOR MOTOR NDE BEARING RTD | F21AG414 NDE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21027A | TI21027A | - | F21-AG-415 CIL4 TANK 5 AGITATOR MOTOR PHASE U RTD | F21AG415 U RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21027B | TI21027B | - | F21-AG-415 CIL4 TANK 5 AGITATOR MOTOR PHASE V RTD | F21AG415 V RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21027C | TI21027C | - | F21-AG-415 CIL4 TANK 5 AGITATOR MOTOR PHASE W RTD | F21AG415 W RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21027D | TI21027D | - | F21-AG-415 CIL4 TANK 5 AGITATOR MOTOR DE BEARING RTD | F21AG415 DE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21027E | TI21027E | - | F21-AG-415 CIL4 TANK 5 AGITATOR MOTOR NDE BEARING RTD | F21AG415 NDE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21028A | TI21028A | - | F21-AG-416 CIL4 TANK 6 AGITATOR MOTOR PHASE U RTD | F21AG416 U RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21028B | TI21028B | - | F21-AG-416 CIL4 TANK 6 AGITATOR MOTOR PHASE V RTD | F21AG416 V RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21028C | TI21028C | - | F21-AG-416 CIL4 TANK 6 AGITATOR MOTOR PHASE W RTD | F21AG416 W RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21028D | TI21028D | - | F21-AG-416 CIL4 TANK 6 AGITATOR MOTOR DE BEARING RTD | F21AG416 DE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21028E | TI21028E | - | F21-AG-416 CIL4 TANK 6 AGITATOR MOTOR NDE BEARING RTD | F21AG416 NDE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21029A | TI21029A | - | F21-AG-417 CIL4 TANK 7 AGITATOR MOTOR PHASE U RTD | F21AG417 U RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21029B | TI21029B | - | F21-AG-417 CIL4 TANK 7 AGITATOR MOTOR PHASE V RTD | F21AG417 V RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21029C | TI21029C | - | F21-AG-417 CIL4 TANK 7 AGITATOR MOTOR PHASE W RTD | F21AG417 W RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21029D | TI21029D | - | F21-AG-417 CIL4 TANK 7 AGITATOR MOTOR DE BEARING RTD | F21AG417 DE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21029E | TI21029E | - | F21-AG-417 CIL4 TANK 7 AGITATOR MOTOR NDE BEARING RTD | F21AG417 NDE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21030A | TI21030A | - | F21-AG-418 CIL4 TANK 8 AGITATOR MOTOR PHASE U RTD | F21AG418 U RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21030B | TI21030B | - | F21-AG-418 CIL4 TANK 8 AGITATOR MOTOR PHASE V RTD | F21AG418 V RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21030C | TI21030C | - | F21-AG-418 CIL4 TANK 8 AGITATOR MOTOR PHASE W RTD | F21AG418 W RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140 | 3 | 150 | 3 | - | N | Alarm Setpoints: A_Hi = 140degC, A_HH = 150degC. Motor is Class F insulation. | C
|  |  |  | TE21030D | TI21030D | - | F21-AG-418 CIL4 TANK 8 AGITATOR MOTOR DE BEARING RTD | F21AG418 DE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | TE21030E | TI21030E | - | F21-AG-418 CIL4 TANK 8 AGITATOR MOTOR NDE BEARING RTD | F21AG418 NDE RTD | 1 | 0 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 3 | 110 | 3 | - | N |  | 0
|  |  |  | UT21016 | TI21016 | - | F21-SR-001 CIL4 415V SWITCHROOM SWITCHROOM TEMPERATURE/HUMIDITY TRANSMITTER | F21SR001 SW Temp | 1 | -5 | 80 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 30 | 5 | - | - | - | N | A_Hi = Alarm. Nominal 24C. Alarm setpoint to be confirmed during commissioning. | 0
|  |  |  | UT21017 | TI21017 | - | F21-SR-001 CIL4 415V SWITCHROOM TRANSFORMER (F21-TR-006) TEMPERATURE/HUMIDITY TRANSMITTER | F21SR001 SW Temp | 1 | -5 | 80 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 30 | 5 | - | - | - | N | A_Hi = Alarm. Nominal 24C. Alarm setpoint to be confirmed during commissioning. | 0
|  |  |  | UT21018 | TI21018 | - | F21-SR-001 CIL4 415V SWITCHROOM TRANSFORMER (F21-TR-007) TEMPERATURE/HUMIDITY TRANSMITTER | F21SR001 SW Temp | 1 | -5 | 80 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 30 | 5 | - | - | - | N | A_Hi = Alarm. Nominal 24C. Alarm setpoint to be confirmed during commissioning. | 0
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
[25 empty] | 128 |  | 128 |  | 128 |  | 128
512
|  |  |  | 115 | 115
115

## 2. Analogue Output
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21) | [17 empty] | Urgent (Critical Failure)
|  |  |  | 2000-F21-LST-PR-10101 | [17 empty] | High (Fault/Error)
|  |  |  | ANALOGUE OUTPUT | [17 empty] | Low (Warning)
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  |  |  | C1 Sign Off |  | C2 Sign Off |  |  |  |  | Information/Event (Journal)
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | Comments | Rev | OK | Date | OK | Date | Comments - Don't put comments in C2 column | Change Date | Change Reference | -
|  |  |  | DY21010S | DY21010 | 2000-F21-PID-PR-10001 | F21-AN-409 CARBON DETECTION ANALYSER 2 DENSITY SIGNAL | F17TH401 U/F Density | 1 | 1 | 1.75 | t/m3 | Soft tag (Modbus Relative Density DI17121) | 2 | [5 empty] | 2025-04-08 | design change TBC vendor documents to confirm hardwired IO
|  |  |  | DY21318S | DY21318 | 2000-F21-PID-PR-10005 | F21-AN-405 CIL 4 CARBON DETECTION ANALYSER DENSITY SIGNAL | CIL4 HCN Conc. | 1 | 1 | 1.75 | t/m3 | Soft tag (Modbus Relative Density DI17121) | 2 | [5 empty] | 2025-04-08 | design change TBC vendor documents to confirm hardwired IO
|  |  |  | DIT17121 | DI17121 | 2000-F17-PID-PR-10002 | Flotation Tailings Thickener Underflow Pumps Discharge Density Indicating Transmitter | F17TH401 U/F Density | 1 | 1 | 1.75 | t/m3 | Density signal is outputted to F21-AN-405 & F21-AN-409 | C | [6 empty] | already in F16,17,18 PCT
|  |  |  | AIT21211 | AI21211 | 2000-F21-PID-PR-10001 | CIL4 Flotation Tails Leaching HCN Gas Analyser Transmitter | CIL4 HCN Conc. | 1 | 0 |  | mg/m3 |  | C
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 2 | 2

## 3. Digital Input
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21) |  |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)*
2000-F21-LST-PR-10101
DIGITAL INSTRUMENTS
[18 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Source | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date | Comments - Don't put comments in C2 column | Change Date | Change Reference
|  |  |  | FSL21321 | FAL21321 | 2000-F24-PID-PR-10003 | F21-PP-478 CIL4 TANK 1 OXYGEN INJECTION PUMP GLAND WATER FLOW SWITCH LOW | F21PP478 GW Lo | Alarm | Normal | Alarm | Hardwired |  | 3 | F21-PP-478 is NOT RUNNING Enable 10s mask delay for pump start-up |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | FSL21325 | FAL21325 | 2000-F24-PID-PR-10003 | F21-PP-491 CIL4 TANK 2 OXYGEN INJECTION PUMP GLAND WATER FLOW SWITCH LOW | F21PP491 GW Lo | Alarm | Normal | Alarm | Hardwired |  | 3 | F21-PP-491 is NOT RUNNING Enable 10s mask delay for pump start-up |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | LSH21131 | LAH21131 | 2000-F21-PID-PR-10001 | F21-PS-414 CIL4 AREA SUMP PUMP 1 LEVEL SWITCH HIGH | F21PS414 Hi | Normal | Alarm | Alarm | Soft Tag |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | XS21006S | XA21006 | 2000-F21-PID-PR-10005 | #N/A | F21AN409 Warning | Normal | Alarm | Alarm | Soft Tag |  | 0 | - | SoftTag (ref 2000-SPC-CS-11001) | 1 | [5 empty] | 8/07/2025 18/08/2025 13/11/2025 | Updated as per KAN-2098 CR-043 https://pastech-2955.atlassian.net/browse/KAN-2498
|  |  |  | ASHH21211 | AAHH21211 | 2000-F21-PID-PR-10001 | CIL4 TANKS 1 AND 2 HCN GAS ALARM SWITCH HIGH HIGH | CIL4 HCN Gas HH1 | Alarm | Normal | Alarm | Hardwired |  | 3 | - | Logic: Include 10 minute off delay on AAHH21211 | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
|  |  |  | LSH21221 | LAH21221 | 2000-F21-PID-PR-10002 | F21-PS-415 CIL4 AREA SUMP PUMP 2 LEVEL SWITCH HIGH | F21PS415 Hi | Normal | Alarm | Alarm | Soft Tag |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | LSH21222 | LAH21222 | 2000-F21-PID-PR-10002 | F21-PS-416 CIL4 AREA SUMP PUMP 3 LEVEL SWITCH HIGH | F21PS416 Hi | Normal | Alarm | Alarm | Soft Tag |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | XA21140 | XA21140_FAULT | 2000-F21-PID-PR-10002 | F21-AN-412 CIL4 CARBON SCOUT CIL4 CARBON SCOUT FAULT | F21AN412 Fault | Normal | Alarm | Alarm | Soft Tag |  | 0 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | ASHH21212 | AAHH21212 | 2000-F21-PID-PR-10002 | CIL4 MID TANK SECTION HCN GAS ALARM SWITCH HIGH HIGH | CIL4 HCN Gas HH2 | Alarm | Normal | Alarm | Hardwired |  | 3 | - | Logic: Include 10 minute off delay on AAHH21212 | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
|  |  |  | LSH21291 | LAH21291 | 2000-F21-PID-PR-10003 | F21-PS-417 CIL4 AREA SUMP PUMP 4 LEVEL SWITCH HIGH | F21PS417 Hi | Normal | Alarm | Alarm | Soft Tag |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | XA21255 | XA21255_FAULT | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS FAULT 1 | F21CA411 Fault | Normal | Alarm | Alarm | Soft Tag |  | 0 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | XA21256 | XA21256_FAULT | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS FAULT 2 | F21CA412 Fault | Normal | Alarm | Alarm | Soft Tag |  | 0 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | ASHH21213 | AAHH21213 | 2000-F21-PID-PR-10003 | CIL4 TANKS 7 AND 8 HCN GAS ALARM SWITCH HIGH HIGH | CIL4 HCN Gas HH3 | Alarm | Normal | Alarm | Hardwired |  | 3 | - | Logic: Include 10 minute off delay on AAHH21213 | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
|  |  |  | XS21318S | XA21318 | 2000-F21-PID-PR-10005 | F21-AN-405 CIL 4 CARBON DETECTION ANALYSER FAULT | F21AN405 Warning | Normal | Alarm | Alarm | Soft Tag |  | 0 | - | SoftTag (ref 2000-SPC-CS-11001) | 1 | [5 empty] | 8/07/2025 18/08/2025 13/11/2025 | Updated as per KAN-2098 CR-043 https://pastech-2955.atlassian.net/browse/KAN-2498
|  |  |  | ZS21310A | ZI21310A | 2000-F21-PID-PR-10005 | F21-SA-431 CIL4 TAILS PRIMARY SAMPLER DRIVE END PARK POSITION SWITCH | F21SA431 Park 1 | Normal | Active | - | Hardwired |  | 0 | - |  | A
|  |  |  | ZS21310B | ZI21310B | 2000-F21-PID-PR-10005 | F21-SA-431 CIL4 TAILS PRIMARY SAMPLER DRIVE END RAMP-DOWN POSITION SWITCH | F21SA431 Ramp | Normal | Active | - | Hardwired |  | 0 | - |  | A
|  |  |  | ZS21310C | ZA21310C | 2000-F21-PID-PR-10005 | F21-SA-431 CIL4 TAILS PRIMARY SAMPLER DRIVE END OVER-TRAVEL POSITION SWITCH | F21SA431 Over | Normal | Alarm | Alarm | Hardwired |  | 3 | - |  | 1 | [5 empty] | 2025-07-08 | Updated as per KAN-2098
|  |  |  | ZS21313A | ZI21313A | 2000-F21-PID-PR-10005 | F21-SA-431 CIL4 TAILS PRIMARY SAMPLER NON-DRIVE END PARK POSITION SWITCH | F21SA431 Park 2 | Normal | Active | - | Hardwired |  | 0 | - |  | A
|  |  |  | ZS21313B | ZI21313B | 2000-F21-PID-PR-10005 | F21-SA-431 CIL4 TAILS PRIMARY SAMPLER NON-DRIVE END RAMP-DOWN POSITION SWITCH | F21SA431 Ramp | Normal | Active | - | Hardwired |  | 0 | - |  | A
|  |  |  | ZS21313C | ZA21313C | 2000-F21-PID-PR-10005 | F21-SA-431 CIL4 TAILS PRIMARY SAMPLER NON-DRIVE END OVER-TRAVEL POSITION SWITCH | F21SA431 Over | Normal | Alarm | Alarm | Hardwired |  | 3 | - |  | A
|  |  |  | XA21309A | XA21309A | #N/A | #N/A | F21SA431 General Fault | Normal | Active | Active | Soft Tag |  | 0 | - |  | A
|  |  |  | ZS21304 | ZI21304 | 2000-F21-PID-PR-10005 | F21-SA-432 CIL4 TAILS SECONDARY SAMPLER PARK POSITION SWITCH | F21SA432 Park | Normal | Active | - | Hardwired |  | 0 | - |  | A
|  |  |  | XA21303A | XA21303A | #N/A | #N/A | F21SA432 General Fault | Normal | Active | Active | Soft Tag |  | 0 | - |  | A
|  |  |  | ZS21307 | ZI21307 | 2000-F21-PID-PR-10005 | F21-SA-433 CIL4 TAILS TERTIARY SAMPLER PARK POSITION SWITCH | F21SA433 Park | Normal | Active | - | Hardwired |  | 0 | - |  | A
|  |  |  | XA21306A | XA21306A | #N/A | #N/A | F21SA433 General Fault | Normal | Active | Active | Soft Tag |  | 0 | - |  | A
|  |  |  | F21DCS411PS1 | F21DCS411_PS1 | - | F21-DCS-411 PS1 24VDC HEALTHY | F21DCS441 PS1 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21DCS411PS2 | F21DCS411_PS2 | - | F21-DCS-411 PS2 24VDC HEALTHY | F21DCS441 PS1 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21SW006PS | F21SW006_PS | - | F21-SW-006 ACB SHUNT TRIP 24VDC OK | F21SW006 ACBSHUNT 24V OK | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | WIP | [5 empty] | 2025-10-23 | Change description
|  |  |  | F21SW006AF | F21SW006_AF | - | F21-SW-006 ARC FLASH DETECTION SYSTEM ALARM | F21SW006 ARC FLASH | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21SW006Q1OP | F21SW006_OP | - | F21-SW-006 MAINS SUPPLY CIRCUIT BREAKER OPENED | F21SW006 BREAKER OPEN | N_Active | Active | - | Hardwired |  | 0 |  |  | C | [5 empty] | 2025-12-01 | Updated to align with programmed - F21 FAT
|  |  |  | F21SW006Q1CL | F21SW006_CL | - | F21-SW-006 MAINS SUPPLY CIRCUIT BREAKER CLOSED | F21SW006 BREAKER CLOSED | N_Active | Active | - | Hardwired |  | 0 |  |  | C | [5 empty] | 2025-12-01 | Updated to align with programmed - F21 FAT
|  |  |  | F21SW006Q1TRP | F21SW006_TRP | - | F21-SW-006 MAINS SUPPLY CIRCUIT BREAKER TRIPPED | F21SW006 BREAKER TRIP | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C
|  |  |  | F21SW006SD | F21SW006_SD | - | F21-SW-006 INCOMER SURGE DIVERTER OK | F21SW006 INC SURGE DIV | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | 21SR001ESTP | F21SR001_ESTP | - | F21-SR-001 SWITCHROOM EMERGENCY SHUTDOWN DCS INPUT | F21SR001 SR ESHUT DCS IN | OK | Alarm | Alarm | Hardwired |  | 0 |  |  | 1 | [5 empty] | 1/05/2025 1/12/2025 | Updated as per KAN-1585 Updated to align with programmed - F21 FAT
|  |  |  | F21SW006PS1 | F21SW006_PS1 | - | F21-SW-006 PS1 24VDC HEALTHY | F21SW006 PS1 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21SW006PS2 | F21SW006_PS2 | - | F21-SW-006 PS2 24VDC HEALTHY | F21SW006 PS2 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21SW007PS | F21SW007_PS | - | F21-SW-007 ACB SHUNT TRIP 24VDC OK | F21SW007 ACBSHUNT 24V OK | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | WIP | [5 empty] | 23//10/2025 | Change description
|  |  |  | F21SW007AF | F21SW007_AF | - | F21-SW-007 ARC FLASH DETECTION SYSTEM ALARM | F21SW007 ARC FLASH | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21SW007Q1OP | F21SW007_OP | - | F21-SW-007 MAINS SUPPLY CIRCUIT BREAKER OPENED | F21SW007 BREAKER OPEN | N_Active | Active | - | Hardwired |  | 0 |  |  | C | [5 empty] | 2025-12-01 | Updated to align with programmed - F21 FAT
|  |  |  | F21SW007Q1CL | F21SW007_CL | - | F21-SW-007 MAINS SUPPLY CIRCUIT BREAKER CLOSED | F21SW007 BREAKER CLOSED | N_Active | Active | - | Hardwired |  | 0 |  |  | C | [5 empty] | 2025-12-01 | Updated to align with programmed - F21 FAT
|  |  |  | F21SW007Q1TRP | F21SW007_TRP | - | F21-SW-007 MAINS SUPPLY CIRCUIT BREAKER TRIPPED | F21SW007 BREAKER TRIP | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C
|  |  |  | F21SW007SD | F21SW007_SD | - | F21-SW-007 INCOMER SURGE DIVERTER OK | F21SW007 INC SURGE DIV | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21SW007PS1 | F21SW007_PS1 | - | F21-SW-007 PS1 24VDC HEALTHY | F21SW007 PS1 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21SW007PS2 | F21SW007_PS2 | - | F21-SW-007 PS2 24VDC HEALTHY | F21SW007 PS2 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21FIP001ALM | F21FIP001_ALM | - | F21-FIP-001 ALARM | F21FIP001 ALARM | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | 1 | [5 empty] | 2025-05-01 | Updated as per KAN-1585
|  |  |  | F21FIP001ISL | F21FIP001_ISL | - | F21-FIP-001 ISOLATED | F21FIP001 ISOLATED | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | 1 | [5 empty] | 2025-05-01 | Updated as per KAN-1585
|  |  |  | F21FIP001FLT | F21FIP001_FLT | - | F21-FIP-001 FAULT | F21FIP001 FAULT | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | 1 | [5 empty] | 2025-05-01 | Updated as per KAN-1585
|  |  |  | F21SW106SD | F21SW106_SD | - | F21-SW-106 SURGE DIVERTER OK | F21SW106 SURGE DIV OK | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | 0 | [6 empty] | Add from IO list
|  |  |  | F21SW106Q1CL | F21SW106Q1_CL | - | F21-SW-106 MAINS SUPPLY CB CLOSED | F21SW106 MAINS CB CLOSE | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | 0 | [6 empty] | Add from IO list
|  |  |  | F21SW106Q1TRP | F21SW106Q1_TRP | - | F21-SW-106 MAINS SUPPLY CB TRIPPED | F21SW106 MAINS CB TRIP | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | 0 | [6 empty] | Add from IO list
|  |  |  | F21SW006Q2OP | F21SW006Q2_OP | - | F21-SW-006 GENERATOR SUPPLY CIRCUIT BREAKER OPENED | F21SW006 GEN CB OPEN | N_Active | Active | - | Hardwired |  | 0 |  |  | 0 | [5 empty] | 2025-12-01 | Updated to align with programmed - F21 FAT
|  |  |  | F21SW006Q2CL | F21SW006Q2_CL | - | F21-SW-006 GENERATOR SUPPLY CIRCUIT BREAKER CLOSED | F21SW006 GEN CB CLOSED | N_Active | Active | - | Hardwired |  | 0 |  |  | 0 | [5 empty] | 2025-12-01 | Updated to align with programmed - F21 FAT
|  |  |  | F21SW006Q2TRP | F21SW006Q2_TRP | - | F21-SW-006 GENERATOR SUPPLY CIRCUIT BREAKER TRIPPED | F21SW006 GEN CB TRIP | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | 0
|  |  |  | F21SW107SD | F21SW107_SD | - | F21-SW-107 SURGE DIVERTER OK | F21SW107 SURGE DIV OK | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | 0 | [6 empty] | Add from IO list
|  |  |  | F21SW107Q1CL | F21SW107Q1_CL | - | F21-SW-107 MAINS SUPPLY CB CLOSED | F21SW107 MAINS CB CLOSE | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | 0 | [6 empty] | Add from IO list
|  |  |  | F21SW107Q1TRP | F21SW107Q1_TRP | - | F21-SW-107 MAINS SUPPLY CB TRIPPED | F21SW107 MAINS CB TRIP | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | 0 | [6 empty] | Add from IO list
|  |  |  | F21SW007Q2OP | F21SW007Q2_OP | - | F21-SW-007 GENERATOR SUPPLY CIRCUIT BREAKER OPENED | F21SW007 GEN CB OPEN | N_Active | Active | - | Hardwired |  | 0 |  |  | 0 | [5 empty] | 2025-12-01 | Updated to align with programmed - F21 FAT
|  |  |  | F21SW007Q2CL | F21SW007Q2_CL | - | F21-SW-007 GENERATOR SUPPLY CIRCUIT BREAKER CLOSED | F21SW007 GEN CB CLOSED | N_Active | Active | - | Hardwired |  | 0 |  |  | 0 | [5 empty] | 2025-12-01 | Updated to align with programmed - F21 FAT
|  |  |  | F21SW007Q2TRP | F21SW007Q2_TRP | - | F21-SW-007 GENERATOR SUPPLY CIRCUIT BREAKER TRIPPED | F21SW007 GEN CB TRIP | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | 0
|  |  |  | LSHH21008 | LAHH21008 | - | F21-GE-006 CIL4 MCC 1 EMERGENCY SUPPLY 415V GENERATOR FUEL LEVEL SWITCH HIGH HIGH | F21GE006 LVL HH | Normal | Alarm | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | LSH21008 | LAH21008 | - | F21-GE-006 CIL4 MCC 1 EMERGENCY SUPPLY 415V GENERATOR FUEL LEVEL SWITCH HIGH | F21GE006 LVL Hi | Normal | Alarm | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | LSL21008 | LAL21008 | - | F21-GE-006 CIL4 MCC 1 EMERGENCY SUPPLY 415V GENERATOR FUEL LEVEL SWITCH LOW | F21GE006 LVL Lo | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | LSHH21009 | LAHH21009 | - | F21-GE-007 CIL4 MCC 2 EMERGENCY SUPPLY 415V GENERATOR FUEL LEVEL SWITCH HIGH HIGH | F21GE007 LVL HH | Normal | Alarm | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | LSH21009 | LAH21009 | - | F21-GE-007 CIL4 MCC 2 EMERGENCY SUPPLY 415V GENERATOR FUEL LEVEL SWITCH HIGH | F21GE007 LVL Hi | Normal | Alarm | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | LSL21009 | LAL21009 | - | F21-GE-007 CIL4 MCC 2 EMERGENCY SUPPLY 415V GENERATOR FUEL LEVEL SWITCH LOW | F21GE007 LVL Lo | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21RIO001PS1 | F21RIO001_PS1 | - | F21-RIO-001 PS1 24VDC HEALTHY | F21RIO001 PS1 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21RIO001PS2 | F21RIO001_PS2 | - | F21-RIO-001 PS2 24VDC HEALTHY | F21RIO001 PS2 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21RIO002PS1 | F21RIO002_PS1 | - | F21-RIO-002 PS1 24VDC HEALTHY | F21RIO0002 PS1 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21RIO002PS2 | F21RIO002_PS2 | - | F21-RIO-002 PS2 24VDC HEALTHY | F21RIO0002 PS2 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21RIO003PS1 | F21RIO003_PS1 | - | F21-RIO-003 PS1 24VDC HEALTHY | F21RIO003 PS1 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | F21RIO003PS2 | F21RIO003_PS2 | - | F21-RIO-003 PS2 24VDC HEALTHY | F21RIO003 PS2 24VDC | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C | [6 empty] | Add from IO list
|  |  |  | HS21316A | HS21316_A | 2000-F21-PID-PR-10005 | F21-SA-433 CIL4 TAILS TERTIARY SAMPLER CUTTER FLUSH PUSHBUTTON | F21SA433 Flush | Inactive | Active | - | Hardwired |  | 0 |  |  | 1 | [5 empty] | 2025-04-08 | KAN-1477
|  |  |  | HS21316B | HS21316_B | 2000-F21-PID-PR-10005 | F21-SA-433 CIL4 TAILS TERTIARY SAMPLER SAMPLE NOW PUSHBUTTON | F21SA433 Sample Now | Inactive | Active | - | Hardwired |  | 0 |  |  | 1 | [5 empty] | 2025-04-08 | KAN-1477
|  |  |  | ZS30461A | ZI30461A | 2000-F30-PID-PR-10011 | F30-SA-443 CIL3 TAILS PRIMARY SAMPLER CUTTER POSITION SWITCH 1 | F30SA443 Park 1 | Inactive | Active | - | Hardwired |  | 0 |  |  | C
|  |  |  | ZS30461B | ZI30461B | 2000-F30-PID-PR-10011 | F30-SA-443 CIL3 TAILS PRIMARY SAMPLER CUTTER POSITION SWITCH 2 | F30SA443 Park 2 | Inactive | Active | - | Hardwired |  | 0 |  |  | C
|  |  |  | ZS30480 | ZI30480 | 2000-F30-PID-PR-10011 | F30-SA-444 CIL3 TAILS SECONDARY SAMPLER CUTTER POSITION SWITCH | F30SA444 Park | Inactive | Active | - | Hardwired |  | 0 |  |  | C
|  |  |  | AAH21315 | AAH21315 | 2000-F21-PID-PR-10005 | F21-AN-405 CIL4 Carbon Detection Analyser Fault | F21AN405 CIL4 Analyser | Alarm | Normal | Alarm | Soft Tag |  | 0 |  |  | C
|  |  |  | ZSC21019 | ZAC21019 | - | F21-TR-006 CIL4 415V MCC 1 TRANSFORMER ENCLOSURE DOOR POSITION SWITCH CLOSED | F21TR006 415VMCC Door CL | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C
|  |  |  | ZSC21020 | ZAC21020 | - | F21-TR-007 CIL4 415V MCC 2 TRANSFORMER ENCLOSURE DOOR POSITION SWITCH CLOSED | F21TR007 415VMCC Door CL | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | C
|  |  |  | FSH21035 | FAH21035 | 2000-F24-PID-PR-10028 | F21-SE-412 CIL4 AREA UPPER SAFETY SHOWER 1 FLOW SWITCH HIGH | F21SE412 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 |  |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH21036 | FAH21036 | 2000-F24-PID-PR-10028 | F21-SE-413 CIL4 AREA UPPER SAFETY SHOWER 2 FLOW SWITCH HIGH | F21SE413 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 |  |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH21037 | FAH21037 | 2000-F24-PID-PR-10028 | F21-SE-414 CIL4 AREA UPPER SAFETY SHOWER 3 FLOW SWITCH HIGH | F21SE414 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 |  |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH21038 | FAH21038 | 2000-F24-PID-PR-10028 | F21-SE-502 CIL4 TAILS UPPER SAFETY SHOWER FLOW SWITCH HIGH | F21SE502 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 |  |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | FSH21039 | FAH21039 | 2000-F24-PID-PR-10028 | F21-SE-503 CIL4 TAILS LOWER SAFETY SHOWER FLOW SWITCH HIGH | F21SE503 Alarm | Alarm | Normal | Alarm | Hardwired |  | 30 |  |  | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
|  |  |  | F21TR006WTH | F21TR006_WTH | - | F21-TR-006 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F21TR006 Temp Hi | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | 1 | [5 empty] | 2025-08-19 | CR-034
|  |  |  | F21TR007WTH | F21TR007_WTH | - | F21-TR-007 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F21TR007 Temp Hi | Alarm | Normal | Alarm | Hardwired |  | 0 |  |  | 1 | [5 empty] | 2025-08-19 | CR-034
|  |  |  | F21GE006CBTRP | 21GE006CBTRP |  | F21-GE-006 CIL4 MCC 1 EMERGENCY SUPPLY 415V GENERATOR CB TRIPPED | F21-GE-006 GEN CB TRP | Alarm | Normal | Alarm | Hardwired to DCS |  | 0 |  |  | 1
|  |  |  | F21GE007CBTRP | 21GE007CBTRP |  | F21-GE-007 CIL4 MCC 2 EMERGENCY SUPPLY 415V GENERATOR CB TRIPPED | F21-GE-007 GEN CB TRP | Alarm | Normal | Alarm | Hardwired to DCS |  | 0 |  |  | 1
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 73 | 73

## 4. Digital Output
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21) |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)* | [15 empty] | Urgent (Critical Failure) | Urgent (Critical Failure) | 0
|  |  |  | 2000-F21-LST-PR-10101 | [19 empty] | High (Fault/Error) | High (Fault/Error) | 0
|  |  |  | DIGITAL OUTPUTS | [19 empty] | Low (Warning) | Low (Warning) | 0
[17 empty] | C1 Sign Off |  | C2 Sign Off |  |  |  |  | Information/Event (Journal) | Information/Event (Journal) | 0
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date | Comments - Don't put comments in C2 column | Change Date | Change Reference |  | - | 0
|  |  |  | YY21211 | YA21211 | 2000-F21-PID-PR-10001 | CIL4 TANKS 1 AND 2 HCN GAS SIREN SIGNAL | CIL4 HCN Alarm 1 | Off | On | - |  | - | - | Siren and Beacon If ASHH21211 = Inactive for 3 seconds: Activate YA21211 If ASHH21211 = Active for 10 minutes: Deactivate YA21211 | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
|  |  |  | YY21212 | YA21212 | 2000-F21-PID-PR-10002 | CIL4 MID TANK SECTION HCN GAS SIREN SIGNAL | CIL4 HCN Alarm 2 | Off | On | - |  | - | - | Siren and Beacon If ASHH21212 = Inactive for 3 seconds: Activate YA21212 If ASHH21212 = Active for 10 minutes: Deactivate YA21212 | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
|  |  |  | YY21213 | YA21213 | 2000-F21-PID-PR-10001 | CIL4 TANKS 7 AND 8 HCN GAS SIREN SIGNAL | CIL4 HCN Alarm 3 | Off | On | - |  | - | - | Siren and Beacon If ASHH21213 = Inactive for 3 seconds: Activate YA21213 If ASHH21213 = Active for 10 minutes: Deactivate YA21213 | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
|  |  |  | YI21211 | #N/A | #N/A | CIL4 Flotation Tails Leaching HCN Gas Beacon | CIL4 HCN Gas Siren | Normal | Active | - |  | - | - | Activate if ASHH21211 = Alarm Deactivate if ASHH23406 = Normal and alarm is reset. | C
|  |  |  | YA21312 | YA21312 | 2000-F21-PID-PR-10005 | CIL4 Carbon Safety Screen Area Acid Wash Siren | CIL4 Carbon Acid Wash | Normal | Active | [5 empty] | C
|  |  |  | YI21312A | YI21312A | 2000-F21-PID-PR-10005 | CIL4 Carbon Safety Screen Area Upper Level Acid Wash Warning Beacon | CIL4 Upper Lvl Acid Wash | Normal | Active | [5 empty] | C
|  |  |  | YI21312B | YI21312B | 2000-F21-PID-PR-10005 | CIL4 Carbon Safety Screen Area Lower Level Acid Wash Warning Beacon | CIL4 Lower Lvl Acid Wash | Normal | Active | [5 empty] | C
|  |  |  | TBC - WAITING VENDOR INFORMATION | - |  | - | [7 empty] | TBC - WAITING VENDOR INFORMATION | B
|  |  |  | TBC - WAITING VENDOR INFORMATION | - |  | - | [7 empty] | TBC - WAITING VENDOR INFORMATION | B
|  |  |  | TBC - WAITING VENDOR INFORMATION | - |  | - | [7 empty] | TBC - WAITING VENDOR INFORMATION | B
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 3 | 3

## 5. Totalisers
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21)
2000-F21-LST-PR-10101
TOTALISERS
[11 empty] | Reset Period |  |  |  |  | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | Type | P&ID | Description | Abbreviated Description (Faceplate) | Units | Shift | Day | Cont | Comments | Rev | OK | Date | OK | Date
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 0 | 0
[8 empty] | 0 | [6 empty] | #NAME?

## 6. OnOff Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21)
2000-F21-LST-PR-10101
OPEN-CLOSE VALVES
[14 empty] | Permissives and Trips | [12 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position (Loss of Power) | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open Interlock | Close Interlock | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date | Comments - Don't put comments in C2 column | Change Date | Change Reference
|  |  |  | XV21011 | #N/A | #N/A | CIL4 Lime Isolate | Detail 3 | FL | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | C
|  |  |  | XV21012 | 2000-F21-PID-PR-10001 | F21-FD-431 CIL4 FEED DISTRIBUTION BOX MILK OF LIME FEED CONTROL VALVE | CIL4 Lime Addn | Detail 3 | FL | X | X | AIC21062 OR AIC21102 | AIC21062 OR AIC21102 | - | - | - | - | - | - | - | - | - | - | - | Valve will be controlled via PID loop controllers AIC21062 or AIC21102. PID control via pulse-width modulation. | C
|  |  |  | XV21001 | 2000-F21-PID-PR-10001 | CYANIDE RINGMAIN CIL 4 FEED VALVE | CIL4 CN Isolate | Detail 9 | FL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV21013A | 2000-F21-PID-PR-10001 | F21-GA-431A CIL4 FEED DISTRIBUTION BOX ISOLATION GATE 1 VALVE A | F21GA431A | Detail 3 | FL | X | X | - | - | CP1 | XV21014A is OPEN AND XV21014B is OPEN | F21-GA-431C and F21-GA-431D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21013B | 2000-F21-PID-PR-10001 | F21-GA-431B CIL4 FEED DISTRIBUTION BOX ISOLATION GATE 2 VALVE B | F21GA431B | Detail 3 | FL | X | X | - | - | CP1 | XV21014A is OPEN AND XV21014B is OPEN | F21-GA-431C and F21-GA-431D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21014A | 2000-F21-PID-PR-10001 | F21-GA-431C CIL4 FEED DISTRIBUTION BOX ISOLATION GATE 3 VALVE A | F21GA431C | Detail 3 | FL | X | X | - | - | CP1 | XV21013A is OPEN AND XV21013B is OPEN | F21-GA-431A and F21-GA-431B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21014B | 2000-F21-PID-PR-10001 | F21-GA-431D CIL4 FEED DISTRIBUTION BOX ISOLATION GATE 4 VALVE B | F21GA431D | Detail 3 | FL | X | X | - | - | CP1 | XV21013A is OPEN AND XV21013B is OPEN | F21-GA-431A and F21-GA-431B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21081A | 2000-F21-PID-PR-10001 | F21-GA-411A CIL4 TANK 1 DISCHARGE LAUNDER ISOLATION GATE 1 VALVE A | F21GA411A | Detail 3 | FL | X | X | - | - | CP1 | XV21082A is OPEN AND XV21082B is OPEN | F21-GA-411C and F21-GA-411D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21081B | 2000-F21-PID-PR-10001 | F21-GA-411B CIL4 TANK 1 DISCHARGE LAUNDER ISOLATION GATE 2 VALVE B | F21GA411B | Detail 3 | FL | X | X | - | - | CP1 | XV21082A is OPEN AND XV21082B is OPEN | F21-GA-411C and F21-GA-411D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21082A | 2000-F21-PID-PR-10001 | F21-GA-411C CIL4 TANK 1 DISCHARGE LAUNDER ISOLATION GATE 3 VALVE A | F21GA411C | Detail 3 | FL | X | X | - | - | CP1 | XV21081A is OPEN AND XV21081B is OPEN | F21-GA-411A and F21-GA-411B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21082B | 2000-F21-PID-PR-10001 | F21-GA-411D CIL4 TANK 1 DISCHARGE LAUNDER ISOLATION GATE 4 VALVE B | F21GA411D | Detail 3 | FL | X | X | - | - | CP1 | XV21081A is OPEN AND XV21081B is OPEN | F21-GA-411A and F21-GA-411B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21121A | 2000-F21-PID-PR-10001 | F21-GA-412A CIL4 TANK 2 DISCHARGE LAUNDER ISOLATION GATE 1 VALVE A | F21GA412A | Detail 3 | FL | X | X | - | - | CP1 | XV21122A is OPEN AND XV21122B is OPEN | F21-GA-412C and F21-GA-412D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21121B | 2000-F21-PID-PR-10001 | F21-GA-412B CIL4 TANK 2 DISCHARGE LAUNDER ISOLATION GATE 2 VALVE B | F21GA412B | Detail 3 | FL | X | X | - | - | CP1 | XV21122A is OPEN AND XV21122B is OPEN | F21-GA-412C and F21-GA-412D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21122A | 2000-F21-PID-PR-10001 | F21-GA-412C CIL4 TANK 2 DISCHARGE LAUNDER ISOLATION GATE 3 VALVE A | F21GA412C | Detail 3 | FL | X | X | - | - | CP1 | XV21121A is OPEN AND XV21121B is OPEN | F21-GA-412A and F21-GA-412B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21122B | 2000-F21-PID-PR-10001 | F21-GA-412D CIL4 TANK 2 DISCHARGE LAUNDER ISOLATION GATE 4 VALVE B | F21GA412D | Detail 3 | FL | X | X | - | - | CP1 | XV21121A is OPEN AND XV21121B is OPEN | F21-GA-412A and F21-GA-412B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21051 | 2000-F21-PID-PR-10001 | F21-PP-478 CIL4 TANK 1 OXYGEN INJECTION PUMP SUCTION VALVE | F21PP478 Suction | Detail 4 | FC | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2025-04-30 | KAN-1611
|  |  |  | XV21052 | 2000-F21-PID-PR-10001 | F21-PP-478 CIL4 TANK 1 OXYGEN INJECTION PUMP SUCTION DRAIN VALVE | F21PP478 Drain 1 | Detail 4 | FO | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2025-04-30 | KAN-1611
|  |  |  | XV21056 | 2000-F21-PID-PR-10001 | F21-PP-478 CIL4 TANK 1 OXYGEN INJECTION PUMP DISCHARGE DRAIN VALVE | F21PP478 Drain 2 | Detail 4 | FO | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2025-04-30 | KAN-1611
|  |  |  | XV21053 | 2000-F21-PID-PR-10001 | F21-TK-411 CIL4 TANK 1 OXYGEN RETURN VALVE | F21PP478 Discharge | Detail 4 | FC | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2025-04-30 | KAN-1611
|  |  |  | SV21320 | 2000-F24-PID-PR-10014 | F21-PP-478 CIL4 TANK 1 OXYGEN INJECTION PUMP GLAND WATER SOLENOID VALVE | F21PP478 Gland | Detail 11 | FO | X | X | F21PP478 is RUNNING | F21PP478 is NOT RUNNING | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV21091 | 2000-F21-PID-PR-10001 | F21-PP-491 CIL4 TANK 2 OXYGEN INJECTION PUMP SUCTION VALVE | F21PP491 Suction | Detail 4 | FC | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2025-04-30 | KAN-1611
|  |  |  | XV21092 | 2000-F21-PID-PR-10001 | F21-PP-491 CIL4 TANK 2 OXYGEN INJECTION PUMP SUCTION DRAIN VALVE | F21PP491 Drain 1 | Detail 4 | FO | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2025-04-30 | KAN-1611
|  |  |  | XV21096 | 2000-F21-PID-PR-10001 | F21-PP-491 CIL4 TANK 2 OXYGEN INJECTION PUMP DISCHARGE DRAIN VALVE | F21PP491 Drain 2 | Detail 4 | FO | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2025-04-30 | KAN-1611
|  |  |  | XV21093 | 2000-F21-PID-PR-10001 | F21-TK-412 CIL4 TANK 2 OXYGEN RETURN VALVE | F21PP491 Discharge | Detail 4 | FC | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2025-04-30 | KAN-1611
|  |  |  | SV21324 | 2000-F24-PID-PR-10014 | F21-PP-491 CIL4 TANK 2 OXYGEN INJECTION PUMP GLAND WATER SOLENOID VALVE | F21PP491 Gland | Detail 11 | FO | X | X | F21PP491 is RUNNING | F21PP491 is NOT RUNNING | - | - | - | - | - | - | - | - | - | - | - |  | 1 | [5 empty] | 2025-12-01 | https://pastech-2955.atlassian.net/browse/PL-434
|  |  |  | XV21161A | 2000-F21-PID-PR-10002 | F21-GA-413A CIL4 TANK 3 DISCHARGE LAUNDER ISOLATION GATE 1 VALVE A | F21GA413A | Detail 3 | FL | X | X | - | - | CP1 | XV21162A is OPEN AND XV21162B is OPEN | F21-GA-413C and F21-GA-413D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21161B | 2000-F21-PID-PR-10002 | F21-GA-413B CIL4 TANK 3 DISCHARGE LAUNDER ISOLATION GATE 2 VALVE B | F21GA413B | Detail 3 | FL | X | X | - | - | CP1 | XV21162A is OPEN AND XV21162B is OPEN | F21-GA-413C and F21-GA-413D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21162A | 2000-F21-PID-PR-10002 | F21-GA-413C CIL4 TANK 3 DISCHARGE LAUNDER ISOLATION GATE 3 VALVE A | F21GA413C | Detail 3 | FL | X | X | - | - | CP1 | XV21161A is OPEN AND XV21161B is OPEN | F21-GA-413A and F21-GA-413B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21162B | 2000-F21-PID-PR-10002 | F21-GA-413D CIL4 TANK 3 DISCHARGE LAUNDER ISOLATION GATE 4 VALVE B | F21GA413D | Detail 3 | FL | X | X | - | - | CP1 | XV21161A is OPEN AND XV21161B is OPEN | F21-GA-413A and F21-GA-413B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21181A | 2000-F21-PID-PR-10002 | F21-GA-414A CIL4 TANK 4 DISCHARGE LAUNDER ISOLATION GATE 1 VALVE A | F21GA414A | Detail 3 | FL | X | X | - | - | CP1 | XV21182A is OPEN AND XV21182B is OPEN | F21-GA-414C and F21-GA-414D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21181B | 2000-F21-PID-PR-10002 | F21-GA-414B CIL4 TANK 4 DISCHARGE LAUNDER ISOLATION GATE 2 VALVE B | F21GA414B | Detail 3 | FL | X | X | - | - | CP1 | XV21182A is OPEN AND XV21182B is OPEN | F21-GA-414C and F21-GA-414D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21182A | 2000-F21-PID-PR-10002 | F21-GA-414C CIL4 TANK 4 DISCHARGE LAUNDER ISOLATION GATE 3 VALVE A | F21GA414C | Detail 3 | FL | X | X | - | - | CP1 | XV21181A is OPEN AND XV21181B is OPEN | F21-GA-414A and F21-GA-414B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21182B | 2000-F21-PID-PR-10002 | F21-GA-414D CIL4 TANK 4 DISCHARGE LAUNDER ISOLATION GATE 4 VALVE B | F21GA414D | Detail 3 | FL | X | X | - | - | CP1 | XV21181A is OPEN AND XV21181B is OPEN | F21-GA-414A and F21-GA-414B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21201A | 2000-F21-PID-PR-10002 | F21-GA-415A CIL4 TANK 5 DISCHARGE LAUNDER ISOLATION GATE 1 VALVE A | F21GA415A | Detail 3 | FL | X | X | - | - | CP1 | XV21202A is OPEN AND XV21202B is OPEN | F21-GA-415C and F21-GA-415D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21201B | 2000-F21-PID-PR-10002 | F21-GA-415B CIL4 TANK 5 DISCHARGE LAUNDER ISOLATION GATE 2 VALVE B | F21GA415B | Detail 3 | FL | X | X | - | - | CP1 | XV21202A is OPEN AND XV21202B is OPEN | F21-GA-415C and F21-GA-415D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21202A | 2000-F21-PID-PR-10002 | F21-GA-415C CIL4 TANK 5 DISCHARGE LAUNDER ISOLATION GATE 3 VALVE A | F21GA415C | Detail 3 | FL | X | X | - | - | CP1 | XV21201A is OPEN AND XV21201B is OPEN | F21-GA-415A and F21-GA-415B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21202B | 2000-F21-PID-PR-10002 | F21-GA-415D CIL4 TANK 5 DISCHARGE LAUNDER ISOLATION GATE 4 VALVE B | F21GA415D | Detail 3 | FL | X | X | - | - | CP1 | XV21201A is OPEN AND XV21201B is OPEN | F21-GA-415A and F21-GA-415B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV22139 | 2000-F21-PID-PR-10002 | F22-HP-445 CIL4 LOADED CARBON TRANSFER VESSEL DISCHARGE VALVE | F22HP445 Outlet | Detail 4 | FC | X | X | MULTIPLE | MULTIPLE | - | - | - | - | - | - | - | - | - | - | - |  | 0
|  |  |  | XV21280 | 2000-F21-PID-PR-10003 | F21-SC-420 CIL4 CARBON SIZING SCREEN SPRAY WATER VALVE | F21SC420 Spray | Detail 7 | FC | X | X | F22-SEQ-0008 | F22-SEQ-0008 | - | - | - | - | - | - | - | - | - | - | - |  | A
|  |  |  | XV21241A | 2000-F21-PID-PR-10003 | F21-GA-416A CIL4 TANK 6 DISCHARGE LAUNDER ISOLATION GATE 1 VALVE A | F21GA416A | Detail 3 | FL | X | X | - | - | CP1 | XV21242A is OPEN AND XV21242B is OPEN | F21-GA-416C and F21-GA-416D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21241B | 2000-F21-PID-PR-10003 | F21-GA-416B CIL4 TANK 6 DISCHARGE LAUNDER ISOLATION GATE 2 VALVE B | F21GA416B | Detail 3 | FL | X | X | - | - | CP1 | XV21242A is OPEN AND XV21242B is OPEN | F21-GA-416C and F21-GA-416D must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21242A | 2000-F21-PID-PR-10003 | F21-GA-416C CIL4 TANK 6 DISCHARGE LAUNDER ISOLATION GATE 3 VALVE A | F21GA416C | Detail 3 | FL | X | X | - | - | CP1 | XV21241A is OPEN AND XV21241B is OPEN | F21-GA-416A and F21-GA-416B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21242B | 2000-F21-PID-PR-10003 | F21-GA-416D CIL4 TANK 6 DISCHARGE LAUNDER ISOLATION GATE 4 VALVE B | F21GA416D | Detail 3 | FL | X | X | - | - | CP1 | XV21241A is OPEN AND XV21241B is OPEN | F21-GA-416A and F21-GA-416B must be in an open position. Can not have two sets of gates closed simultaneously. | - | - | - | X | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21261A | 2000-F21-PID-PR-10003 | F21-GA-417A CIL4 TANK 7 DISCHARGE LAUNDER ISOLATION GATE 1 VALVE A | F21GA417A | Detail 3 | FL | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 0 | [5 empty] | No conditions placed on these valves otherwise the operation of XV21262 in relation with XV21271 will cause spillage. This allows XV21261 to close when XV21271 does. - JBa
|  |  |  | XV21261B | 2000-F21-PID-PR-10003 | F21-GA-417B CIL4 TANK 7 DISCHARGE LAUNDER ISOLATION GATE 2 VALVE B | F21GA417B | Detail 3 | FL | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 0 | [5 empty] | No conditions placed on these valves otherwise the operation of XV21262 in relation with XV21271 will cause spillage. This allows XV21261 to close when XV21271 does. - JBa
|  |  |  | XV21262A | 2000-F21-PID-PR-10003 | F21-GA-417C CIL4 TANK 7 DISCHARGE LAUNDER ISOLATION GATE 3 VALVE A | F21GA417C | Detail 3 | FL | X | X | - | - | OP1 | XV21271A is CLOSED AND XV21271B is CLOSED | F21-GA-418A and F21-GA-418B must be in a closed position. Can not have two sets of gates opened simultaneously. | - | - | X | - | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21262B | 2000-F21-PID-PR-10003 | F21-GA-417D CIL4 TANK 7 DISCHARGE LAUNDER ISOLATION GATE 4 VALVE B | F21GA417D | Detail 3 | FL | X | X | - | - | OP1 | XV21271A is CLOSED AND XV21271B is CLOSED | F21-GA-418A and F21-GA-418B must be in a closed position. Can not have two sets of gates opened simultaneously. | - | - | X | - | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21271A | 2000-F21-PID-PR-10003 | F21-GA-418A CIL4 TANK 8 DISCHARGE LAUNDER ISOLATION GATE 1 VALVE A | F21GA418A | Detail 3 | FL | X | X | - | - | OP1 | XV21262A is CLOSED AND XV21262B is CLOSED | F21-GA-417C and F21-GA-417D must be in a closed position. Can not have two sets of gates opened simultaneously. | - | - | X | - | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21271B | 2000-F21-PID-PR-10003 | F21-GA-418B CIL4 TANK 8 DISCHARGE LAUNDER ISOLATION GATE 2 VALVE B | F21GA418B | Detail 3 | FL | X | X | - | - | OP1 | XV21262A is CLOSED AND XV21262B is CLOSED | F21-GA-417C and F21-GA-417D must be in a closed position. Can not have two sets of gates opened simultaneously. | - | - | X | - | - | - | X | - |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | XV21011 | 2000-F21-PID-PR-10001 | LIME RINGMAIN F21 AREA DEAD-LEG DRAIN | F21 Lime Drain | Detail 12 | FL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Local operation in field only, with position feedback to DCS | 1 | [5 empty] | 2025-05-15 | Updated as per discussion with client 15/05/2025
|  |  |  | SV21305 | 2000-F21-PID-PR-10005 | F21-SA-432 CIL4 TAILS SECONDARY SAMPLER CUTTER FLUSHING SOLENOID VALVE | F21SA432 CIL4 Tails Sec | Detail 11 | FC | X | X | F21-SEQ-0004 & F21-SEQ-0006 | F21-SEQ-0004 & F21-SEQ-0006 | - | - | - | - | - | - | - | - | - | - | - | Single digital output solenoid. | 0
|  |  |  | SV21308 | 2000-F21-PID-PR-10005 | F21-SA-433 CIL4 TAILS TERTIARY SAMPLER CUTTER FLUSHING SOLENOID VALVE | F21SA433 CIL4 Tails Tert | Detail 11 | FC | X | X | F21-SEQ-0004 & F21-SEQ-0007 | F21-SEQ-0004 & F21-SEQ-0007 | - | - | - | - | - | - | - | - | - | - | - | Single digital output solenoid. | 0
|  |  |  | SV21311 | 2000-F21-PID-PR-10005 | F21-SA-431 CIL4 TAILS PRIMARY SAMPLER CUTTER FLUSHING SOLENOID VALVE | F21SA431 CIL4 Tails Pri | Detail 11 | FC | X | X | F21-SEQ-0004 & F21-SEQ-0005 | F21-SEQ-0004 & F21-SEQ-0005 | - | - | - | - | - | - | - | - | - | - | - | Single digital output solenoid. | 0
|  |  |  | SV21317 | 2000-F21-PID-PR-10005 | F21-FI-420 CIL4 TAILS FINAL SAMPLE DEWATERING MODULE AIR SUPPLY SOLENOID VALVE | F21SA420 CIL4 Final Tail | Detail 11 | FC | X | X | TBC - WAITING VENDOR INFORMATION | TBC - WAITING VENDOR INFORMATION | - | - | - | - | - | - | - | - | - | - | - | Single digital output solenoid. | C
|  |  |  | SV30460 | 2000-F30-PID-PR-10011 | F30-SA-443 CIL3 TAILS PRIMARY SAMPLER FLUSHING WATER SOLENOID VALVE | F30SA443 Flush | Detail 11 | FC | X | X | MULTIPLE | MULTIPLE | - | - | - | - | - | - | - | - | - | - | - | Single digital output solenoid. | 0
|  |  |  | SV30479 | 2000-F30-PID-PR-10011 | F30-SA-444 CIL3 TAILS SECONDARY SAMPLER FLUSHING WATER SOLENOID VALVE | F30SA444 Flush | Detail 11 | FC | X | X | MULTIPLE | MULTIPLE | - | - | - | - | - | - | - | - | - | - | - | Single digital output solenoid. | 0
-
|  |  |  | DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE | [11 empty] | -
53
1

## 8. PID Cont
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21) | [60 empty] | High | Urgent (Critical Failure) | 0
|  |  |  | 2000-F21-LST-PR-10101 | [60 empty] | Med | High (Fault/Error) | 0
|  |  |  | PID Controllers | [60 empty] | Low | Low (Warning) | 0
[10 empty] | Modes |  |  |  | Setpoint |  |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [7 empty] | Alarm Priority |  |  |  |  | Controlled/Manipulated Variable | [10 empty] | Comment | Rev | C1 Sign Off |  | C2 Sign Off |  |  |  |  | n/a | Information/Event (Journal) | 0
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Controller Description | Abbreviated Description (Faceplate) | Normal Operating Mode | Manual | Auto | Cascade | Process Value Tag | Min | Max | Unit | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | A_LL | A_Lo | A_Hi | A_HH | Alarm Masking Conditions | Range Min | Range Max | Lower Limit | Upper Limit | Unit | Destination Description | Destination (Output) Tag | Direct / Reverse Acting | P | I | D |  |  | OK | Date | OK | Date | Comments - Don't put comments in C2 column | Change Date | Change Reference
|  |  |  | FIT21002 | FIC-21002 | 2000-F21-PID-PR-10001 | F21-FD-431 CIL4 FEED DISTRIBUTION BOX CYANIDE FEED FLOW INDICATING TRANSMITTER | F21FD431 CN Ctrl | Automatic | X | X | AIC21243 OR F21-CALC-0001 | FIT21002 | 0 | 30 | m3/h | 0 | 40 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1.5 | 5 | - | - | - | - |  |  |  |  | XV21001 is CLOSED OR (F72PP675 AND F72PP676 is NOT RUNNING) Enable 10s delay mask for pump start-up | 0 | 100 | 0 | 100 | % Open | F21-FD-431 Cyanide FCV | F21-FCV-21002 | Reverse | TBC | TBC | TBC | Cascade input into FIC-21002 from either AIC-21243 or F21-CALC-0001 is selected from the PCS via selector switch HS-21002. | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | FIT21003 | FIC-21003 | 2000-F21-PID-PR-10001 | F21-TK-411 CIL4 TANK 1 CYANIDE FEED FLOW INDICATING TRANSMITTER | F21TK411 CN Ctrl | Automatic | X | X | - | FIT21003 | 0 | 30 | m3/h | 0 | 40 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 5 | - | - | - | - |  |  |  |  | XV21001 is CLOSED OR (F72PP675 AND F72PP676 is NOT RUNNING) Enable 10s delay mask for pump start-up | 0 | 100 | 0 | 100 | % Open | F21-TK-411 Cyanide FCV | F21-FCV-21003 | Reverse | TBC | TBC | TBC |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | FIT21004 | FIC-21004 | 2000-F21-PID-PR-10001 | F21-TK-412 CIL4 TANK 2 CYANIDE FEED FLOW INDICATING TRANSMITTER | F21TK412 CN Ctrl | Automatic | X | X | - | FIT21004 | 0 | 30 | m3/h | 0 | 40 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 5 | - | - | - | - |  |  |  |  | XV21001 is CLOSED OR (F72PP675 AND F72PP676 is NOT RUNNING) Enable 10s delay mask for pump start-up | 0 | 100 | 0 | 100 | % Open | F21-TK-412 Cyanide FCV | F21-FCV-21004 | Reverse | TBC | TBC | TBC |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | AIT21062 | AIC-21062 | 2000-F21-PID-PR-10001 | F21-TK-411 CIL4 TANK 1 PH TRANSMITTER | F21TK411 pH Ctrl | Automatic | X | X | - | AIT21062 | 9 | 12 | - | 1 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | - | 8 | 5 | 8.5 | 5 | - | - | - | - |  |  |  |  | - | 0 | 100 | 0 | 100 | s | F21-FD-431 Lime Valve | F21-XV-21012 | Reverse | TBC | TBC | TBC | Duty Cycle control of F21-XV-21012. Control of valve will be from either AIC-21062 or AIC-21102 and will be selected from the PCS via selctor switch HS-21062. | 1 | [5 empty] | 2026-04-09 | PL-437
|  |  |  | AIT21102 | AIC-21102 | 2000-F21-PID-PR-10001 | F21-TK-412 CIL4 TANK 2 PH TRANSMITTER | F21TK412 pH Ctrl | Automatic | X | X | - | AIT21102 | 9 | 12 | - | 1 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | - | 8 | 5 | 8.5 | 5 | - | - | - | - |  |  |  |  | - | 0 | 100 | 0 | 100 | s | F21-FD-431 Lime Valve | F21-XV-21012 | Reverse | TBC | TBC | TBC | Duty Cycle control of F21-XV-21012. Control of valve will be from either AIC-21062 or AIC-21102 and will be selected from the PCS via selctor switch HS-21062. | 1 | [5 empty] | 2026-04-09 | PL-437
|  |  |  | FIT21059 | FIC-21059 | 2000-F21-PID-PR-10011 | F21-PP-478 CIL4 TANK 1 OXYGEN INJECTION PUMP DISCHARGE FLOW INDICATING TRANSMITTER | F21PP478 Flow | Automatic | X | X | - | FIT21059 | 1000 | 1200 | m3/h | 0 | 1500 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | 800 | 5 | 900 | 5 | - | - | - | - |  |  |  |  | F21PP478 is NOT RUNNING Enable 10s delay mask for pump start-up | 0 | 100 | 0 | 100 | % Speed | F21-PP-478 CIL4 Tank 1 Oxygen Injection Pump | F21-PP-478 VSD | Reverse | TBC | TBC | TBC |  | 0
|  |  |  | FIT21099 | FIC-21099 | 2000-F21-PID-PR-10001 | F21-PP-491 CIL4 TANK 2 OXYGEN INJECTION PUMP DISCHARGE FLOW INDICATING TRANSMITTER | F21PP491 Flow | Automatic | X | X | - | FIT21099 | 1000 | 1200 | m3/h | 0 | 1500 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | 800 | 5 | 900 | 5 | - | - | - | - |  |  |  |  | F21PP491 is NOT RUNNING Enable 10s delay mask for pump start-up | 0 | 100 | 0 | 100 | % Speed | F21-PP-491 CIL4 Tank 1 Oxygen Injection Pump | F21-VSD-491 VSD | Reverse | TBC | TBC | TBC |  | 0
|  |  |  | FIT21033 | FIC-21033 | 2000-F21-PID-PR-10001 | CIL4 Tank 1 Oxygen Injection Flow Indicating Transmitter | F21PP478 O2 Ctrl | Automatic | X | X | - | FIT21033 |  |  | m3/h | 0 |  | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 5 | 200 | 5 | - | - |  |  |  |  | - | 0 | 100 | 0 | 100 | % Open | F21-PP-478 Oxygen FCV | F21-FCV-21033 | Reverse | TBC | TBC | TBC | Series 150 Oxygen Injector has nominal flowrate of 75 m3/h. | C
|  |  |  | FIT21043 | FIC-21043 | 2000-F21-PID-PR-10001 | CIL4 Tank 2 Oxygen Injection Flow Indicating Transmitter | F21PP491 O2 Ctrl | Automatic | X | X | - | FIT21043 |  |  | m3/h | 0 |  | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | 5 | 200 | 5 | - | - |  |  |  |  | - | 0 | 100 | 0 | 100 | % Open | F21-PP-491 Oxygen FCV | F21-FCV-21043 | Reverse | TBC | TBC | TBC |  | C
|  |  |  | FIT21347 | FIC-21347 | 2000-F72-PID-PR-10011 | F21-TK-411 CIL4 TANK 1 OXYGEN INJECTION 1 FLOW INDICATING TRANSMITTER | F21PP478 O2Ctrl1 | Automatic | X | X | - | FIT21347 | 0 | 90 | m3/h | 0 | 100 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 50 | 5 | 95 | 5 | - | - |  |  |  |  | A_Lo: 'F21PP478 is NOT RUNNING Enable 10s delay mask for pump start-up | 0 | 100 | 0 | 100 | % Open | F21-PP-478 Oxygen FCV 1 | F21-FCV-21347 | Reverse | TBC | TBC | TBC | Series 150 Oxygen Injector has nominal flowrate of 75 m3/h. | 1 | [5 empty] | 2025-05-08 | KAN-1483
|  |  |  | FIT21349 | FIC-21349 | 2000-F72-PID-PR-10011 | F21-TK-411 CIL4 TANK 1 OXYGEN INJECTION 2 FLOW INDICATING TRANSMITTER | F21PP478 O2Ctrl2 | Automatic | X | X | - | FIT21349 | 0 | 90 | m3/h | 0 | 100 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 50 | 5 | 95 | 5 | - | - |  |  |  |  | A_Lo: 'F21PP478 is NOT RUNNING Enable 10s delay mask for pump start-up | 0 | 100 | 0 | 100 | % Open | F21-PP-478 Oxygen FCV 2 | F21-FCV-21349 | Reverse | TBC | TBC | TBC | Series 150 Oxygen Injector has nominal flowrate of 75 m3/h. | 1 | [5 empty] | 2025-05-08 | KAN-1483
|  |  |  | FIT21356 | FIC-21356 | 2000-F72-PID-PR-10011 | F21-TK-412 CIL4 TANK 2 OXYGEN INJECTION 1 FLOW INDICATING TRANSMITTER | F21PP491 O2Ctrl1 | Automatic | X | X | - | FIT21356 | 0 | 90 | m3/h | 0 | 100 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 50 | 5 | 95 | 5 | - | - |  |  |  |  | A_Lo: 'F21PP491 is NOT RUNNING Enable 10s delay mask for pump start-up | 0 | 100 | 0 | 100 | % Open | F21-PP-491 Oxygen FCV 1 | F21-FCV-21356 | Reverse | TBC | TBC | TBC | Series 150 Oxygen Injector has nominal flowrate of 75 m3/h. | 1 | [5 empty] | 2025-05-08 | KAN-1483
|  |  |  | FIT21358 | FIC-21358 | 2000-F72-PID-PR-10011 | F21-TK-412 CIL4 TANK 2 OXYGEN INJECTION 2 FLOW INDICATING TRANSMITTER | F21PP491 O2Ctrl2 | Automatic | X | X | - | FIT21358 | 0 | 90 | m3/h | 0 | 100 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 50 | 5 | 95 | 5 | - | - |  |  |  |  | A_Lo: 'F21PP491 is NOT RUNNING Enable 10s delay mask for pump start-up | 0 | 100 | 0 | 100 | % Open | F21-PP-491 Oxygen FCV 1 | F21-FCV-21358 | Reverse | TBC | TBC | TBC | Series 150 Oxygen Injector has nominal flowrate of 75 m3/h. | 1 | [5 empty] | 2025-05-08 | KAN-1483
|  |  |  | FIT21005 | FIC-21005 | 2000-F21-PID-PR-10002 | F21-TK-413 CIL4 TANK 3 CYANIDE FEED FLOW TRANSMITTER | F21TK413 CN Ctrl | Automatic | X | X | - | FIT21005 | 0 | 30 | m3/h | 0 | 40 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 5 | - | - | - | - |  |  |  |  | XV21001 is CLOSED OR (F72PP675 AND F72PP676 is NOT RUNNING) Enable 10s delay mask for pump start-up | 0 | 100 | 0 | 100 | % Open | F21-TK-413 Cyanide FCV | F21-FCV-21005 | Reverse | TBC | TBC | TBC |  | 1 | [5 empty] | 2025-05-08 | KAN-1484
|  |  |  | AIC21243 | AIC-21243 | 2000-F21-PID-PR-10003 | F21-CA-411/412 CIL 4 CYANIDE ANALYSERS CYANIDE CONCENTRATION 1 | CIL4 CN Ctrl | Automatic | X | X | - | AI21243S OR AI21244S | 0 | 200 | ppm | 0 | 500 | ppm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | - | 0 | 30 | 0 | 30 | m3/h | F21FD431 CN Ctrl | FIC-21002 | Reverse | TBC | TBC | TBC | Input into AIC-21243 from either AI-21243 or AI-21244 is selected from the PCS via selector switch HS-21243. | 1 | [5 empty] | 2025-08-04 | KAN-2149
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 13 | 13

## 7. Control Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21)
|  |  |  | 2000-F21-LST-PR-10101 | [29 empty] | Fail Open
|  |  |  | CONTROL VALVES | [29 empty] | Fail Closed
[14 empty] | Permissive and Trips | [12 empty] | C1 Sign Off |  | C2 Sign Off |  |  |  |  | Fail Last
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open Interlock | Close Interlock | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date | Comments - Don't put comments in C2 column | Change Date | Change Reference
|  |  |  | XV21012 | 2000-F21-PID-PR-10001 | F21-FD-431 CIL4 FEED DISTRIBUTION BOX MILK OF LIME FEED CONTROL VALVE | CIL4 Lime Addn | Detail 3 | FL | X | X | - | - | - | - | - | - | - | - | - | - | - | - | - | Valve will be controlled via PID loop controllers AIC21062 or AIC21102. PID control via pulse-width modulation. | C
|  |  |  | FCV21002 | 2000-F21-PID-PR-10001 | F21-FD-431 CIL4 FEED DISTRIBUTION BOX CYANIDE FEED FLOW CONTROL VALVE | F21FD431 Cyanide | Detail 1 | FC | X | X | - | - | CT1 | AIC21062 < A_LL OR AIC21102 < A_LL | - | 300 | - | - | - | - | X | X | - | Refer to PID Controller FIC-21002 | 1 | [5 empty] | 2025-04-04 | Design change - HAZID 4/04/2025
|  |  |  | FCV21003 | 2000-F21-PID-PR-10001 | F21-TK-411 CIL4 TANK 1 CYANIDE FEED FLOW CONTROL VALVE | F21TK411 Cyanide | Detail 1 | FC | X | X | - | - | CT1 | AIC21062 < A_LL OR AIC21102 < A_LL | - | 300 | - | - | - | - | X | X | - | Refer to PID Controller FIC-21003 | 1 | [5 empty] | 2025-04-04 | Design change - HAZID 4/04/2025
|  |  |  | FCV21004 | 2000-F21-PID-PR-10001 | F21-TK-412 CIL4 TANK 2 CYANIDE FEED FLOW CONTROL VALVE | F21TK412 Cyanide | Detail 1 | FC | X | X | - | - | CT1 | AIC21062 < A_LL OR AIC21102 < A_LL | - | 300 | - | - | - | - | X | X | - | Refer to PID Controller FIC-21004 | 1 | [5 empty] | 2025-04-04 | Design change - HAZID 4/04/2025
|  |  |  | FCV21033 | 2000-F21-PID-PR-10001 | CIL4 Tank 1 Oxygen Injection Flow Control Valve | F21PP478 Oxygen | Detail 1 | FC | X | X | - | - | CTx | F21-PP-478 Not Running | - | - | - | - | - | - | X | - | - | Refer to PID Controller FIC-21033 | C
|  |  |  | FCV21043 | 2000-F21-PID-PR-10001 | CIL4 Tank 2 Oxygen Injection Flow Control Valve | F21PP491 Oxygen | Detail 1 | FC | X | X | - | - | CTx | F21-PP-491 Not Running | - | - | - | - | - | - | X | - | - | Refer to PID Controller FIC-21043 | C
|  |  |  | FCV21347 | 2000-F72-PID-PR-10011 | F21-TK-411 CIL4 TANK 1 OXYGEN INJECTION 1 FLOW CONTROL VALVE | F21PP478 Oxygen1 | Detail 1 | FC | X | X | - | - | CT1 | F21-PP-478 is NOT RUNNING | - | - | - | - | - | - | X | - | - | No bypass option allowed for this interlock, as per HAZOP item F21-01.1.11 Refer to PID Controller FIC-21347 | 0
[14 empty] | CT2 | PI21348 ≥ A_HH | - | 5 | - | - | - | - | X | X | - |  | 1 | [5 empty] | 2025-06-05 | Design change - HAZID 4/04/2025
|  |  |  | FCV21349 | 2000-F72-PID-PR-10011 | F21-TK-411 CIL4 TANK 1 OXYGEN INJECTION 2 FLOW CONTROL VALVE | F21PP478 Oxygen2 | Detail 1 | FC | X | X | - | - | CT1 | F21-PP-478 is NOT RUNNING | - | - | - | - | - | - | X | - | - | No bypass option allowed for this interlock, as per HAZOP item F21-01.1.11 Refer to PID Controller FIC-21349 | 0
[14 empty] | CT2 | PI21350 ≥ A_HH | - | 5 | - | - | - | - | X | X | - |  | 1 | [5 empty] | 2025-06-05 | Design change - HAZID 4/04/2025
|  |  |  | FCV21356 | 2000-F72-PID-PR-10011 | F21-TK-412 CIL4 TANK 2 OXYGEN INJECTION 1 FLOW CONTROL VALVE | F21PP491 Oxygen1 | Detail 1 | FC | X | X | - | - | CT1 | F21-PP-491 is NOT RUNNING | - | - | - | - | - | - | X | - | - | No bypass option allowed for this interlock, as per HAZOP item F21-01.1.11 Refer to PID Controller FIC-21356 | 0
[14 empty] | CT2 | PI21357 ≥ A_HH | - | 5 | - | - | - | - | X | X | - |  | 1 | [5 empty] | 2025-06-05 | Design change - HAZID 4/04/2025
|  |  |  | FCV21358 | 2000-F72-PID-PR-10011 | F21-TK-412 CIL4 TANK 2 OXYGEN INJECTION 2 FLOW CONTROL VALVE | F21PP491 Oxygen2 | Detail 1 | FC | X | X | - | - | CT1 | F21-PP-491 is NOT RUNNING | - | - | - | - | - | - | X | - | - | No bypass option allowed for this interlock, as per HAZOP item F21-01.1.11 Refer to PID Controller FIC-21358 | 0
[14 empty] | CT2 | PI21359 ≥ A_HH | - | 5 | - | - | - | - | X | X | - |  | 1 | [5 empty] | 2025-06-05 | Design change - HAZID 4/04/2025
|  |  |  | FCV21005 | 2000-F21-PID-PR-10002 | F21-TK-413 CIL4 TANK 3 CYANIDE FEED FLOW CONTROL VALVE | F21TK413 Cyanide | Detail 1 | FC | X | X | - | - | CT1 | AIC21062 < A_LL OR AIC21102 < A_LL | - | 300 | - | - | - | - | X | X | - | Refer to PID Controller FIC-21005 | 1 | [5 empty] | 2025-04-04 | Design change - HAZID 4/04/2025
[5 empty] | 0 | 0
[5 empty] | 0 | 0
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
9

## 9. Drives
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21)
2000-F21-LST-PR-10101
DRIVE INTERLOCKS AND CONTROL
[15 empty] | Description (Unhealthy Interlocks) |  |  |  | Interlocks | [6 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Name | Drive Type | Speed Min | Speed Max | Speed Units | SP Lower Limit | SP Upper Limit | Current Max | Manual | Auto | Start Condition (Auto Mode) | Stop Condition (Auto Mode) | # |  | Delay On | Delay Off | Start Permissive | Process | Critical | Hardwired to Drive | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date | Comments - Don't put comments in C2 column | Change Date | Change Reference
F21-AG-411 | 2000-F21-PID-PR-10001 | CIL4 Tank 1 Agitator | DOL | - | - | - | - | - | 416 | X | X | F21-SEQ-0008 | F21-SEQ-0008 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-2123
[14 empty] | 1 | F21-AG-411 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-AG-411 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-AG-411 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-AG-411 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-AG-411 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-AG-411 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-AG-411 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | TI21023A ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase U High-High | 0
[14 empty] | 9 | TI21023B ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase V High-High | 0
[14 empty] | 10 | TI21023C ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase W High-High | 0
[14 empty] | 11 | TI21023D ≥ A_HH | 3 |  |  |  | X |  |  |  | DE Motor bearing temperature High-High | 0
[14 empty] | 12 | TI21023E ≥ A_HH | 3 |  |  |  | X |  |  |  | NDE Motor bearing temperature High-High | 0
F21-AG-412 | 2000-F21-PID-PR-10001 | CIL4 Tank 2 Agitator | DOL | - | - | - | - | - | 416 | X | X | F21-SEQ-0008 | F21-SEQ-0008 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-2123
[14 empty] | 1 | F21-AG-412 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-AG-412 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-AG-412 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-AG-412 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-AG-412 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-AG-412 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-AG-412 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | TI21024A ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase U High-High | 0
[14 empty] | 9 | TI21024B ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase V High-High | 0
[14 empty] | 10 | TI21024C ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase W High-High | 0
[14 empty] | 11 | TI21024D ≥ A_HH | 3 |  |  |  | X |  |  |  | DE Motor bearing temperature High-High | 0
[14 empty] | 12 | TI21024E ≥ A_HH | 3 |  |  |  | X |  |  |  | NDE Motor bearing temperature High-High | 0
F21-AG-413 | 2000-F21-PID-PR-10002 | CIL4 Tank 3 Agitator | DOL | - | - | - | - | - | 416 | X | X | F21-SEQ-0008 | F21-SEQ-0008 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-2123
[14 empty] | 1 | F21-AG-413 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-AG-413 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-AG-413 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-AG-413 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-AG-413 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-AG-413 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-AG-413 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | TI21025A ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase U High-High | 0
[14 empty] | 9 | TI21025B ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase V High-High | 0
[14 empty] | 10 | TI21025C ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase W High-High | 0
[14 empty] | 11 | TI21025D ≥ A_HH | 3 |  |  |  | X |  |  |  | DE Motor bearing temperature High-High | 0
[14 empty] | 12 | TI21025E ≥ A_HH | 3 |  |  |  | X |  |  |  | NDE Motor bearing temperature High-High | 0
F21-AG-414 | 2000-F21-PID-PR-10002 | CIL4 Tank 4 Agitator | DOL | - | - | - | - | - | 416 | X | X | F21-SEQ-0008 | F21-SEQ-0008 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-2123
[14 empty] | 1 | F21-AG-414 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-AG-414 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-AG-414 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-AG-414 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-AG-414 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-AG-414 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-AG-414 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | TI21026A ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase U High-High | 0
[14 empty] | 9 | TI21026B ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase V High-High | 0
[14 empty] | 10 | TI21026C ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase W High-High | 0
[14 empty] | 11 | TI21026D ≥ A_HH | 3 |  |  |  | X |  |  |  | DE Motor bearing temperature High-High | 0
[14 empty] | 12 | TI21026E ≥ A_HH | 3 |  |  |  | X |  |  |  | NDE Motor bearing temperature High-High | 0
F21-AG-415 | 2000-F21-PID-PR-10002 | CIL4 Tank 5 Agitator | DOL | - | - | - | - | - | 416 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-AG-415 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-AG-415 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-AG-415 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-AG-415 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-AG-415 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-AG-415 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-AG-415 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | TI21027A ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase U High-High | 0
[14 empty] | 9 | TI21027B ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase V High-High | 0
[14 empty] | 10 | TI21027C ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase W High-High | 0
[14 empty] | 11 | TI21027D ≥ A_HH | 3 |  |  |  | X |  |  |  | DE Motor bearing temperature High-High | 0
[14 empty] | 12 | TI21027E ≥ A_HH | 3 |  |  |  | X |  |  |  | NDE Motor bearing temperature High-High | 0
F21-AG-416 | 2000-F21-PID-PR-10003 | CIL4 Tank 6 Agitator | DOL | - | - | - | - | - | 416 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-AG-416 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-AG-416 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-AG-416 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-AG-416 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-AG-416 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-AG-416 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-AG-416 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | TI21028A ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase U High-High | 0
[14 empty] | 9 | TI21028B ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase V High-High | 0
[14 empty] | 10 | TI21028C ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase W High-High | 0
[14 empty] | 11 | TI21028D ≥ A_HH | 3 |  |  |  | X |  |  |  | DE Motor bearing temperature High-High | 0
[14 empty] | 12 | TI21028E ≥ A_HH | 3 |  |  |  | X |  |  |  | NDE Motor bearing temperature High-High | 0
F21-AG-417 | 2000-F21-PID-PR-10003 | CIL4 Tank 7 Agitator | DOL | - | - | - | - | - | 416 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-AG-417 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-AG-417 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-AG-417 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-AG-417 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-AG-417 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-AG-417 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-AG-417 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | TI21029A ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase U High-High | 0
[14 empty] | 9 | TI21029B ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase V High-High | 0
[14 empty] | 10 | TI21029C ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase W High-High | 0
[14 empty] | 11 | TI21029D ≥ A_HH | 3 |  |  |  | X |  |  |  | DE Motor bearing temperature High-High | 0
[14 empty] | 12 | TI21029E ≥ A_HH | 3 |  |  |  | X |  |  |  | NDE Motor bearing temperature High-High | 0
F21-AG-418 | 2000-F21-PID-PR-10003 | CIL4 Tank 8 Agitator | DOL | - | - | - | - | - | 416 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-AG-418 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-AG-418 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-AG-418 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-AG-418 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-AG-418 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-AG-418 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-AG-418 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | TI21030A ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase U High-High | 0
[14 empty] | 9 | TI21030B ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase V High-High | 0
[14 empty] | 10 | TI21030C ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase W High-High | 0
[14 empty] | 11 | TI21030D ≥ A_HH | 3 |  |  |  | X |  |  |  | DE Motor bearing temperature High-High | 0
[14 empty] | 12 | TI21030E ≥ A_HH | 3 |  |  |  | X |  |  |  | NDE Motor bearing temperature High-High | 0
F21-PP-478 | 2000-F21-PID-PR-10001 | CIL4 Tank 1 Oxygen Injection Pump | VSD | 0 | 100 | % | 40 | 100 | 421 | X | X | - | - |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597
[14 empty] | 1 | F21-PP-478 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-PP-478 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-PP-478 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-PP-478 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-PP-478 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-PP-478 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-PP-478 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 9 | FSL21321 ACTIVE AND F21-PP-478 RUNNING | 600 |  |  | X |  |  | X |  | Low Gland Water Flow | 0
[14 empty] | 10 | XV21051 is CLOSED | 3 |  |  | X |  |  | X |  | Suction Valve is Closed | 1 | [5 empty] | 2025-05-08 | KAN-1484
[14 empty] | 11 | XV21053 is CLOSED | 3 |  |  | X |  |  | X |  | Discharge Valve is Closed | 1 | [5 empty] | 2025-05-08 | KAN-1484
[14 empty] | 12 | PI21054 ≤ A_LL AND F21-PP-478 RUNNING | 120 |  |  | X |  |  | X |  | Post Oxygen Injector Low-Low Pressure. Possible loss of containment. | 0
[14 empty] | 13 | PI21054 ≥ A_HH | 120 |  |  | X |  |  | X |  | Post Oxygen Injector High-High Pressure. Possible blockage. | A
[14 empty] | 14 | PI21055 ≤ A_LL AND F21-PP-478 RUNNING | 120 |  |  | X |  |  | X |  | Pre Oxygen Injector Low-Low Pressure. Possible loss of containment. | 0
[14 empty] | 15 | PI21055 ≥ A_HH | 120 |  |  | X |  |  | X |  | Pre Oxygen Injector High-High Pressure. Possible blockage. | A
[14 empty] | 16 | TI21031A ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase U High-High | 0
[14 empty] | 17 | TI21031B ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase V High-High | 0
[14 empty] | 18 | TI21031C ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase W High-High | 0
[14 empty] | 19 | TI21031D ≥ A_HH | 3 |  |  |  | X |  |  |  | DE Motor bearing temperature High-High | 0
[14 empty] | 20 | TI21031E ≥ A_HH | 3 |  |  |  | X |  |  |  | NDE Motor bearing temperature High-High | 0
[14 empty] | 21 | FIC21059 ≤ A_LL AND F21-PP-478 RUNNING | 120 |  |  | X |  |  | X |  | Discharge Flowmeter Low-Low Flow | 0
[14 empty] | 22 | SV21320 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve is in auto or open | 1 | [5 empty] | 2025-05-22 | Updated for consistent gland water logic
F21-PP-491 | 2000-F21-PID-PR-10001 | CIL4 Tank 2 Oxygen Injection Pump | VSD | 0 | 100 | % | 40 | 100 | 421 | X | X | - | - |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597
[14 empty] | 1 | F21-PP-491 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-PP-491 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-PP-491 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-PP-491 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-PP-491 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-PP-491 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-PP-491 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 9 | FSL21325 ACTIVE AND F21-PP-491 RUNNING | 600 |  |  | X |  |  | X |  | Low Gland Water Flow | 0
[14 empty] | 10 | XV21091 is CLOSED | 3 |  |  | X |  |  | X |  | Suction Valve is Closed | 1 | [5 empty] | 2025-05-08 | KAN-1484
[14 empty] | 11 | XV21093 is CLOSED | 3 |  |  | X |  |  | X |  | Discharge Valve is Closed | 1 | [5 empty] | 2025-05-08 | KAN-1484
[14 empty] | 12 | PI21094 ≤ A_LL AND F21-PP-491 RUNNING | 120 |  |  | X |  |  | X |  | Post Oxygen Injector Low-Low Pressure. Possible loss of containment. | 0
[14 empty] | 13 | PI21094 ≥ A_HH | 120 |  |  | X |  |  | X |  | Post Oxygen Injector High-High Pressure. Possible blockage. | A
[14 empty] | 14 | PI21095 ≤ A_LL AND F21-PP-491 RUNNING | 120 |  |  | X |  |  | X |  | Pre Oxygen Injector Low-Low Pressure. Possible loss of containment. | 0
[14 empty] | 15 | PI21095 ≥ A_HH | 120 |  |  | X |  |  | X |  | Pre Oxygen Injector High-High Pressure. Possible blockage. | A
[14 empty] | 16 | TI21034A ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase U High-High | 0
[14 empty] | 17 | TI21034B ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase V High-High | 0
[14 empty] | 18 | TI21034C ≥ A_HH | 3 |  |  |  | X |  |  |  | Motor phase W High-High | 0
[14 empty] | 19 | TI21034D ≥ A_HH | 3 |  |  |  | X |  |  |  | DE Motor bearing temperature High-High | 0
[14 empty] | 20 | TI21034E ≥ A_HH | 3 |  |  |  | X |  |  |  | NDE Motor bearing temperature High-High | 0
[14 empty] | 21 | FIC21099 ≤ A_LL AND F21-PP-491 RUNNING | 120 |  |  | X |  |  | X |  | Discharge Flowmeter Low-Low Flow | 0
[14 empty] | 22 | SV21324 Auto OR Open | 3 |  | X |  |  |  | X |  | Gland water valve is in auto or open | 1 | [5 empty] | 2025-05-22 | Updated for consistent gland water logic
F21-PP-470 | 2000-F21-PID-PR-10002 | CIL4 Loaded Carbon Pump | VSD | 0 | 100 | % | 40 | 100 | 92.8 | X | X | F21-SEQ-0003 | F21-SEQ-0003 |  | Drive Operation | [8 empty] | Note: Maximum VSD speed to be limited to prevent carbon wear. Limit to be established during commissioning. | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597
[14 empty] | 1 | F21-PP-470 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-PP-470 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-PP-470 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-PP-470 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-PP-470 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-PP-470 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-PP-470 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 9 | LSH22137 is ACTIVE | 10 |  |  | X |  |  | X |  | CIL4 Loaded Carbon Transfer Vessel Level Switch High | 1 | [5 empty] | 2025-07-11 | Updated as per KAN-2109
[14 empty] | 10 | F22-SC-421 is NOT RUNNING | 3 |  |  | X |  |  | X |  | CIL4 Loaded Carbon Screen is Not Running | A
F21-PP-471 | 2000-F21-PID-PR-10002 | CIL4 Carbon Transfer Pump 1 | VSD | 0 | 100 | % | 40 | 100 | 92.8 | X | X | F21-SEQ-0001 | F21-SEQ-0001 |  | Drive Operation | [8 empty] | Note: Maximum VSD speed to be limited to prevent carbon wear. Limit to be established during commissioning. | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-2123
[14 empty] | 1 | F21-PP-471 Comms Failure | 0 |  |  |  | X |  |  |  | CIL4 Carbon Scout (F21-AN-412) start/stop signals to be sent via modbus | 1 | [5 empty] | 2025-07-11 | Updated as per KAN-2114
[14 empty] | 2 | F21-PP-471 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-PP-471 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-PP-471 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-PP-471 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-PP-471 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-PP-471 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 9 | LSH22137 ACTIVE and CIL4TK3BYP ACTIVE | 10 |  |  | X |  |  | X |  | CIL4 Loaded Carbon Transfer Vessel Level Switch High and CIL4 Tank 3 is bypassed | 1 | [5 empty] | 2026-04-09
[14 empty] | 10 | F22-SC-421 NOT RUNNING and CIL4TK3BYP ACTIVE | 3 |  |  | X |  |  | X |  | CIL4 Loaded Carbon Screen is Not Running and CIL4 Tank 3 is bypassed | 1 | [5 empty] | 2026-04-09
F21-PP-472 | 2000-F21-PID-PR-10002 | CIL4 Carbon Transfer Pump 2 | DOL | - | - | - | - | - | 51.4 | X | X | F21-SEQ-0001 | F21-SEQ-0001 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597
[14 empty] | 1 | F21-PP-472 Comms Failure | 0 |  |  |  | X |  |  |  | CIL4 Carbon Scout (F21-AN-412) start/stop signals to be sent via modbus | 1 | [5 empty] | 2025-07-11 | Updated as per KAN-2114
[14 empty] | 2 | F21-PP-472 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-PP-472 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-PP-472 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-PP-472 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-PP-472 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-PP-472 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
F21-PP-473 | 2000-F21-PID-PR-10003 | CIL4 Carbon Transfer Pump 3 | DOL | - | - | - | - | - | 51.4 | X | X | F21-SEQ-0001 | F21-SEQ-0001 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-2123
[14 empty] | 1 | F21-PP-473 Comms Failure | 0 |  |  |  | X |  |  |  | CIL4 Carbon Scout (F21-AN-412) start/stop signals to be sent via modbus | 1 | [5 empty] | 2025-07-11 | Updated as per KAN-2114
[14 empty] | 2 | F21-PP-473 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-PP-473 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-PP-473 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-PP-473 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-PP-473 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-PP-473 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
F21-PP-474 | 2000-F21-PID-PR-10003 | CIL4 Carbon Transfer Pump 4 | DOL | - | - | - | - | - | 51.4 | X | X | F21-SEQ-0001 | F21-SEQ-0001 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597
[14 empty] | 1 | F21-PP-474 Comms Failure | 0 |  |  |  | X |  |  |  | CIL4 Carbon Scout (F21-AN-412) start/stop signals to be sent via modbus | 1 | [5 empty] | 2025-07-11 | Updated as per KAN-2114
[14 empty] | 2 | F21-PP-474 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-PP-474 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-PP-474 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-PP-474 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-PP-474 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-PP-474 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
F21-PP-475 | 2000-F21-PID-PR-10003 | CIL4 Carbon Transfer Pump 5 | DOL | - | - | - | - | - | 51.4 | X | X | F21-SEQ-0001 | F21-SEQ-0001 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-2123
[14 empty] | 1 | F21-PP-475 Comms Failure | 0 |  |  |  | X |  |  |  | CIL4 Carbon Scout (F21-AN-412) start/stop signals to be sent via modbus | 1 | [5 empty] | 2025-07-11 | Updated as per KAN-2114
[14 empty] | 2 | F21-PP-475 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-PP-475 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-PP-475 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-PP-475 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-PP-475 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-PP-475 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
F21-PS-414 | 2000-F21-PID-PR-10001 | CIL4 Area Sump Pump 1 | DOL SP | - | - | - | - | - | 92.8 | X | X | LSH21131 is ACTIVE | LSH21131 INACTIVE for 600 seconds |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-PS-414 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-PS-414 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-PS-414 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-PS-414 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-PS-414 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-PS-414 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-PS-414 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
F21-PS-415 | 2000-F21-PID-PR-10002 | CIL4 Area Sump Pump 2 | DOL SP | - | - | - | - | - | 92.8 | X | X | LSH21221 is ACTIVE | LSH21221 INACTIVE for 600 seconds |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-PS-415 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-PS-415 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-PS-415 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-PS-415 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-PS-415 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-PS-415 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-PS-415 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
F21-PS-416 | 2000-F21-PID-PR-10002 | CIL4 Area Sump Pump 3 | DOL SP | - | - | - | - | - | 92.8 | X | X | LSH21222 is ACTIVE | LSH21222 INACTIVE for 600 seconds |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-PS-416 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-PS-416 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-PS-416 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-PS-416 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-PS-416 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-PS-416 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-PS-416 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW007Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
F21-PS-417 | 2000-F21-PID-PR-10003 | CIL4 Area Sump Pump 4 | DOL SP | - | - | - | - | - | 92.8 | X | X | LSH21291 is ACTIVE | LSH21291 INACTIVE for 600 seconds |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-PS-417 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-PS-417 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-PS-417 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-PS-417 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-PS-417 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-PS-417 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-PS-417 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW007Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
F21-PP-493 | 2000-F21-PID-PR-10002 | CIL4 Carbon Scout Sample Pump | DOL | - | - | - | - | - | 34.7 | X | X | - | - |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597
[14 empty] | 1 | F21-PP-493 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-PP-493 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-PP-493 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-PP-493 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-PP-493 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-PP-493 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-PP-493 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
F21-SC-413A | 2000-F21-PID-PR-10002 | CIL4 Tank 3 Intertank Screen 1 | DOL | - | - | - | - | - | 127 | X | X | F21-SEQ-0008 | F21-SEQ-0008 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-SC-413A Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SC-413A Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SC-413A Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SC-413A E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SC-413A MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SC-413A Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SC-413A Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F21-SC-413B | 2000-F21-PID-PR-10002 | CIL4 Tank 3 Intertank Screen 2 | DOL | - | - | - | - | - | 127 | X | X | F21-SEQ-0008 | F21-SEQ-0008 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-SC-413B Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SC-413B Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SC-413B Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SC-413B E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SC-413B MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SC-413B Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SC-413B Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F21-SC-414A | 2000-F21-PID-PR-10002 | CIL4 Tank 4 Intertank Screen 1 | DOL | - | - | - | - | - | 127 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-SC-414A Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SC-414A Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SC-414A Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SC-414A E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SC-414A MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SC-414A Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SC-414A Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F21-SC-414B | 2000-F21-PID-PR-10002 | CIL4 Tank 4 Intertank Screen 2 | DOL | - | - | - | - | - | 127 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-SC-414B Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SC-414B Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SC-414B Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SC-414B E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SC-414B MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SC-414B Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SC-414B Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F21-SC-415A | 2000-F21-PID-PR-10002 | CIL4 Tank 5 Intertank Screen 1 | DOL | - | - | - | - | - | 127 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-SC-415A Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SC-415A Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SC-415A Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SC-415A E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SC-415A MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SC-415A Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SC-415A Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F21-SC-415B | 2000-F21-PID-PR-10002 | CIL4 Tank 5 Intertank Screen 2 | DOL | - | - | - | - | - | 127 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-SC-415B Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SC-415B Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SC-415B Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SC-415B E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SC-415B MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SC-415B Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SC-415B Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F21-SC-416A | 2000-F21-PID-PR-10003 | CIL4 Tank 6 Intertank Screen 1 | DOL | - | - | - | - | - | 127 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-SC-416A Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SC-416A Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SC-416A Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SC-416A E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SC-416A MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SC-416A Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SC-416A Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F21-SC-416B | 2000-F21-PID-PR-10003 | CIL4 Tank 6 Intertank Screen 2 | DOL | - | - | - | - | - | 127 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-SC-416B Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SC-416B Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SC-416B Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SC-416B E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SC-416B MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SC-416B Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SC-416B Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F21-SC-417A | 2000-F21-PID-PR-10003 | CIL4 Tank 7 Intertank Screen 1 | DOL | - | - | - | - | - | 127 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-SC-417A Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SC-417A Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SC-417A Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SC-417A E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SC-417A MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SC-417A Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SC-417A Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F21-SC-417B | 2000-F21-PID-PR-10003 | CIL4 Tank 7 Intertank Screen 2 | DOL | - | - | - | - | - | 127 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-SC-417B Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SC-417B Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SC-417B Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SC-417B E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SC-417B MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SC-417B Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SC-417B Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F21-SC-418A | 2000-F21-PID-PR-10003 | CIL4 Tank 8 Intertank Screen 1 | DOL | - | - | - | - | - | 127 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-SC-418A Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SC-418A Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SC-418A Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SC-418A E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SC-418A MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SC-418A Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SC-418A Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F21-SC-418B | 2000-F21-PID-PR-10003 | CIL4 Tank 8 Intertank Screen 2 | DOL | - | - | - | - | - | 127 | X | X | F21-SEQ-0009 | F21-SEQ-0009 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-1602
[14 empty] | 1 | F21-SC-418B Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SC-418B Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SC-418B Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SC-418B E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SC-418B MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SC-418B Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SC-418B Drive Ready | 0 |  |  |  | X |  |  |  |  | C
F21-SC-420 | 2000-F21-PID-PR-10003 | CIL4 Carbon Sizing Screen | DOL | - | - | - | - | - | 9.7 | X | X | - | - |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597
[14 empty] | 1 | F21-SC-420 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SC-420 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SC-420 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SC-420 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SC-420 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SC-420 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SC-420 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW007Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
F21-SA-431 | 2000-F21-PID-PR-10005 | CIL4 Primary Tails Sampler | VSD (FWD / REV) | 0 | 100 | % | 40 | 100 | 4.27 | X | X | F21-SEQ-0004 & F21-SEQ-0005 | F21-SEQ-0004 & F21-SEQ-0005 |  | Drive Operation | [8 empty] | Drive is forward / reverse type | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597 & KAN-2079
[14 empty] | 1 | F21-SA-431 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SA-431 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SA-431 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SA-431 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SA-431 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SA-431 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SA-431 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 9 | ZS21310C is ACTIVE | 3 |  |  | X |  |  | X |  | CIL4 Primary Tails Sampler Overtravel 1 | A
[14 empty] | 10 | ZS21313C is ACTIVE | 3 |  |  | X |  |  | X |  | CIL4 Primary Tails Sampler Overtravel 2 | A
F21-SA-432 | 2000-F21-PID-PR-10005 | CIL4 Secondary Tails Sampler | DOL | - | - | - | - | - | 1 | X | X | F21-SEQ-0004 & F21-SEQ-0006 | F21-SEQ-0004 & F21-SEQ-0006 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597
[14 empty] | 1 | F21-SA-432 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SA-432 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SA-432 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SA-432 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SA-432 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SA-432 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SA-432 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
F21-SA-433 | 2000-F21-PID-PR-10005 | Final Tails Tertiary Sampler | DOL | - | - | - | - | - | 0.58 | X | X | F21-SEQ-0004 & F21-SEQ-0007 | F21-SEQ-0004 & F21-SEQ-0007 |  | Drive Operation | [9 empty] | 1 | [5 empty] | 2025-03-19 | Updated as per KAN-1597
[14 empty] | 1 | F21-SA-433 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F21-SA-433 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 3 | F21-SA-433 Drive Fault | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 4 | F21-SA-433 E-Stop | 0 |  |  |  | X | X |  |  |  | C
[14 empty] | 5 | F21-SA-433 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F21-SA-433 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F21-SA-433 Drive Ready | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 8 | F21SW006Q2_CL is ACTIVE | 0 |  |  |  | X |  |  |  |  | 0
37
Notes:
1. "VSD UNHEALTHY" encompasses the following conditions: VSD Modbus Comms Not Healthy, General fault, Main Circuit Breaker Not Closed and Drive Circuit Breaker Not Closed.
2. "DOL UNHEALTHY" encompasses the following conditions: DOL Modbus Comms Not Healthy, General Fault, Main Circuit Breaker Not Closed and Drive Circuit Breaker Not Closed
`

## 10. Sequence
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21)
2000-F21-LST-PR-10101
SEQUENCES
Seq No. | Seq Description | Step | Action | Tag / Item | Description | Next Step Delay (s) | Step Advance Condition | Comments | Rev | Equipment Permissives | Recovery Seq. No if Step Faults
PLEASE REFER TO SEQUENCE FLOWCHART DELIVERABLE DOCUMENTS
0

## 11. Calculation
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21)
2000-F21-LST-PR-10101
CALCULATIONS
|  |  | Unit | Inputs |  |  |  | Operator Input | Calc. Value | Manual Input | [5 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Description (Software Tag Only) |  | # | Tag | Unit | Description |  |  | Nom | Min | Max | Calculation | Comments | Rev | OK | Date | OK | Date | Comments - Don't put comments in C2 column | Change Date | Change Reference
F21-CALC-0001 | 2000-F21-PID-PR-10001 | F21FD431 CN Addition | m3/h | 1 | WI17121 | t/h (Dry) | Flotation Tailings Thickener Underflow Dry Solids Mass Flow | [5 empty] | F21-CALC-0001 = [(WI17121 * F21FD431_Parameter_1) / (F21FD431_Parameter_2 * 10)] / 1000 |  | A
|  |  |  | 2 | F21FD431_Parameter_1 | g/t | Cyanide Consumption Rate | X |  | 220 | 40 | 300 |  |  | A
|  |  |  | 3 | F21FD431_Parameter_2 | % w/w | Cyanide Solution Concentration | X |  | 29 | 25 | 35 |  |  | 1 | [5 empty] | 2025-12-03 | Updated to correct units. DCS ok
|  |  |  | 4 | F21-CALC-0001 | m3/h | F21-FD-431 Cyanide Addition Flowrate |  | X | [5 empty] | A
F21-CALC-0002 | - | F21PP471 Run Time | min | 1 | F21PP471_RUN | min | F21PP471 Run Rime |  | X |  |  |  | IF AI21142C_C > F21TK413_CTRGT then F21PP471_RUN = 0 OTHERWISE F21PP471_RUN = 60 * (5600/220) * (((F21TK413_CTRGT)-(F21TK413_CCONC))/F21TK414_CCONC) | Timer for F21-SEQ-0001. Refer Sequence document 2000-F21-LST-PR-10102 | 1 | [5 empty] | 2025-04-30 | KAN-1648
|  |  |  | 2 | F21TK413_CTRGT | g/L | F21TK413 Carbon Target | X |  | 12.5 | 10 | 20 |  | If F21PP471_RUN is calculated to be ≤ 1 min, please treat this as a run time of 0 mins (i.e. pump to not run). | 1 | [5 empty] | 2025-04-30 | KAN-1645
|  |  |  | 3 | F21TK413_CCONC | g/L | F21TK413 C Conc. | [6 empty] | Refer to Misc. for function of F21TK413_CCONC tag | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser | AI21142C_C
|  |  |  | 4 | F21TK414_CCONC | g/L | F21TK414 C Conc. | [6 empty] | Refer to Misc. for function of F21TK414_CCONC tag | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser | AI21143C_C
F21-CALC-0003 | - | F21PP472 Run Time | min | 1 | F21PP472_RUN | min | F21PP472 Run Time |  | X |  |  |  | 'IF AI21143C_C > F21TK414_CTRGT then F21PP472_RUN = 0 OTHERWISE F21PP472_RUN = 60 * (5600/220) * (((F21TK414_CTRGT)-(F21TK414_CCONC))/F21TK415_CCONC) | Timer for F21-SEQ-0001. Refer Sequence document 2000-F21-LST-PR-10102 | 1 | [5 empty] | 2025-04-30 | KAN-1648 | F21PP472_RUN
|  |  |  | 2 | F21TK414_CTRGT | g/L | F21TK414 Carbon Target | X |  | 12.5 | 10 | 20 |  | If F21PP472_RUN is calculated to be ≤ 1 min, please treat this as a run time of 0 mins (i.e. pump to not run). | 1 | [5 empty] | 2025-04-30 | KAN-1645 | F21TK414_CTRGT
|  |  |  | 3 | F21TK414_CCONC | g/L | F21TK414 C Conc. | [6 empty] | Refer to Misc. for function of F21TK414_CCONC tag | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser | AI21143C_C
|  |  |  | 4 | F21TK415_CCONC | g/L | F21TK415 C Conc. | [6 empty] | Refer to Misc. for function of F21TK415_CCONC tag | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser | AI21144C_C
F21-CALC-0004 | - | F21PP473 Run Time | min | 1 | F21PP473_RUN | min | F21PP473 Run Time |  | X |  |  |  | 'IF AI21144C_C > F21TK415_CTRGT then F21PP473_RUN = 0 OTHERWISE F21PP473_RUN = 60 * (5600/220) * (((F21TK415_CTRGT)-(F21TK415_CCONC))/F21TK416_CCONC) | Timer for F21-SEQ-0001. Refer Sequence document 2000-F21-LST-PR-10102 | 1 | [5 empty] | 2025-04-30 | KAN-1648 | F21PP473_RUN
|  |  |  | 2 | F21TK415_CTRGT | g/L | F21TK415 Carbon Target | X |  | 12.5 | 10 | 20 |  | If F21PP473_RUN is calculated to be ≤ 1 min, please treat this as a run time of 0 mins (i.e. pump to not run). | 1 | [5 empty] | 2025-04-30 | KAN-1645 | F21TK415_CTRGT
|  |  |  | 3 | F21TK415_CCONC | g/L | F21TK415 C Conc. | [6 empty] | Refer to Misc. for function of F21TK415_CCONC tag | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser | AI21144C_C
|  |  |  | 4 | F21TK416_CCONC | g/L | F21TK416 C Conc. | [6 empty] | Refer to Misc. for function of F21TK416_CCONC tag | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser | AI21145C_C
F21-CALC-0005 | - | F21PP474 Run Time | min | 1 | F21PP474_RUN | min | F21PP474 Run Time |  | X |  |  |  | 'IF AI21145C_C > F21TK416_CTRGT then F21PP474_RUN = 0 OTHERWISE F21PP474_RUN = 60 * (5600/220) * (((F21TK416_CTRGT)-(F21TK416_CCONC))/F21TK417_CCONC) | Timer for F21-SEQ-0001. Refer Sequence document 2000-F21-LST-PR-10102 | 1 | [5 empty] | 2025-04-30 | KAN-1648 | F21PP474_RUN
|  |  |  | 2 | F21TK416_CTRGT | g/L | F21TK416 Carbon Target | X |  | 12.5 | 10 | 20 |  | If F21PP474_RUN is calculated to be ≤ 1 min, please treat this as a run time of 0 mins (i.e. pump to not run). | 1 | [5 empty] | 2025-04-30 | KAN-1645 | F21TK416_CTRGT
|  |  |  | 3 | F21TK416_CCONC | g/L | F21TK416 C Conc. | [6 empty] | Refer to Misc. for function of F21TK416_CCONC tag | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser | AI21145C_C
|  |  |  | 4 | F21TK417_CCONC | g/L | F21TK417 C Conc. | [6 empty] | Refer to Misc. for function of F21TK417_CCONC tag | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser | AI21146C_C
F21-CALC-0006 | - | F21PP475 Run Time | min | 1 | F21PP475_RUN | min | F21PP475 Run Time |  | X |  |  |  | 'IF AI21146C_C > F21TK417_CTRGT then F21PP475_RUN = 0 OTHERWISE F21PP475_RUN = 60 * (5600/220) * (((F21TK417_CTRGT)-(F21TK417_CCONC))/F21TK418_CCONC) | Timer for F21-SEQ-0001. Refer Sequence document 2000-F21-LST-PR-10102 | 1 | [5 empty] | 2025-04-30 | KAN-1648 | F21PP475_RUN
|  |  |  | 2 | F21TK417_CTRGT | g/L | F21TK417 Carbon Target | X |  | 12.5 | 10 | 20 |  | If F21PP475_RUN is calculated to be ≤ 1 min, please treat this as a run time of 0 mins (i.e. pump to not run). | 1 | [5 empty] | 2025-04-30 | KAN-1645 | F21TK417_CTRGT
|  |  |  | 3 | F21TK417_CCONC | g/L | F21TK417 C Conc. | [6 empty] | Refer to Misc. for function of F21TK417_CCONC tag | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser | AI21146C_C
|  |  |  | 4 | F21TK418_CCONC | g/L | F21TK418 C Conc. | [6 empty] | Refer to Misc. for function of F21TK418_CCONC tag | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser | AI21147C_C
6 | 6

## 12. Misc
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21)
2000-F21-LST-PR-10101
MISC. INSTRUMENTS AND CONTROLLERS
[11 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Description | Normal State | Alarm State | Hardwired (y/n) | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date | Comments - Don't put comments in C2 column | Change Date | Change Reference
HS21002 | 2000-F21-PID-PR-10001 | FIC21002 Cascade Input | Operator Selection |  | N |  |  |  | Selector for the input into the Flow Controller when operating in Cascade mode: Faceplate Selection: • F21-CALC-0001 OR • Cyanide Analyser Concentration (AIC21243) | A
HS21062 | 2000-F21-PID-PR-10001 | CIL4 Lime Addition Contr | Operator Selection |  | N |  |  |  | Selector for the master pH Controller for lime addition: Faceplate Selection: • CIL4 Tank 1 pH (AIC21062) OR • CIL4 Tank 2 pH (AIC21102) | A
HS21243 | 2000-F21-PID-PR-10003 | CIL4 CN Analyser Ctrl | Operator Selection |  | N |  |  |  | Selector for the input into the Cyanide Concentration Controller: Faceplate Selection: • CIL4 Tank 1 CN Concentration (AI21243) OR • CIL4 Tank 2 CN Concentration (AI21244) | A
F21TK413_CTRGT | - | F21TK413 Carbon Target | Operator Selection |  | N |  |  |  | Part of F21-CALC-0002. Operator entered setpoint value. Graphically, please show this tag in close proximity to the CIL4 Leach Tanks. Please refer to Figure 1 for example of what client currently has implemented. | 0
F21TK414_CTRGT | - | F21TK414 Carbon Target | Operator Selection |  | N |  |  |  | Part of F21-CALC-0003. Operator entered setpoint value. Graphically, please show this tag in close proximity to the CIL4 Leach Tanks. Please refer to Figure 1 for example of what client currently has implemented. | 0
F21TK415_CTRGT | - | F21TK415 Carbon Target | Operator Selection |  | N |  |  |  | Part of F21-CALC-0004. Operator entered setpoint value. Graphically, please show this tag in close proximity to the CIL4 Leach Tanks. Please refer to Figure 1 for example of what client currently has implemented. | 0
F21TK416_CTRGT | - | F21TK416 Carbon Target | Operator Selection |  | N |  |  |  | Part of F21-CALC-0005. Operator entered setpoint value. Graphically, please show this tag in close proximity to the CIL4 Leach Tanks. Please refer to Figure 1 for example of what client currently has implemented. | 0
F21TK417_CTRGT | - | F21TK418 Carbon Target | Operator Selection |  | N |  |  |  | Part of F21-CALC-0006. Operator entered setpoint value. Graphically, please show this tag in close proximity to the CIL4 Leach Tanks. Please refer to Figure 1 for example of what client currently has implemented. | 0
F21TK413_CCONC | - | F21TK413 C Conc. | Operator Selection |  | N |  |  |  | F21TK413_CCONC is a selection between: - Manually entered value, of selectable range 0 - 20 g/L - Analyser output, tag name AI21142C_C | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser
F21TK414_CCONC | - | F21TK414 C Conc. | Operator Selection |  | N |  |  |  | F21TK414_CCONC is a selection between: - Manually entered value, of selectable range 0 - 20 g/L - Analyser output, tag name AI21143C_C | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser
F21TK415_CCONC | - | F21TK415 C Conc. | Operator Selection |  | N |  |  |  | F21TK415_CCONC is a selection between: - Manually entered value, of selectable range 0 - 20 g/L - Analyser output, tag name AI21144C_C | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser
F21TK416_CCONC | - | F21TK416 C Conc. | Operator Selection |  | N |  |  |  | F21TK416_CCONC is a selection between: - Manually entered value, of selectable range 0 - 20 g/L - Analyser output, tag name AI21145C_C | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser
F21TK417_CCONC | - | F21TK417 C Conc. | Operator Selection |  | N |  |  |  | F21TK417_CCONC is a selection between: - Manually entered value, of selectable range 0 - 20 g/L - Analyser output, tag name AI21146C_C | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser
F21TK418_CCONC | - | F21TK418 C Conc. | Operator Selection |  | N |  |  |  | F21TK418_CCONC is a selection between: - Manually entered value, of selectable range 0 - 20 g/L - Analyser output, tag name AI21147C_C | 1 | [5 empty] | 2025-05-20 | New tag created, that allows selection of manually entered value or measured value via analyser
14

## 13. Alarm Database
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FLOTATION TAILINGS CIL4 (AREA F21)
2000-F21-LST-PR-10101
ALARM DATABASE
[14 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Abbreviated Description (Faceplate) | Type | Alarm State | Alarm Value | Alarm Units | On Delay (sec) | Alarm Masking Condition | Impact | Urgency | Priority | Operator Response | Rev | OK | Date | OK | Date | Comments - Don't put comments in C2 column | Change Date | Change Reference
FIC21002 | 2000-F21-PID-PR-10001 | F21FD431 CN Addn | Analogue | A_Lo | 1.5 | m3/h | 5 | XV21001 is CLOSED OR (F72PP675 AND F72PP676 is NOT RUNNING) Enabale 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | 1 | [5 empty] | 2025-07-25 | KAN-1484 & KAN-2159
FIC21003 | 2000-F21-PID-PR-10001 | F21TK411 CN Addn | Analogue | A_Lo | 1 | m3/h | 5 | XV21001 is CLOSED OR (F72PP675 AND F72PP676 is NOT RUNNING) Enabale 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | 1 | [5 empty] | 2025-07-25 | KAN-1484 & KAN-2159
FIC21004 | 2000-F21-PID-PR-10001 | F21TK412 CN Addn | Analogue | A_Lo | 1 | m3/h | 5 | XV21001 is CLOSED OR (F72PP675 AND F72PP676 is NOT RUNNING) Enabale 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | 1 | [5 empty] | 2025-07-25 | KAN-1484 & KAN-2159
PIT21071 | 2000-F21-PID-PR-10001 | F21TK411 Lance 1 | Analogue | A_Lo | 360 | kPa(g) | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | 0
PIT21072 | 2000-F21-PID-PR-10001 | F21TK411 Lance 2 | Analogue | A_Lo | 360 | kPa(g) | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | 0
PIT21073 | 2000-F21-PID-PR-10001 | F21TK411 Lance 3 | Analogue | A_Lo | 360 | kPa(g) | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | 0
PIT21074 | 2000-F21-PID-PR-10001 | F21TK411 Lance 4 | Analogue | A_Lo | 360 | kPa(g) | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | 0
PI21054 | 2000-F21-PID-PR-10001 | F21PP478 Post Inject | Analogue | A_LL | 100 | kPa | 5 | F21PP478 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate oxygen injectors and recirc pump | 0
PI21054 | 2000-F21-PID-PR-10001 | F21PP478 Post Inject | Analogue | A_Hi | 500 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate oxygen injectors and recirc pump | 0
PI21054 | 2000-F21-PID-PR-10001 | F21PP478 Post Inject | Analogue | A_HH | 550 | kPa | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate oxygen injectors and recirc pump | C
PI21055 | 2000-F21-PID-PR-10001 | F21PP478 Pre Inject | Analogue | A_LL | 100 | kPa | 5 | F21PP478 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate oxygen injectors and recirc pump | 0
PI21055 | 2000-F21-PID-PR-10001 | F21PP478 Pre Inject | Analogue | A_Hi | 500 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate oxygen injectors and recirc pump | 0
PI21055 | 2000-F21-PID-PR-10001 | F21PP478 Pre Inject | Analogue | A_HH | 550 | kPa | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate oxygen injectors and recirc pump | C
PIT21032 | 2000-F21-PID-PR-10001 | F21TK411 Injector Header | Analogue | A_Lo | - | kPa | - | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen injectors and/or oxygen plant | C
PIT21032 | 2000-F21-PID-PR-10001 | F21TK411 Injector Header | Analogue | A_Hi | - | kPa | - | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen injectors and/or oxygen plant | C
FIT21033 | 2000-F21-PID-PR-10001 | F21TK411 Injector Header | Analogue | A_Lo | 100 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen injectors and/or oxygen plant | C
FIT21033 | 2000-F21-PID-PR-10001 | F21TK411 Injector Header | Analogue | A_Hi | 200 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen injectors and/or oxygen plant | C
PIT21111 | 2000-F21-PID-PR-10001 | F21TK412 Lance 1 | Analogue | A_Lo | 360 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | C
PIT21112 | 2000-F21-PID-PR-10001 | F21TK412 Lance 2 | Analogue | A_Lo | 360 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | C
PIT21113 | 2000-F21-PID-PR-10001 | F21TK412 Lance 3 | Analogue | A_Lo | 360 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | C
PIT21114 | 2000-F21-PID-PR-10001 | F21TK412 Lance 4 | Analogue | A_Lo | 360 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | C
PI21094 | 2000-F21-PID-PR-10001 | F21PP491 Post Inject | Analogue | A_LL | 100 | kPa | 5 | F21PP491 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate oxygen injectors and recirc pump | 0
PI21094 | 2000-F21-PID-PR-10001 | F21PP491 Post Inject | Analogue | A_Hi | 500 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate oxygen injectors and recirc pump | 0
PI21094 | 2000-F21-PID-PR-10001 | F21PP491 Post Inject | Analogue | A_HH | 550 | kPa | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate oxygen injectors and recirc pump | C
PI21095 | 2000-F21-PID-PR-10001 | F21PP491 Pre Inject | Analogue | A_LL | 100 | kPa | 5 | F21PP491 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate oxygen injectors and recirc pump | 0
PI21095 | 2000-F21-PID-PR-10001 | F21PP491 Pre Inject | Analogue | A_Hi | 500 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate oxygen injectors and recirc pump | 0
PI21095 | 2000-F21-PID-PR-10001 | F21PP491 Pre Inject | Analogue | A_HH | 550 | kPa | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate oxygen injectors and recirc pump | C
PIT21042 | 2000-F21-PID-PR-10001 | F21TK412 Injector Header | Analogue | A_Lo | - | kPa | - | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen injectors and/or oxygen plant | C
PIT21042 | 2000-F21-PID-PR-10001 | F21TK412 Injector Header | Analogue | A_Hi | - | kPa | - | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen injectors and/or oxygen plant | C
FIT21043 | 2000-F21-PID-PR-10001 | F21TK412 Injector Header | Analogue | A_Lo | 100 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen injectors and/or oxygen plant | C
FIT21043 | 2000-F21-PID-PR-10001 | F21TK412 Injector Header | Analogue | A_Hi | 200 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen injectors and/or oxygen plant | C
AI21061 | 2000-F21-PID-PR-10001 | F21TK411 DO | Analogue | A_Lo | 10 | ppm | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | A
AIC21062 | 2000-F21-PID-PR-10001 | F21TK411 pH | Analogue | A_Lo | 8.5 | ppm | 5 | - | Personnel1: First Aid Injury, Reversible health effects | Rapid (>5 to <15 minutes) | Low | Operator to ensure adequate addition of lime and cyanide into CIL4 circuit. Low pH conditions promote HCN formation | 1 | [5 empty] | 2025-07-25 | KAN-2159
AIC21062 | 2000-F21-PID-PR-10001 | F21TK411 pH | Analogue | A_LL | 8 | ppm | 5 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Operator to force lime addition control, or, cut cyanide addition momentarily to raise pH to safe level. Field personel to evacuate CIL4 top of tank area. | 1 | [5 empty] | 2025-07-25 | KAN-2159
AIT21211 | 2000-F21-PID-PR-10001 | CIL4 HCN Conc. 1 | Analogue | A_Hi | 4 | mg/m3 | 1 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Rapid (>5 to <15 minutes) |  | Operator to ensure adequate addition of lime and cyanide into CIL4 circuit. Low pH conditions promote HCN formation | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
AIT21211 | 2000-F21-PID-PR-10001 | CIL4 HCN Conc. 1 | Analogue | A_HH | 5 | mg/m3 | 1 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) |  | Operator to force lime addition control, or, cut cyanide addition momentarily to raise pH to safe level. Field personel to evacuate CIL4 top of tank area. | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
AI21101 | 2000-F21-PID-PR-10001 | F21TK412 DO | Analogue | A_Lo | 10 | ppm | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | A
AIC21102 | 2000-F21-PID-PR-10001 | F21TK412 pH | Analogue | A_Lo | 8.5 | ppm | 5 | - | Personnel1: First Aid Injury, Reversible health effects | Rapid (>5 to <15 minutes) | Low | Operator to ensure adequate addition of lime and cyanide into CIL4 circuit. Low pH conditions promote HCN formation | 1 | [5 empty] | 2025-07-25 | KAN-2159
AIC21102 | 2000-F21-PID-PR-10001 | F21TK412 pH | Analogue | A_LL | 8 | ppm | 5 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Operator to force lime addition control, or, cut cyanide addition momentarily to raise pH to safe level. Field personel to evacuate CIL4 top of tank area. | 1 | [5 empty] | 2025-07-25 | KAN-2159
FIC21005 | 2000-F21-PID-PR-10002 | F21TK413 CN Addn | Analogue | A_Lo | 1 | m3/h | 5 | XV21001 is CLOSED OR (F72PP675 AND F72PP676 is NOT RUNNING) Enabale 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate | 1 | [5 empty] | 2025-07-25 | KAN-1484 & KAN-2159
PIT21151 | 2000-F21-PID-PR-10002 | F21TK413 Lance 1 | Analogue | A_Lo | 360 | kPa(g) | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | 0
PIT21152 | 2000-F21-PID-PR-10002 | F21TK413 Lance 2 | Analogue | A_Lo | 360 | kPa(g) | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | 0
PIT21153 | 2000-F21-PID-PR-10002 | F21TK413 Lance 3 | Analogue | A_Lo | 360 | kPa(g) | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | 0
PIT21154 | 2000-F21-PID-PR-10002 | F21TK413 Lance 4 | Analogue | A_Lo | 360 | kPa(g) | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | 0
PIT21191 | 2000-F21-PID-PR-10002 | F21TK414 Lance 1 | Analogue | A_Lo | 360 | kPa(g) | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | 0
PIT21192 | 2000-F21-PID-PR-10002 | F21TK414 Lance 2 | Analogue | A_Lo | 360 | kPa(g) | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | 0
PIT21193 | 2000-F21-PID-PR-10002 | F21TK414 Lance 3 | Analogue | A_Lo | 360 | kPa(g) | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | 0
PIT21194 | 2000-F21-PID-PR-10002 | F21TK414 Lance 4 | Analogue | A_Lo | 360 | kPa(g) | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to investigate oxygen lance for wear and/or blockage | 0
AI21007 | 2000-F21-PID-PR-10001 | F21AN409 C Conc. | Analogue | A_Hi | - | g/L | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) |  | Possible loss of carbon event, operator to inspect CIL4 top of tank area | 0
AI21007 | 2000-F21-PID-PR-10001 | F21AN409 C Conc. | Analogue | A_HH | - | g/L | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) |  | Loss of carbon event | 0
AI21319 | 2000-F21-PID-PR-10005 | F21AN405 C Conc. | Analogue | A_Hi | 2 | g/L | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Possible loss of carbon event, operator to inspect CIL4 top of tank area | 0
AI21319 | 2000-F21-PID-PR-10005 | F21AN405 C Conc. | Analogue | A_HH | 5 | g/L | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Loss of carbon event, suggest plant feed to be stopped. | 0
AI21212 | 2000-F21-PID-PR-10002 | CIL4 HCN Conc. 2 | Analogue | A_Hi | 4 | mg/m3 | 1 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Rapid (>5 to <15 minutes) |  | Operator to ensure adequate addition of lime and cyanide into CIL4 circuit. Low pH conditions promote HCN formation | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
AI21212 | 2000-F21-PID-PR-10002 | CIL4 HCN Conc. 2 | Analogue | A_HH | 5 | mg/m3 | 1 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) |  | Operator to force lime addition control, or, cut cyanide addition momentarily to raise pH to safe level. Field personel to evacuate CIL4 top of tank area. | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
AI21213 | 2000-F21-PID-PR-10003 | CIL4 HCN Conc. 3 | Analogue | A_Hi | 4 | mg/m3 | 1 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Rapid (>5 to <15 minutes) |  | Operator to ensure adequate addition of lime and cyanide into CIL4 circuit. Low pH conditions promote HCN formation | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
AI21213 | 2000-F21-PID-PR-10003 | CIL4 HCN Conc. 3 | Analogue | A_HH | 5 | mg/m3 | 1 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) |  | Operator to force lime addition control, or, cut cyanide addition momentarily to raise pH to safe level. Field personel to evacuate CIL4 top of tank area. | 1 | [5 empty] | 2025-04-08 | TBC information confirmed
PI21348 | 2000-F72-PID-PR-10011 | F21TK411 Injct 1 | Analogue | A_Lo | 400 | kPa | 5 | F21PP478 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate oxygen injector and distribution. | 0
PI21348 | 2000-F72-PID-PR-10011 | F21TK411 Injct 1 | Analogue | A_Hi | 720 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate oxygen injector and distribution. | 1 | [5 empty] | 2025-04-09 | Design change - HAZID 4/04/2025
PI21348 | 2000-F72-PID-PR-10011 | F21TK411 Injct 1 | Analogue | A_HH | 750 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate oxygen injector and distribution. | 1 | [5 empty] | 2025-04-09 | Design change - HAZID 4/04/2025
PI21350 | 2000-F72-PID-PR-10011 | F21TK411 Injct 2 | Analogue | A_Lo | 400 | kPa | 5 | F21PP478 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate oxygen injector and distribution. | 0
PI21350 | 2000-F72-PID-PR-10011 | F21TK411 Injct 2 | Analogue | A_Hi | 720 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate oxygen injector and distribution. | 1 | [5 empty] | 2025-04-09 | Design change - HAZID 4/04/2025
PI21350 | 2000-F72-PID-PR-10011 | F21TK411 Injct 2 | Analogue | A_HH | 750 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate oxygen injector and distribution. | 1 | [5 empty] | 2025-04-09 | Design change - HAZID 4/04/2025
PI21357 | 2000-F72-PID-PR-10011 | F21TK412 Injct 1 | Analogue | A_Lo | 400 | kPa | 5 | F21PP491 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate oxygen injector and distribution. | 0
PI21357 | 2000-F72-PID-PR-10011 | F21TK412 Injct 1 | Analogue | A_Hi | 720 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate oxygen injector and distribution. | 1 | [5 empty] | 2025-04-09 | Design change - HAZID 4/04/2025
PI21357 | 2000-F72-PID-PR-10011 | F21TK412 Injct 1 | Analogue | A_HH | 750 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate oxygen injector and distribution. | 1 | [5 empty] | 2025-04-09 | Design change - HAZID 4/04/2025
PI21359 | 2000-F72-PID-PR-10011 | F21TK412 Injct 2 | Analogue | A_Lo | 400 | kPa | 5 | F21PP491 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate oxygen injector and distribution. | 0
PI21359 | 2000-F72-PID-PR-10011 | F21TK412 Injct 2 | Analogue | A_Hi | 720 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate oxygen injector and distribution. | 1 | [5 empty] | 2025-04-09 | Design change - HAZID 4/04/2025
PI21359 | 2000-F72-PID-PR-10011 | F21TK412 Injct 2 | Analogue | A_HH | 750 | kPa | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate oxygen injector and distribution. | 1 | [5 empty] | 2025-04-09 | Design change - HAZID 4/04/2025
PI21332 | 2000-F24-PID-PR-10016 | F21RA409 Press. | Analogue | A_Hi | 1300 | kPa | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate air receiver and compressed air distribution. | 1 | [5 empty] | 2025-09-30 | https://pastech-2955.atlassian.net/browse/PL-406
PI21332 | 2000-F24-PID-PR-10016 | F21RA409 Press. | Analogue | A_Lo | 900 | kPa | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate air receiver and compressed air distribution. | 1 | [5 empty] | 2025-09-30 | https://pastech-2955.atlassian.net/browse/PL-406
FIC21059 | 2000-F21-PID-PR-10001 | F21PP478 Flow | Analogue | A_Lo | 900 | m3/h | 5 | F21PP478 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate. | 1 | [5 empty] | 2025-07-25 | KAN-2159
FIC21059 | 2000-F21-PID-PR-10001 | F21PP478 Flow | Analogue | A_LL | 800 | m3/h | 5 | F21PP478 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate. | 1 | [5 empty] | 2025-07-25 | KAN-2159
FIC21099 | 2000-F21-PID-PR-10001 | F21PP491 Flow | Analogue | A_Lo | 900 | m3/h | 5 | F21PP491 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate. | 1 | [5 empty] | 2025-07-25 | KAN-2159
FIC21099 | 2000-F21-PID-PR-10001 | F21PP491 Flow | Analogue | A_LL | 800 | m3/h | 5 | F21PP491 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate. | 1 | [5 empty] | 2025-07-25 | KAN-2159
FIC21347 | 2000-F72-PID-PR-10011 | F21PP478 O2Ctrl1 | Analogue | A_Hi | 90 | m3/h | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate. | 1 | [5 empty] | 2025-07-25 | KAN-2159
FIC21347 | 2000-F72-PID-PR-10011 | F21PP478 O2Ctrl1 | Analogue | A_Lo | 50 | m3/h | 5 | F21PP478 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate. | 1 | [5 empty] | 2025-07-25 | KAN-2159
FIC21349 | 2000-F72-PID-PR-10011 | F21PP478 O2Ctrl2 | Analogue | A_Hi | 90 | m3/h | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate. | 1 | [5 empty] | 2025-07-25 | KAN-2159
FIC21349 | 2000-F72-PID-PR-10011 | F21PP478 O2Ctrl2 | Analogue | A_Lo | 50 | m3/h | 5 | F21PP478 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate. | 1 | [5 empty] | 2025-07-25 | KAN-2159
FIC21356 | 2000-F72-PID-PR-10011 | F21PP491 O2Ctrl1 | Analogue | A_Hi | 90 | m3/h | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate. | 1 | [5 empty] | 2025-07-25 | KAN-2159
FIC21356 | 2000-F72-PID-PR-10011 | F21PP491 O2Ctrl1 | Analogue | A_Lo | 50 | m3/h | 5 | F21PP491 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate. | 1 | [5 empty] | 2025-07-25 | KAN-2159
FIC21358 | 2000-F72-PID-PR-10011 | F21PP491 O2Ctrl2 | Analogue | A_Hi | 90 | m3/h | 5 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate. | 1 | [5 empty] | 2025-07-25 | KAN-2159
FIC21358 | 2000-F72-PID-PR-10011 | F21PP491 O2Ctrl2 | Analogue | A_Lo | 50 | m3/h | 5 | F21PP491 is NOT RUNNING Enable 10s delay mask for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate. | 1 | [5 empty] | 2025-07-25 | KAN-2159
TI21023A | - | F21AG411 U RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21023A | - | F21AG411 U RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21023B | - | F21AG411 V RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21023B | - | F21AG411 V RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21023C | - | F21AG411 W RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21023C | - | F21AG411 W RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21023D | - | F21AG411 DE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21023D | - | F21AG411 DE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21023E | - | F21AG411 NDE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21023E | - | F21AG411 NDE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21024A | - | F21AG412 U RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21024A | - | F21AG412 U RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21024B | - | F21AG412 V RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21024B | - | F21AG412 V RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21024C | - | F21AG412 W RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21024C | - | F21AG412 W RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21024D | - | F21AG412 DE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21024D | - | F21AG412 DE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21024E | - | F21AG412 NDE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21024E | - | F21AG412 NDE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21025A | - | F21AG413 U RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21025A | - | F21AG413 U RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21025B | - | F21AG413 V RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21025B | - | F21AG413 V RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21025C | - | F21AG413 W RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21025C | - | F21AG413 W RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21025D | - | F21AG413 DE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21025D | - | F21AG413 DE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21025E | - | F21AG413 NDE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21025E | - | F21AG413 NDE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21026A | - | F21AG414 U RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21026A | - | F21AG414 U RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21026B | - | F21AG414 V RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21026B | - | F21AG414 V RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21026C | - | F21AG414 W RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21026C | - | F21AG414 W RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21026D | - | F21AG414 DE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21026D | - | F21AG414 DE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21026E | - | F21AG414 NDE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21026E | - | F21AG414 NDE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21027A | - | F21AG415 U RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21027A | - | F21AG415 U RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21027B | - | F21AG415 V RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21027B | - | F21AG415 V RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21027C | - | F21AG415 W RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21027C | - | F21AG415 W RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21027D | - | F21AG415 DE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21027D | - | F21AG415 DE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21027E | - | F21AG415 NDE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21027E | - | F21AG415 NDE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21028A | - | F21AG416 U RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21028A | - | F21AG416 U RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21028B | - | F21AG416 V RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21028B | - | F21AG416 V RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21028C | - | F21AG416 W RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21028C | - | F21AG416 W RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21028D | - | F21AG416 DE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21028D | - | F21AG416 DE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21028E | - | F21AG416 NDE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21028E | - | F21AG416 NDE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21029A | - | F21AG417 U RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21029A | - | F21AG417 U RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21029B | - | F21AG417 V RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21029B | - | F21AG417 V RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21029C | - | F21AG417 W RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21029C | - | F21AG417 W RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21029D | - | F21AG417 DE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21029D | - | F21AG417 DE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21029E | - | F21AG417 NDE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21029E | - | F21AG417 NDE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21030A | - | F21AG418 U RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21030A | - | F21AG418 U RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21030B | - | F21AG418 V RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21030B | - | F21AG418 V RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21030C | - | F21AG418 W RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21030C | - | F21AG418 W RTD | Analogue | A_HH | 150 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21030D | - | F21AG418 DE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21030D | - | F21AG418 DE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21030E | - | F21AG418 NDE RTD | Analogue | A_Hi | 100 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21030E | - | F21AG418 NDE RTD | Analogue | A_HH | 110 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. Consider bypassing associated CIL4 Tank. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21031A | - | F21PP478 U RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21031A | - | F21PP478 U RTD | Analogue | A_HH | 180 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21031B | - | F21PP478 V RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21031B | - | F21PP478 V RTD | Analogue | A_HH | 180 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21031C | - | F21PP478 W RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21031C | - | F21PP478 W RTD | Analogue | A_HH | 180 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21031D | - | F21PP478 DE RTD | Analogue | A_Hi | 95 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21031D | - | F21PP478 DE RTD | Analogue | A_HH | 105 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21031E | - | F21PP478 NDE RTD | Analogue | A_Hi | 95 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21031E | - | F21PP478 NDE RTD | Analogue | A_HH | 105 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21034A | - | F21PP491 U RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21034A | - | F21PP491 U RTD | Analogue | A_HH | 180 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21034B | - | F21PP491 V RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21034B | - | F21PP491 V RTD | Analogue | A_HH | 180 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21034C | - | F21PP491 W RTD | Analogue | A_Hi | 140 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21034C | - | F21PP491 W RTD | Analogue | A_HH | 180 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21034D | - | F21PP491 DE RTD | Analogue | A_Hi | 95 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21034D | - | F21PP491 DE RTD | Analogue | A_HH | 105 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21034E | - | F21PP491 NDE RTD | Analogue | A_Hi | 95 | °C | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
TI21034E | - | F21PP491 NDE RTD | Analogue | A_HH | 105 | °C | 3 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Maintenace to investigate. | 0 | [5 empty] | 2026-01-31 | TE changed to TI. Document change only.
FAL21321 | 2000-F24-PID-PR-10003 | F21PP478 GW Low | Digital | A_Lo | - | - | 3 | F21-SV-21320 is INACTIVE | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
FAL21325 | 2000-F24-PID-PR-10003 | F21PP491 GW Low | Digital | A_Lo | - | - | 3 | F21-SV-21324 is INACTIVE | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
LAH21131 | 2000-F21-PID-PR-10001 | F21PS414 High Lvl | Digital | A_Hi | - | - | 3 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Operator to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
XA21006 | 2000-F21-PID-PR-10001 | F21AN409 General Fault | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to inspect Carbon Detection Analyser control panel for fault code | A
AAHH21211 | 2000-F21-PID-PR-10001 | CIL4 HCN Gas HH1 | Digital | Alarm | - | - | 0 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Operator to force lime addition control, or, cut cyanide addition momentarily to raise pH to safe level. Field personel to evacuate CIL4 top of tank area. | 1 | [5 empty] | 2025-04-30 | KAN-1598
LAH21221 | 2000-F21-PID-PR-10002 | F21PS415 High Lvl | Digital | Alarm | - | - | 3 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Operator to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
LAH21222 | 2000-F21-PID-PR-10002 | F21PS416 High Lvl | Digital | Alarm | - | - | 3 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Operator to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
XA21140 | 2000-F21-PID-PR-10002 | F21AN412 General Fault | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging | Operator to inspect Carbon Scout control panel for fault code | A
AAHH21212 | 2000-F21-PID-PR-10002 | CIL4 HCN Gas HH2 | Digital | Alarm | - | - | 0 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Operator to force lime addition control, or, cut cyanide addition momentarily to raise pH to safe level. Field personel to evacuate CIL4 top of tank area. | 1 | [5 empty] | 2025-04-30 | KAN-1598
LAH21291 | 2000-F21-PID-PR-10003 | F21PS417 High Lvl | Digital | Alarm | - | - | 3 | - | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Operator to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
XA21255 | 2000-F21-PID-PR-10003 | F21CA411 General Fault | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging | Operator to inspect Cyanide Analyser control panel for fault code | 1 | [5 empty] | 2025-04-30 | KAN-1598
XA21256 | 2000-F21-PID-PR-10003 | F21CA412 General Fault | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging | Operator to inspect Cyanide Analyser control panel for fault code | 1 | [5 empty] | 2025-04-30 | KAN-1598
AAHH21213 | 2000-F21-PID-PR-10003 | CIL4 HCN Gas HH3 | Digital | Alarm | - | - | 0 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Operator to force lime addition control, or, cut cyanide addition momentarily to raise pH to safe level. Field personel to evacuate CIL4 top of tank area. | 1 | [5 empty] | 2025-04-30 | KAN-1598
XA21318 | 2000-F21-PID-PR-10005 | F21AN405 General Fault | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Not Urgent (>30 minutes) | Logging | Operator to inspect Carbon Detection Analyser control panel for fault code | 1 | [5 empty] | 2025-04-30 | KAN-1598
ZI21310A | 2000-F21-PID-PR-10005 | F21SA431 Park 1 | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | No action required | 1 | [5 empty] | 2025-07-25 | KAN-2159
ZI21310B | 2000-F21-PID-PR-10005 | F21SA431 Ramp Down 1 | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | No action required | 1 | [5 empty] | 2025-07-25 | KAN-2159
ZA21310C | 2000-F21-PID-PR-10005 | F21SA431 Overtravel 1 | Digital | Alarm | - | - | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to inspect sampler | 1 | [5 empty] | 2025-04-30 | KAN-1598
ZI21313A | 2000-F21-PID-PR-10005 | F21SA431 Park 2 | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | No action required | 1 | [5 empty] | 2025-07-25 | KAN-2159
ZI21313B | 2000-F21-PID-PR-10005 | F21SA431 Ramp Down 2 | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | No action required | 1 | [5 empty] | 2025-07-25 | KAN-2159
ZA21313C | 2000-F21-PID-PR-10005 | F21SA431 Overtravel 2 | Digital | Alarm | - | - | 3 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to inspect sampler | 1 | [5 empty] | 2025-04-30 | KAN-1598
XA21309A | 2000-F21-PID-PR-10005 | F21SA431 General Fault | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to inspect sampler | 0
ZI21304 | 2000-F21-PID-PR-10005 | F21SA432 Park | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | No action required | 1 | [5 empty] | 2025-07-25 | KAN-2159
XA21303A | 2000-F21-PID-PR-10005 | F21SA432 General Fault | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to inspect sampler | 0
ZI21307 | 2000-F21-PID-PR-10005 | F21SA433 Park | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | No action required | 1 | [5 empty] | 2025-07-25 | KAN-2159
XA21306A | 2000-F21-PID-PR-10005 | F21SA433 General Fault | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | Operator to inspect sampler | 0
F21DCS411_PS1 | - | F21DCS441 PS1 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21DCS411_PS2 | - | F21DCS441 PS1 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW006_PS | - | F21SW006 24VDC Trip | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW006_AF | - | F21SW006 Arc Flash | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW006_OP | - | F21SW006 Breaker Open | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | No response required. | 1 | [5 empty] | 2025-07-25 | KAN-2159
F21SW006_CL | - | F21SW006 Breaker Closed | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | No response required. | 1 | [5 empty] | 2025-07-25 | KAN-2159
F21SW006_TRP | - | F21SW006 Breaker Trip | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW006_SD | - | F21SW006 Surge Diverter | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SR001_ESTP | - | F21SR001 Emergency Shut | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW006_PS1 | - | F21SW006 PS1 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW006_PS2 | - | F21SW006 PS2 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW007_PS | - | F21SW007 24VDC Trip | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW007_AF | - | F21SW007 Arc Flash | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW007_OP | - | F21SW007 Breaker Open | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | No response required. | 1 | [5 empty] | 2025-07-25 | KAN-2159
F21SW007_CL | - | F21SW007 Breaker Closed | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | No response required. | 1 | [5 empty] | 2025-07-25 | KAN-2159
F21SW007_TRP | - | F21SW007 Breaker Trip | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW007_SD | - | F21SW007 Surge Diverter | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW007_PS1 | - | F21SW007 PS1 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW007_PS2 | - | F21SW007 PS2 24VDC | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21FIP001_ALM | - | F21FIP001 Alarm | Digital | Alarm | - | - | 0 | - | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm. Follow site specific Fire Emergency Plan. | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21FIP001_ISL | - | F21FIP001 Isolated | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) | No Alarm | Fire alarm. Follow site specific Fire Emergency Plan. | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21FIP001_FLT | - | F21FIP001 Fault | Digital | Alarm | - | - | 0 | - | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm fault. Follow site specific Fire Emergency Plan. | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW106_SD | F21SW106_SD | F21SW106 Surge Diverter | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped |  | Switchroom tripped. Electrician to investigate | 0
F21SW106Q1_CL | F21SW106Q1_CL | F21SW106 Main CB Closed | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | Switchroom tripped. Electrician to investigate | 0
F21SW106Q1_TRP | F21SW106Q1_TRP | F21SW106 Main CB Trip | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | SWB tripped. Electrician to investigate/ to Confirm manual generator changeover in operation | 0
F21SW006Q2_OP | - | F21SW006 GEN CB OPEN | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-07-25 | KAN-2159
F21SW006Q2_CL | - | F21SW006 GEN CB CLOSED | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-07-25 | KAN-2159
F21SW006Q2_TRP | - | F21SW006 GEN CB TRIP | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) | No Alarm | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21SW107_SD | F21SW107_SD | F21SW107 Surge Diverter | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped |  | Switchroom tripped. Electrician to investigate | 0
F21SW107Q1_CL | F21SW107Q1_CL | F21SW107 Main CB Closed | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | Switchroom tripped. Electrician to investigate | 0
F21SW107Q1_TRP | F21SW107Q1_TRP | F21SW107 Main CB Trip | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) |  | SWB tripped. Electrician to investigate/ to Confirm manual generator changeover in operation | 0
F21SW007Q2_OP | - | F21SW007 GEN CB OPEN | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-07-25 | KAN-2159
F21SW007Q2_CL | - | F21SW007 GEN CB CLOSED | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) |  | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-07-25 | KAN-2159
F21SW007Q2_TRP | - | F21SW007 GEN CB TRIP | Digital | Alarm | - | - | 0 | - | None | Not Urgent (>30 minutes) | No Alarm | Switchroom tripped. Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
LSHH21008 | - | F21GE006 Fuel Level | Digital | Alarm | - | - | 0 | - | Environmental2: Minor on-site environmental impact, reportable to regulators. | Immediate (<5 minutes) |  | Operator to cease re-fuelling immediately, likely diesel spillage. Operator to investigat in-field and respond in-line with company combustible material spillage protocol. | C
LAH21008 | - | F21GE006 Fuel Level | Digital | Alarm | - | - | 0 | - | None | Rapid (>5 to <15 minutes) | No Alarm | High fuel level in generator fuel reservoir. Operator to radio local field operator to cease re-fuelling. | 1 | [5 empty] | 2025-04-30 | KAN-1598
LAL21008 | - | F21GE006 Fuel Level | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operational risk for backup power. Operator to organise re-fuelling. | 1 | [5 empty] | 2025-04-30 | KAN-1598
LSHH21009 | - | F21GE007 Fuel Level | Digital | Alarm | - | - | 0 | - | Environmental2: Minor on-site environmental impact, reportable to regulators. | Immediate (<5 minutes) |  | Operator to cease re-fuelling immediately, likely diesel spillage. Operator to investigat in-field and respond in-line with company combustible material spillage protocol. | C
LAH21009 | - | F21GE007 Fuel Level | Digital | Alarm | - | - | 0 | - | None | Rapid (>5 to <15 minutes) | No Alarm | High fuel level in generator fuel reservoir. Operator to radio local field operator to cease re-fuelling. | 1 | [5 empty] | 2025-04-30 | KAN-1598
LAL21009 | - | F21GE007 Fuel Level | Digital | Alarm | - | - | 0 | - | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operational risk for backup power. Operator to organise re-fuelling. | 1 | [5 empty] | 2025-04-30 | KAN-1598
UT21016 | - | F21SR001 SW Temp | Analogue | A_Hi | 30 | °C | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate air conditioning and cause of high room temperatures. | C
UT21017 | - | F21SR001 SW Temp | Analogue | A_Hi | 30 | °C | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate air conditioning and cause of high room temperatures. | C
UT21018 | - | F21SR001 SW Temp | Analogue | A_Hi | 30 | °C | 5 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate air conditioning and cause of high room temperatures. | C
F21RIO001_PS1 | - | F21-RIO-001 PS1 24VDC HEALTHY | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21RIO001_PS2 | - | F21-RIO-001 PS2 24VDC HEALTHY | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21RIO002_PS1 | - | F21-RIO-002 PS1 24VDC HEALTHY | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21RIO002_PS2 | - | F21-RIO-002 PS2 24VDC HEALTHY | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21RIO003_PS1 | - | F21-RIO-003 PS1 24VDC HEALTHY | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
F21RIO003_PS2 | - | F21-RIO-003 PS2 24VDC HEALTHY | Digital | Alarm | - | - | 0 | - | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 1 | [5 empty] | 2025-04-30 | KAN-1598
ZAC21019 | - | F21TR006 415VMCC Door CL | Digital | Alarm | - | - | 0 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Restricted work area potential safety breach/issue | 1 | [5 empty] | 2025-04-30 | KAN-1598
ZAC21020 | - | F21TR007 415VMCC Door CL | Digital | Alarm | - | - | 0 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Restricted work area potential safety breach/issue | 1 | [5 empty] | 2025-04-30 | KAN-1598
FAH21035 | 2000-F24-PID-PR-10028 | F21SE412 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH21036 | 2000-F24-PID-PR-10028 | F21SE413 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH21037 | 2000-F24-PID-PR-10028 | F21SE414 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH21038 | 2000-F24-PID-PR-10028 | F21SE502 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH21039 | 2000-F24-PID-PR-10028 | F21SE503 Alarm | Digital | Alarm | - | - | 30 | - | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 | [5 empty] | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
F21TR006_WTH | - | F21TR006 Temp Hi | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrican to investigate high transformer winding temperature alarm | 1 | [5 empty] | 2025-08-19 | CR-034
F21TR007_WTH | - | F21TR007 Temp Hi | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrican to investigate high transformer winding temperature alarm | 1 | [5 empty] | 2025-08-19 | CR-034
F21GE006CBTRP | - | F21-GE-006 GEN CB TRP | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to manually change over generator | 1
F21GE007CBTRP | - | F21-GE-007 GEN CB TRP | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to manually change over generator | 1