## Revisions
PROCESS CONTROL TABLES
REVISION HISTORY
KCGM GROWTH PROJECT
2000-F24-LST-PR-10001
NORTHERN STAR RESOURCES LIMITED
Revision | Document Changes | Date
A for Sequence Flowchart Review Only | - Vendor data TBC highlighted or red-text | 2023-12-12
- Does not include the remainder of the Process Control Tables
B for Internal Review | - Vendor data TBC highlighted or red-text | 2024-04-05
C for Client Review | - Vendor data TBC highlighted or red-text | 2024-05-20
0 for Design | - Vendor data TBC highlighted or red-text | 2024-11-13
- Updated tag name/sources
1 Re-Issued for Design | - General updates highlighted | 2025-02-13
- Compressor input and control updated
- Fire water system updated
2 Post software FAT update | - Updated with post-software FAT punch items (Jira) | 2025-11-18
| - Updated with change requests (internal document) | 2025-11-18
- Changed transitions / steps are highlighted orange
2RL1 As Commissioned | -SAT testing checked on document | 2026-08-05

## 1. Analogue Input
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - AIR & WATER SERVICES (F24)
2000-F24-LST-PR-10001
ANALOGUE INSTRUMENTS (AI)
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [11 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Controller (Y/N) | Comments | Rev | OK | Date | OK | Date | C1 Comments
|  |  |  | PIT24484 | PI24484 | 2000-F24-PID-PR-10007 | Plant Air Receiver Pressure Indicating Transmitter | F24RA401 Disch Pressure | 1 | 0 | 1000 | kPa | [14 empty] | 600 | 5 | 980 | 5 |  |  |  | N | A_Hi = Warning A_Lo = Warning Normal operating = 9.8 bar Maximum operating pressure = 10 bar Minimum system outlet pressure = 6 bar Nominal values and alarm setpoints to be confirmed during commissioning | 3 | [5 empty] | 2025-09-10 | KAN-2443 : removed masking
|  |  |  | PT24442 | PI24442 | 2000-F24-PID-PR-10002 | F24-PW-406/407 Raw Water Pumps Discharge Pressure Indicating Transmitter | F24PW406/407 Discharge | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - | 150 | 5 | 400 | 5 | 600 | 5 | 750 | 5 | Duty F24-PW-406/407 NOT RUNNING Enable 10s delay on Pump Start-up | N | PE8 Maximum Pressure = 700kPa (2000-F00-DSH-PP-PE8) - pressure drop. Discharge Pressure = 60m TDH = 588 kPa (Design) A_HH = Trip F24-PW-406/407 A_Hi = Warning A_Lo = Operator to investigate and utilise standby pump if issue not rectified. A_LL = Trip F24-PW-406/407 Nominal values and alarm setpoints to be confirmed during commissioning | 2
|  |  |  | PT24451 | PI24451 | 2000-F24-PID-PR-10003 | LP Gland Seal Water Pumps Discharge Pressure Indicating Transmitter | F24PW408/409 Discharge | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 570 | 5 | 650 | 5 | 670 | 5 | Duty F24-PW-408/409 NOT RUNNING Enable 10s delay on Pump Start-up | N | PE8 / SS1 Maximum Pressure = 700kPa (2000-F00-DSH-PP-PE8/SS1) Largest pressures required at manifold = 570kPa. A_HH = Trip F24-PW-408/409 A_Hi = Warning (Pressure Regulating Valve possibly not working) A_Lo = Warning (not getting adequate seal pressure for downstream Pumps) Nominal values and alarm setpoints to be confirmed during commissioning | 2
|  |  |  | PT24461 | PI24461 | 2000-F24-PID-PR-10004 | HP Gland Seal Water Pumps Discharge Pressure Indicating Transmitter | F24PW419/420 Discharge | 1 | 0 | 1500 | kPa | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 1040 | 5 | 1340 | 5 | 1360 | 5 | Duty F24-PW-419/420 NOT RUNNING Enable 10s delay on Pump Start-up | N | PE20 / SS2 Maximum Pressure = 1400kPa (2000-F00-DSH-PP-PE20/SS2) Largest pressure required at manifold = 1090kPa. Pump Design Duty Point: 51m3/h @ 139m TDH. A_HH = Trip F24-PW-419/420 A_Hi = Warning (Pressure Regulating Valve possibly not working) A_Lo = Operator to invesitgate issue and swap pump if alarm not cleared Nominal values and alarm setpoints to be confirmed during commissioning | 2 |  |  |  |  | MOC-707 new alarm setpoints
|  |  |  | PIT24509 | PI24509 | 2000-F24-PID-PR-10017 | F24-PW-451/452 Raw Water Feed Booster Pump 1 and 2 Suction Pressure Indicating Transmitter | F24PW451/452 Suction | 1 | 0 | 500 | kPa | [14 empty] | 20 | 5 |  |  |  |  | Duty F24-PW-451/452 NOT RUNNING |  | Installed on common suction manifold of Raw Water Feed Booster Pump 1 & 2, to aid in detecting cavitation. Sulzer Pump Curve @ duty point (990rpm): NPSHr = 2m = 20 kPa A_Lo = Trip F24-PW-451/452 DRA Dam 3 Saline Water Pumps designed for 50kPa(g) discharge pressure | 2
|  |  |  | PT24505 | PI24505 | 2000-F24-PID-PR-10017 | Raw Water Feed Booster Pumps Discharge Pressure Indicating Transmitter | F24PW451/452 Discharge | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 190 | 5 | 240 | 5 | 260 | 5 | Duty F24-PW-451/452 NOT RUNNING Enable 10s delay on Pump Start-up | N | Piping PE8 / SS1 Maximum Pressure = 700kPa (2000-F00-DSH-PP-PE8/SS1) Pump Discharge Pressure = 22.7m TDH = 222 kPa A_HH = Trip F24-PW-451/452 A_Hi = Warning A_Lo = Warning Nominal values and alarm setpoints to be confirmed during commissioning | 2
|  |  |  | FIT24506 | FI24506 | 2000-F24-PID-PR-10017 | Raw Water Feed Booster Pumps Discharge Flow Indicating Transmitter | F24PW451/452 Disch Flow | 1 | 0 | 750 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | 250 | 5 | 450 | 5 | 580 | 5 |  |  | Duty F24-PW-451/452 NOT RUNNING Enable 10s delay on Pump Start-up | N | Design = 563 m3/h @ 22.7m TDH. A_Hi = Warning A_Lo = Warning A_LL = Trip duty pump Nominal values and alarm setpoints to be confirmed during commissioning | 2 | [5 empty] | 2025-08-07 | KAN-2253
|  |  |  | PT28452 | PI28452 | 2000-F24-PID-PR-10027 | F28-RA-408 UFG 2/3 Air Receiver Outlet Pressure Indicating Transmitter | F28RA408 Disch Pressure | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 600 | 5 | 980 | 5 |  |  |  | N | A_Hi = Warning A_Lo = Warning Normal operating = 9.8 bar Maximum operating pressure = 10 bar Minimum system outlet pressure = 6 bar Nominal values and alarm setpoints to be confirmed during commissioning | 3 | [5 empty] | 2025-09-10 | KAN-2443 : removed masking
|  |  |  | PT24637 | PI24637 | 2000-F24-PID-PR-10013 | F24-RA-403 Process Water/Reagents/Trash Screens Air Receiver Outlet Pressure Indicating Transmitter | F24RA403 Disch Pressure | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 600 | 5 | 980 | 5 |  |  |  | N | A_Hi = Warning A_Lo = Warning Normal operating = 9.8 bar Maximum operating pressure = 10 bar Minimum system outlet pressure = 6 bar Nominal values and alarm setpoints to be confirmed during commissioning | 3 | [5 empty] | 2025-09-10 | KAN-2443 : removed masking
|  |  |  | PIT13456 | PI13456 | 2000-F24-PID-PR-10011 | F13-RA-404 Mill Air Receiver Outlet Pressure Indicating Transmitter | F13RA404 Disch Pressure | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 600 | 5 | 980 | 5 |  |  |  | N | A_Hi = Warning A_Lo = Warning Normal operating = 9.8 bar Maximum operating pressure = 10 bar Minimum system outlet pressure = 6 bar Nominal values and alarm setpoints to be confirmed during commissioning | 3 | [5 empty] | 2025-09-10 | KAN-2443 : removed masking
|  |  |  | PIT13457 | PI13457 | 2000-F24-PID-PR-10011 | F13-RA-405 Classification Air Receiver Outlet Pressure Indicating Transmitter | F13RA405 Disch Pressure | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 600 | 5 | 980 | 5 |  |  |  | N | A_Hi = Warning A_Lo = Warning Normal operating = 9.8 bar Maximum operating pressure = 10 bar Minimum system outlet pressure = 6 bar Nominal values and alarm setpoints to be confirmed during commissioning | 3 | [5 empty] | 2025-09-10 | KAN-2443 : removed masking
|  |  |  | PT13458 | PI13458 | 2000-F24-PID-PR-10012 | F13-RA-406 Recycle Crushing/COS Vault Air Receiver Outlet Pressure Indicating Transmitter | F13RA406 Disch Pressure | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 600 | 5 | 980 | 5 |  |  |  | N | A_Hi = Warning A_Lo = Warning Normal operating = 9.8 bar Maximum operating pressure = 10 bar Minimum system outlet pressure = 6 bar Nominal values and alarm setpoints to be confirmed during commissioning | 3 | [5 empty] | 2025-09-10 | KAN-2443 : removed masking
|  |  |  | PIT24457 | PI24457 | 2000-F24-PID-PR-10006 | F24-PW-453 Scheme Water Booster Pump Suction Pressure Transmitter | F24PW453 Suction Press | 1 | 0 | 500 | kPa | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 37.278 | 5 |  |  |  |  | F24-PW-453 NOT RUNNING Enable 10s delay on Pump Start-up |  | A_Lo = Warning. 3.8m NPSHr. F24-PW-453 Scheme Water Booster Pump - Sulzer Pump Performance Curve Nominal values and alarm setpoints to be confirmed during commissioning | 2
|  |  |  | PT24458 | PI24458 | 2000-F24-PID-PR-10006 | F24-PW-453 Scheme Water Booster Pump Discharge Pressure Transmitter | F24PW453 Disch Pressure | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 100 | 5 | 650 | 5 | 700 | 5 | F24-PW-453 NOT RUNNING Enable 10s delay on Pump Start-up | N | Line Maximum Pressure = 14 bar Discharge Pressure = 35m TDH = 343 kPa A_HH = Trip F24-PW-453 A_Hi = Warning A_Lo = Warning F24-PW-453 Scheme Water Booster Pump - Sulzer Pump Performance Curve Nominal values and alarm setpoints to be confirmed during commissioning | 2 |  |  |  |  | MOC to change Hi and HH setpoints | 2025-05-26 | A_Lo alarm added as per HAZOP Causes: F24-09.3.1
|  |  |  | FIT24459 | FI24459 | 2000-F24-PID-PR-10006 |  | F24PW453 Disch Flow | 1 | 0 | 100 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 5 | 2 | 5 |  |  |  |  | F24-PW-453 NOT RUNNING Enable 10s delay on Pump Start-up |  |  | 2 | [5 empty] | 2025-07-07 | Updated as per HAZOP Causes F24-09.9.1
|  |  |  | PT24460 | PI24460 | 2000-F24-PID-PR-10020 | F24-PW-410 Raw Water Booster Pump Discharge Pressure Transmitter | F24PW410 Disch Pressure | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 100 | 5 | 200 | 5 | 250 | 5 | F24-PW-410 NOT RUNNING Enable 10s delay on Pump Start-up | N | Line Maximum Pressure = 14 bar Pump Design Duty Point: 220m3/h @ 15m TDH. A_HH = Trip F24-PW-410 A_Hi = Warning A_Lo = Warning Nominal values and alarm setpoints to be confirmed during commissioning | 2
|  |  |  | PIT72489 | PI72489 | 2000-F24-PID-PR-10016 | F72-RA-410 CIL4 Reagents Air Receiver | F72RA410 Disch Pressure | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 600 | 5 | 980 | 5 |  |  |  | N | A_Hi = Warning A_Lo = Warning Normal operating = 9.8 bar Maximum operating pressure = 10 bar Minimum system outlet pressure = 6 bar Nominal values and alarm setpoints to be confirmed during commissioning | 3 | [5 empty] | 2025-09-10 | KAN-2443 : removed masking
|  |  |  | PT75428 | PI75428 | 2000-F24-PID-PR-10016 | F24-PW-403/404/405 Saline Water Pump 1/2/3 Discharge Pressure Indicating Transmitter | F24PW403/4/5 Discharge | 1 | 0 | 1000 | kPa | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 300 | 5 | 400 | 5 | 440 | 5 | F24-PW-403/404/405 NOT RUNNING Enable 10s delay on Pump Start-up | N | PE8 Maximum Pressure = 700kPa (2000-F00-DSH-PP-PE8) Pump Design Duty Point: 1000m3/h @ 39.3m TDH. A_HH = Trip Duty F24-PW-403/404/405. A_Hi = Warning A_Lo = Warning Nominal values and alarm setpoints to be confirmed during commissioning | 2
|  |  |  | FIT75429 | FI75429 | 2000-F75-PID-PR-10002 | F24-PW-403/404/405 Saline Water Pump 1/2/3 Discharge Flow Indicating Transmitter | F24PW403/4/5 Disch Flow | 1 | 0 | 3500 | m3/h | - | - | - | - | - | - | - | - | - | - | - | - |  |  | 740 | 5 | 3200 | 5 |  |  | F24-PW-403/404/405 NOT RUNNING Enable 10s delay on Pump Start-up | N | Pump Design Duty Point: 1000m3/h @ 39.3m TDH. Designed for 3 duty if required during Tails Flushing. A_Hi = Warning A_Lo = Warning Nominal values and alarm setpoint to be confirmed during commissioning | 2 |  |  |  |  | SCR-26 changes low limit to 0 PH 03/02/2026
|  |  |  | TE75410A | TI75410A | 2000-F75-PID-PR-10002 | F24-PW-403 Saline Water Pump 1 Motor Phase U RTD | F24PW403 Motor U RTD | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 140 | 5 | 150 | 5 |  | N | A_HH = Trip F24-PW-403 A_Hi = Warning | 0
|  |  |  | TE75410B | TI75410B | 2000-F75-PID-PR-10002 | F24-PW-403 Saline Water Pump 1 Motor Phase V RTD | F24PW403 Motor V RTD | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 140 | 5 | 150 | 5 |  | N | A_HH = Trip F24-PW-403 A_Hi = Warning | 0
|  |  |  | TE75410C | TI75410C | 2000-F75-PID-PR-10002 | F24-PW-403 Saline Water Pump 1 Motor Phase W RTD | F24PW403 Motor W RTD | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 140 | 5 | 150 | 5 |  | N | A_HH = Trip F24-PW-403 A_Hi = Warning | 0
|  |  |  | TE75410D | TI75410D | 2000-F75-PID-PR-10002 | F24-PW-403 Saline Water Pump 1 Motor DE Bearing RTD | F24PW403 DE Bearing | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 95 | 5 | 100 | 5 |  | N | A_HH = Trip F24-PW-403 A_Hi = Warning | 0
|  |  |  | TE75410E | TI75410E | 2000-F75-PID-PR-10002 | F24-PW-403 Saline Water Pump 1 Motor NDE Bearing RTD | F24PW403 NDE Bearing | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 95 | 5 | 100 | 5 |  | N | A_HH = Trip F24-PW-403 A_Hi = Warning | 0
|  |  |  | TE75420A | TI75420A | 2000-F75-PID-PR-10002 | F24-PW-404 Saline Water Pump 1 Motor Phase U RTD | F24PW404 Motor U RTD | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 140 | 5 | 150 | 5 |  | N | A_HH = Trip F24-PW-404 A_Hi = Warning | 0
|  |  |  | TE75420B | TI75420B | 2000-F75-PID-PR-10002 | F24-PW-404 Saline Water Pump 1 Motor Phase V RTD | F24PW404 Motor V RTD | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 140 | 5 | 150 | 5 |  | N | A_HH = Trip F24-PW-404 A_Hi = Warning | 0
|  |  |  | TE75420C | TI75420C | 2000-F75-PID-PR-10002 | F24-PW-404 Saline Water Pump 1 Motor Phase W RTD | F24PW404 Motor W RTD | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 140 | 5 | 150 | 5 |  | N | A_HH = Trip F24-PW-404 A_Hi = Warning | 0
|  |  |  | TE75420D | TI75420D | 2000-F75-PID-PR-10002 | F24-PW-404 Saline Water Pump 1 Motor DE Bearing RTD | F24PW404 DE Bearing | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 95 | 5 | 100 | 5 |  | N | A_HH = Trip F24-PW-404 A_Hi = Warning | 0
|  |  |  | TE75420E | TI75420E | 2000-F75-PID-PR-10002 | F24-PW-404 Saline Water Pump 1 Motor NDE Bearing RTD | F24PW404 NDE Bearing | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 95 | 5 | 100 | 5 |  | N | A_HH = Trip F24-PW-404 A_Hi = Warning | 0
|  |  |  | TE75430A | TI75430A | 2000-F75-PID-PR-10002 | F24-PW-405 Saline Water Pump 1 Motor Phase U RTD | F24PW405 Motor U RTD | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 140 | 5 | 150 | 5 |  | N | A_HH = Trip F24-PW-405 A_Hi = Warning | 0
|  |  |  | TE75430B | TI75430B | 2000-F75-PID-PR-10002 | F24-PW-405 Saline Water Pump 1 Motor Phase V RTD | F24PW405 Motor V RTD | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 140 | 5 | 150 | 5 |  | N | A_HH = Trip F24-PW-405 A_Hi = Warning | 0
|  |  |  | TE75430C | TI75430C | 2000-F75-PID-PR-10002 | F24-PW-405 Saline Water Pump 1 Motor Phase W RTD | F24PW405 Motor W RTD | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 140 | 5 | 150 | 5 |  | N | A_HH = Trip F24-PW-405 A_Hi = Warning | 0
|  |  |  | TE75430D | TI75430D | 2000-F75-PID-PR-10002 | F24-PW-405 Saline Water Pump 1 Motor DE Bearing RTD | F24PW405 DE Bearing | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 95 | 5 | 100 | 5 |  | N | A_HH = Trip F24-PW-405 A_Hi = Warning | 0
|  |  |  | TE75430E | TI75430E | 2000-F75-PID-PR-10002 | F24-PW-405 Saline Water Pump 1 Motor NDE Bearing RTD | F24PW405 NDE Bearing | 1 | -5 | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  |  | 95 | 5 | 100 | 5 |  | N | A_HH = Trip F24-PW-405 A_Hi = Warning | 0
|  |  |  | TT24410 | TI24410 | 2000-F24-PID-PR-10001 | F24-PW-401 MILL WATER PUMP 1 GEARBOX TEMPERATURE TRANSMITTER | F24PW401 Gearbox Temp | 1 | 0 | 100 | °C | [16 empty] | 85 | 5 | 90 | 5 |  |  | A_HH = Trip F24-PW-401 A_Hi = Warning | 2 |  |  |  |  | VV 06/06/2026 - Field wiring Issue as per Manesh - fixed by changing from 2-wire to 4-wire | 28/10/22025 | New instrument added
|  |  |  | TT24420 | TI24420 | 2000-F24-PID-PR-10001 | F24-PW-402 MILL WATER PUMP 2 GEARBOX TEMPERATURE TRANSMITTER | F24PW402 Gearbox Temp | 1 | 0 | 100 | °C | [16 empty] | 85 | 5 | 90 | 5 |  |  | A_HH = Trip F24-PW-402 A_Hi = Warning | 2 |  |  |  |  | VV 06/06/2026 - Field wiring Issue as per Manesh - fixed by changing from 2-wire to 4-wire | 2025-10-28 | New instrument added
|  |  |  | TT24432 | TI24432 | 2000-F24-PID-PR-10001 | F24-PW-417 HIGH PRESSURE PROCESS WATER PUMP 1 GEARBOX TEMPERATURE TRANSMITTER | F24PW417 Gearbox Temp | 1 | -50 | 150 | °C | [16 empty] | 85 | 5 | 90 | 5 |  |  | A_HH = Trip F24-PW-417 A_Hi = Warning | 2 | [5 empty] | 2025-10-28 | New instrument added
|  |  |  | TT24434 | TI24434 | 2000-F24-PID-PR-10001 | F24-PW-418 HIGH PRESSURE PROCESS WATER PUMP 2 GEARBOX TEMPERATURE TRANSMITTER | F24PW418 Gearbox Temp | 1 | -50 | 150 | °C | [16 empty] | 85 | 5 | 90 | 5 |  |  | A_HH = Trip F24-PW-418 A_Hi = Warning | 2 | [5 empty] | 2025-10-28 | New instrument added
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 34 | 34

## 2. Analogue Output
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - AIR & WATER SERVICES (F24)
2000-F24-LST-PR-10001
ANALOGUE INSTRUMENTS (AO)
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  |  |  | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | Comments | Rev | OK | Date | OK | Date
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 0 | 0

## 3. Digital Input
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - AIR & WATER SERVICES (F24) |  |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)*
2000-F24-LST-PR-10001
DIGITAL INSTRUMENTS (DI)
[17 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Source | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date | C1 Comments
|  |  |  | FSL24510 | FAL24510 | 2000-F24-PID-PR-10003 | F24-PW-401 Mill Water Pump 1 Gland Water Flow Switch | F24PW401 GW Lo Flow | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F24PW401 Not Running |  | 1
|  |  |  | FSL24513 | FAL24513 | 2000-F24-PID-PR-10003 | F24-PW-401 Mill Water Pump 1 Gland Water Flow Switch | F24PW402 GlW Lo Flow | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F24PW402 Not Running |  | 1
|  |  |  | FSL24516 | FAL24516 | 2000-F24-PID-PR-10004 | F24-PW-417 High Pressure Process Water Pump 1 Gland Water Flow Switch | F24PW417 GW Lo Flow | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F24PW417 Not Running |  | 1
|  |  |  | FSL24519 | FAL24519 | 2000-F24-PID-PR-10004 | F24-PW-418 High Pressure Process Water Pump 2 Gland Water Flow Switch | F24PW418 GW Lo Flow | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F24PW418 Not Running |  | 1
|  |  |  | ZSO24507 | ZIO24507 | 2000-F24-PID-PR-10017 | Raw Water Feed Booster Pump discharge selection valve Position Switch Open | F24TK501 Dam 3 Fill Opn | N_Open | Open |  | Hardwired to DCS |  |  | No Alarm. Manual valve with Position Indication. | 0
|  |  |  | ZSC24507 | ZIC24507 | 2000-F24-PID-PR-10017 | Raw Water Feed Booster Pump discharge selection valve Position Switch Closed | F24TK501 Dam 3 Fill Clsd | N_Closed | Closed |  | Hardwired to DCS |  |  | No Alarm. Manual valve with Position Indication. | 0
|  |  |  | ZSO24508 | ZIO24508 | 2000-F24-PID-PR-10017 | Raw Water Feed Booster Pump discharge selection valve Position Switch Open | F24TK501 Saline Fill Opn | N_Open | Open |  | Hardwired to DCS |  |  | No Alarm. Manual valve with Position Indication. | 0
|  |  |  | ZSC24508 | ZIC24508 | 2000-F24-PID-PR-10017 | Raw Water Feed Booster Pump discharge selection valve Position Switch Closed | F24TK501 Saline Fil Clsd | N_Closed | Closed |  | Hardwired to DCS |  |  | No Alarm. Manual valve with Position Indication. | 0
|  |  |  | XS24468 | XI24468 | 2000-F24-PID-PR-10007 | F24-CM-401 Plant Air Compressor 1 Remote / Auto | F24CM401 Mode Selection | Local | Remote |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | 1 |  |  |  |  | Looks like load/unload indication
|  |  |  | XS24469 | XI24469 | 2000-F24-PID-PR-10007 | F24-CM-401 Plant Air Compressor 1 Drive Motor Running | F24CM401 Motor1 Running | Off | Running |  | Hardwired to DCS |  |  | No Alarm. Running Feedback once compressor is Started | 1
|  |  |  | XS24465 | XI24465 | 2000-F24-PID-PR-10007 | F24-CM-401 Plant Air Compressor 1 Fan Motor Running | F24CM401 Motor2 Running | Off | Running |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | 0
|  |  |  | XS24470 | XI24470 | 2000-F24-PID-PR-10007 | F24-CM-401 Plant Air Compressor 1 Warning | F24CM401 Warning | Active | Inactive | Active | Hardwired to DCS | 0 |  | Alarm. Operator to investigate on Compressor HMI. | 0 |  |  |  |  | No change when warning is simulated. I invert the input because its neutral state is 1 when no alarms or warnings is observed.
|  |  |  | XS24471 | XI24471 | 2000-F24-PID-PR-10007 | F24-CM-401 Plant Air Compressor 1 Shutdown | F24CM401 Shutdown | Shutdown | Inactive |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | 0 |  |  |  |  | When estop is pressed the input deactivates, hence I invert the input
|  |  |  | XS24475 | XI24475 | 2000-F24-PID-PR-10007 | F24-CM-402 Plant Air Compressor 2 Remote / Auto | F24CM402 Mode Selection | Local | Remote |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | 1 |  |  |  |  | Looks like load/unload indication
|  |  |  | XS24476 | XI24476 | 2000-F24-PID-PR-10007 | F24-CM-402 Plant Air Compressor 2 Drive Motor Running | F24CM402 Motor1 Running | Off | Running |  | Hardwired to DCS |  |  | No Alarm. Running Feedback once compressor is Started | 1
|  |  |  | XS24472 | XI24472 | 2000-F24-PID-PR-10007 | F24-CM-402 Plant Air Compressor 2 Fan Motor Running | F24CM402 Motor2 Running | Off | Running |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | 0
|  |  |  | XS24477 | XI24477 | 2000-F24-PID-PR-10007 | F24-CM-402 Plant Air Compressor 2 Warning | F24CM402 Warning | Active | Inactive | Active | Hardwired to DCS | 0 |  | Alarm. Operator to investigate on Compressor HMI. | 0 |  |  |  |  | condensate warning comes up when starting up, which is how this tag was verified. Nothing happened to CM401
|  |  |  | XS24478 | XI24478 | 2000-F24-PID-PR-10007 | F24-CM-402 Plant Air Compressor 2 Shutdown | F24CM402 Shutdown | Shutdown | Inactive |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | 0 |  |  |  |  | When estop is pressed the input deactivates, hence I invert the input
|  |  |  | XS24487 | XI24487 | 2000-F24-PID-PR-10007 | F24-CM-403 Plant Air Compressor 3 Remote / Auto | F24CM403 Mode Selection | Local | Remote |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | 1
|  |  |  | XS24488 | XI24488 | 2000-F24-PID-PR-10007 | F24-CM-403 Plant Air Compressor 3 Drive Motor Running | F24CM403 Motor1 Running | Off | Running |  | Hardwired to DCS |  |  | No Alarm. Running Feedback once compressor is Started | 1
|  |  |  | XS24479 | XI24479 | 2000-F24-PID-PR-10007 | F24-CM-403 Plant Air Compressor 3 Fan Motor Running | F24CM403 Motor2 Running | Off | Running |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | 0
|  |  |  | XS24489 | XI24489 | 2000-F24-PID-PR-10007 | F24-CM-403 Plant Air Compressor 3 Warning | F24CM403 Warning | Active | Inactive | Active | Hardwired to DCS | 0 |  | Alarm. Operator to investigate on Compressor HMI. | 0
|  |  |  | XS24490 | XI24490 | 2000-F24-PID-PR-10007 | F24-CM-403 Plant Air Compressor 3 Shutdown | F24CM403 Shutdown | Shutdown | Inactive |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | 0
|  |  |  | DPI24491 | DPAH24491 | 2000-F24-PID-PR-10007 | F24-CM-401 Plant Air Compressor 1 Dust Filter Differential Pressure | F24FI421 Diff. Pressure | Inactive | Active | Active | Hardwired to DCS | 3 |  | Initiate field operator to conduct filter changeover | 0 |  |  |  |  | Test is done from the panel. Unable to simulate from device.
|  |  |  | DPI24492 | DPAH24492 | 2000-F24-PID-PR-10007 | F24-CM-402 Plant Air Compressor 2 Dust Filter Differential Pressure | F24FI422 Diff. Pressure | Inactive | Active | Active | Hardwired to DCS | 3 |  | Initiate field operator to conduct filter changeover | 0 |  |  |  |  | Test is done from the panel. Unable to simulate from device.
|  |  |  | DPI24493 | DPAH24493 | 2000-F24-PID-PR-10007 | F24-CM-402 Plant Air Compressor 3 Dust Filter Differential Pressure | F24FI423 Diff. Pressure | Inactive | Active | Active | Hardwired to DCS | 3 |  | Initiate field operator to conduct filter changeover | 0 |  |  |  |  | Test is done from the panel. Unable to simulate from device.
|  |  |  | DPI24494 | DPAH24494 | 2000-F24-PID-PR-10007 | F24-CM-401 Plant Air Compressor 1 Coalesc. Filter Differential Pressure | F24FI424 Diff. Pressure | Inactive | Active | Active | Hardwired to DCS | 3 |  | Initiate field operator to conduct filter changeover | 0 |  |  |  |  | Test is done from the panel. Unable to simulate from device.
|  |  |  | DPI24495 | DPAH24495 | 2000-F24-PID-PR-10007 | F24-CM-402 Plant Air Compressor 2 Coalesc. Filter Differential Pressure | F24FI425 Diff. Pressure | Inactive | Active | Active | Hardwired to DCS | 3 |  | Initiate field operator to conduct filter changeover | 0 |  |  |  |  | Test is done from the panel. Unable to simulate from device.
|  |  |  | DPI24496 | DPAH24496 | 2000-F24-PID-PR-10007 | F24-CM-403 Plant Air Compressor 3 Coalesc. Filter Differential Pressure | F24FI426 Diff. Pressure | Inactive | Active | Active | Hardwired to DCS | 3 |  | Initiate field operator to conduct filter changeover | 0 |  |  |  |  | Test is done from the panel. Unable to simulate from device.
|  |  |  | ZSO75401 | ZIO75401 | 2000-F75-PID-PR-10002 | F24-PW-403 Saline Water Pump 1 Suction Valve Position Switch Open | F24PW403 Suction Open | N_Open | Open |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | C
|  |  |  | ZSC75401 | ZIC75401 | 2000-F75-PID-PR-10002 | F24-PW-403 Saline Water Pump 1 Suction Valve Position Switch Closed | F24PW403 Suction Closed | N_Closed | Closed |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | C
|  |  |  | ZSO75403 | ZIO75403 | 2000-F75-PID-PR-10002 | F24-PW-403 Saline Water Pump 1 Discharge Valve Position Switch Open | F24PW403 Disch Open | N_Open | Open |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | C
|  |  |  | ZSC75403 | ZIC75403 | 2000-F75-PID-PR-10002 | F24-PW-403 Saline Water Pump 1 Discharge Valve Position Switch Closed | F24PW403 Disch Closed | N_Closed | Closed |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | C
|  |  |  | ZSO75411 | ZIO75411 | 2000-F75-PID-PR-10002 | F24-PW-404 Saline Water Pump 2 Suction Valve Position Switch Open | F24PW404 Suction Open | N_Open | Open |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | C
|  |  |  | ZSC75411 | ZIC75411 | 2000-F75-PID-PR-10002 | F24-PW-404 Saline Water Pump 2 Suction Valve Position Switch Closed | F24PW404 Suction Closed | N_Closed | Closed |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | C
|  |  |  | ZSO75413 | ZIO75413 | 2000-F75-PID-PR-10002 | F24-PW-404 Saline Water Pump 2 Discharge Valve Position Switch Open | F24PW404 Disch Open | N_Open | Open |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | C
|  |  |  | ZSC75413 | ZIC75413 | 2000-F75-PID-PR-10002 | F24-PW-404 Saline Water Pump 2 Discharge Valve Position Switch Closed | F24PW404 Disch Closed | N_Closed | Closed |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | C
|  |  |  | ZSO75421 | ZIO75421 | 2000-F75-PID-PR-10002 | F24-PW-405 Saline Water Pump 3 Suction Valve Position Switch Open | F24PW405 Suction Opn | N_Open | Open |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | C
|  |  |  | ZSC75421 | ZIC75421 | 2000-F75-PID-PR-10002 | F24-PW-405 Saline Water Pump 3 Suction Valve Position Switch Closed | F24PW405 Suction Closed | N_Closed | Closed |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | C
|  |  |  | ZSO75423 | ZIO75423 | 2000-F75-PID-PR-10002 | F24-PW-405 Saline Water Pump 3 Discharge Valve Position Switch Open | F24PW405 Disch. Open | N_Open | Open |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | C
|  |  |  | ZSC75423 | ZIC75423 | 2000-F75-PID-PR-10002 | F24-PW-405 Saline Water Pump 3 Discharge Valve Position Switch Closed | F24PW405 Disch. Closed | N_Closed | Closed |  | Hardwired to DCS |  |  | No Alarm. Indication Only. | C
|  |  |  | PSL24651 | PAL24651 | 2000-F24-PID-PR-10009 | F17-TH-401 Thickener Hydraulic Drive Sprinkler System Alarm Check Valve Pressure Switch Low | F17TH401 HU Drive Fire | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | PSL24653 | PAL24653 | 2000-F24-PID-PR-10009 | F72-TK-432 Frother Storage Tank Perimeter Sprinkler System Alarm Check Valve Pressure Switch Low | F72TK432 Perimeter Fire1 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | YD24655 | YA24655 | 2000-F24-PID-PR-10009 | F72-TK-432 Frother Storage Tank Linear Heat Detector Alarm | F72TK432 Perimeter Fire2 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | PSL24656 | PAL24656 | 2000-F24-PID-PR-10009 | Recycle Crushing Building Sprinkler System Alarm Check Valve Pressure Switch Low | Recycle Crushing Fire1 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | YD24658A | YA24658 | 2000-F24-PID-PR-10009 | F13-LU-403/404 Recycle Crushers Lubrication Unit Infrared Heat Detector Alarm | Recycle Crushing Fire2 | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | See YA24658_ALM in MISC tab for conditions See MOC-506 | 0
YD24658B
|  |  |  | PSL24662 | PAL24662 | 2000-F24-PID-PR-10009 | F13-CV-403 SAG Mill Feed Conveyor Tail Sprinkler System Alarm Check Valve Pressure Switch Low | F13CV403 Tail Fire1 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | YD24664 | YA24664 | 2000-F24-PID-PR-10009 | F13-CV-403 SAG Mill Feed Conveyor Tail Linear Heat Detector Heat Alarm | F13CV403 Tail Fire2 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | PSL24671 | PAL24671 | 2000-F24-PID-PR-10026 | Elution Heater Oil Sprinkler System Alarm Check Valve Pressure Switch Low | Elution Heater Fire | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 |  |  |  |  | This tag is from FCS0412 not yet handed over
|  |  |  | PSL24674 | PAL24674 | 2000-F24-PID-PR-10015 | F28-MUF-402/403 UFG Mill 2/3 Sprinkler System Alarm Check Valve Pressure Switch Low | F28MUF402/403 Fire1 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | YD24676A | YA24676 | 2000-F24-PID-PR-10015 | F28-MUF-402/403 UFG Mill 2/3 Lubrication Units Infrared Flame Detector A | F28MUF402/403 Fire2 | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | See YA24676_ALM in MISC tab for conditions See MOC-506 | 1
|  |  |  | YD24676B |  |  | F28-MUF-402/403 UFG Mill 2/3 Lubrication Units Infrared Flame Detector B | [8 empty] | 1
|  |  |  | YD24676C |  |  | F28-MUF-402/403 UFG Mill 2/3 Lubrication Units Infrared Flame Detector C | [8 empty] | 1
|  |  |  | PSL24686 | PAL24686 | 2000-F24-PID-PR-10022 | F12-CV-401 Primary Crusher 2 Discharge Conveyor Tail Sprinkler System Alarm Check Valve Pressure Switch Low | F12CV401 Tail Fire | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | YD24688 | YA24688 | 2000-F24-PID-PR-10022 | F12-CV-401 Primary Crusher 2 Discharge Conveyor Head Linear Heat Detector Alarm | F12CV401 Tail Fire2 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 4
|  |  |  | YD24690 | YA24690 | 2000-F24-PID-PR-10022 | F12-LU-401 Primary Crusher 2 Lube System Infrared Heat Detector Alarm | F12LU401 Fire | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | See MOC-506 | 0
|  |  |  | PSL24693 | PAL24693 | 2000-F24-PID-PR-10022 | F12-HU-402 Primary Crusher 2 Rockbreaker HPU Sprinkler System Alarm Check Valve Pressure Switch Low | F12HU402 Fire | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | PSL24681 | PAL24681 | 2000-F24-PID-PR-10022 | F12-CV-402 Stockpile Feed Conveyor Head Sprinkler System Alarm Check Valve Pressure Switch Low | F12CV402 Head Fire | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | YD24683 | YA24683 | 2000-F24-PID-PR-10022 | F12-CV-402 Stockpile Feed Conveyor Head Linear Heat Detector Alarm | F12CV402 Head Fire2 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | PSL24683 | PAL24683 | 2000-F24-PID-PR-10022 | F12-CV-401 Primary Crusher 2 Discharge Conveyor Head Sprinkler System Alarm Check Valve Pressure Switch Low | F12CV401 Head Fire1 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | YD24685 | YA24685 | 2000-F24-PID-PR-10022 | F12-CV-401 Primary Crusher 2 Discharge Conveyor Head Linear Heat Detector Alarm | F12CV401 Head Fire2 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | PSL24711 | PAL24711 | 2000-F24-PID-PR-10023 | F13-CV-403 SAG Mill Feed Conveyor Head Sprinkler System Alarm Check Valve Pressure Switch Low | F13CV403 Head Fire1 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | YD24713 | YA24713 | 2000-F24-PID-PR-10023 | F13-CV-403 SAG Mill Feed Conveyor Head Linear Heat Detector Alarm | F13CV403 Head Fire2 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | PSL24701 | PAL24701 | 2000-F24-PID-PR-10023 | SAG Mill Lube Units Sprinkler System Alarm Check Valve Pressure Switch Low | SAG Mill Lube Fire1 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | YD24703A | YA24703 | 2000-F24-PID-PR-10023 | SAG Mill Lube Units Infrared Heat Detector Alarm | SAG Mill Lube Fire2 | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | See YA24703_ALM in MISC tab for conditions See MOC-506 | 0
YD24703B
|  |  |  | PSL24706 | PAL24706 | 2000-F24-PID-PR-10023 | Ball Mill Lube Units Sprinkler System Alarm Check Valve Pressure Switch Low | Ball Mill Lube Fire1 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | YD24708A | YA24708 | 2000-F24-PID-PR-10023 | Ball Mill Lube Units Infrared Heat Detector Alarm | Ball Mill Lube Fire2 | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | See YA24708_ALM in MISC tab for conditions See MOC-506 | 0
YD24708B
|  |  |  | YD24500A | YA24500 | 2000-F24-PID-PR-10007 | Air Compressors Area Linear Heat Detector Alarm | Air Compressor Fire | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | See YA24500_ALM in MISC tab for conditions. See MOC 506 | 1
YD24500B
|  |  |  | PSL24715 | PAL24715 | 2000-F24-PID-PR-10023 | F13-CV-405 Recycle Conveyor 2 Head Sprinkler System Alarm Check Valve Pressure Switch Low | F13CV405 Fire1 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | YD24717 | YA24717 | 2000-F24-PID-PR-10023 | F13-CV-405 Recycle Conveyor 2 Head Linear Heat Detector Alarm | F13CV405 Fire2 | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | FQ24506 | FQS24506 | N/A | F24-PW-451/452 Raw Water Booster Pumps Discharge Flow Totaliser Pulse | F24PW451/452 Tot Pulse | OFF | ON | - | Hardwired | 0 |  |  | 1
|  |  |  | XS24678A | YA24678 | 2000-F24-PID-PR-10023 | F13-SC-401SAG Mill Discharge Screen Fire Panel Alarm | F13SC401 Fire | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  | FIP contact for YD24678 LHD installed and connected to FIP24678 | 1
|  |  |  | XS24678B | XA24678A | 2000-F24-PID-PR-10023 | F13-SC-401SAG Mill Discharge Screen Fire Panel isolated | F13SC401 FIP Isolated | Inactive | Active |  | Hardwired to DCS | 0 |  |  | 1
|  |  |  | XS24678C | XA24678B | 2000-F24-PID-PR-10023 | F13-SC-401SAG Mill Discharge Screen Fire Panel Fault | F13SC401 FIP Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1
|  |  |  | XS24679A | YA24679 | 2000-F24-PID-PR-10023 | F13-SC-403 Trash Dewatering Screen Fire Panel Alarm | F13SC403 Fire | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  | FIP contact for YD24679 LHD installed and connected to FIP24679 | 1
|  |  |  | XS24679B | XA24679A | 2000-F24-PID-PR-10023 | F13-SC-403 Trash Dewatering Screen Fire Panel isolated | F13SC403 FIP Isolated | Inactive | Active |  | Hardwired to DCS | 0 |  |  | 1
|  |  |  | XS24679C | XA24679B | 2000-F24-PID-PR-10023 | F13-SC-403 Trash Dewatering Screen Fire Panel Fault | F13SC403 FIP Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1
|  |  |  | XS24673A | YA24673 | 2000-F24-PID-PR-10026 | F22-SC-421 CIL4 Loaded Carbon Screen Fire Panel Alarm | F22SC421 Fire | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  | FIP contact for YD24673 LHD installed and connected to FIP24673 | 1
|  |  |  | XS24673B | XA24673A | 2000-F24-PID-PR-10026 | F22-SC-421 CIL4 Loaded Carbon Screen Fire Panel isolated | F22SC421 FIP Isolated | Inactive | Active |  | Hardwired to DCS | 0 |  |  | 1
|  |  |  | XS24673C | XA24673B | 2000-F24-PID-PR-10026 | F22-SC-421 CIL4 Loaded Carbon Screen Fire Panel Fault | F22SC421 FIP Fault | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1
|  |  |  | XS75404 | XA75404 | 2000-F75-PID-PR-10002 | F24-PW-403 Saline Water Pump Dry Run Protection Switch | F24PW403 Dry Run | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F24PW403 Stopped Mask for 30 seconds on F24PW403 start up |  | 2 | [5 empty] | 20/03/2025 23/09/2025 | Changed instrumentation form PIT to a dry run protection switch Update as per PL-394
|  |  |  | XS75414 | XA75414 | 2000-F75-PID-PR-10002 | F24-PW-404 Saline Water Pump Dry Run Protection Switch | F24PW404 Dry Run | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F24PW404 Stopped Mask for 30 seconds on F24PW404 start up |  | 2 | [5 empty] | 21/03/2025 23/09/2025 | Changed instrumentation form PIT to a dry run protection switch PL-394
|  |  |  | XS75424 | XA75424 | 2000-F75-PID-PR-10002 | F24-PW-405 Saline Water Pump Dry Run Protection Switch | F24PW405 Dry Run | Alarm | Normal | Alarm | Hardwired to DCS | 3 | F24PW405 Stopped Mask for 30 seconds on F24PW405 start up |  | 2 | [5 empty] | 2025-03-22 | Changed instrumentation form PIT to a dry run protection switch
|  |  |  | F24RIO001PS1 | 24RIO001_PS1 | N/A | F24-RIO-001 PS1 24VDC HEALTHY | F24RIO001 PS1 24VDC HTY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | F24RIO001PS2 | 24RIO001_PS2 | N/A | F24-RIO-001 PS2 24VDC HEALTHY | F24RIO001 PS2 24VDC HTY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | F24RIO002PS1 | 24RIO002_PS1 | N/A | F24-RIO-002 PS1 24VDC HEALTHY | F24RIO002 PS1 24VDC HTY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | F24RIO002PS2 | 24RIO002_PS2 | N/A | F24-RIO-002 PS2 24VDC HEALTHY | F24RIO002 PS2 24VDC HTY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 0
|  |  |  | F24RIO100PS1 | 24RIO100_PS1 | N/A | F24-RIO-100 PS1 24VDC HEALTHY | F24RIO100 PS1 24VDC HTY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2 | [5 empty] | 2025-03-20 | added DI from F75 area
|  |  |  | F24RIO100PS2 | 24RIO100_PS2 | N/A | F24-RIO-100 PS2 24VDC HEALTHY | F24RIO100 PS2 24VDC HTY | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2 | [5 empty] | 2025-03-20 | added DI from F75 area
|  |  |  | F24SW024PS | 24SW024_PS | N/A | F24-SW-024 ACB SHUNT TRIP 24VDC OK | F24SW024 ACBSHUNT 24V OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2 | [5 empty] | 2025-10-23 | abbreviated description
|  |  |  | F24SW024AF | 24SW024_AF | N/A | F24-SW-024 ARC FLASH DETECTION SYSTEM ALARM | F24SW024 ARC FLASH | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2 |  |  |  |  | MOC125 | 2025-03-20 | added DI from F75 area
|  |  |  | F24SW024OP | 24SW024_OP | N/A | F24-SW-024 CIRCUIT BREAKER OPENED | F24SW024 CB OPEN | N_Active | Active |  | Hardwired to DCS |  |  |  | 2 | [5 empty] | 2025-03-20 | added DI from F75 area
|  |  |  | F24SW024CL | 24SW024_CL | N/A | F24-SW-024 CIRCUIT BREAKER CLOSED | F24SW024 CB CLOSED | N_Active | Active |  | Hardwired to DCS |  |  |  | 2 | [5 empty] | 2025-03-20 | added DI from F75 area
|  |  |  | F24SW024TRP | 24SW024_TRP | N/A | F24-SW-024 CIRCUIT BREAKER TRIPPED | F24SW024 CB TRIP | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  |  | 2 |  |  |  |  | MOC125 | 2025-03-20 | added DI from F75 area
|  |  |  | F24SW024SD | 24SW024_SD | N/A | F24-SW-024 INCOMER SURGE DIVERTER OK | F24SW024 INC SURGEDIV OK | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 2 |  |  |  |  | MOC125 | 2025-03-20 | added DI from F75 area
|  |  |  | F24TR024OTH | 24TR024_OTH | N/A | F24-TR-024 TRANSFORMER OIL TEMPERATURE HIGH ALARM | F24SW024 TR OILTEMP HI | Normal | Alarm | Alarm | Hardwired to DCS | 0 |  | BCK - This appears to be wired Normally open not normally closed as per design. No NC contact availabale Updated States and logic - MOC-099 | 2 | [5 empty] | 2025-03-20 | added DI from F75 area
|  |  |  | F24TR024WTH | 24TR024_WTH | N/A | F24-TR-024 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F24SW024 TR WINDTEMP HI | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  | BCK - was initially connected to NO contact. Misha Chaned to NC contact | 2 |  |  |  |  | MOC-240 VV 14/04/2026 | 2025-03-20 | added DI from F75 area
|  |  |  | F24TR024LSL | 24TR024_LSL | N/A | F24-TR-024 TRANSFORMER OIL LEVEL LOW ALARM | F24SW024 TR OILLVL LO | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  | BCK - Termination schedule shows 07/01/11 SPARE MOC-100 Removed from DCS (was 24TR024LSL) | [6 empty] | 2025-03-20 | added DI from F75 area
|  |  |  | PSL24433 | PAL24433 | 2000-F24-PID-PR-10001 | F24-PW-417 HIGH PRESSURE PROCESS WATER PUMP 1 GEARBOX PRESSURE SWITCH LOW | F24PW417 Gearbox Pres Lo | Alarm | Normal | Alarm | Hardwired to DCS | 30 | F24PW417 Stopped Mask for 30 seconds on F24PW417 start up |  | 2 | [5 empty] | 2025-10-28 | New Instrument added
|  |  |  | PSL24435 | PAL24435 | 2000-F24-PID-PR-10001 | F24-PW-418 HIGH PRESSURE PROCESS WATER PUMP 2 GEARBOX PRESSURE SWITCH LOW | F24PW418 Gearbox Pres Lo | Alarm | Normal | Alarm | Hardwired to DCS | 30 | F24PW418 Stopped Mask for 30 seconds on F24PW418 start up |  | 2 | [5 empty] | 2025-10-28 | New Instrument added
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 91 | 85
____

## 4. Digital Output
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - AIR & WATER SERVICES (F24) | [5 empty] | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)*
2000-F24-LST-PR-10001
DIGITAL INSTRUMENTS (DO)
[16 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date | C1 Comments
|  |  |  | HS24466 | HS24466LD |  | Plant Air Compressor 1 Load/Unload | F24-CM-401 Lead/Lag | OFF | ON |  | - |  | Pressure Band control of compressors. Refer to 24CM401_FP1 for the designation of the Duty Lead/Duty Lag/Standby compressors and associated pressure duty ON = LEAD Pressure band OFF = LAG Pressure band Each compressor has two pressure bands settings that will be configured during commissioning | 1 |  |  |  |  | It triggers the load and unload
|  |  |  | HS24467 | HS24467STT |  | Plant Air Compressor 1 Start / Stop | F24-CM-401 Start/Stop | STOP | START |  | - |  | Remote Start/Stop function. This can only be enabled if Remote mode HS244497REM is Activated | 2
|  |  |  | HS24497 | HS24497REM |  | Plant Air Compressor 1 Start / Stop | F24-CM-401 Remote | N_Activated | Activated |  | - |  | Remote functionality to Start/Stop the controllers by digital input with Local Pressure Control (using Pressure Bands settings in the PLC as assigned by 24CM401_FP1) | 1 |  |  |  |  | JWHO 26/4/26 :Does not work as intended
|  |  |  | HS24473 | HS24473LD |  | Plant Air Compressor 2 Load / Unload | F24-CM-402 Lead/Lag | OFF | ON |  | - |  | Pressure Band control of compressors. Refer to 24CM401_FP1 for the designation of the Duty Lead/Duty Lag/Standby compressors and associated pressure duty ON = LEAD Pressure band OFF = LAG Pressure band Each compressor has two pressure bands settings that will be configured during commissioning | 1 |  |  |  |  | It triggers the load and unload
|  |  |  | HS24474 | HS24474STT |  | Plant Air Compressor 2 Start / Stop | F24-CM-402 Start/Stop | STOP | START |  | - |  | Remote Start/Stop function. This can only be enabled if Remote mode HS244498REM is Activated | 1
|  |  |  | HS24498 | HS24498REM |  | Plant Air Compressor 1 Start / Stop | F24-CM-402 Remote | N_Activated | Activated |  | - |  | Remote functionality to Start/Stop the controllers by digital input with Local Pressure Control (using Pressure Bands settings in the PLC as assigned by 24CM401_FP1) | 1 |  |  |  |  | JWHO 26/4/26 :Does not work as intended
|  |  |  | HS24485 | HS24485LD |  | Plant Air Compressor 3 Load / Unload | F24-CM-403 Lead/Lag | OFF | ON |  | - |  | Pressure Band control of compressors. Refer to 24CM401_FP1 for the designation of the Duty Lead/Duty Lag/Standby compressors and associated pressure duty ON = LEAD Pressure band OFF = LAG Pressure band Each compressor has two pressure bands settings that will be configured during commissioning | 1
|  |  |  | HS24486 | HS24486STT |  | Plant Air Compressor 3 Start / Stop | F24-CM-403 Start | STOP | START |  | - |  | Remote Start/Stop function. This can only be enabled if Remote mode HS244499REM is Activated | 1
|  |  |  | HS24499 | HS24499REM |  | Plant Air Compressor 1 Start / Stop | F24-CM-403 Remote | N_Activated | Activated |  | - |  | Remote functionality to Start/Stop the controllers by digital input with Local Pressure Control (using Pressure Bands settings in the PLC as assigned by 24CM401_FP1) | 1
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 8 | 8

## 5. Totalisers
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - AIR & WATER SERVICES (F24)
2000-F24-LST-PR-10001
TOTALISERS
[11 empty] | Reset Period |  |  |  |  | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | Type | P&ID | Description | Abbreviated Description (Faceplate) | Units | Shift | Day | Cont | Comments | Rev | OK | Date | OK | Date | Comments
|  |  |  | FI24506 | FQI24506 | FQI | 2000-F24-PID-PR-10017 | F24-PW-451/452 Raw Water Feed Booster Pump 1/2 Discharge Flow Totaliser | F24PW451/452 Total Flow | m3 | X | X | X |  | 0
|  |  |  | FI75429 | FQI75429 | FQI | 2000-F75-PID-PR-10002 | F24-PW-403/404/405 Saline Water Pump 1/2/3 Discharge Flow Totaliser | F24PW403/4/5 Total Flow | m3 | X | X | X |  | 0
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 2 | 2
1

## 6. OnOff Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - AIR & WATER SERVICES (F24)
2000-F24-LST-PR-10001
OPEN-CLOSE VALVES
[14 empty] | Permissives and Trips | [12 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | ACTUATIO | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (Faceplate) | Delay On | Delay Off | Open Permissive | Close Permissive | Open | Close | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date | C1 Comments
|  |  |  | XV24402 | 2000-F24-PID-PR-10001 | F24-TK-401 Process Water Tank Saline Water Feed Valve | F24TK401 Saline Valve | 7 | FC | X |  |  |  | OP1 | LIC24401 < P_Hi | LIC24401 < P_Hi | 5 |  | X |  |  |  | X |  | Prevents overflow of Process Water Tank | 0
[14 empty] | CT1 | LIC24401 >= A_HH | LIC24401 > A_HH | 5 |  |  |  |  | X | X |  | Prevents overflow of Process Water Tank | 0
|  |  |  | XV24421 | 2000-F24-PID-PR-10001 | F24-PW-417 High Pressure Process Water Pump 1 Suction Valve | F24PW417 Suction Valve | 9 | FL | X | X | F24-SEQ-0003 START | F24-SEQ-0004 STOP | [12 empty] | 1
|  |  |  | XV24422 | 2000-F24-PID-PR-10001 | F24-PW-417 High Pressure Process Water Pump 1 Discharge Valve | F24PW417 Discharge Valve | 9 | FL | X | X | F24-SEQ-0003 START | F24-SEQ-0004 STOP | [12 empty] | 1
|  |  |  | XV24423 | 2000-F24-PID-PR-10001 | F24-PW-418 High Pressure Process Water Pump 2 Suction Valve | F24PW418 Suction Valve | 9 | FL | X | X | F24-SEQ-0003 START | F24-SEQ-0004 STOP | [12 empty] | 1
|  |  |  | XV24424 | 2000-F24-PID-PR-10001 | F24-PW-418 High Pressure Process Water Pump 2 Discharge Valve | F24PW418 Discharge Valve | 9 | FL | X | X | F24-SEQ-0003 START | F24-SEQ-0004 STOP | [12 empty] | 1
|  |  |  | XV24411 | 2000-F24-PID-PR-10001 | F24-PW-401 Mill Water Pump 1 Suction Valve | F24PW401 Suction Valve | 9 | FL | X | X | F24-SEQ-0001 START | F24-SEQ-002 STOP | [12 empty] | 1 |  |  |  |  | Valve MTM time to probably increase due to size of the valve. Changed to 12s
|  |  |  | XV24412 | 2000-F24-PID-PR-10001 | F24-PW-401 Mill Water Pump 1 Discharge Valve | F24PW401 Discharge Valve | 9 | FL | X | X | F24-SEQ-0001 START | F24-SEQ-002 STOP | [12 empty] | 1 |  |  |  |  | Valve MTM time to probably increase due to size of the valve. Changed to 12s
|  |  |  | XV24413 | 2000-F24-PID-PR-10001 | F24-PW-402 Mill Water Pump 2 Suction Valve | F24PW402 Suction Valve | 9 | FL | X | X | F24-SEQ-0001 START | F24-SEQ-002 STOP | [12 empty] | 1 |  |  |  |  | Valve MTM time to probably increase due to size of the valve. Changed to 12s
|  |  |  | XV24414 | 2000-F24-PID-PR-10001 | F24-PW-402 Mill Water Pump 2 Discharge Valve | F24PW402 Discharge Valve | 9 | FL | X | X | F24-SEQ-0001 START | F24-SEQ-002 STOP | [12 empty] | 1 |  |  |  |  | Valve MTM time to probably increase due to size of the valve. Changed to 12s
|  |  |  | SV24518 | 2000-F24-PID-PR-10003 | F24-PW-417 High Pressure Process Water Pump 1 Gland Water Solenoid Valve | F24PW417 Gland Water | 11 | FO | X | X | F24-SEQ-0003 START OR F24-PW-417 START | F24-SEQ-0004 STOP | [12 empty] | 2 | [5 empty] | 2025-03-18 | PCT alignment action register (gland water valve pump start condition)
|  |  |  | SV24521 | 2000-F24-PID-PR-10003 | F24-PW-418 High Pressure Process Water Pump 2 Gland Water Solenoid Valve | F24PW418 Gland Water | 11 | FO | X | X | F24-SEQ-0003 START OR F24-PW-418 START | F24-SEQ-0004 STOP | [12 empty] | 2 | [5 empty] | 2025-03-18 | PCT alignment action register (gland water valve pump start condition)
|  |  |  | SV24512 | 2000-F24-PID-PR-10003 | F24-PW-401 Mill Water Pump 1 Gland Water Solenoid Valve | F24PW401 Gland Water | 11 | FO | X | X | F24-SEQ-0001 START OR F24-PW-401 START | F24-SEQ-0002 STOP | [12 empty] | 2 |  |  |  |  | Loop checked only | 2025-03-18 | PCT alignment action register (gland water valve pump start condition)
|  |  |  | SV24515 | 2000-F24-PID-PR-10003 | F24-PW-402 Mill Water Pump 2 Gland Water Solenoid Valve | F24PW402 Gland Water | 11 | FO | X | X | F24-SEQ-0001 START OR F24-PW-402 START | F24-SEQ-0002 STOP | [12 empty] | 2 |  |  |  |  | Loop checked only | 2025-03-18 | PCT alignment action register (gland water valve pump start condition)
|  |  |  | XV24501 | 2000-F24-PID-PR-10017 | F24-PW-451 Raw Water Feed Booster Pump 1 Suction Valve | F24PW451 Suction Valve | 9 | FL | X | [15 empty] | 1
|  |  |  | XV24502 | 2000-F24-PID-PR-10017 | F24-PW-451 Raw Water Feed Booster Pump 1 Discharge Valve | F24PW451 Discharge Valve | 9 | FL | X | [15 empty] | 1
|  |  |  | XV24503 | 2000-F24-PID-PR-10017 | F24-PW-451 Raw Water Feed Booster Pump 2 Suction Valve | F24PW452 Suction Valve | 9 | FL | X | [15 empty] | 1
|  |  |  | XV24504 | 2000-F24-PID-PR-10017 | F24-PW-451 Raw Water Feed Booster Pump 2 Discharge Valve | F24PW452 Discharge Valve | 9 | FL | X | [15 empty] | 1
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
17

## 7. Control Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - AIR & WATER SERVICES (F24)
2000-F24-LST-PR-10001
CONTROL VALVES
[14 empty] | Permissive and Trips | [12 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open | Close | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date | Comments
|  |  |  | LCV24401 | 2000-F24-PID-PR-10001 | F24-TK-401 Process Water Tank Level Control Valve | F24TK401 Saline Wtr Addn | Detail 1 | FC | X | X | [14 empty] | 0
|  |  |  | LCV24431 | 2000-F24-PID-PR-10002 | F24-TK-501 Raw Water Tank Level Control Valve | F24TK501 Raw Wtr Addn | Detail 1 | FC | X | X | [14 empty] | 1
|  |  |  | LCV24456 | 2000-F24-PID-PR-10020 | F24-TK-402 Raw Water Booster Tank Level Control Valve | F24TK402 Raw Wtr Addn | Detail 1 | FC | X | X | [14 empty] | 0
|  |  |  | LCV75690A | 2000-F75-PID-PR-10007 | 75-TK-463 Gland Water Tank Level Control Valve | 75TK63 Gland Wtr Addn | Detail 1 | FC | X | X | [14 empty] | 1
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
4

## 8. PID Cont
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - AIR & WATER SERVICES (F24)
2000-F24-LST-PR-10001
PID Controllers
[10 empty] | Modes |  |  |  | Setpoint |  |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [7 empty] | Alarm Priority |  |  |  |  | Controlled/Manipulated Variable | [12 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Controller Description | Abbreviated Description (Faceplate) | Normal Operating Mode | Manual | Auto | Cascade | Process Value Tag | Min | Max | Unit | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | A_LL | A_Lo | A_Hi | A_HH | Alarm Masking Conditions | Range Min | Range Max | Lower Limit | Upper Limit | Unit | Destination Description | Destination (Output) Tag | Direct / Reverse Acting | P | I | D | Comment | Rev | OK | Date | OK | Date | Comments
|  |  |  | LIT24401 | LIC24401 | 2000-F24-PID-PR-10001 | F24-TK-401 Process Water Tank Level Indicating Transmitter | F24TK401 Level Ctrl A | AUTO | X | X |  | LIT24401 | 0 | 100 | % | 0 | 100 | % | [6 empty] | 75 | 5 |  |  |  |  | 15 | 5 | 20 | 5 | 80 | 5 | 90 | 5 | [5 empty] | 0 | 100 | 0 | 100 | %Open | Process Water Tank Level Control Valve | LCV24401 | Reverse |  |  |  | A_LL = Trip F24-PW-401/402/417/418, Trip open LCV24401 A_Lo = Warning A_Hi = Warning A_HH = Trips XV24402 P_Hi = Open permissived for XV24402 Nominal values and alarm setpoints to be determined during commissioning | 1
|  |  |  | PIT24415 | PIC24415 | 2000-F24-PID-PR-10001 | F24-PW-401 Mill Water Pump 1 Discharge Pressure Indicating Transmitter | F24PW401 Dschge Ctrl | AUTO | X | X |  | PIT24415 | 0 | 500 | kPa | 0 | 500 | kPa | [14 empty] | 200 | 5 | 370 | 5 | 440 | 5 |  |  |  |  | F24-PW-401 NOT RUNNING Enable 10s delay on Pump Start-up | 0 | 100 | 40 | 100 | VSD Speed % | Mill Water Pump 1 VSD | F24-PW-401 VSD | Reverse |  |  |  | PE8 / RL1 Maximum Pressure = 700kPa (2000-F00-DSH-PP-PE8/RL1) Alarms based on design flowrate 5000m3/h (370kPag) A_HH = Trip F24-PW-401 A_Hi = Warning A_Lo = Warning Nominal values and alarm setpoints to be confirmed during commissioning | 1
|  |  |  | PIT24416 | PIC24416 | 2000-F24-PID-PR-10001 | F24-PW-402 Mill Water Pump 2 Discharge Pressure Indicating Transmitter | F24PW402 Dschge Ctrl | AUTO | X | X |  | PIT24416 | 0 | 500 | kPa | 0 | 500 | kPa | [14 empty] | 200 | 5 | 370 | 5 | 440 | 5 |  |  |  |  | F24-PW-402 NOT RUNNING Enable 10s delay on Pump Start-up | 0 | 100 | 40 | 100 | VSD Speed % | Mill Water Pump 2 VSD | F24-PW-402 VSD | Reverse |  |  |  | PE8 / RL1 Maximum Pressure = 700kPa (2000-F00-DSH-PP-PE8/RL1) Alarms based on design flowrate 5000m3/h (370kPag) A_HH = Trip F24-PW-402 A_Hi = Warning A_Lo = Warning Nominal values and alarm setpoints to be confirmed during commissioning Alarm enabled delay of 10 seconds on Pump start-up | 1
|  |  |  | PIT24425 | PIC24425 | 2000-F24-PID-PR-10001 | F24-PW-417 High Pressure Process Water Pumps Discharge Pressure Indicating Transmitter | F24PW417 Dschge Ctrl | AUTO | X | X |  | PIT24425 | 0 | 700 | kPa | 0 | 1000 | 24 | [14 empty] | 500 | 5 | 750 | 5 | 900 | 5 |  |  |  |  | F24-PW-417 NOT RUNNING Enable 10s delay on Pump Start-up | 0 | 100 | 40 | 100 | VSD Speed % | High PressureProcess Water Pump 1 and 2 VSD | F24-PW-417 VSD | Reverse |  |  |  | PE16 / RL2 Maximum Pressure = 1400kPa (2000-F00-DSH-PP-PE16/RL2) Alarms based on design flowrate 3462m3/h (688kPag) A_HH = Trip F24-PW-417 A_Hi = Warning A_Lo = Warning Nominal values and alarm setpoints to be confirmed during commissioning | 1
|  |  |  | PIT24426 | PIC24426 | 2000-F24-PID-PR-10001 | F24-PW-418 High Pressure Process Water Pumps Discharge Pressure Indicating Transmitter | F24PW418 Dschge Ctrl | AUTO | X | X |  | PIT24426 | 0 | 700 | kPa | 0 | 1000 | kPa | [14 empty] | 500 | 5 | 750 | 5 | 900 | 5 |  |  |  |  | F24-PW-418 NOT RUNNING Enable 10s delay on Pump Start-up | 0 | 100 | 40 | 100 | VSD Speed % | High PressureProcess Water Pump 1 and 2 VSD | F24-PW-418 VSD | Reverse |  |  |  | PE16 / RL2 Maximum Pressure = 1400kPa (2000-F00-DSH-PP-PE16/RL2) Alarms based on design flowrate 3462m3/h (688kPag) A_HH = Trip F24-PW-418 A_Hi = Warning A_Lo = Warning Nominal values and alarm setpoints to be confirmed during commissioning | 1
|  |  |  | LIT24431 | LIC24431 | 2000-F24-PID-PR-10001 | F24-TK-501 Raw Water Tank Level Indicating Transmitter | F24TK501 Level Ctrl | AUTO | X | X |  | LIT24431 | 0 | 100 | % | 0 | 100 | % |  |  |  | 25 | 5 |  |  |  |  | 85 | 5 |  | 15 | 5 | 20 | 5 | 80 | 5 | 90 | 5 | [5 empty] | 0 | 100 | 0 | 100 | %Open | Raw Water Tank Level Control Valve | LCV24431 | Reverse |  |  |  | A_LL = Trip F24-PW-406/407 A_Lo = Warning A_Hi = Warning A_HH = Warning P_Lo = Start F24-PW-451/452 in Auto P_HH = Stop F24-PW-451/452 in Auto Nominal values and alarm setpoints to be determined during commissioning | 1 |  |  |  |  | LIC Loop Tested Bret Huett and Dion Govender 25/02/2025
|  |  |  | LIT24456 | LIC24456 | 2000-F24-PID-PR-10020 | F24-TK-402 Raw Water Booster Tank Level Indicating Transmitter | F24TK402 Level Ctrl | AUTO | X | X |  | LIT24456 | 0 | 100 | % | 0 | 100 | % |  |  |  | 25 | 5 |  |  |  |  | 85 | 5 |  | 15 | 5 | 20 | 5 | 80 | 5 | 90 | 5 | [5 empty] | 0 | 100 | 0 | 100 | %Open | Raw Water Booster Tank Level Control Valve | LCV24456 | Reverse |  |  |  | A_LL = Trip F24-PW-410 A_Lo = Warning A_Hi = Warning A_HH = Trip F24-PW-453 P_Lo = Start F24-PW-453 in Auto P_HH = Stop F24-PW-453 in Auto Nominal values and alarm setpoints to be determined during commissioning | 1
|  |  |  | LIT75690 | LIC75690A | 2000-F75-PID-PR-10007 | 75-TK-63 Gland Water Tank Level Indicating Transmitter | 75TK63 Level Ctrl | AUTO | X | X |  | LIT75690 | 0 | 100 | % | 0 | 100 | % | [25 empty] | 0 | 100 | 0 | 100 | %Open | Gland Water Tank Level Control Valve | LCV75690A | Reverse |  |  |  | Brownfield level transmitter LIT75690 used in the new controller for the new level control valve to manage raw water addition to the tank. | 1
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 8 | 8

## 10. Sequence
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - AIR & WATER SERVICES (F24)
2000-F24-LST-PR-10001
SEQUENCES
Seq No. | Seq Description | Step | Action | Tag / Item | Description | Next Step Delay (s) | Step Advance Condition | Comments | Rev | Equipment Permissives | Recovery Seq. No if Step Faults
PLEASE REFER TO SEQUENCE FLOWCHART DOCUMENT (2000-F24-LST-PR-10002)
0

## 9. Drives
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - AIR & WATER SERVICES (F24)
2000-F24-LST-PR-10001
DRIVE INTERLOCKS AND CONTROL | [26 empty] | General: | Standby pump running removed as interlock to facilitate on the run pump swap
[15 empty] | Description (Unhealthy Interlocks) |  |  |  | Interlocks | [9 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Name | Drive Type | Speed Min | Speed Max | Speed Units | SP Lower Limit | SP Upper Limit | Current Max | Manual | Auto | Start Condition (Auto Mode) | Stop Condition (Auto Mode) | # |  | Delay On | Delay Off | Start Permissive | Process | Critical | Hardwired to Drive | Bypass | Reset Required | Comments | Rev |  |  |  | OK | Date | OK | Date | Comments
F24-PW-401 | 2000-F24-PID-PR-10001 | Mill Water Pump 1 | VSD1 | 0 | 100 | % | 40 | 100 | 41.9891104865182 165 | X | X | F24-SEQ-0001 START | F24-SEQ-0002 STOP | [11 empty] | 1
[14 empty] | 1 | F24-PW-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-401 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | SV24512 Auto or Open | 3 |  | X |  |  |  | X |  | Gland water valve is in auto or open | 1
[14 empty] | 9 | FSL24510 Inactive AND F24-PW-401 RUN | 25 |  |  | X |  |  | X |  | Stop pump if gland water low flow | 2 | 2025-03-18 | PCT alignment (switch flow state changed)
[14 empty] | 10 | XV24411 is Closed | 3 |  |  | X |  |  | X |  | Prevent start-up or trip pump if inlet valve is closed to prevent cavitating the pump | 0
[14 empty] | 11 | XV24412 is Closed | 3 |  |  | X |  |  | X |  | Prevent start-up or trip pump if discharge valve is closed to prevent dead heading the pump. | 0
[14 empty] | 12 | LIC24401 ≤ A_LL | 15 |  |  | X |  |  | X |  | Prevent start-up or trip pump if Process Water Tank level <= A_LL. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 13 | PIC24415 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 15 | TT24410 >= A_HH | 5 |  |  | X |  |  | X |  | Gearbox Temperature Hi-Hi | 2 | 2025-10-28
F24-PW-402 | 2000-F24-PID-PR-10001 | Mill Water Pump 2 | VSD1 | 0 | 100 | % | 40 | 100 | 41.9891104865182 165 | X | X | F24-SEQ-0001 START | F24-SEQ-0002 STOP | [11 empty] | 1
[14 empty] | 1 | F24-PW-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-402 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | SV24515 Auto or Open | 3 |  | X |  |  |  | X |  | Gland water valve is in auto or open | 1
[14 empty] | 9 | FSL24513 Inactive AND F24-PW-402 RUN | 25 |  |  | X |  |  | X |  | Stop pump if gland water low flow. | 2 | 2025-03-18 | PCT alignment (switch flow state changed). Delay in comment removed
[14 empty] | 10 | XV24413 is Closed | 3 |  |  | X |  |  | X |  | Prevent start-up or trip pump if inlet valve is closed to prevent cavitating the pump | 0
[14 empty] | 11 | XV24414 is Closed | 3 |  |  | X |  |  | X |  | Prevent start-up or trip pump if discharge valve is closed to prevent dead heading the pump. | 0
[14 empty] | 12 | LIC24401 ≤ A_LL | 15 |  |  | X |  |  | X |  | Prevent start-up or trip pump if Process Water Tank level <= A_LL. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 13 | PIC24416 >= A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 15 | TT24420 >= A_HH | 5 |  |  | X |  |  | X |  | Gearbox Temperature Hi-Hi | 2 | 2025-10-28
F24-PW-403 | 2000-F75-PID-PR-10002 | Saline Water Pump 1 | DOL | [5 empty] | 347.8014 | X |  | Manually Started by CRO | Manually Stopped by CRO | [11 empty] | 2 | 2025-09-16 | Removed AUT. No action required on DCS
[14 empty] | 1 | F24-PW-403 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-403 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-403 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-403 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-403 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-403 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-403 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | ZIC75401 Closed | 3 |  |  | X |  |  | X |  | HV75401 close limit is active | 0
[14 empty] | 9 | ZIC75403 Closed | 3 |  |  | X |  |  | X |  | HV75403 close limit is active | 0
[14 empty] | 10 | ZIO75401 N_Open | 3 |  |  | X |  |  | X |  | HV75401 open limit is inactive | 0
[14 empty] | 11 | ZIO75403 N_Open | 3 |  |  | X |  |  | X |  | HV75403 open limit is inactive | 0
[14 empty] | 12 | TI75410A ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor U RTD temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 13 | TI75410B ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor V RTD temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 14 | TI75410C ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor W RTD temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 15 | TI75410D ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor DE Bearing temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 16 | TI75410E ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor NDE Bearing temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 17 | LI7526 ≤ A_LL | 15 |  |  | X |  |  | X |  | Bore Water Dam 2 (South Dam) water level <= A_LL Level transmitter is an existing instrument | 1
[14 empty] | 18 | PI75428 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 19 | XS75404 Inactive AND F24-PW-403 Running | 30 |  |  | X |  |  | X |  | Trip pump if dry run protection switch is inactive | 2 | 2025-03-24 | PIT chnaged to dry run protection switch
F24-PW-404 | 2000-F75-PID-PR-10002 | Saline Water Pump 2 | DOL | [5 empty] | 347.8014 | X |  | Manually Started by CRO | Manually Stopped by CRO | [11 empty] | 2 | 2025-09-16 | Removed AUT. No action required on DCS
[14 empty] | 1 | F24-PW-404 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-404 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-404 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-404 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-404 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-404 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-404 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | ZIC75411 Closed | 3 |  |  | X |  |  | X |  | HV75411 close limit is active | 0
[14 empty] | 9 | ZIC75413 Closed | 3 |  |  | X |  |  | X |  | HV75413 close limit is active | 0
[14 empty] | 10 | ZIO75411 N_Open | 3 |  |  | X |  |  | X |  | HV75411 open limit is inactive | 0
[14 empty] | 11 | ZIO75413 N_Open | 3 |  |  | X |  |  | X |  | HV75413 open limit is inactive | 0
[14 empty] | 12 | TI75420A ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor U RTD temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 13 | TI75420B ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor V RTD temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 14 | TI75420C ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor W RTD temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 15 | TI75420D ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor DE Bearing temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 16 | TI75420E ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor NDE Bearing temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 17 | LI7526 ≤ A_LL | 15 |  |  | X |  |  | X |  |  | 1 | [7 empty] | Cannot test due to Level transmitter not connected yet
[14 empty] | 18 | PI75428 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 19 | XS75414 Inactive AND F24-PW-404 Running | 30 |  |  | X |  |  | X |  | Trip pump if dry run protection switch is inactive | 2 | 2025-03-24 | PIT chnaged to dry run protection switch
F24-PW-405 | 2000-F75-PI-PR-10002 | Saline Water Pump 3 | DOL | [5 empty] | 347.8014 | X |  | Manually Started by CRO | Manually Stopped by CRO | [11 empty] | 2 | 2025-09-16 | Removed AUT. No action required on DCS
[14 empty] | 1 | F24-PW-405 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-405 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-405 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-405 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-405 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-405 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-405 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | ZIC75421 Closed | 3 |  |  | X |  |  | X |  | HV75421 close limit is active | 0
[14 empty] | 9 | ZIC75423 Closed | 3 |  |  | X |  |  | X |  | HV75423 close limit is active | 0
[14 empty] | 10 | ZIO75421 N_Open | 3 |  |  | X |  |  | X |  | HV75421 open limit is inactive | 0
[14 empty] | 11 | ZIO75423 N_Open | 3 |  |  | X |  |  | X |  | HV75423 open limit is inactive | 0
[14 empty] | 12 | TI75430A ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor U RTD temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 13 | TI75430B ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor V RTD temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 14 | TI75430C ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor W RTD temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 15 | TI75430D ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor DE Bearing temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 16 | TI75430E ≥ A_HH | 60 |  |  |  | X |  | X |  | Trip pump if Motor NDE Bearing temperature >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 17 | LI7526 ≤ A_LL | 15 |  |  | X |  |  | X |  | Bore Water Dam 2 (South Dam) water level <= A_LL Level transmitter is an existing instrument | 1 | [7 empty] | Cannot test due to Level transmitter not connected yet
[14 empty] | 18 | PI75428 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 19 | XS75424 Inactive AND F24-PW-405 Running | 30 |  |  | X |  |  | X |  | Trip pump if dry run protection switch is inactive | 2 | 2025-03-24 | PIT chnaged to dry run protection switch
F24-XM-409 | 2000-F75-PI-PR-10002 | Saline Water Pumps Vacuum Priming Unit | DOL | [5 empty] | 5.34 |  |  | Manually Started by CRO | Manually Stopped by CRO | [11 empty] | 2 | 16/09/2025 16/09/2025 | KAN2139 Removed AUT
[14 empty] | 1 | F24-XM-409 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2 | 2025-09-16 | KAN2139
[14 empty] | 2 | F24-XM-409 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-XM-409 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-XM-409 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-XM-409 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-XM-409 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-XM-409 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | Prime Timer Complete | 600 |  |  | X |  |  | X |  | Logic: F24-XM-409 = Running On-delay TBC during commissioning | 2 | 2025-09-16 | KAN2139
F24-PW-417 | 2000-F24-PID-PR-10001 | High Pressure Process Water Pump 1 | VSD1 | 0 | 100 | % | 40 | 100 | 41.9891104865182 165 | X | X | F24-SEQ-0003 START | F24-SEQ-0004 STOP | [11 empty] | C
[14 empty] | 1 | F24-PW-417 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-417 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-417 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-417 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-417 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-417 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-417 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | SV24518 is Auto or Open | 3 |  | X |  |  |  | X |  | Gland water valve is in auto or open | 2 | 2025-03-18 | PCT alignment (gland water valve in auto or open)
[14 empty] | 9 | FSL24516 Inactive AND F24-PW-417 RUN | 25 |  |  | X |  |  | X |  | Stop pump if gland water low flow | 2 | 2025-03-18 | PCT alignment (switch flow state changed). Delay in comment removed
[14 empty] | 10 | XV24421 is Closed | 3 |  |  | X |  |  | X |  | Prevent start-up or trip pump if inlet valve is closed to prevent cavitating the pump | 0
[14 empty] | 11 | XV24422 is Closed | 3 |  |  | X |  |  | X |  | Prevent start-up or trip pump if discharge valve is closed to prevent dead heading the pump. | 0
[14 empty] | 12 | LIC24401 ≤ A_LL | 15 |  |  | X |  |  | X |  | Prevent start-up or trip pump if Process Water Tank level <= A_LL. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 13 | PIC24425 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 14 | F24-FN-417 Not Running AND F24-PW-417 Running | 30 |  |  |  | X |  |  |  | Trip pump if Gearbox Fan is not running and pump running for 30 seconds | 2 | 2025-05-26 | Added condition the pump is running for 30 seconds prior tripping the pump due to fan not running
[14 empty] | 15 | TT24432 >= A_HH | 5 |  |  | X |  |  | X |  | Gearbox Temperature Hi-Hi | 2 | 2025-10-28
F24-PW-418 | 2000-F24-PID-PR-10001 | High Pressure Process Water Pump 2 | VSD1 | 0 | 100 | % | 40 | 100 | 41.9891104865182 165 | X | X | F24-SEQ-0003 START | F24-SEQ-0004 STOP | [11 empty] | C
[14 empty] | 1 | F24-PW-418 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-418 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-418 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-418 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-418 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-418 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-418 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | SV24521 Auto or Open | 3 |  | X |  |  |  | X |  | Gland water valve is in auto or open | 1
[14 empty] | 9 | FSL24519 Inactive AND F24-PW-418 RUN | 25 |  |  | X |  |  | X |  | Stop pump if gland water low flow | 2 | 2025-03-18 | PCT alignment (switch flow state changed). Delay in comment removed
[14 empty] | 10 | XV24423 is Closed | 3 |  |  | X |  |  | X |  | Prevent start-up or trip pump if inlet valve is closed to prevent cavitating the pump | 0
[14 empty] | 11 | XV24424 is Closed | 3 |  |  | X |  |  | X |  | Prevent start-up or trip pump if discharge valve is closed to prevent dead heading the pump. | 0
[14 empty] | 12 | LIC24401 ≤ A_LL | 15 |  |  | X |  |  | X |  | Prevent start-up or trip pump if Process Water Tank level <= A_LL. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 13 | PIC24426 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 14 | F24-FN-418 Not Running AND F24-PW-418 Running | 30 |  |  |  | X |  |  |  | Trip pump if Gearbox Fan is not running and pump running for 30 seconds | 2 | 2025-05-26 | Added condition the pump is running for 30 seconds prior tripping the pump due to fan not running
[14 empty] | 15 | TT24434 >= A_HH | 5 |  |  | X |  |  | X |  | Gear Box Temperature Hi-Hi | 2 | 2025-10-28
F24-FN-417 | 2000-F24-PID-PR-10001 | High Pressure Process Water Pump 1 Gearbox Fan | DOL | [5 empty] | 0.57 | X | X | F24-PW-417 START | F24-PW-417 STOPPED for 15 seconds | [11 empty] | 2 | 2025-05-26 | AUTO START/STOP condition changed to the pump starting/stopping from pump SEQ START/STOP
[14 empty] | 1 | F24-FN-417 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-FN-417 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-FN-417 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-FN-417 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-FN-417 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-FN-417 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-FN-417 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F24-FN-418 | 2000-F24-PID-PR-10001 | High Pressure Process Water Pump 2 Gearbox Fan | DOL | [5 empty] | 0.57 | X | X | F24-PW-418 START | F24-PW-418 STOPPED for 15 seconds | [11 empty] | 2 | 2025-05-26 | AUTO START/STOP condition changed to the pump starting/stopping from pump SEQ START/STOP
[14 empty] | 1 | F24-FN-418 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-FN-418 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-FN-418 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-FN-418 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-FN-418 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-FN-418 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-FN-418 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
F24-PW-451 | 2000-F24-PID-PR-10017 | Raw Water Feed Booster Pump 1 | DOL | [5 empty] | 76.5 97.7 | X | X | F24-PW-451 = DUTY Selected AND LIC24431 ≤ P_Lo | F24-PW-451 = DUTY Selected AND LIC24431 ≥ P_HH | [10 empty] | FLC updated to motor nameplate, changed current signal conversion to Comms input and set gain to 0.01 LR 20/03/2026 | 2 | 2025-09-16 | Requires AUT. No action on DCS
[12 empty] | Started Manually By Operator | Stopped Manually By Operator | 1 | F24-PW-451 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-451 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-451 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-451 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-451 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-451 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-451 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | PI24505 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure ≥ A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 9 | Duty F75-PW-489/490/491 Not Running | 3 |  |  | X |  |  | X |  | Logic: (F75-PW-489 AND F75-PW-490 Not Running) OR (F75-PW-489 AND F75-PW-491 Not Running) OR (F75-PW-490 AND F75-PW-491 Not Running) To be controlled by a new PLC set-up and integrated to the existing WSCS Prevent start-up or trip pump if Duty Saline Water Dam #3 pumps are stopped. Reference for Equipment tag: DRG 2000-F00-PFD-PR-40005 | 1 | [7 empty] | VV 28/06/26 ; MOC-591
[14 empty] | 10 | ZSO24507 N_Open | 3 |  |  | X |  |  | X |  | Common Raw Water discharge manual valve is not opened | 0
[14 empty] | 11 | ZSC24507 Closed | 3 |  |  | X |  |  | X |  | Common Raw Water discharge manual valve is closed | 0
[14 empty] | 12 | ZSO24508 Open | 3 |  |  | X |  |  | X |  | Saline Water Pumps discharge manual valve is opened | 0
[14 empty] | 13 | ZSC24508 N_Closed | 3 |  |  | X |  |  | X |  | Saline Water Pumps discharge manual valve is not closed | 0
[14 empty] | 14 | XV24501 Closed | 3 |  |  | X |  |  | X |  | Suction valve closed | 0
[14 empty] | 15 | XV24502 Closed | 3 |  |  | X |  |  | X |  | Discharge valve closed | 0
[14 empty] | 16 | FI24506 ≤ A_LL AND F24-PW-451 RUN | 15 |  |  | X |  |  | X |  | Discharge flow transmitter flow low-low. | 1
[14 empty] | 17 | PI24509 ≤ A_Lo AND F24-PW-451 RUN | 15 |  |  | X |  |  | X |  | Suction pressure transmitter low | 1 | [7 empty] | VV 28/06/26 ; MOC-591
F24-PW-452 | 2000-F24-PID-PR-10017 | Raw Water Feed Booster Pump 2 | DOL | [5 empty] | 76.5 97.7 | X | X | F24-PW-452 = DUTY Selected AND LIC24431 ≤ P_Lo | F24-PW-452 = DUTY Selected AND LIC24431 ≥ P_HH | [10 empty] | FLC updated to motor nameplate, changed current signal conversion to Comms input and set gain to 0.01 LR 20/03/2026 | 2 | 2025-09-16 | Requires AUT. No action on DCS
[12 empty] | Started Manually By Operator | Stopped Manually By Operator | 1 | F24-PW-452 Comms Failure | 0 |  |  |  | X |  |  |  | Duty Saline Dam 3 Pumps 1/2/3 Ref: DRG 75\E\6105-001 to 003 | 0
[14 empty] | 2 | F24-PW-452 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-452 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-452 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-452 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-452 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-452 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | PI24505 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 9 | Duty F75-PW-489/490/491 Not Running | 3 |  |  | X |  |  | X |  | Logic: (F75-PW-489 AND F75-PW-490 Not Running) OR (F75-PW-489 AND F75-PW-491 Not Running) OR (F75-PW-490 AND F75-PW-491 Not Running) To be controlled by a new PLC set-up and integrated to the existing WSCS Prevent start-up or trip pump if Duty Saline Water Dam #3 pumps are stopped. Reference for Equipment tag: DRG 2000-F00-PFD-PR-40005 | 1 | [7 empty] | VV 28/06/26 ; MOC-591
[14 empty] | 10 | ZSO24507 N_Open | 3 |  |  | X |  |  | X |  | Common Raw Water discharge manual valve is not opened | 0
[14 empty] | 11 | ZSC24507 Closed | 3 |  |  | X |  |  | X |  | Common Raw Water discharge manual valve is closed | 0
[14 empty] | 12 | ZSO24508 Open | 3 |  |  | X |  |  | X |  | Saline Water Pumps discharge manual valve is opened | 0
[14 empty] | 13 | ZSC24508 N_Closed | 3 |  |  | X |  |  | X |  | Saline Water Pumps discharge manual valve is not closed | 0
[14 empty] | 14 | XV24503 Closed | 3 |  |  | X |  |  | X |  | Suction valve closed | 0
[14 empty] | 15 | XV24504 Closed | 3 |  |  | X |  |  | X |  | Discharge valve closed | 0
[14 empty] | 16 | FI24506 ≤ A_LL AND F24-PW-452 RUN | 15 |  |  | X |  |  | X |  | Discharge flow transmitter flow low-low. | 1
[14 empty] | 17 | PI24509 ≤ A_Lo AND F24-PW-452 RUN | 15 |  |  | X |  |  | X |  | Suction pressure transmitter low | 1 | [7 empty] | VV 28/06/26 ; MOC-591
F24-PW-453 | 2000-F24-PID-PR-10006 | Scheme Water Booster Pump | DOL | [5 empty] | 15.3033 | X | X | XV12005 OPENED OR XV12259 OPENED | XV12005 CLOSED AND XV12259 CLOSED | [11 empty] | 2 | 2025-05-26 | Removed AUTO STOP/START based on the LIC24456 raw water booster tank level
[14 empty] | 1 | F24-PW-453 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2 | 2025-05-26 | Removed AUTO STOP/START based on the LIC24456 raw water booster tank level
[14 empty] | 2 | F24-PW-453 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-453 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-453 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-453 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-453 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-453 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | F75-PW-481/482/483 Not Running | 3 |  |  | X |  |  | X |  | Prevent start-up or trip pump if all scheme pumps are not running. | 0
[14 empty] | 9 | PI24458 ≥ A_HH AND | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 11 | FI24459 ≤A_LL AND F24-PW-453 RUN | 30 |  |  | X |  |  | X |  | Trip pump if discharge flow <= A_LL | 2 | 2025-07-07 | Updated as per HAZOP Causes F24-09.9.1
F24-PW-406 | 2000-F24-PID-PR-10002 | Raw Water Pump 1 | DOL | [5 empty] | 306.1 373 | X | [13 empty] | FLC changed to match nameplate LR 20/03/2026 | C
[14 empty] | 1 | F24-PW-406 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-406 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-406 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-406 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-406 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-406 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-406 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | PI24442 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 9 | LIC24431 ≤ A_LL | 60 |  |  | X |  |  | X |  | Prevent start-up or trip pump if Raw Water Tank level <= A_LL. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 10 | PI24442 ≤ A_LL AND F24-PW-406 RUN | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure <= A_LL. Bypass if instrument is faulty or for maintenance purposes. | 1
F24-PW-407 | 2000-F24-PID-PR-10002 | Raw Water Pump 2 | DOL | [5 empty] | 306.1 373 | X | [13 empty] | FLC changed to match nameplate LR 20/03/2026 | C
[14 empty] | 1 | F24-PW-407 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-407 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-407 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-407 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-407 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-407 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-407 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | PI24442 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure > A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 9 | LIC24431 ≤ A_LL | 60 |  |  | X |  |  | X |  | Prevent start-up or trip pump if Raw Water Tank level<A_LL. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 10 | PI24442 ≤ A_LL AND F24-PW-407 RUN | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure <= A_LL. Bypass if instrument is faulty or for maintenance purposes. | 1
F24-PW-410 | 2000-F24-PID-PR-10020 | Raw Water Booster Pump | DOL | [5 empty] | 53.8 | X | [14 empty] | 2 | 2025-09-16 | Removed aut. No change on DCS required
[14 empty] | 1 | F24-PW-410 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-410 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-410 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-410 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-410 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C | [7 empty] | VG 07/11/2026: there is no MCC Unhealthy signal
[14 empty] | 6 | F24-PW-410 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-410 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LIC24456 ≤ A_LL | 60 |  |  | X |  |  | X |  | Prevent start-up or trip pump if Raw Water Booster Tank level ≤ A_LL. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 9 | PI24460 >= A_HH | 15 |  |  | X |  |  | X |  | Stop pump if discharge pressure is equal to or greater than pressure High-High setpoint. | 2 | 2025-03-18 | Removed pump running condition
F24-PW-408 | 2000-F24-PID-PR-10003 | LP Gland Seal Water Pump 1 | DOL | [5 empty] | 25.7373 | X | X | F24PW408_ES | [12 empty] | 2 | 2025-10-02 | CR-010
[14 empty] | 1 | F24-PW-408 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-408 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-408 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-408 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-408 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-408 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-408 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | PI24451 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 9 | LIC24431 ≤ A_LL | 60 |  |  | X |  |  | X |  | Prevent start-up or trip pump if Raw Water Tank level <= A_LL. Bypass if instrument is faulty or for maintenance purposes. | 1
F24-PW-409 | 2000-F24-PID-PR-10003 | LP Gland Seal Water Pump 2 | DOL | [5 empty] | 25.7373 | X | X | F24PW409_ES | [12 empty] | 2 | 2025-10-02 | CR-010
[14 empty] | 1 | F24-PW-409 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-409 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-409 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-409 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-409 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-409 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-409 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | PI24451 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 9 | LIC24431 ≤ A_LL | 60 |  |  | X |  |  | X |  | Prevent start-up or trip pump if Raw Water Tank level <= A_LL. Bypass if instrument is faulty or for maintenance purposes. | 1
F24-PW-419 | 2000-F24-PID-PR-10004 | HP Gland Seal Water Pump 1 | DOL | [5 empty] | 125.2 149 | X | X | F24PW419_ES | [11 empty] | FLC updated to motor nameplate LR 20/03/2026 | 2 | 2025-10-02 | CR-010
[14 empty] | 1 | F24-PW-419 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-419 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-419 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-419 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-419 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-419 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-419 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | PI24461 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 9 | LIC24431 ≤ A_LL | 60 |  |  | X |  |  | X |  | Prevent start-up or trip pump if Raw Water Tank level <= A_LL. Bypass if instrument is faulty or for maintenance purposes. | 1
F24-PW-420 | 2000-F24-PID-PR-10004 | HP Gland Seal Water Pump 2 | DOL | [5 empty] | 125.2 149 | X | X | F24PW420_ES | [11 empty] | FLC updated to motor nameplate LR 20/03/2026 | 2 | 2025-10-02 | CR-010
[14 empty] | 1 | F24-PW-420 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F24-PW-420 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 3 | F24-PW-420 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F24-PW-420 E-Stop | 0 |  |  |  | X | X |  |  | Prevent start-up or trip pump if E-Stop is pushed in. | 0
[14 empty] | 5 | F24-PW-420 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F24-PW-420 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F24-PW-420 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | PI24461 ≥ A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure >= A_HH. Bypass if instrument is faulty or for maintenance purposes. | 1
[14 empty] | 9 | LIC24431 ≤ A_LL | 60 |  |  | X |  |  | X |  | Prevent start-up or trip pump if Raw Water Tank level <= A_LL. Bypass if instrument is faulty or for maintenance purposes. | 1
F24-CM-401 | 2000-F24-PID-PR-10007 | Plant Air Compressor 1 | Vendor Package | [5 empty] | 429.326 | X | X | F24CM401_FP1 | F24CM401_FP1 | 1 | YA24500_ALM Active | 5 |  |  |  | X |  |  |  | See 2000-ME024-E02-10001 and 2000-ME024-J02-10001 for Schematic Diagram and IOM | 3 | [7 empty] | AP 2/08/2026 for auto start/stop
See F24CM401_FP1 Misc tab
F24-CM-402 | 2000-F24-PID-PR-10007 | Plant Air Compressor 2 | Vendor Package | [5 empty] | 429.326 | X | X | F24CM401_FP1 | F24CM401_FP1 | 1 | YA24500_ALM Active | 5 |  |  |  | X |  |  |  | See 2000-ME024-E02-10001 and 2000-ME024-J02-10001 for Schematic Diagram and IOM | 3 | [7 empty] | AP 2/08/2026 for auto start/stop
See F24CM401_FP1 Misc tab
F24-CM-403 | 2000-F24-PID-PR-10007 | Plant Air Compressor 3 | Vendor Package | [5 empty] | 429.326 | X | X | F24CM401_FP1 | F24CM401_FP1 | 1 | YA24500_ALM Active | 5 |  |  |  | X |  |  |  | See 2000-ME024-E02-10001 and 2000-ME024-J02-10001 for Schematic Diagram and IOM | 3 | [7 empty] | AP 2/08/2026 for auto start/stop
See F24CM401_FP1 Misc tab
24

## 11. Calculation
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - AIR & WATER SERVICES (F24)
2000-F24-LST-PR-10001
CALCULATIONS
|  |  | Unit | Inputs |  |  |  | Operator Input | Calc. Value | Manual Input | [5 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Description (Software Tag Only) |  | # | Tag | Unit | Description |  |  | Nom | Min | Max | Calculation | Comments | Rev | OK | Date | OK | Date
0 | 0

## 13. Alarm Database
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - AIR & WATER SERVICES (F24)
2000-F24-LST-PR-10001
ALARM DATABASE
[14 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Abbreviated Description (Faceplate) | Type | Alarm State | Alarm Value | Alarm Units | On Delay (sec) | Alarm Masking Condition | Impact | Urgency | Priority | Operator Response | Rev | OK | Date | OK | Date | Comments
PI13456 | 2000-F24-PID-PR-10011 | F13RA404 Discharge | Analogue | A_Lo | 600 | kPa | 5 | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are NOT RUNNING Enable 30s delay on Compressor start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate and initiate compressor changeover if alarm not cleared with fault finding. | 1 |  |  |  |  | Masking removed AP 2/08/2026
PI13456 | 2000-F24-PID-PR-10011 | F13RA404 Discharge | Analogue | A_Hi | 1000 | kPa | 5 | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are NOT RUNNING Enable 30s delay on Compressor start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate and initiate compressor changeover if alarm not cleared with fault finding. | 1 |  |  |  |  | Masking removed AP 2/08/2027
PI13457 | 2000-F24-PID-PR-10011 | F13RA405 Discharge | Analogue | A_Lo | 600 | kPa | 5 | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are NOT RUNNING Enable 30s delay on Compressor start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate and initiate compressor changeover if alarm not cleared with fault finding. | 1 |  |  |  |  | Masking removed AP 2/08/2028
PI13457 | 2000-F24-PID-PR-10011 | F13RA405 Discharge | Analogue | A_Hi | 980 | kPa | 5 | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are NOT RUNNING Enable 30s delay on Compressor start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate and initiate compressor changeover if alarm not cleared with fault finding. | 1 |  |  |  |  | Masking removed AP 2/08/2029
PI13458 | 2000-F24-PID-PR-10012 | F13RA406 Discharge | Analogue | A_Lo | 600 | kPa | 5 | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are NOT RUNNING Enable 30s delay on Compressor start-up | Personnel1: First Aid Injury, Reversible health effects | Immediate (<5 minutes) | High | Operator to investigate and initiate compressor changeover if alarm not cleared with fault finding. | 1 |  |  |  |  | Masking removed AP 2/08/2030
PI13458 | 2000-F24-PID-PR-10012 | F13RA406 Discharge | Analogue | A_Hi | 1000 | kPa | 5 | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are NOT RUNNING Enable 30s delay on Compressor start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate and initiate compressor changeover if alarm not cleared with fault finding. | 1 |  |  |  |  | Masking removed AP 2/08/2031
PI24442 | 2000-F24-PID-PR-10002 | F24PW406/407 Discharge | Analogue | A_LL | 150 | kPa | 5 | Duty F24-PW-406/407 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 1
PI24442 | 2000-F24-PID-PR-10002 | F24PW406/407 Discharge | Analogue | A_Lo | 400 | kPa | 5 | Duty F24-PW-406/407 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 1
PI24442 | 2000-F24-PID-PR-10002 | F24PW406/407 Discharge | Analogue | A_Hi | 600 | kPa | 5 | Duty F24-PW-406/407 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 1
PI24442 | 2000-F24-PID-PR-10002 | F24PW406/407 Discharge | Analogue | A_HH | 750 | kPa | 5 | Duty F24-PW-406/407 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 1
PI24451 | 2000-F24-PID-PR-10003 | F24PW408/409 Discharge | Analogue | A_Lo | 570 | kPa | 5 | Duty F24-PW-408/409 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 1
PI24451 | 2000-F24-PID-PR-10003 | F24PW408/409 Discharge | Analogue | A_Hi | 650 | kPa | 5 | Duty F24-PW-408/409 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 1
PI24451 | 2000-F24-PID-PR-10003 | F24PW408/409 Discharge | Analogue | A_HH | 670 | kPa | 5 | Duty F24-PW-408/409 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 1
PI24461 | 2000-F24-PID-PR-10004 | F24PW419/420 Discharge | Analogue | A_Lo | 1040 | kPa | 5 | Duty F24-PW-419/420 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 1 |  |  |  |  | MOC-707 new setpoints
PI24461 | 2000-F24-PID-PR-10004 | F24PW419/420 Discharge | Analogue | A_Hi | 1340 | kPa | 5 | Duty F24-PW-419/420 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 1 |  |  |  |  | MOC-707 new setpoints
PI24461 | 2000-F24-PID-PR-10004 | F24PW419/420 Discharge | Analogue | A_HH | 1360 | kPa | 5 | Duty F24-PW-419/420 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 1 |  |  |  |  | MOC-707 new setpoints
PI24484 | 2000-F24-PID-PR-10007 | F24RA401 Discharge | Analogue | A_Lo | 600 | kPa | 5 | Mask alarms when F24-CM-401, 402 AND 403 are NOT RUNNING Enable 30s delay on compressor start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate and initiate compressor changeover if alarm not cleared with fault finding. | 1
PI24484 | 2000-F24-PID-PR-10007 | F24RA401 Discharge | Analogue | A_Hi | 1000 | kPa | 5 | Mask alarms when F24-CM-401, 402 AND 403 are NOT RUNNING Enable 30s delay on compressor start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate and initiate compressor changeover if alarm not cleared with fault finding. | 1
PI24509 | 2000-F24-PID-PR-10017 | F24PW451/452 Suction | Analogue | A_Lo | 20 | kPa | 5 | Duty F24-PW-451/452 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to evaluate if Dam 3 Saline Water Pumps are operational. Potential cavitation risk if duty Raw Water Feed Booster Pump is started. | 1
PI24505 | 2000-F24-PID-PR-10017 | F24PW451/452 Discharge | Analogue | A_Lo | 190 | kPa | 5 | Duty F24-PW-451/452 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of low pressure. | 1
PI24505 | 2000-F24-PID-PR-10017 | F24PW451/452 Discharge | Analogue | A_Hi | 240 | kPa | 5 | Duty F24-PW-451/452 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high pressure. | 1
PI24505 | 2000-F24-PID-PR-10017 | F24PW451/452 Discharge | Analogue | A_HH | 260 | kPa | 5 | Duty F24-PW-451/452 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 1
FI24506 | 2000-F24-PID-PR-10017 | F24PW451/452 Discharge | Analogue | A_LL | 250 | m3/h | 5 | Duty F24-PW-451/452 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 1
FI24506 | 2000-F24-PID-PR-10017 | F24PW451/452 Discharge | Analogue | A_Lo | 450 | m3/h | 5 | Duty F24-PW-451/452 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to monitor condition and initiate pump changeover sequence and /or engage with field operator to change manual valve selection to allow saline water addition if alarm not cleared. | 1
FI24506 | 2000-F24-PID-PR-10017 | F24PW451/452 Discharge | Analogue | A_Hi | 580 | m3/h | 5 | Duty F24-PW-451/452 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 1
PI24637 | 2000-F24-PID-PR-10013 | F24RA403 Discharge | Analogue | A_Lo | 600 | kPa | 5 | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are NOT RUNNING Enable 30s delay on Compressor start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate and initiate compressor changeover if alarm not cleared with fault finding. | 1
PI24637 | 2000-F24-PID-PR-10013 | F24RA403 Discharge | Analogue | A_Hi | 1000 | kPa | 5 | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are NOT RUNNING Enable 30s delay on Compressor start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate and initiate compressor changeover if alarm not cleared with fault finding. | 1
PI24457 | 2000-F24-PID-PR-10006 | F24PW453 Suction | Analogue | A_Lo | 37.278 | kPa | 5 | F24-PW-453 NOT RUNNING Enable 10s delay on pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate cause of low pressure | 1
PI24458 | 2000-F24-PID-PR-10006 | F24PW453 Discharge | Analogue | A_Lo | 100 | kPa | 5 | F24-PW-453 NOT RUNNING Enable 10s delay on pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate low pressure | 2 |  |  |  |  | 2025-09-23 | https://pastech-2955.atlassian.net/browse/KAN-2463
PI24458 | 2000-F24-PID-PR-10006 | F24PW453 Discharge | Analogue | A_Hi | 380 | kPa | 5 | F24-PW-453 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate cause of high pressure. | 1
PI24458 | 2000-F24-PID-PR-10006 | F24PW453 Discharge | Analogue | A_HH | 420 | kPa | 5 | F24-PW-453 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 1
PI24460 | 2000-F24-PID-PR-10020 | F24PW410 Discharge | Analogue | A_Lo | 100 | kPa | 5 | F24-PW-410 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of low pressure | 1
PI24460 | 2000-F24-PID-PR-10020 | F24PW410 Discharge | Analogue | A_Hi | 625 | kPa | 5 | F24-PW-410 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate cause of high pressure. | MOC-581
PI24460 | 2000-F24-PID-PR-10020 | F24PW410 Discharge | Analogue | A_HH | 650 | kPa | 5 | F24-PW-410 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | MOC-581
PI72489 | 2000-F24-PID-PR-10016 | F72RA410 Disch Pressure | Analogue | A_Lo | 600 | kPa | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate and initiate compressor changeover if alarm not cleared with fault finding. | 2 | [5 empty] | https://pastech-2955.atlassian.net/browse/KAN-2464
PI72489 | 2000-F24-PID-PR-10016 | F72RA410 Disch Pressure | Analogue | A_Hi | 1000 | kPa | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate and initiate compressor changeover if alarm not cleared with fault finding. | 2 |  |  |  |  | 2025-09-23 | https://pastech-2955.atlassian.net/browse/KAN-2464
PI75428 | 2000-F75-PID-PR-10002 | F24PW403/4/5 Discharge | Analogue | A_Lo | 300 | kPa | 5 | F24-PW-403/404/405 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of low pressure | 1
PI75428 | 2000-F75-PID-PR-10002 | F24PW403/4/5 Discharge | Analogue | A_Hi | 400 | kPa | 5 | F24-PW-403/404/405 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high pressure. | 1
PI75428 | 2000-F75-PID-PR-10002 | F24PW403/4/5 Discharge | Analogue | A_HH | 440 | kPa | 5 | F24-PW-403/404/405 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 1
FI75429 | 2000-F75-PID-PR-10002 | F24PW403/4/5 Discharge | Analogue | A_Lo | 740 | m3/h | 5 | F24-PW-403/404/405 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of low flow. | 1
FI75429 | 2000-F75-PID-PR-10002 | F24PW403/4/5 Discharge | Analogue | A_Hi | 3200 | m3/h | 5 | F24-PW-403/404/405 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high flow. | 1 | [6 empty] | `
LIC24401 | 2000-F24-PID-PR-10001 | F24TK401 Level Ctrl | Analogue | A_LL | 15 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 0
LIC24401 | 2000-F24-PID-PR-10001 | F24TK401 Level Ctrl | Analogue | A_Lo | 20 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor level and organise additional feed as required. | 0
LIC24401 | 2000-F24-PID-PR-10001 | F24TK401 Level Ctrl | Analogue | A_Hi | 80 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to monitor level and reduce feed as required. | 0
LIC24401 | 2000-F24-PID-PR-10001 | F24TK401 Level Ctrl | Analogue | A_HH | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Plant Tripped | Logging | Feed valve tripped to close to prevent overflow of the tank | 0
PIC24415 | 2000-F24-PID-PR-10001 | F24PW401 Dschge Ctrl | Analogue | A_Lo | 200 | kPa | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 0
PIC24415 | 2000-F24-PID-PR-10001 | F24PW401 Dschge Ctrl | Analogue | A_Hi | 370 | kPa | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 0
PIC24415 | 2000-F24-PID-PR-10001 | F24PW401 Dschge Ctrl | Analogue | A_HH | 440 | kPa | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 0
PIC24416 | 2000-F24-PID-PR-10001 | F24PW402 Dschge Ctrl | Analogue | A_Lo | 200 | kPa | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 0
PIC24416 | 2000-F24-PID-PR-10001 | F24PW402 Dschge Ctrl | Analogue | A_Hi | 370 | kPa | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 0
PIC24416 | 2000-F24-PID-PR-10001 | F24PW402 Dschge Ctrl | Analogue | A_HH | 440 | kPa | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 0
PIC24425 | 2000-F24-PID-PR-10001 | F24PW417 Dschge Ctrl | Analogue | A_Lo | 500 | 24 | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 0
PIC24425 | 2000-F24-PID-PR-10001 | F24PW417 Dschge Ctrl | Analogue | A_Hi | 750 | 24 | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 0
PIC24425 | 2000-F24-PID-PR-10001 | F24PW417 Dschge Ctrl | Analogue | A_HH | 900 | 24 | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 0
PIC24426 | 2000-F24-PID-PR-10001 | F24PW418 Dschge Ctrl | Analogue | A_Lo | 500 | kPa | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 0
PIC24426 | 2000-F24-PID-PR-10001 | F24PW418 Dschge Ctrl | Analogue | A_Hi | 750 | kPa | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor condition and initiate pump changeover sequence if alarm not cleared. | 0
PIC24426 | 2000-F24-PID-PR-10001 | F24PW418 Dschge Ctrl | Analogue | A_HH | 900 | kPa | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 0
LIC24456 | 2000-F24-PID-PR-10020 | F24TK402 Level Ctrl | Analogue | A_LL | 15 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Raw Water booster pump tripped. Operator to investigate & organise raw water pump increase flow or scheme water booster pump flow to the tank | 0
LIC24456 | 2000-F24-PID-PR-10020 | F24TK402 Level Ctrl | Analogue | A_Lo | 20 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor level and organise additional water as required. | 0
LIC24456 | 2000-F24-PID-PR-10020 | F24TK402 Level Ctrl | Analogue | A_Hi | 80 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to monitor level and reduce feed as required. | 0
LIC24456 | 2000-F24-PID-PR-10020 | F24TK402 Level Ctrl | Analogue | A_HH | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 0
LIC24431 | 2000-F24-PID-PR-10002 | F24TK501 Level | Analogue | A_LL | 15 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Raw Water pumps tripped. Operator to investigate & organise saline water fast fill if available. | 0
LIC24431 | 2000-F24-PID-PR-10002 | F24TK501 Level | Analogue | A_Lo | 20 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to monitor level and organise additional feed as required. | 0
LIC24431 | 2000-F24-PID-PR-10002 | F24TK501 Level | Analogue | A_Hi | 80 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to monitor level and reduce feed water as required. | 0
LIC24431 | 2000-F24-PID-PR-10002 | F24TK501 Level | Analogue | A_HH | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Immediate (<5 minutes) | High | Operator to check if any feed water still goes to the tank | 1
TI75410A | 2000-F75-PID-PR-10002 | F24PW403 Motor U RTD | Analogue | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75410A | 2000-F75-PID-PR-10002 | F24PW403 Motor U RTD | Analogue | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75410B | 2000-F75-PID-PR-10002 | F24PW403 Motor V RTD | Analogue | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75410B | 2000-F75-PID-PR-10002 | F24PW403 Motor V RTD | Analogue | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75410C | 2000-F75-PID-PR-10002 | F24PW403 Motor W RTD | Analogue | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75410C | 2000-F75-PID-PR-10002 | F24PW403 Motor W RTD | Analogue | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75410D | 2000-F75-PID-PR-10002 | F24PW403 DE Bearing | Analogue | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75410D | 2000-F75-PID-PR-10002 | F24PW403 DE Bearing | Analogue | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75410E | 2000-F75-PID-PR-10002 | F24PW403 NDE Bearing | Analogue | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75410E | 2000-F75-PID-PR-10002 | F24PW403 NDE Bearing | Analogue | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75420A | 2000-F75-PID-PR-10002 | F24PW404 Motor U RTD | Analogue | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75420A | 2000-F75-PID-PR-10002 | F24PW404 Motor U RTD | Analogue | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75420B | 2000-F75-PID-PR-10002 | F24PW404 Motor V RTD | Analogue | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75420B | 2000-F75-PID-PR-10002 | F24PW404 Motor V RTD | Analogue | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75420C | 2000-F75-PID-PR-10002 | F24PW404 Motor W RTD | Analogue | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75420C | 2000-F75-PID-PR-10002 | F24PW404 Motor W RTD | Analogue | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75420D | 2000-F75-PID-PR-10002 | F24PW404 DE Bearing | Analogue | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75420D | 2000-F75-PID-PR-10002 | F24PW404 DE Bearing | Analogue | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75420E | 2000-F75-PID-PR-10002 | F24PW404 NDE Bearing | Analogue | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75420E | 2000-F75-PID-PR-10002 | F24PW404 NDE Bearing | Analogue | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75430A | 2000-F75-PID-PR-10002 | F24PW405 Motor U RTD | Analogue | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75430A | 2000-F75-PID-PR-10002 | F24PW405 Motor U RTD | Analogue | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75430B | 2000-F75-PID-PR-10002 | F24PW405 Motor V RTD | Analogue | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75430B | 2000-F75-PID-PR-10002 | F24PW405 Motor V RTD | Analogue | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75430C | 2000-F75-PID-PR-10002 | F24PW405 Motor W RTD | Analogue | A_Hi | 140 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75430C | 2000-F75-PID-PR-10002 | F24PW405 Motor W RTD | Analogue | A_HH | 150 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75430D | 2000-F75-PID-PR-10002 | F24PW405 DE Bearing | Analogue | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
TI75430D | 2000-F75-PID-PR-10002 | F24PW405 DE Bearing | Analogue | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
TI75430E | 2000-F75-PID-PR-10002 | F24PW405 NDE Bearing | Analogue | A_Hi | 95 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | CRO to report and investigate high temperature from pump motor | 0
FI24459 | 2000-F24-PID-PR-10006 | F24PW453 Disch Flow | Analogue | A_Lo | 2 | m3/h | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate position of spray water solenoid valves | 2 |  |  |  |  | 2025-07-07 | Updated as per HAZOP Causes F24-09.9.1
FI24459 | 2000-F24-PID-PR-10006 | F24PW453 Disch Flow | Analogue | A_LL | 1 | m3/h | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate position of spray water solenoid valves | 2 |  |  |  |  | 2025-07-07 | Updated as per HAZOP Causes F24-09.9.1
TI75430E | 2000-F75-PID-PR-10002 | F24PW405 NDE Bearing | Analogue | A_HH | 100 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate & escalate to maintenance | 0
XI24470 | 2000-F24-PID-PR-10007 | F24CM401 Warning | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of warning via Vendor HMI. | 0
XI24477 | 2000-F24-PID-PR-10007 | F24CM402 Warning | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of warning via Vendor HMI. | 0
XI24489 | 2000-F24-PID-PR-10007 | F24CM403 Warning | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of warning via Vendor HMI. | 0
DPAH24491 | 2000-F24-PID-PR-10007 | F24FI423 Diff. Pressure | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to initiate filter changout and/or duty compressor change. | 0
DPAH24492 | 2000-F24-PID-PR-10007 | F24FI422 Diff. Pressure | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to initiate filter changout and/or duty compressor change. | 0
DPAH24493 | 2000-F24-PID-PR-10007 | F24FI421 Diff. Pressure | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to initiate filter changout and/or duty compressor change. | 0
DPAH24494 | 2000-F24-PID-PR-10007 | F24FI424 Diff. Pressure | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to initiate filter changout and/or duty compressor change. | 0
DPAH24495 | 2000-F24-PID-PR-10007 | F24FI425 Diff. Pressure | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to initiate filter changout and/or duty compressor change. | 0
DPAH24496 | 2000-F24-PID-PR-10007 | F24FI426 Diff. Pressure | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to initiate filter changout and/or duty compressor change. | 0
YA24500 | 2000-F24-PID-PR-10007 | Air Compressor Fire | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 2 |  |  |  |  | 2025-09-10 | KAN-2442
FAL24510 | 2000-F24-PID-PR-10001 | F24PW401 GW Lo Flow | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check gland water system is healthy and inline auto valves are in the correct position. Swap to Standby pump. Advise Field Operator / Maintenance to investigate when practical. | 1
FAL24513 | 2000-F24-PID-PR-10001 | F24PW402 GW Lo Flow | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check gland water system is healthy and inline auto valves are in the correct position. Swap to Standby pump. Advise Field Operator / Maintenance to investigate when practical. | 1
FAL24516 | 2000-F24-PID-PR-10001 | F24PW417 GW Lo Flow | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check gland water system is healthy and inline auto valves are in the correct position. Swap to Standby pump. Advise Field Operator / Maintenance to investigate when practical. | 1
FAL24519 | 2000-F24-PID-PR-10001 | F24PW418 GW Lo Flow | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Check gland water system is healthy and inline auto valves are in the correct position. Swap to Standby pump. Advise Field Operator / Maintenance to investigate when practical. | 1
PAL24651 | 2000-F24-PID-PR-10009 | F17TH401 HU Drive Fire | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
PAL24653 | 2000-F24-PID-PR-10009 | F72TK432 Perimeter Fire1 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
YA24655 | 2000-F24-PID-PR-10009 | F72TK432 Perimeter Fire2 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
PAL24656 | 2000-F24-PID-PR-10009 | Recycle Crushing Fire | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
YA24658 | 2000-F24-PID-PR-10009 | Recycle Crushing Fire2 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
PAL24662 | 2000-F24-PID-PR-10009 | F13CV403 Tail Fire1 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
YA24664 | 2000-F24-PID-PR-10009 | F13CV403 Tail Fire2 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
PAL24671 | 2000-F24-PID-PR-10026 | Elution Heater Fire | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 1 |  |  |  |  | 2025-09-10 | Tag did not match Digital inputs sheet. Updates tag to match
YA24673 | 2000-F24-PID-PR-10015 | Elution Heater Fire2 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 1
PAL24674 | 2000-F24-PID-PR-10015 | F28MUF402/403 Fire | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
YA24676 | 2000-F24-PID-PR-10015 | F28MUF402/403 Fire2 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
PAL24686 | 2000-F24-PID-PR-10022 | F12CV401 Tail Fire | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
YA24690 | 2000-F24-PID-PR-10022 | F12LU401 Fire | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
PAL24693 | 2000-F24-PID-PR-10022 | F12HU402 Fire | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
PAL24681 | 2000-F24-PID-PR-10022 | F12CV402 Head Fire | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
YA24683 | 2000-F24-PID-PR-10022 | F12CV402 Head Fire2 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
PAL24683 | 2000-F24-PID-PR-10022 | F12CV401 Head Fire1 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
YA24685 | 2000-F24-PID-PR-10022 | F12CV402 Head Fire2 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
PAL24711 | 2000-F24-PID-PR-10023 | F13CV403 Head Fire1 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
YA24713 | 2000-F24-PID-PR-10023 | F13CV403 Head Fire2 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
PAL24701 | 2000-F24-PID-PR-10023 | SAG Mill Lube Fire1 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
YA24703 | 2000-F24-PID-PR-10023 | SAG Mill Lube Fire2 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
PAL24706 | 2000-F24-PID-PR-10023 | Ball Mill Lube Fire1 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
YA24708 | 2000-F24-PID-PR-10023 | Ball Mill Lube Fire2 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
PAL24715 | 2000-F24-PID-PR-10023 | F13CV405 Fire1 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
YA24717 | 2000-F24-PID-PR-10023 | F13CV405 Fire2 | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 0
YA24678 | 2000-F24-PID-PR-10023 | F13SC401 Fire | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 1
XA24678B | 2000-F24-PID-PR-10023 | F13SC401 FIP Fault | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire Panel Fault Escalate and resport to maintenance to check the fire indicator panel | 1
YA24679 | 2000-F24-PID-PR-10023 | F13SC403 Fire | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 1
XA24679B | 2000-F24-PID-PR-10023 | F13SC403 FIP Fault | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire Panel Fault Escalate and resport to maintenance to check the fire indicator panel | 1
YA24673 | 2000-F24-PID-PR-10026 | F22SC421 Fire | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Fire Alarm in the Area Associated equipment tripped/stopped to contain and prevent fire. Operator to immediately escalate to the Shift Supervisor/ERT and advise all personnel in the area | 1
XA24673B | 2000-F24-PID-PR-10026 | F22SC421 FIP Fault | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Fire Panel Fault Escalate and resport to maintenance to check the fire indicator panel | 1
XA75404 | 2000-F75-PID-PR-10002 | F24PW403 Dry Run | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Saline Water Pump 1 tripped. Operator to check status of the suction line/ pump flow | 2
XA75414 | 2000-F75-PID-PR-10002 | F24PW404 Dry Run | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Saline Water Pump 1 tripped. Operator to check status of the suction line/ pump flow | 2
XA75424 | 2000-F75-PID-PR-10002 | F24PW405 Dry Run | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Saline Water Pump 1 tripped. Operator to check status of the suction line/ pump flow | 2
24RIO001_PS1 | N/A | F24RIO001 PS1 24VDC HTY | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
24RIO001_PS2 | N/A | F24RIO001 PS224VDC HTY | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
24RIO002_PS1 | N/A | F24RIO002 PS1 24VDC HTY | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
24RIO002_PS2 | N/A | F24RIO002 PS2 24VDC HTY | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 0
24RIO100_PS1 | N/A | F24RIO100 PS1 24VDC HTY | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2
24RIO001_PS2 | N/A | F24RIO100 PS2 24VDC HTY | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2
24SW024_PS | N/A | F24SW024 ACBSHUNT 24V OK | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2 |  |  |  |  | 23/010/2025
24SW024_AF | N/A | F24SW024 ARC FLASH | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2
24SW024_TRP | N/A | F24SW024 CB TRIP | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2
24SW024_SD | N/A | F24SW024 INC SURGEDIV OK | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2
24TR024_OTH | N/A | F24SW024 TR OILTEMP HI | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
24TR024_WTH | N/A | F24SW024 TR WINDTEMP HI | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to investigate | 2
24TR024_LSL | N/A | F24SW024 TR OILLVL LO | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Electrician to investigate
PAL24433 | 2000-F24-PID-PR-10001 | F24PW417 Gearbox Pres Lo | Digital | Alarm |  |  | 30 | F24-PW-453 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Electrician to investigate | 2 |  |  |  |  | 2025-10-28 | New Instrument Added
PAL24435 | 2000-F24-PID-PR-10001 | F24PW418 Gearbox Pres Lo | Digital | Alarm |  |  | 30 | F24-PW-453 NOT RUNNING Enable 10s delay on pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Electrician to investigate | 2 |  |  |  |  | 2025-10-28 | New Instrument Added
TI24410 | 2000-F24-PID-PR-10001 | F24PW401 Gearbox Temperature | Analogue | A_Hi | 85 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Electrician to investigate | 2 |  |  |  |  | 2025-10-28 | New Instrument Added
TI24410 | 2000-F24-PID-PR-10001 | F24PW401 Gearbox Temperature | Analogue | A_HH | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2 |  |  |  |  | 2025-10-28 | New Instrument Added
TI24420 | 2000-F24-PID-PR-10001 | F24PW402 Gearbox Temperature | Analogue | A_Hi | 85 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Electrician to investigate | 2 |  |  |  |  | 2025-10-28 | New Instrument Added
TI24420 | 2000-F24-PID-PR-10001 | F24PW402 Gearbox Temperature | Analogue | A_HH | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2 |  |  |  |  | 2025-10-28 | New Instrument Added
TI24432 | 2000-F24-PID-PR-10001 | F24PW417 Gearbox Temperature | Analogue | A_Hi | 85 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Electrician to investigate | 2 |  |  |  |  | 2025-10-28 | New Instrument Added
TI24432 | 2000-F24-PID-PR-10001 | F24PW417 Gearbox Temperature | Analogue | A_HH | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2 |  |  |  |  | 2025-10-28 | New Instrument Added
TI24434 | 2000-F24-PID-PR-10001 | F24PW418 Gearbox Temperature | Analogue | A_Hi | 85 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Electrician to investigate | 2 |  |  |  |  | 2025-10-28 | New Instrument Added
TI24434 | 2000-F24-PID-PR-10001 | F24PW418 Gearbox Temperature | Analogue | A_HH | 90 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2 |  |  |  |  | 2025-10-28 | New Instrument Added

## 12. Misc
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - AIR & WATER SERVICES (F24)
2000-F24-LST-PR-10001
MISC. INSTRUMENTS AND CONTROLLERS
[10 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Description | Normal State | Alarm State | Hardwired (y/n) | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date | Comments
F24CM401_FP1 | 2000-F24-PID-PR-10007 | Duty Compressor Select | Operator Selection | No alarm | N | 0 |  | Include a graphic to select lead, lag and standby duty for the air compressors (F24-CM-401, F24-CM-402, F24-CM-403): DUTY LEAD DUTY LAG STANDBY IF 2x STANDBY Compressors are selected, THEN the remaining Compressor must be DUTY LEAD. Note that normal configuration for the compressors operate with 1 Lead, 1 Lag, and 1 Standby unit. Duty Selection for compressors will enable the following output signal/status: F24-CM-401: IF DUTY LEAD is selected THEN HS24497REM Activated AND HS24466LD ON IF DUTY LAG is selected THEN HS24497REM Activated, HS24466LD OFF IF STANDBY is selected THEN HS24497REM Activated Remote START/STOP command HS24467STT is available to start/stop the compressor F24-CM-402: IF DUTY LEAD is selected THEN HS24498REM Activated AND HS24473LD ON IF DUTY LAG is selected THEN HS24498REM Activated AND HS24473LD OFF IF STANDBY is selected THEN HS24498REM Activated Remote START/STOP command HS24474STT is available to start/stop the compressor. F24-CM-403: IF DUTY LEAD is selected THEN HS24499REM Activated AND HS24485LD ON IF DUTY LAG is selected THEN HS24499REM Activated, HS24485LD OFF IF STANDBY is selected THEN HS24499REM Activated Remote START/STOP command HS24486STT is available to start/stop the compressor STANDBY compressors when started will be re-assigned as DUTY LEAD OR DUTY LAG and will follow the above output signals The Atlas Copco PLC will control the pressure setpoint that the compressors run to. See Digital Outputs sheet for further details. | 2 |  |  |  |  | 2025-09-16 | Deleted CM-402 comment "ANDHS24473LD OFF". Not required. No action on DCS
YA24658_ALM | 2000-F24-PID-PR-10009 | YD24658A/B Alarm | Inactive |  | N |  |  | Logic: YD24658A AND YD24658B send their signal to the same control tag YA24658 YD24658A OR YD24658B activates YA24658 to Alarm | 1
YA24676_ALM | 2000-F24-PID-PR-10015 | YD24676A/B/C Alarm | Inactive |  | N |  |  | Logic: YD24676A AND YD24676B AND YD24676C send their signal to the same control tag YA24676 YD24676A OR YD24676B OR YD24676C activates YA24676 to Alarm | 1
YA24703_ALM | 2000-F24-PID-PR-10023 | YD24703A/B Alarm | Inactive |  | N |  |  | Logic: YD24703A AND YD24703B send their signal to the same control tag YA24703 YD24703A OR YD24703B activates YA24703 to Alarm | 0
YA24708_ALM | 2000-F24-PID-PR-10023 | YD24708A/B Alarm | Inactive |  | N |  |  | Logic: YD24708A AND YD24708B send their signal to the same control tag YA24708 YD24708A OR YD24708B activates YA24708 to Alarm | 0
YA24500_ALM | 2000-F24-PID-PR-10007 | YD24500A/B Alarm | Inactive |  | N |  |  | Logic: YD24500A AND YD24500B send their signal to the same control tag YA24500 YD24500A OR YD24500B activates YA24708 to Alarm if YA24500 is active, set all compressors to stop ( HS24467STT , HS24468STT & HS24469STT) | 2 |  |  |  |  | 2025-07-29 |  | NOVD137 (CR-011) Change request to trip Air Compressor when fire detected
PIC24415SPP | 2000-F24-PID-PR-10001 | F24PW401 Start SP | Setpoint |  | N |  |  | Operator-adjustable start-up setpoint variable for Mill Water Pump 1. PIC24415SPP [=] kPa (Engineering Units). Configurable Range: 300 - 500 kPa. Setpoint used in F24-SEQ-0001. This will set the SV of PIC24415 when changed to AUTO Range to be confirmed during commissioning. | 1 | [6 empty] | Verified range and set in Sequence - no actual faceplate or tag with this number just a settable sequence constant
PIC24416SPP | 2000-F24-PID-PR-10001 | F24PW402 Start SP | Setpoint |  | N |  |  | Operator-adjustable start-up setpoint variable for Mill Water Pump 2. PIC24416SPP [=] kPa (Engineering Units). Configurable Range: 300 - 500 kPa. Setpoint used in F24-SEQ-0001. This will set the SV of PIC24415 when changed to AUTO Range to be confirmed during commissioning. | 1 | [6 empty] | Verified range and set in Sequence - no actual faceplate or tag with this number just a settable sequence constant
PIC24425SPP | 2000-F24-PID-PR-10001 | F24PW417 Start SP | Setpoint |  | N |  |  | Operator-adjustable start-up setpoint variable for HP Process Water Pump 1. PIC24425SPP [=] kPa (Engineering Units). Configurable Range: 550 - 700 kPa. Setpoint used in F24-SEQ-0003. This will set the SV of PIC24425 when changed to AUTO Range to be confirmed during commissioning. | 1 | [6 empty] | Verified range and set in Sequence - no actual faceplate or tag with this number just a settable sequence constant
PIC24426SPP | 2000-F24-PID-PR-10001 | F24PW418 Start SP | Setpoint |  | N |  |  | Operator-adjustable start-up setpoint variable for HP Process Water Pump 1. PIC24426SPP [=] kPa (Engineering Units). Configurable Range: 550 - 700 kPa. Setpoint used in F24-SEQ-0003. This will set the SV of PIC24426 when changed to AUTO Range to be confirmed during commissioning. | 1 | [6 empty] | Verified range and set in Sequence - no actual faceplate or tag with this number just a settable sequence constant
F24PW408_ES | 2000-F24-PID-PR-10003 | F24PW408 Emergency Start | Logic |  | N |  |  | if F23-GE-123 = running and F23SW123Q2CL = active and F24PW408 = duty: pulse F24PW408 to auto and pulse F24PW408 start | 2 |  |  |  |  | 2025-10-02 | CR-010
F24PW409_ES | 2000-F24-PID-PR-10003 | F24PW409 Emergency Start | Logic |  | N |  |  | if F23-GE-123 = running and F23SW123Q2CL = active and F24PW409 = duty: pulse F24PW409 to auto and pulse F24PW409 start | 2 |  |  |  |  | 2025-10-02 | CR-010
F24PW419_ES | 2000-F24-PID-PR-10004 | F24PW419 Emergency Start | Logic |  | N |  |  | if F23-GE-123 = running and F23SW123Q2CL = active and F24PW419 = duty: pulse F24PW419 to auto and pulse F24PW419 start | 2 |  |  |  |  | 2025-10-02 | CR-010
F24PW420_ES | 2000-F24-PID-PR-10004 | F24PW420 Emergency Start | Logic |  | N |  |  | if F23-GE-123 = running and F23SW123Q2CL = active and F24PW420 = duty: pulse F24PW420 to auto and pulse F24PW420 start | 2 |  |  |  |  | 2025-10-02 | CR-010
14 | 14

## RiskMatrix
Consequence | None | Personnel1: First Aid Injury, Reversible health effects | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Environmental2: Minor on-site environmental impact, reportable to regulators. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness. | Environmental3: Moderate environmental impacts, extends beyond site boundary or regulatory violations with fines. | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k
Not Urgent (>30 minutes) | No Alarm | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Low \ Review the alarm for urgency | Low \ Review the alarm for urgency | Low \ Review the alarm for urgency | High \ Review the alarm for urgency | High \ Review the alarm for urgency | High \ Review the alarm for urgency
Prompt (>15 to <30 minutes) | No Alarm | Low | Low | Low | Low | Low | Low | High | High | High
Rapid (>5 to <15 minutes) | No Alarm | Low | Low | Low | High | High | High | Urgent | Urgent | Urgent
Immediate (<5 minutes) | No Alarm | High | High | High | Urgent | Urgent | Urgent | Invalid | Invalid | Invalid
Plant Tripped | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Logging | Logging | Logging | Logging | Logging | Logging | Logging | Logging | Logging
|  | Priority | Description
|  | Low | Indicates that the process in no longer within nominal operational limits and a prompt operator intervention is required before the process becomes unrecoverable, resulting in minor safety, environmental or financial impacts.
|  | High | Indicates that the process is no longer within nominal operational limits and a rapid operator intervention is required before the process becomes unrecoverable resulting in serious safety, environmental or financial impacts.
|  | Urgent | Indicates that the process is no longer within nominal operational limits and a immediate operator intervention is required before the process becomes unrecoverable resulting in catastrophic safety, environmental or financial impacts.
|  | Logging | Indicates that the process or equipment has reached a unrecoverable or inoperable state and has been stopped. Logging alarms are for post event investigation and are not to enunciate to the operator.
|  | No Alarm | This condition does not meet the minimum requirements required under ISA 18.2 for a alarm to be generated. Including being a abnormal event\condition, requiring an operator response, undertaking a defined action within a defined time limit and having a defined consequences of no action is taken.
|  | Invalid | This senario is likely to be already unrecovreable and as such is unacceptable. Additional solutions such as automated repsonses, re-engeering or modifications the the process \ equipment is required.

## ReferenceList
Consequences
None
Personnel1: First Aid Injury, Reversible health effects
Environmental1: Localised environmental impact, contained, with no regulatory reporting
Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000
Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment.
Environmental2: Minor on-site environmental impact, reportable to regulators.
Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k.
Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness.
Environmental3: Moderate environmental impacts, extends beyond site boundary or regulatory violations with fines.
Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k
Type
Analogue
Digital
Alarm State
High-High
High
Low
Low-Low
Active