## Equipment list
Rev | Equip. Number | Equipment Name | Qty | Description | Make | Model | Supplied By | Installed By | Comments | Page
0 | F13-SR-004 | Recycle Crushing 415V Switchroom | 1 | Transportable switchroom complete with 1.8m legs and landings, transported to site 600kms on sealed roads. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero | Refer 2000-F00-DSH-EL-11001 | 2
0 | - | Recycle Crushing 415V Switchroom Landings and Stairs | 1 | Equipment Landing to be structural steel baseframe complete with 1.8m legs, designed to support heaviest piece of equipment to be installed in room. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero |  | 2
0 | - | Recycle Crushing LV Switchroom Transformer cubicle | 1 | Separate dry transformer enclosure with removable wall panel and personnel access door Fortress key locked (Keyed alike) with 33kV feeder earth switch on F00-SW-010 33kV switchgear | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Access to transformer cubicle is only possible with 33kV Feeder isolated and earthed. Switchroom manufacturer to coordinate Fortress keys with TEKSAL. | 2
0 | - | Recycle Crushing LV Switchroom Transformer cubicle | 1 | TRANSFORMER ENCLOSURE F13-TR-014 33,000/433 VOLTS (Modify to suit) DANGER – HIGH VOLTAGE (with the lightning bolt sign) NO UNAUTHORISED ACCESS – ENSURE SUPPLY IS ISOLATED AND EARTHED PRIOR TO ENTRY ISOLATE AT F00-SW-010, PANEL BXX (BXX being the 33kV panel/tier number) | Switchroom Vendor |  | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Signage to be placed on outside of transformer enclosure | 2
0 | F13-TR-014 | Recycle Crushing 415V MCC Transformer | 1 | 33/0.433kV, 2500kVA, ANAF | Siemens | 33/0.433kV 2500kVA | Primero | Switchroom/MCC Vendor | Vendor to remove wheels and secure transformer once installed. Wheels to be stored securely within the transformer room. Vendor to bolt down/brace for transport. Refer transformer GAs. | 2
0 | F13-SW-014 | Recycle Crushing 415V MCC | 1 | Demountable Form 4a double sided 415V Switchboard, 4000A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Vendor to install free issued network switches in MCC Refer datasheet 2000-F00-DSH-EL-11008 | 2
0 | F13-SW-114 | Recycle Crushing Esential 415V Switchboard | 1 | Demountable Form 4a single sided 415V Essential Switchboard, 400A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Refer datasheet 2000-F00-DSH-EL-11012 | 2
0 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | 1 | 415V 3Ø 250A DB. Fitted with incoming isolator, PE Cell circuit (night/day), Auto / Manual selector, Emergency light test controller, Rapidtest RCD test units, Lighting Contactors, air conditioner Contactors and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-EL-10025 & 2000-F00-STD-EL-10022; Switchroom Vendor to calculate number of required poles including the number of circuits for Air conditioners, 20% loaded Spare circuit breakers and 20% spare space. | 2
0 | F13-DB-204 | Recycle Crushing 415V Switchroom 240V UPS Distribution Board | 1 | 240VAC 250A UPS DB. Fitted with incoming isolator and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-EL-10027. Switchroom Vendor to calculate number of required poles including 20% loaded Spare circuit breakers and 20% spare space. | 2
0 | F13-UPS-004 | Recycle Crushing 415V Switchroom 240VAC UPS | 1 | LV Switchroom 240V AC, 10kVA UPS, free-standing. 8 hours autonomy time. 3-Phase in / 1-Phase Out. | Riello | S3M 10 XTD A0 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 10kVA/10kW Sentryum Xtend UPS - 3 Phase in- 1 out. Vendor to secure wheels once installed. Vendor to bolt down/brace for transport. W: 440mm, D: 840mm, H: 1320mm, Weight: 103Kg | 2
0 | F13-BA-004 | Recycle Crushing 415V Switchroom 240VAC UPS Battery Bank | 1 | UPS Battery Cabinet w/ 40 x 55Ah batteries | Riello | BB 1900 480-V5 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 480V Extension Battery Cabinet with 40 x 55Ah Long life batteries. Cabinet shipped empty with the batteries packed separately W: 860mm, D: 800mm, H: 1900mm, Weight: 900Kg | 2
0 | - | Recycle Crushing 415V Switchroom 240VAC UPS Ethernet Card | 1 | Netman UPS Ethernet Card | Riello | Netman 208 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Supplied and installed into UPS by Switchroom Vendor | 2
0 | - | Recycle Crushing 415V Switchroom 240VAC UPS Dry Contact Relay Card | 1 | Multicom Configurable Slot In Relay Card, 3 Inputs & 8 Outputs | Riello | Mulitcom 392 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Supplied and installed into UPS by Switchroom Vendor | 2
0 | F13UPS004-ISL | Recycle Crushing 415V Switchroom 240VAC UPS Maintenance Bypass Switch | 1 | External Wall-mount 3-Position Rotary Type bypass switch. | Riello | WABS 0063A-31H | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Wall mounted rotary style bypass switch. 3Ph in/1Ph out, 10kVA. Dimensions: 400 x 300 x 210mm | 2
0 | F13CC401-VS | Recycle Crusher C LV VSD | 1 | Allen-Bradley 375 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20-750- 20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G11BC1K0JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F13CC402-VS | Recycle Crusher D LV VSD | 1 | Allen-Bradley 375 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20-750- 20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G11BC1K0JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F13CV403-VS | SAG Mill Feed Conveyor LV VSD | 1 | Allen-Bradley 355 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20-750- 20COMM + 20-COMM-M, 20-750-2262C-2R, 20-750-ENC-1 | Allen-Bradley | 20G1ABC770JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F13CV405-VS | Recycle Conveyor 2 LV VSD | 1 | Allen-Bradley 75 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750- APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 20-750-2262C-2R, 20-750-ENC-1 | Allen-Bradley | 20G1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F13CV406-VS | Recycle Crusher Discharge Conveyor LV VSD | 1 | Allen-Bradley 45 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F5, 20-HIM-A6, 20-750- APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 20-750-2262C-2R, 20-750-ENC-1 | Allen-Bradley | 20G11NC104JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F13FA411-VS | Crushed Ore Reclaim Feeder 1 LV VSD | 1 | Allen-Bradley 280 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20-750- 20COMM + 20-COMM-M, 20-750-2262C-2R, 20-750-ENC-1 | Allen-Bradley | 20G1ABC650JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F13FA412-VS | Crushed Ore Reclaim Feeder 2 LV VSD | 1 | Allen-Bradley 280 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20-750- 20COMM + 20-COMM-M, 20-750-2262C-2R, 20-750-ENC-1 | Allen-Bradley | 20G1ABC650JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F13FA414-VS | Emergency Feeder LV VSD | 1 | Allen-Bradley 90 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750- APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 20-750-ENC-1 | Allen-Bradley | 20F1ANC205JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F13FV401-VS | Recycle Crusher C Feeder LV VSD | 1 | Allen-Bradley 9.62 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F3, 20-HIM-A6, 20-750- APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20F11NC030JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F13FV402-VS | Recycle Crusher D Feeder LV VSD | 1 | Allen-Bradley 9.62 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F3, 20-HIM-A6, 20-750- APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20F11NC030JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
1 | F13-HF-014 | Recycle Crushing 415V MCC Active Harmonic Filter | 1 | Schneider AccuSine PCS+ 200A Active Harmonic Filter, 380-480VAC, IP54. | Schneider | PCSP200D5IP54 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Vendor to supply and install as per OEM recommendations including upstream breaker and CT's | 3
3 | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | 1 | HMI Control Panel Mounted on Switchroom Wall | Rema Tiptop | Rip Prevent+ | Primero | Switchroom/MCC Vendor |  | 3
0 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | 1 | Communications Rack, Free Standing 19", 42U, 1000mm deep, Mesh door, Lift Off Side Panels. Fitted with 10 way 240VAC plug power distribution panel, wire management covers, shelves and cage nuts. Fitted out with FOBOTs (vendor supplied), DIN rail adapter (vendor supplied), and network switches (free issued). | Rittal | TS IT Enclosure (P/N 5514.110) + Accessories | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-IC-10101 | 3
1 | F13COM004-JB | Recycle Crushing 415V Switchroom Communications Rack 240VAC UPS Junction Box | 1 | Junction box mounted on the rear of the communications rack. All 240VAC UPS powered non-RCD Protected outlets shall be red with a "Warning. Socket not RCD Protected" Warning label. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Junction box for PDU Rail | 3
0 | F13-FOB-301 | Recycle Crushing 415V Switchroom Fibre Optic Breakout Tray | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | 3
0 | F13-FOB-302 | Recycle Crushing 415V Switchroom Fibre Optic Breakout Tray | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | 3
0 | F13-FOB-303A/B | Recycle Crushing 415V Switchroom RIO Circuit Fibre Optic Breakout Ring 1 Tray #1 | 1 | 2 X 12C SMOF Capacity FOBOT C/W Splice hardware & 1-6 LC Duplex Faceplate (LHS) + 1-6 LC Duplex Faceplate (RHS) | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. One FOBOT with two 12C faceplates. Vendor to label each side as per equipment number and name. | 3
0 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | 1 | Custom Built Panel. Indoor, Mild Steel. Contains DCS hardware, power supply, MCBs and marshalling terminals. | Fabricated Panel | Custom | Primero | Switchroom/MCC Vendor |  | 3
0 | F13SR004-LCS | Recycle Crushing 415V Switchroom Emergency Shutdown | 1 | Switchroom Emergency Shutdown C/w shroud or lift-up flap and labelling | Fabricated Panel | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | With E34 Red 40mm Mushroom pushbutton (P/N E34LB2), and 2 off 2 N/O Contact Blocks (10250T2). Refer 2000-F00-STS-EL-10011 Section 4.19. | 3
0 | F13-FIP-004 | Recycle Crushing 415V Switchroom Fire Indicator Panel | 1 | Fire Indicator Panel c/w full installation, wiring, certification, testing and commissioning. HVAC trip upon alarm. FIP shall include SMOF modem(s) for connection to site-wide fire system network. | Wormald | Vigilant 8 Zone F3200 Conventional SHCIE FIP | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Rated to operate in 50C ambience temperature | 3
0 | F13FIP004-XE1 | Recycle Crushing 415V Switchroom VESDA Panel | 1 | VESDA Panel c/w full installation, wiring, certification, testing and commissioning.Alarm and fault signals to fire panel. | Xtralis | VESDA LaserPlus Scanner 12 relay VLS300 ASD system | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Rated to operate in 50C ambience temperature | 3
0 | F13FIP004-XE2 | Recycle Crushing 415V Switchroom Manual Call Points | VTA | Fire system Manual Call points (internal and external) as required by Australian Standards | Wormald | Manual Call Points | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Manual call points shall be tagged in sequential order | 3
0 | F13FIP004-XE3 | Recycle Crushing 415V Switchroom Smoke Detector | VTA | Fire system smoke detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order | 3
0 | F13FIP004-XE4 | Recycle Crushing 415V Switchroom Heat Detector | VTA | Fire system heat detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order | 3
0 | F13FIP004-UA | Recycle Crushing 415V Switchroom External Alarm Bells | VTA | Fire system alarm bells as required by Australian Standards | Wormald | External Sounder / Red Strobe | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Alarm sirens shall be tagged in sequential order | 3
0 | F13FIP004-XE5 | Recycle Crushing 415V Switchroom Gas Suppression System (Inergen) | 1 | Inergen gas suppression system incl. all valves and pipework, gas cylinders placed inside switchroom, refer to Switchroom General Arrangement | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Recycle Crushing 415V Switchroom Fire Extinguishers | VTA | 5kg dry powder fire extinguishers complete with wall mount and signage. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Recycle Crushing 415V Switchroom Automatic External Defibrillator | 1 | Automatic external defibrillator complete with wall-mounted cabinet. | Physio Control | Lifepak Defibrillator CR2 Fully Automatic | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Recycle Crushing 415V Switchroom LV Rescue Kit | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Recycle Crushing 415V Switchroom CPR Signage | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Recycle Crushing 415V Switchroom HVAC Controller | VTA | Wall mounted Air Conditioner Controller, with relay contacts for Faulty & Healthy | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | One wall mounted controller to control all A/C's per room (One per transformer room, LV room, HV room). | 3
0 | F13-AC-4XX | Recycle Crushing 415V Switchroom Air Conditioners | VTA | High Wall split system, single phase, MULTIPLE (N+1 reqd) with drip trays if necessary | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. AC units shall be tagged in Numerical Order eg. F13-AC-401, F13-AC-402 etc | 3
0 | F13AC4XX-ISL | Recycle Crushing 415V Switchroom Air Conditioner Isolators | VTA | Field isolator, one per split system AC | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Isolators shall be tagged with the respective AC equipment number (e.g. F13AC4xx-ISL etc) | 3
0 | - | Recycle Crushing 415V Switchroom Normal Light Fittings | 1 lot | Lighting to meet National Construction Code | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | 3
0 | - | Recycle Crushing 415V Switchroom Emergency Light Fittings | 1 lot | Lighting to meet National Construction Code; C/w built in battery pack. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | 3
0 | UT13045 | F13-SR-004 Recycle Crushing 415V Switchroom Temperature/Humidity Transmitter | 1 | 415V Switchroom Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | 3
0 | UT13046 | F13-SR-004 Recycle Crushing 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | 1 | Transformer Room Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | 3
0 | F13-PE-004 | Recycle Crushing 415V Switchroom Photo-electric cell | 1 | Switchroom Photo-electric cell | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | PE Cell - 1 per building. Vendor to position | 3
0 | F13SW014-LCS | Recycle Crushing 415V MCC Remote Switching Panel | 1 | LV MCC Incomer Remote Switching Panel | NHP | TemRack LCS | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | 1 | External to Room: 50 x 6.3mm Tinned Flat Copper Bus bar mounted on insulated standoffs under switchroom floor. Drilled/punch 12mm diameter holes suitable for connection of all internal equipment earth cables to meet requirements of cable schedule. To have spare capacity for connection of an additional 4 x 120mm2 conductors and 4 x 70mm2 conductors, as a minimum. | GVK or similar | - | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | F13TR014-EB01 | Recycle Crushing 415V Switchroom Transformer Earth bar | 1 | 50 x 6.3mm Tinned Flat Copper Bus bar mounted on insulated standoffs on Transformer. | Generic |  | Transformer Vendor | Transformer Vendor |  | 4
0 | F13SW014-EB01 | Recycle Crushing 415V MCC Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on insulated standoffs inside MCC. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | F13SW114-EB01 | Recycle Crushing Esential 415V Switchboard Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on insulated standoffs inside MCC. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4

## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Siz | eInsulation(kV) | No. of Cores / Pair | Conductor | Construction | Sheath(Preferred colou | Installation | Cable Description | Supplied By | Installed By | Revision | Comments | Page
F13SW014-P1-R | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-P1-W | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-P1-B | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-P2-R | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-P2-W | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-P2-B | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-P3-R | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-P3-W | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-P3-B | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-P4-R | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-P4-W | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-P4-B | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-N-1 | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-N-2 | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-N-3 | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW014-N-4 | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | 500mm2 0.6/1kV 1C Cu XLPE- 110/PVC Flex Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13SW114-P1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13-SW-114 | Recycle Crushing Esential 415V Switchboard | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 120mm2 0.6/1kV 4C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 1 |  | 5
F13SW114-P2 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13-SW-114 | Recycle Crushing Esential 415V Switchboard | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 120mm2 0.6/1kV 4C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 1 |  | 5
F13CC401VS-P1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13CC401-VS | Recycle Crusher C LV VSD | Recycle Crushing 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 240mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13CC401VS-P2 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13CC401-VS | Recycle Crusher C LV VSD | Recycle Crushing 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 240mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13CC402VS-P1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13CC402-VS | Recycle Crusher D LV VSD | Recycle Crushing 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 240mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13CC402VS-P2 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13CC402-VS | Recycle Crusher D LV VSD | Recycle Crushing 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 240mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13CV403VS-P1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13CV403-VS | SAG Mill Feed Conveyor LV VSD | Recycle Crushing 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 240mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13CV403VS-P2 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13CV403-VS | SAG Mill Feed Conveyor LV VSD | Recycle Crushing 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 240mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13FA411VS-P1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FA411-VS | Crushed Ore Reclaim Feeder 1 LV VSD | Recycle Crushing 415V Switchroom | 150 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 150mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13FA411VS-P2 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FA411-VS | Crushed Ore Reclaim Feeder 1 LV VSD | Recycle Crushing 415V Switchroom | 150 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 150mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F13FA412VS-P1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FA412-VS | Crushed Ore Reclaim Feeder 2 LV VSD | Recycle Crushing 415V Switchroom | 150 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 150mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F13FA412VS-P2 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FA412-VS | Crushed Ore Reclaim Feeder 2 LV VSD | Recycle Crushing 415V Switchroom | 150 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 150mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F13CV405VS-P1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13CV405-VS | Recycle Conveyor 2 LV VSD | Recycle Crushing 415V Switchroom | 95 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 95mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F13FA414VS-P1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FA414-VS | Emergency Feeder LV VSD | Recycle Crushing 415V Switchroom | 150 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 150mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F13FV401VS-P1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FV401-VS | Recycle Crusher C Feeder LV VSD | Recycle Crushing 415V Switchroom | 10 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | 10mm2 0.6/1kV 3C+E Cu PVC/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F13FV401JB-P1 | F13FV401-VS | Recycle Crusher C Feeder LV VSD | Recycle Crushing 415V Switchroom | F13FV401-JB | Recycle Crusher C Feeder TOL JB | Recycle Crushing 415V Switchroom | 10 | 0.6/1 | 3C+3E | Cu | PVC/SCN/PVC | Black | Ladder - Subframe | 10mm2 0.6/1kV 3C+3E Cu PVC/SCN/PVC Black | Switchroom Vendor | Switchroom Vendor | 4 |  | 6
F13FV402VS-P1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FV402-VS | Recycle Crusher D Feeder LV VSD | Recycle Crushing 415V Switchroom | 10 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | 10mm2 0.6/1kV 3C+E Cu PVC/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F13FV402JB-P1 | F13FV402-VS | Recycle Crusher D Feeder LV VSD | Recycle Crushing 415V Switchroom | F13FV402-JB | Recycle Crusher C Feeder TOL JB | Recycle Crushing 415V Switchroom | 10 | 0.6/1 | 3C+3E | Cu | PVC/SCN/PVC | Black | Ladder - Subframe | 10mm2 0.6/1kV 3C+3E Cu PVC/SCN/PVC Black | Switchroom Vendor | Switchroom Vendor | 4 |  | 6
F13CV406VS-P1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13CV406-VS | Recycle Crusher Discharge Conveyor LV VSD | Recycle Crushing 415V Switchroom | 35 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 35mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F13HF014-P1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13-HF-014 | Recycle Crushing 415V MCC Active Harmonic Filter | Recycle Crushing 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 70mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 1 |  | 6
F13HF014-P2 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13-HF-014 | Recycle Crushing 415V MCC Active Harmonic Filter | Recycle Crushing 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 70mm2 0.6/1kV 3C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 1 |  | 6
F13DB004-P1 | F13-SW-114 | Recycle Crushing Esential 415V Switchboard | Recycle Crushing 415V Switchroom | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | 150 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 150mm2 0.6/1kV 4C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 1 |  | 6
F13UPS004ISL-P1 | F13-SW-114 | Recycle Crushing Esential 415V Switchboard | Recycle Crushing 415V Switchroom | F13UPS004-ISL | Recycle Crushing 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | 16mm2 0.6/1kV 4C+E Cu XLPE/PVC Orange | Switchroom Vendor | Switchroom Vendor | 1 | MCC to Bypass Switch. | 6
F13UPS004-P1 | F13UPS004-ISL | Recycle Crushing 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Recycle Crushing 415V Switchroom | F13-UPS-004 | Recycle Crushing 415V Switchroom 240VAC UPS | Recycle Crushing 415V Switchroom | 10 | 0.6/1 | 4C+E | Cu | R-EP-90 | Black | Ladder - Subframe | 10mm2 0.6/1kV 4C+E Cu R- EP-90 Black | Switchroom Vendor | Switchroom Vendor | 4 | Bypass Switch to UPS. | 6
F13UPS004ISL-P2 | F13-UPS-004 | Recycle Crushing 415V Switchroom 240VAC UPS | Recycle Crushing 415V Switchroom | F13UPS004-ISL | Recycle Crushing 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Recycle Crushing 415V Switchroom | 10 | 0.6/1 | 2C+E | Cu | R-EP-90 | Black | Ladder - Subframe | 10mm2 0.6/1kV 2C+E Cu R- EP-90 Black | Switchroom Vendor | Switchroom Vendor | 4 | UPS to Bypass Switch | 6
F13BA004-P1 | F13-UPS-004 | Recycle Crushing 415V Switchroom 240VAC UPS | Recycle Crushing 415V Switchroom | F13-BA-004 | Recycle Crushing 415V Switchroom 240VAC UPS Battery Bank | Recycle Crushing 415V Switchroom | 10 | 0.6/1 | 3C+E | Cu | R-EP-90 | Black | Ladder - Subframe | 10mm2 0.6/1kV 3C+E Cu R- EP-90 Black | Switchroom Vendor | Switchroom Vendor | 4 |  | 6
F13DB204-P1 | F13UPS004-ISL | Recycle Crushing 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Recycle Crushing 415V Switchroom | F13-DB-204 | Recycle Crushing 415V Switchroom 240V UPS Distribution Board | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | 16mm2 0.6/1kV 2C+E Cu PVC/PVC Orange | Switchroom Vendor | Switchroom Vendor | 1 | Bypass Switch to UPS DB | 6
F13COM004-P1 | F13-DB-204 | Recycle Crushing 415V Switchroom 240V UPS Distribution Board | Recycle Crushing 415V Switchroom | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | 4mm2 0.6/1kV 2C+E Cu PVC/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F13DCS406-P1 | F13-DB-204 | Recycle Crushing 415V Switchroom 240V UPS Distribution Board | Recycle Crushing 415V Switchroom | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | 4mm2 0.6/1kV 2C+E Cu PVC/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F13DB204-P5 | F13-DB-204 | Recycle Crushing 415V Switchroom 240V UPS Distribution Board | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | 4mm2 0.6/1kV 2C+E Cu PVC/PVC Orange | Switchroom Vendor | Switchroom Vendor | 4 |  | 6
F13DB204-P6 | F13-DB-204 | Recycle Crushing 415V Switchroom 240V UPS Distribution Board | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | 4mm2 0.6/1kV 2C+E Cu PVC/PVC Orange | Switchroom Vendor | Switchroom Vendor | 4 |  | 6
F13SW114-P3 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13-SW-114 | Recycle Crushing Esential 415V Switchboard | Recycle Crushing 415V Switchroom | 10 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | 10mm2 0.6/1kV 2C+E Cu PVC/PVC Orange | Switchroom Vendor | Switchroom Vendor | 0 | 24VDC Supply to Essential Board | 6
F13TR014-P2 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | 4mm2 0.6/1kV 2C+E Cu PVC/PVC Orange | Switchroom Vendor | Switchroom Vendor | 2 | 240V for transformer cooling fans | 6
F13FIP004-P1 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | F13-FIP-004 | Recycle Crushing 415V Switchroom Fire Indicator Panel | Recycle Crushing 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Ladder - Subframe | 2.5mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 6
F13FIP004XE1-P1 | F13-FIP-004 | Recycle Crushing 415V Switchroom Fire Indicator Panel | Recycle Crushing 415V Switchroom | F13FIP004-XE1 | Recycle Crushing 415V Switchroom VESDA Panel | Recycle Crushing 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Ladder - Subframe | 2.5mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 6
BRS13000CP-P1 | F13-DB-204 | Recycle Crushing 415V Switchroom 240V UPS Distribution Board | Recycle Crushing 415V Switchroom | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | Recycle Crushing 415V Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | R-EP-90 | Black | Ladder - Subframe | 2.5mm2 0.6/1kV 2C+E Cu R- EP-90 Black | Switchroom Vendor | Switchroom Vendor | 4 |  | 6
F13DB004-R13 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | F13AC401-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 1 Isolator | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 6
F13AC401-P1 | F13AC401-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 1 Isolator | Recycle Crushing 415V Switchroom | F13-AC-401 | Recycle Crushing 415V Switchroom Air Conditioner No. 1 | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-W13 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | F13AC402-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 2 Isolator | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13AC402-P1 | F13AC402-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 2 Isolator | Recycle Crushing 415V Switchroom | F13-AC-402 | Recycle Crushing 415V Switchroom Air Conditioner No. 2 | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-B13 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | F13AC403-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 3 Isolator | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13AC403-P1 | F13AC403-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 3 Isolator | Recycle Crushing 415V Switchroom | F13-AC-403 | Recycle Crushing 415V Switchroom Air Conditioner No. 3 | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-R15 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | F13AC404-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 4 Isolator | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13AC404-P1 | F13AC404-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 4 Isolator | Recycle Crushing 415V Switchroom | F13-AC-404 | Recycle Crushing 415V Switchroom Air Conditioner No. 4 | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-W15 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | F13AC405-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 5 Isolator | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13AC405-P1 | F13AC405-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 5 Isolator | Recycle Crushing 415V Switchroom | F13-AC-405 | Recycle Crushing 415V Switchroom Air Conditioner No. 5 | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-B15 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | F13AC406-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 6 Isolator | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13AC406-P1 | F13AC406-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 6 Isolator | Recycle Crushing 415V Switchroom | F13-AC-406 | Recycle Crushing 415V Switchroom Air Conditioner No. 6 | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-R14 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | F13AC407-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 7 Isolator | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13AC407-P1 | F13AC407-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 7 Isolator | Recycle Crushing 415V Switchroom | F13-AC-407 | Recycle Crushing 415V Switchroom Air Conditioner No. 7 | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-W14 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | F13AC408-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 8 Isolator | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13AC408-P1 | F13AC408-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 8 Isolator | Recycle Crushing 415V Switchroom | F13-AC-408 | Recycle Crushing 415V Switchroom Air Conditioner No. 8 | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-B14 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | F13AC409-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 9 Isolator | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13AC409-P1 | F13AC409-ISL | Recycle Crushing 415V Switchroom Air Conditioner No. 9 Isolator | Recycle Crushing 415V Switchroom | F13-AC-409 | Recycle Crushing 415V Switchroom Air Conditioner No. 9 | Recycle Crushing 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 10mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-R11 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom |  | Lighting - Switchroom Internal 2 (High Side of Roof) | Recycle Crushing 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 2.5mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-R11_ | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom |  | Lighting - Switchroom Internal 2 (Emergency) | Recycle Crushing 415V Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | 2.5mm2 0.45/0.75kV 1C Cu PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-W11 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom |  | Lighting - Switchroom Internal 1 (Low Side of Roof) | Recycle Crushing 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 2.5mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-W11_ | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom |  | Lighting - Switchroom Internal 1 (Emergency) | Recycle Crushing 415V Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | 2.5mm2 0.45/0.75kV 1C Cu PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-W12 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom |  | Lighting - Switchroom External 1 | Recycle Crushing 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 2.5mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-W12_ | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom |  | Lighting - Switchroom External 1 (Emergency) | Recycle Crushing 415V Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | 2.5mm2 0.45/0.75kV 1C Cu PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-R03 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom |  | General Power - Recycle Crushing 415V Switchroom GPO's | Recycle Crushing 415V Switchroom | 4 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | 4mm2 0.45/0.75kV 2C+E Cu Flat - PVC/PVC White | Switchroom Vendor | Switchroom Vendor | 4 |  | 7
F13DB004-B10 | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom |  | Lighting - Switchroom External Lighting Junction Box (for site use) | Recycle Crushing 415V Switchroom | 4 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Walls | 4mm2 0.6/1kV 4C+E Cu PVC/PVC Orange | Switchroom Vendor | Switchroom Vendor | 4 |  | 8
F13SW014-C1 | F13SR004-LCS | Recycle Crushing 415V Switchroom Emergency Shutdown | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 6C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 1 | Emerg/ Shutdown Circuit. E-stop to trip incomer | 8
F13TR014-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 4C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13CC401VS-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13CC401-VS | Recycle Crusher C LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 10C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13CC402VS-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13CC402-VS | Recycle Crusher D LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 10C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13CV403VS-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13CV403-VS | SAG Mill Feed Conveyor LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 15C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13CV403VS-C2 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | F13CV403-VS | SAG Mill Feed Conveyor LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.15 | 4 PR | Cu | PVC/OS/PVC | Black | Ladder - Subframe | 1.5mm2 0.15kV 4 PR Cu PVC/OS/PVC Black | Switchroom Vendor | Switchroom Vendor | 1 | Encoder Signals to VSD. | 8
F13FA411VS-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FA411-VS | Crushed Ore Reclaim Feeder 1 LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 10C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13FA411VS-C2 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FA411-VS | Crushed Ore Reclaim Feeder 1 LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.15 | 4 PR | Cu | PVC/OS/PVC | Black | Ladder - Subframe | 1.5mm2 0.15kV 4 PR Cu PVC/OS/PVC Black | Switchroom Vendor | Switchroom Vendor | 4 |  | 8
F13FA412VS-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FA412-VS | Crushed Ore Reclaim Feeder 2 LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 10C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13FA412VS-C2 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FA412-VS | Crushed Ore Reclaim Feeder 2 LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.15 | 4 PR | Cu | PVC/OS/PVC | Black | Ladder - Subframe | 1.5mm2 0.15kV 4 PR Cu PVC/OS/PVC Black | Switchroom Vendor | Switchroom Vendor | 4 |  | 8
F13FA414VS-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FA414-VS | Emergency Feeder LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 10C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13FV401VS-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FV401-VS | Recycle Crusher C Feeder LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 10C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13FV401VS-C2 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FV401-VS | Recycle Crusher C Feeder LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.15 | 4 PR | Cu | PVC/OS/PVC | Black | Ladder - Subframe | 1.5mm2 0.15kV 4 PR Cu PVC/OS/PVC Black | Switchroom Vendor | Switchroom Vendor | 4 |  | 8
F13FV401JB-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FV401-JB | Recycle Crusher C Feeder TOL JB | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 4C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13FV402VS-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FV402-VS | Recycle Crusher D Feeder LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 10C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13FV402JB-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13FV402-JB | Recycle Crusher D Feeder TOL JB | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 4C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13CV405VS-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13CV405-VS | Recycle Conveyor 2 LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 15C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13CV405VS-C2 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | F13CV405-VS | Recycle Conveyor 2 LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.15 | 4 PR | Cu | PVC/OS/PVC | Black | Ladder - Subframe | 1.5mm2 0.15kV 4 PR Cu PVC/OS/PVC Black | Switchroom Vendor | Switchroom Vendor | 1 | Encoder Signals to VSD. | 8
F13CV406VS-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13CV406-VS | Recycle Crusher Discharge Conveyor LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 15C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13CV406VS-C2 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | F13CV406-VS | Recycle Crusher Discharge Conveyor LV VSD | Recycle Crushing 415V Switchroom | 1.5 | 0.15 | 4 PR | Cu | PVC/OS/PVC | Black | Ladder - Subframe | 1.5mm2 0.15kV 4 PR Cu PVC/OS/PVC Black | Switchroom Vendor | Switchroom Vendor | 1 | Encoder Signals to VSD. | 8
F13SW014-C2 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 15C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 1 | MCC Incomer Signals to DCS. | 8
F13SW114-C2 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | F13-SW-114 | Recycle Crushing Esential 415V Switchboard | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 10C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 | MCC Incomer Signals to DCS | 8
F13DB004-C1 | F13-FIP-004 | Recycle Crushing 415V Switchroom Fire Indicator Panel | Recycle Crushing 415V Switchroom | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 2C | Cu | R-EP-110 | Red | Ladder | 1.5mm2 0.6/1kV 2C Cu R-EP- 110 Red | Switchroom Vendor | Switchroom Vendor | 4 | HVAC trip. | 8
F13FIP004-C1 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | F13-FIP-004 | Recycle Crushing 415V Switchroom Fire Indicator Panel | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 10C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F13DB004-C2 | F13-PE-004 | Recycle Crushing 415V Switchroom Photo-electric cell | Recycle Crushing 415V Switchroom | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | 2.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | 2.5mm2 0.6/1kV 4C+E Cu PVC/PVC Orange | Switchroom Vendor | Switchroom Vendor | 4 | Lighting Control | 8
UT13045-I1 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | UT13045 | F13-SR-004 Recycle Crushing 415V Switchroom Temperature/Humidity Transmitter | Recycle Crushing 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder | 1.5mm2 0.15kV 2 PR Cu PVC/IOSCN/PVC Black | Switchroom Vendor | Switchroom Vendor | 1 |  | 8
UT13046-I1 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | UT13046 | F13-SR-004 Recycle Crushing 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | Recycle Crushing 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder | 1.5mm2 0.15kV 2 PR Cu PVC/IOSCN/PVC Black | Switchroom Vendor | Switchroom Vendor | 1 |  | 8
F13SR004LCS-C1 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | F13SR004-LCS | Recycle Crushing 415V Switchroom Emergency Shutdown | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 4C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 1 | 24VDC Supply to PILZ Relay in Switchroom E-Shut | 8
ZSC13030-I1 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | ZSC13030 | F13-SR-004 Recycle Crushing 415V MCC Transformer Enclosure Door Position Switch Closed | Recycle Crushing 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder | 1.5mm2 0.15kV 2 PR Cu PVC/IOSCN/PVC Black | Switchroom Vendor | Switchroom Vendor | 1 | Transformer Enclosure Door feedback | 9
F13UPS004-C1 | F13UPS004-ISL | Recycle Crushing 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Recycle Crushing 415V Switchroom | F13-UPS-004 | Recycle Crushing 415V Switchroom 240VAC UPS | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder | 1.5mm2 0.6/1kV 6C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 4 | UPS Bypass | 9
F13HF014-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13-HF-014 | Recycle Crushing 415V MCC Active Harmonic Filter | Recycle Crushing 415V Switchroom | 2.5 | 0.6/1 | 6C+E | Cu | R-EP-90 | Black | Ladder - Subframe | 2.5mm2 0.6/1kV 6C+E Cu R- EP-90 Black | Switchroom Vendor | Switchroom Vendor | 4 | HF to MCC Incomer | 9
F13SW014-C51 | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | R-EP-90 | Black | Ladder - Subframe | 6mm2 0.6/1kV 2C+E Cu R-EP- 90 Black | Switchroom Vendor | Switchroom Vendor | 4 | AFD CT to MCC Incomer | 9
F13SW014-C52 | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | R-EP-90 | Black | Ladder - Subframe | 6mm2 0.6/1kV 2C+E Cu R-EP- 90 Black | Switchroom Vendor | Switchroom Vendor | 4 | AFD CT to MCC Incomer | 9
F13SW014-C53 | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | R-EP-90 | Black | Ladder - Subframe | 6mm2 0.6/1kV 2C+E Cu R-EP- 90 Black | Switchroom Vendor | Switchroom Vendor | 4 | AFD CT to MCC Incomer | 9
F13SW014-C3 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 4C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 | 24VDC PSU Feedback | 9
F13SW014-C4 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 4C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 1 | 24VDC PSU Feedback | 9
F13SW014LCS-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13SW014-LCS | Recycle Crushing 415V MCC Remote Switching Panel | Recycle Crushing 415V Switchroom | 1.5 | 0.6/1 | 20C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.6/1kV 20C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 0 | MCC Incomer to MCC LCS | 9
BRS13000CP-C1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | Recycle Crushing 415V Switchroom | 1.5 | 0.25/0.44 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.25/0.44kV 4C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 4 | CT1 | 9
BRS13000CP-C2 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | Recycle Crushing 415V Switchroom | 1.5 | 0.25/0.44 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.25/0.44kV 4C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 4 | CT2 | 9
BRS13000CP-C3 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | Recycle Crushing 415V Switchroom | 1.5 | 0.25/0.44 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | 1.5mm2 0.25/0.44kV 4C+E Cu PVC/PVC Black | Switchroom Vendor | Switchroom Vendor | 4 | CT3 | 9
BRS13000CP-C4 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | Recycle Crushing 415V Switchroom | 2.5 | 0.6/1 | 4C+E | Cu | R-EP-90 | Black | Ladder - Subframe | 2.5mm2 0.6/1kV 4C+E Cu R- EP-90 Black | Switchroom Vendor | Switchroom Vendor | 4 | Voltage Ref | 9
BRS13000CP-C5 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | Recycle Crushing 415V Switchroom | 0.5 | 0.3/0.5 | 2C+E | Cu | PVC/PVC | Grey | Ladder - Subframe | 0.5mm2 0.3/0.5kV 2C+E Cu PVC/PVC Grey | Switchroom Vendor | Switchroom Vendor | 4 | Reset | 9
BRS13000CP-C6 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | Recycle Crushing 415V Switchroom | 0.5 | 0.3/0.5 | 2C+E | Cu | PVC/PVC | Grey | Ladder - Subframe | 0.5mm2 0.3/0.5kV 2C+E Cu PVC/PVC Grey | Switchroom Vendor | Switchroom Vendor | 4 | Status Alarm | 9
BRS13000CP-C7 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | Recycle Crushing 415V Switchroom | 0.5 | 0.3/0.5 | 2C+E | Cu | PVC/PVC | Grey | Ladder - Subframe | 0.5mm2 0.3/0.5kV 2C+E Cu PVC/PVC Grey | Switchroom Vendor | Switchroom Vendor | 4 | Fault Alarm | 9
BRS13000CP-C8 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | Recycle Crushing 415V Switchroom | 0.5 | 0.3/0.5 | 2C+E | Cu | PVC/PVC | Grey | Ladder - Subframe | 0.5mm2 0.3/0.5kV 2C+E Cu PVC/PVC Grey | Switchroom Vendor | Switchroom Vendor | 4 | Critical Alarm | 9
BRS13000CP-C9 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | Recycle Crushing 415V Switchroom | 0.5 | 0.3/0.5 | 2C+E | Cu | PVC/PVC | Grey | Ladder - Subframe | 0.5mm2 0.3/0.5kV 2C+E Cu PVC/PVC Grey | Switchroom Vendor | Switchroom Vendor | 4 |  | 9
BRS13000CP-C10 | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | Recycle Crushing 415V Switchroom | 0.5 | 0.3/0.5 | 2C+E | Cu | PVC/PVC | Grey | Ladder - Subframe | 0.5mm2 0.3/0.5kV 2C+E Cu PVC/PVC Grey | Switchroom Vendor | Switchroom Vendor | 4 |  | 9
BRS13000CP-C11 | BRS13000-TE | F13-CV-403 Belt Rip Switch Control Panel Temperature Probe | Recycle Crushing 415V Switchroom | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | Recycle Crushing 415V Switchroom | 0.5 | 0.3/0.5 | 2C+E | Cu | PVC/PVC | Grey | Ladder - Subframe | 0.5mm2 0.3/0.5kV 2C+E Cu PVC/PVC Grey | Switchroom Vendor | Switchroom Vendor | 4 |  | 9
F13FIP004-FO1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-FIP-004 | Recycle Crushing 415V Switchroom Fire Indicator Panel | Recycle Crushing 415V Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | N/Amm2 N/AkV 2C Fibre LC- ST Patch (SMFO) Yellow | Switchroom Vendor | Switchroom Vendor | 0 | Site-Wide Fire network - patch to FIP. | 9
F13FIP004-FO2 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-FIP-004 | Recycle Crushing 415V Switchroom Fire Indicator Panel | Recycle Crushing 415V Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | N/Amm2 N/AkV 2C Fibre LC- ST Patch (SMFO) Yellow | Switchroom Vendor | Switchroom Vendor | 0 | Site-Wide Fire network - patch to FIP. | 9
F13SW114-D1 | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | F13-SW-114 | Recycle Crushing Esential 415V Switchboard | Recycle Crushing 415V Switchroom | N/A | N/A | N/A | N/A | VAMP CAN Bus | Grey | Suspended Tray / Duct on wall | N/Amm2 N/AkV N/A N/A VAMP CAN Bus Grey | Switchroom Vendor | Switchroom Vendor | 4 | VAMP CAN Bus Cable. | 9
F13SW114-D2 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-SW-114 | Recycle Crushing Esential 415V Switchboard | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 0 | Ethernet allowance | 9
F13UPS004-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-UPS-004 | Recycle Crushing 415V Switchroom 240VAC UPS | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F13CC401VS-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13CC401-VS | Recycle Crusher C LV VSD | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F13CC402VS-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13CC402-VS | Recycle Crusher D LV VSD | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F13CV403VS-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13CV403-VS | SAG Mill Feed Conveyor LV VSD | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F13FA411VS-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13FA411-VS | Crushed Ore Reclaim Feeder 1 LV VSD | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13FA412VS-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13FA412-VS | Crushed Ore Reclaim Feeder 2 LV VSD | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13FA414VS-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13FA414-VS | Emergency Feeder LV VSD | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13FV401VS-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13FV401-VS | Recycle Crusher C Feeder LV VSD | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13FV402VS-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13FV402-VS | Recycle Crusher D Feeder LV VSD | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13CV405VS-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13CV405-VS | Recycle Conveyor 2 LV VSD | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13CV406VS-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13CV406-VS | Recycle Crusher Discharge Conveyor LV VSD | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13SW014-D11 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches | 10
F13SW014-D12 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches | 10
F13SW014-D13 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches | 10
F13SW014-D14 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches | 10
F13SW014-D15 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches | 10
F13SW014-D16 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-SW-014 | Recycle Crushing 415V MCC | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches | 10
F13HF014-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-HF-014 | Recycle Crushing 415V MCC Active Harmonic Filter | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13DCS406-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Orange | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Orange | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 1 PRIMARY | 10
F13DCS406-D2 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Orange | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Orange | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 1 SECONDARY | 10
F13DCS406-D3 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Purple | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Purple | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 2 PRIMARY | 10
F13DCS406-D4 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Purple | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Purple | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 2 SECONDARY | 10
F13DCS406-D5 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 1 | DCS Comms Allowance - ALE CARD (AS REQUIRED) | 10
F13DCS406-D6 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 1 | DCS Comms Allowance - ALE CARD (AS REQUIRED) | 10
F13DCS406-F01 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | N/Amm2 N/AkV 2C Fibre OS2 SMOF Fibre Patch Lead Yellow | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED) | 10
F13DCS406-F02 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | N/Amm2 N/AkV 2C Fibre OS2 SMOF Fibre Patch Lead Yellow | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED) | 10
BRS13000CP-D1 | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | Multiple | Misc SMOF Patch leads in Panel | Recycle Crushing 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | N/Amm2 N/AkV 4 pr Cu CAT6A (Shielded) Green | Switchroom Vendor | Switchroom Vendor | 3 |  | 10
F13TR014EB01-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13TR014-EB01 | Recycle Crushing 415V Switchroom Transformer Earth bar | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13TR014EB01-E2 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13TR014-EB01 | Recycle Crushing 415V Switchroom Transformer Earth bar | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13SW014EB01-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13SW014-EB01 | Recycle Crushing 415V MCC Earth Bar | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13SW014EB01-E2 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13SW014-EB01 | Recycle Crushing 415V MCC Earth Bar | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13SW114EB01-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13SW114-EB01 | Recycle Crushing Esential 415V Switchboard Earth Bar | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13SW114EB01-E2 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13SW114-EB01 | Recycle Crushing Esential 415V Switchboard Earth Bar | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F13CC401VS-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13CC401-VS | Recycle Crusher C LV VSD | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F13CC402VS-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13CC402-VS | Recycle Crusher D LV VSD | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F13CV403VS-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13CV403-VS | SAG Mill Feed Conveyor LV VSD | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F13CV405VS-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13CV405-VS | Recycle Conveyor 2 LV VSD | Recycle Crushing 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 70mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F13CV406VS-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13CV406-VS | Recycle Crusher Discharge Conveyor LV VSD | Recycle Crushing 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 35mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13FA411VS-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13FA411-VS | Crushed Ore Reclaim Feeder 1 LV VSD | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13FA412VS-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13FA412-VS | Crushed Ore Reclaim Feeder 2 LV VSD | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13FA414VS-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13FA414-VS | Emergency Feeder LV VSD | Recycle Crushing 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 70mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F13FV401VS-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13FV401-VS | Recycle Crusher C Feeder LV VSD | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F13FV402VS-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13FV402-VS | Recycle Crusher D Feeder LV VSD | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F13FV401JB-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13FV401-JB | Recycle Crusher C Feeder TOL JB | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13FV402JB-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13FV402-JB | Recycle Crusher C Feeder TOL JB | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13SR004LCS-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13SR004-LCS | Recycle Crushing 415V Switchroom Emergency Shutdown | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13SW014LCS-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13SW014-LCS | Recycle Crushing 415V MCC Remote Switching Panel | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13FIP004-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13-FIP-004 | Recycle Crushing 415V Switchroom Fire Indicator Panel | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
BRS13000CP-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | BRS13000-CP | F12-CV-401 PRIMARY CRUSHER DISCHARGE CONVEYOR BELT RIP SWITCH CONTROL PANEL | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13DB004-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13-DB-004 | Recycle Crushing 415V Switchroom L&SP Distribution Board | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13HF014-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13-HF-014 | Recycle Crushing 415V MCC Active Harmonic Filter | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13UPS004-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13-UPS-004 | Recycle Crushing 415V Switchroom 240VAC UPS | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13UPS004ISL-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13UPS004-ISL | Recycle Crushing 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13BA004-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13-BA-004 | Recycle Crushing 415V Switchroom 240VAC UPS Battery Bank | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13DB204-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13-DB-204 | Recycle Crushing 415V Switchroom 240V UPS Distribution Board | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13COM004-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13-COM-004 | Recycle Crushing 415V Switchroom Communications Rack | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13DCS406-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13-DCS-406 | Recycle Crushing 415V Switchroom DCS Panel | Recycle Crushing 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 16mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13SR004-E3 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13-SR-004 | Subfloor Cable Ladder | Recycle Crushing 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 35mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13SR004-E4 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13-SR-004 | Subfloor Cable Ladder | Recycle Crushing 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 35mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13SR004-E5 | F13-SR-004 | Subfloor Cable Ladder | Recycle Crushing 415V Switchroom | F13-SR-004 | Subfloor Cable Ladder | Recycle Crushing 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 35mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13SR004-E1 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13-SR-004 | Switchroom Subframe | Recycle Crushing 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 70mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13SR004-E2 | F13SR004-EB01 | Recycle Crushing 415V Switchroom Earth Bar | Recycle Crushing 415V Switchroom | F13-SR-004 | Switchroom Subframe | Recycle Crushing 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 70mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13TR014-E3 | F13TR014-EB01 | Recycle Crushing 415V Switchroom Transformer Earth bar | Recycle Crushing 415V Switchroom | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 11
F13TR014-E4 | F13TR014-EB01 | Recycle Crushing 415V Switchroom Transformer Earth bar | Recycle Crushing 415V Switchroom | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 12
F13TR014-E5 | F13TR014-EB01 | Recycle Crushing 415V Switchroom Transformer Earth bar | Recycle Crushing 415V Switchroom | F13-TR-014 | Recycle Crushing 415V MCC Transformer | Recycle Crushing 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 120mm2 0.6/1kV 1C Cu PVC Green/Yellow | Switchroom Vendor | Switchroom Vendor | 4 |  | 12