## Cable schedule
Cable Number | Equip. Number - From | Equipment Name - From | Location - From | Equip. Number - To | Equipment Name - To | Location - To o | nductor Size (mm | Insulation(kV) | Length | o. of Cores / Pa | Conductor | Construction | eath(Preferred colou | Installation Method | Supplied By | Installed By | Area | Rev | Comments | Page
F16AG421-P1 | F16AG421-VS | ROUGHER FLOTATION CELL 1 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-421 | ROUGHER FLOTATION CELL 1 AGITATOR | ROUGHER FLOTATION | 35 | 1.9/3.3 | 145 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D | Primero | Primero | 160 | 0 |  | 2
F16AG422-P1 | F16AG422-VS | ROUGHER FLOTATION CELL 2 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-422 | ROUGHER FLOTATION CELL 2 AGITATOR | ROUGHER FLOTATION | 35 | 1.9/3.3 | 135 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D | Primero | Primero | 160 | 0 |  | 2
F16AG423-P1 | F16AG423-VS | ROUGHER FLOTATION CELL 3 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-423 | ROUGHER FLOTATION CELL 3 AGITATOR | ROUGHER FLOTATION | 35 | 1.9/3.3 | 125 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D | Primero | Primero | 160 | 0 |  | 2
F16AG424-P1 | F16AG424-VS | SCAVENGER FLOTATION CELL 1 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-424 | SCAVENGER FLOTATION CELL 1 AGITATOR | SCAVENGER FLOTATION | 35 | 1.9/3.3 | 115 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D | Primero | Primero | 160 | 0 |  | 2
F16AG425-P1 | F16AG425-VS | SCAVENGER FLOTATION CELL 2 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-425 | SCAVENGER FLOTATION CELL 2 AGITATOR | SCAVENGER FLOTATION | 35 | 1.9/3.3 | 125 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D | Primero | Primero | 160 | 0 |  | 2
F16SW011-P1-R | F16-TR-011 | FLOTATION 33/11KV TRANSFORMER | FLOTATION 33/11KV TRANSFORMER | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | 120 | 6.35/11 | 35 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D | Primero | Primero | 160 | 0 |  | 2
F16SW011-P2-R | F16-TR-011 | FLOTATION 33/11KV TRANSFORMER | FLOTATION 33/11KV TRANSFORMER | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | 120 | 6.35/11 | 35 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D | Primero | Primero | 160 | 0 |  | 2
F16SW011-P1-W | F16-TR-011 | FLOTATION 33/11KV TRANSFORMER | FLOTATION 33/11KV TRANSFORMER | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | 120 | 6.35/11 | 35 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D | Primero | Primero | 160 | 0 |  | 2
F16SW011-P2-W | F16-TR-011 | FLOTATION 33/11KV TRANSFORMER | FLOTATION 33/11KV TRANSFORMER | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | 120 | 6.35/11 | 35 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D | Primero | Primero | 160 | 0 |  | 2
F16SW011-P1-B | F16-TR-011 | FLOTATION 33/11KV TRANSFORMER | FLOTATION 33/11KV TRANSFORMER | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | 120 | 6.35/11 | 35 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D | Primero | Primero | 160 | 0 |  | 2
F16SW011-P2-B | F16-TR-011 | FLOTATION 33/11KV TRANSFORMER | FLOTATION 33/11KV TRANSFORMER | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | 120 | 6.35/11 | 35 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D | Primero | Primero | 160 | 0 |  | 2
F16NR011-N1 | F16-TR-011 | FLOTATION 33/11KV TRANSFORMER | FLOTATION 33/11KV TRANSFORMER | F16-NR-011 | FLOTATION 33/11KV TRANSFORMER NEUTRAL EARTHING RESISTOR | FLOTATION 33/11KV TRANSFORMER | 50 | 6.35/11 | 16 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, Touching | Primero | Primero | 160 | 0 | NER Cable - From TX Secondary Neutral to NER. | 2
F16AG426-P1 | F16AG426-VS | SCAVENGER FLOTATION CELL 3 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-426 | SCAVENGER FLOTATION CELL 3 AGITATOR | SCAVENGER FLOTATION | 35 | 1.9/3.3 | 135 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D | Primero | Primero | 160 | 0 |  | 2
F16AG427-P1 | F16AG427-VS | SCAVENGER FLOTATION CELL 4 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-427 | SCAVENGER FLOTATION CELL 4 AGITATOR | SCAVENGER FLOTATION | 35 | 1.9/3.3 | 145 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D | Primero | Primero | 160 | 0 |  | 2
F24PW401-P1 | F24PW401-VS | MILL WATER PUMP 1 HV VSD | FLOTATION 11KV SWITCHROOM | F24-PW-401 | MILL WATER PUMP 1 | PROCESS WATER TANK | 120 | 1.9/3.3 | 95 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F24PW402-P1 | F24PW402-VS | MILL WATER PUMP 2 HV VSD | FLOTATION 11KV SWITCHROOM | F24-PW-402 | MILL WATER PUMP 2 | PROCESS WATER TANK | 120 | 1.9/3.3 | 100 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F16GE001-P1-R | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | F16-GE-001 | FLOTATION EMERGENCY SUPPLY 11KV GENERATOR | FLOTATION 11KV GENERATOR | 50 | 6.35/11 | 75 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D | Primero | Primero | 160 | 0 |  | 2
F16GE001-P1-W | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | F16-GE-001 | FLOTATION EMERGENCY SUPPLY 11KV GENERATOR | FLOTATION 11KV GENERATOR | 50 | 6.35/11 | 75 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D | Primero | Primero | 160 | 0 |  | 2
F16GE001-P1-B | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | F16-GE-001 | FLOTATION EMERGENCY SUPPLY 11KV GENERATOR | FLOTATION 11KV GENERATOR | 50 | 6.35/11 | 75 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D | Primero | Primero | 160 | 0 |  | 2
F16GE001-N1 | F16GE001-NR | FLOTATION EMERGENCY SUPPLY 11KV GENERATOR NEUTRAL EARTHING RESISTOR | FLOTATION 11KV GENERATOR | F16-GE-001 | FLOTATION EMERGENCY SUPPLY 11KV GENERATOR | FLOTATION 11KV GENERATOR | 50 | 6.35/11 | 15 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D | Primero | Primero | 160 | 0 | NER Cable - From Generator Star Point to NER | 2
F16TR008-P1 | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | F16-TR-008 | THICKENER EMERGENCY POWER 415V MCC TRANSFORMER | FLOTATION 415V SWITCHROOM | 50 | 6.35/11 | 50 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D | Primero | Primero | 160 | 0 |  | 2
F24PW417-P1 | F24PW417-VS | HIGH PRESSURE PROCESS WATER PUMP 1 HV VSD | FLOTATION 11KV SWITCHROOM | F24-PW-417 | HIGH PRESSURE PROCESS WATER PUMP 1 | PROCESS WATER TANK | 120 | 1.9/3.3 | 105 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F24PW418-P1 | F24PW418-VS | HIGH PRESSURE PROCESS WATER PUMP 2 HV VSD | FLOTATION 11KV SWITCHROOM | F24-PW-418 | HIGH PRESSURE PROCESS WATER PUMP 2 | PROCESS WATER TANK | 120 | 1.9/3.3 | 110 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F17PP455-P1 | F17PP455-VS | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 1 HV VSD | FLOTATION 11KV SWITCHROOM | F17-PP-455 | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 1 | FLOTATION TAILINGS THICKENER | 120 | 1.9/3.3 | 185 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D / Buried in Conduit | Primero | Primero | 170 | 0 |  | 2
F17PP456-P1 | F17PP456-VS | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 2 HV VSD | FLOTATION 11KV SWITCHROOM | F17-PP-456 | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 2 | FLOTATION TAILINGS THICKENER | 120 | 1.9/3.3 | 190 | 3C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, spaced 1D / Buried in Conduit | Primero | Primero | 170 | 0 |  | 2