## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | Length (m) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred colour) | Installation Method | Supplied By | Installed By | Area | Rev | Comments | Page
F16HT541-P1 | F16AG421-VS | ROUGHER FLOTATION CELL 1 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-HT-541 | ROUGHER FLOTATION CELL 1 SPACE HEATER | ROUGHER FLOTATION | 2.5 | 0.6/1 | 145 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16AG421-I1 | F16AG421-VS | ROUGHER FLOTATION CELL 1 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-421 | ROUGHER FLOTATION CELL 1 AGITATOR RTD | ROUGHER FLOTATION | 1.5 | 0.11 | 145 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16AG421LCS-C1 | F16AG421-VS | ROUGHER FLOTATION CELL 1 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16AG421-LCS | ROUGHER FLOTATION CELL 1 AGITATOR LOCAL CONTROL STATION | ROUGHER FLOTATION | 1.5 | 0.6/1 | 145 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16HT542-P2 | F16AG422-VS | ROUGHER FLOTATION CELL 2 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-HT-542 | ROUGHER FLOTATION CELL 2 SPACE HEATER | ROUGHER FLOTATION | 2.5 | 0.6/1 | 135 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16AG422-I1 | F16AG422-VS | ROUGHER FLOTATION CELL 2 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-422 | ROUGHER FLOTATION CELL 2 AGITATOR RTD | ROUGHER FLOTATION | 1.5 | 0.11 | 135 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16AG422LCS-C1 | F16AG422-VS | ROUGHER FLOTATION CELL 2 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16AG422-LCS | ROUGHER FLOTATION CELL 2 AGITATOR LOCAL CONTROL STATION | ROUGHER FLOTATION | 1.5 | 0.6/1 | 135 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16HT543-P1 | F16AG423-VS | ROUGHER FLOTATION CELL 3 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-HT-543 | ROUGHER FLOTATION CELL 3 SPACE HEATER | ROUGHER FLOTATION | 2.5 | 0.6/1 | 125 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16AG423-I1 | F16AG423-VS | ROUGHER FLOTATION CELL 3 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-423 | ROUGHER FLOTATION CELL 3 AGITATOR RTD | ROUGHER FLOTATION | 1.5 | 0.11 | 125 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16AG423LCS-C1 | F16AG423-VS | ROUGHER FLOTATION CELL 3 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16AG423-LCS | ROUGHER FLOTATION CELL 3 AGITATOR LOCAL CONTROL STATION | ROUGHER FLOTATION | 1.5 | 0.6/1 | 125 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16HT544-P1 | F16AG424-VS | SCAVENGER FLOTATION CELL 1 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-HT-544 | SCAVENGER FLOTATION CELL 1 SPACE HEATER | SCAVENGER FLOTATION | 2.5 | 0.6/1 | 115 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16AG424-I1 | F16AG424-VS | SCAVENGER FLOTATION CELL 1 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-424 | SCAVENGER FLOTATION CELL 1 AGITATOR RTD | SCAVENGER FLOTATION | 1.5 | 0.11 | 115 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16AG424LCS-C1 | F16AG424-VS | SCAVENGER FLOTATION CELL 1 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16AG424-LCS | SCAVENGER FLOTATION CELL 1 AGITATOR LOCAL CONTROL STATION | SCAVENGER FLOTATION | 1.5 | 0.6/1 | 115 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16HT545-P1 | F16AG425-VS | SCAVENGER FLOTATION CELL 2 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-HT-545 | SCAVENGER FLOTATION CELL 2 SPACE HEATER | SCAVENGER FLOTATION | 2.5 | 0.6/1 | 125 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16AG425-I1 | F16AG425-VS | SCAVENGER FLOTATION CELL 2 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-425 | SCAVENGER FLOTATION CELL 2 AGITATOR RTD | SCAVENGER FLOTATION | 1.5 | 0.11 | 125 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16AG425LCS-C1 | F16AG425-VS | SCAVENGER FLOTATION CELL 2 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16AG425-LCS | SCAVENGER FLOTATION CELL 2 AGITATOR LOCAL CONTROL STATION | SCAVENGER FLOTATION | 1.5 | 0.6/1 | 125 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16NR011-P1 | F16-DB-001 | FLOTATION 11KV SWITCHROOM L&SP DISTRIBUTION BOARD | FLOTATION 33/11KV TRANSFORMER | F16-NR-011 | FLOTATION 33/11KV TRANSFORMER NEUTRAL EARTHING RESISTOR | FLOTATION 33/11KV TRANSFORMER | 2.5 | 0.6/1 | 16 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Flat, Touching | Primero | Primero | 160 | 0 | NER Anti-condensation heater | 2
F16NR011-C1 | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | F16-NR-011 | FLOTATION 33/11KV TRANSFORMER NEUTRAL EARTHING RESISTOR | FLOTATION 33/11KV TRANSFORMER | 4 | 0.6/1 | 35 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 | NER CT + Sensing Resistor Signals | 2
F16TR011-C1 | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | F16-TR-011 | FLOTATION 33/11KV TRANSFORMER | FLOTATION 33/11KV TRANSFORMER | 1.5 | 0.6/1 | 35 | 20C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 | Transformer Signals to Protection Relay | 2
F16TR011EB01-E1 | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | F16TR011-EB01 | F16-TR-011 FLOTATION 11KV TRANSFORMER COMPOUND EARTH BAR | FLOTATION 33/11KV TRANSFORMER | 120 | 0.6/1 | 35 | 1C | Cu | PVC | Green/Yellow | Ladder | Primero | Primero | 160 | 0 |  | 2
F16TR011EB01-E2 | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | F16TR011-EB01 | F16-TR-011 FLOTATION 11KV TRANSFORMER COMPOUND EARTH BAR | FLOTATION 33/11KV TRANSFORMER | 120 | 0.6/1 | 35 | 1C | Cu | PVC | Green/Yellow | Ladder | Primero | Primero | 160 | 0 |  | 2
F16HT546-P1 | F16AG426-VS | SCAVENGER FLOTATION CELL 3 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-HT-546 | SCAVENGER FLOTATION CELL 3 SPACE HEATER | SCAVENGER FLOTATION | 2.5 | 0.6/1 | 135 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16AG426-I1 | F16AG426-VS | SCAVENGER FLOTATION CELL 3 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-426 | SCAVENGER FLOTATION CELL 3 AGITATOR RTD | SCAVENGER FLOTATION | 1.5 | 0.11 | 135 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16AG426LCS-C1 | F16AG426-VS | SCAVENGER FLOTATION CELL 3 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16AG426-LCS | SCAVENGER FLOTATION CELL 3 AGITATOR LOCAL CONTROL STATION | SCAVENGER FLOTATION | 1.5 | 0.6/1 | 135 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16HT547-P1 | F16AG427-VS | SCAVENGER FLOTATION CELL 4 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-HT-547 | SCAVENGER FLOTATION CELL 4 SPACE HEATER | SCAVENGER FLOTATION | 2.5 | 0.6/1 | 145 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16AG427-I1 | F16AG427-VS | SCAVENGER FLOTATION CELL 4 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16-AG-427 | SCAVENGER FLOTATION CELL 4 AGITATOR RTD | SCAVENGER FLOTATION | 1.5 | 0.11 | 145 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16AG427LCS-C1 | F16AG427-VS | SCAVENGER FLOTATION CELL 4 AGITATOR HV VSD | FLOTATION 11KV SWITCHROOM | F16AG427-LCS | SCAVENGER FLOTATION CELL 4 AGITATOR LOCAL CONTROL STATION | SCAVENGER FLOTATION | 1.5 | 0.6/1 | 145 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F24PW401-P2 | F24PW401-VS | MILL WATER PUMP 1 HV VSD | FLOTATION 11KV SWITCHROOM | F24-PW-401 | MILL WATER PUMP 1 SPACE HEATER | PROCESS WATER TANK | 2.5 | 0.6/1 | 95 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F24PW401-I1 | F24PW401-VS | MILL WATER PUMP 1 HV VSD | FLOTATION 11KV SWITCHROOM | F24-PW-401 | MILL WATER PUMP 1 RTD | PROCESS WATER TANK | 1.5 | 0.11 | 95 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F24PW401LCS-C1 | F24PW401-VS | MILL WATER PUMP 1 HV VSD | FLOTATION 11KV SWITCHROOM | F24PW401-LCS | MILL WATER PUMP 1 LOCAL CONTROL STATION | PROCESS WATER TANK | 1.5 | 0.6/1 | 95 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F24PW402-P2 | F24PW402-VS | MILL WATER PUMP 2 HV VSD | FLOTATION 11KV SWITCHROOM | F24-PW-402 | MILL WATER PUMP 2 SPACE HEATER | PROCESS WATER TANK | 2.5 | 0.6/1 | 100 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F24PW402-I1 | F24PW402-VS | MILL WATER PUMP 2 HV VSD | FLOTATION 11KV SWITCHROOM | F24-PW-402 | MILL WATER PUMP 2 RTD | PROCESS WATER TANK | 1.5 | 0.11 | 100 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F24PW402LCS-C1 | F24PW402-VS | MILL WATER PUMP 2 HV VSD | FLOTATION 11KV SWITCHROOM | F24PW402-LCS | MILL WATER PUMP 2 LOCAL CONTROL STATION | PROCESS WATER TANK | 1.5 | 0.6/1 | 100 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F16GE001-E3 | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | F16-GE-001 | FLOTATION EMERGENCY SUPPLY 11KV GENERATOR | FLOTATION 11KV GENERATOR | 120 | 0.6/1 | 75 | 1C | Cu | PVC | Green/Yellow | Ladder | Primero | Primero | 160 | 0 |  | 2
F16GE001-C1 | F16-RIO-100 | FLOTATION 11KV SWITCHROOM N-IO PANEL | FLOTATION 11KV SWITCHROOM | F16-GE-001 | FLOTATION EMERGENCY SUPPLY 11KV GENERATOR | FLOTATION 11KV GENERATOR | 1.5 | 0.6/1 | 75 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 | Emergency Generator Signals to DCS | 2
F16GE001-C2 | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | F16-GE-001 | FLOTATION EMERGENCY SUPPLY 11KV GENERATOR | FLOTATION 11KV GENERATOR | 1.5 | 0.6/1 | 75 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 | Emergency Generator Signals to SWBD | 2
F16GE001-C3 | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | F16-GE-001 | FLOTATION EMERGENCY SUPPLY 11KV GENERATOR | FLOTATION 11KV GENERATOR | 4 | 0.6/1 | 75 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 | NER CT + Sensing Resistor | 2
F16GE001-C4 | F16SR001-LCS | FLOTATION 11KV SWITCHROOM EMERGENCY SHUTDOWN | FLOTATION 11KV SWITCHROOM | F16-GE-001 | FLOTATION EMERGENCY SUPPLY 11KV GENERATOR | FLOTATION 11KV GENERATOR | 1.5 | 0.6/1 | 75 | 2C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 | Eshut generator shutdown | 2
F16GE001CP-D1 | F16-COM-001 | FLOTATION 11KV SWITCHROOM COMMUNICATIONS RACK | FLOTATION 11KV SWITCHROOM | F16GE001-CP | FLOTATION EMERGENCY SUPPLY 11KV GENERATOR CONTROL PANEL | FLOTATION 11KV GENERATOR | N/A | N/A | 75 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 | Generator Comms | 2
F16SW008-C10 | F16-SW-011 | FLOTATION 11KV SWITCHBOARD | FLOTATION 11KV SWITCHROOM | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | 1.5 | 0.6/1 | 50 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 | Intertrip Signals | 2
F24PW417-P2 | F24PW417-VS | HIGH PRESSURE PROCESS WATER PUMP 1 HV VSD | FLOTATION 11KV SWITCHROOM | F24-PW-417 | HIGH PRESSURE PROCESS WATER PUMP 1 SPACE HEATER | PROCESS WATER TANK | 2.5 | 0.6/1 | 105 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F24PW417-I1 | F24PW417-VS | HIGH PRESSURE PROCESS WATER PUMP 1 HV VSD | FLOTATION 11KV SWITCHROOM | F24-PW-417 | HIGH PRESSURE PROCESS WATER PUMP 1 RTD | PROCESS WATER TANK | 1.5 | 0.11 | 105 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F24PW417LCS-C1 | F24PW417-VS | HIGH PRESSURE PROCESS WATER PUMP 1 HV VSD | FLOTATION 11KV SWITCHROOM | F24PW417-LCS | HIGH PRESSURE PROCESS WATER PUMP 1 LOCAL CONTROL STATION | PROCESS WATER TANK | 1.5 | 0.6/1 | 105 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F24PW418-P2 | F24PW418-VS | HIGH PRESSURE PROCESS WATER PUMP 2 HV VSD | FLOTATION 11KV SWITCHROOM | F24-PW-418 | HIGH PRESSURE PROCESS WATER PUMP 2 SPACE HEATER | PROCESS WATER TANK | 2.5 | 0.6/1 | 110 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F24PW418-I1 | F24PW418-VS | HIGH PRESSURE PROCESS WATER PUMP 2 HV VSD | FLOTATION 11KV SWITCHROOM | F24-PW-418 | HIGH PRESSURE PROCESS WATER PUMP 2 RTD | PROCESS WATER TANK | 1.5 | 0.11 | 110 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F24PW418LCS-C1 | F24PW418-VS | HIGH PRESSURE PROCESS WATER PUMP 2 HV VSD | FLOTATION 11KV SWITCHROOM | F24PW418-LCS | HIGH PRESSURE PROCESS WATER PUMP 2 LOCAL CONTROL STATION | PROCESS WATER TANK | 1.5 | 0.6/1 | 110 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 240 | 0 |  | 2
F17PP455-P2 | F17PP455-VS | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 1 HV VSD | FLOTATION 11KV SWITCHROOM | F17-PP-455 | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 1 SPACE HEATER | FLOTATION TAILINGS THICKENER | 2.5 | 0.6/1 | 185 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 170 | 0 |  | 3
F17PP455-I1 | F17PP455-VS | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 1 HV VSD | FLOTATION 11KV SWITCHROOM | F17-PP-455 | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 1 RTD | FLOTATION TAILINGS THICKENER | 1.5 | 0.11 | 185 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 170 | 0 |  | 3
F17PP455LCS-C1 | F17PP455-VS | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 1 HV VSD | FLOTATION 11KV SWITCHROOM | F17PP455-LCS | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 1 LOCAL CONTROL STATION | FLOTATION TAILINGS THICKENER | 1.5 | 0.6/1 | 185 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 170 | 0 |  | 3
F17PP455-E1 | --- | HV CABLE LADDER RUNNING EARTH | MAIN PIPE RACK | F17-PP-455 | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 1 PUMP FRAME | FLOTATION TAILINGS THICKENER | 120 | 0.6/1 | 25 | 1C | Cu | PVC | Green/Yellow | Buried in Conduit | Primero | Primero | 170 | 0 |  | 3
F17PP456-P2 | F17PP456-VS | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 2 HV VSD | FLOTATION 11KV SWITCHROOM | F17-PP-456 | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 2 SPACE HEATER | FLOTATION TAILINGS THICKENER | 2.5 | 0.6/1 | 190 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 170 | 0 |  | 3
F17PP456-I1 | F17PP456-VS | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 2 HV VSD | FLOTATION 11KV SWITCHROOM | F17-PP-456 | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 2 RTD | FLOTATION TAILINGS THICKENER | 1.5 | 0.11 | 190 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 170 | 0 |  | 3
F17PP456LCS-C1 | F17PP456-VS | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 2 HV VSD | FLOTATION 11KV SWITCHROOM | F17PP456-LCS | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 2 LOCAL CONTROL STATION | FLOTATION TAILINGS THICKENER | 1.5 | 0.6/1 | 190 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 170 | 0 |  | 3
F17PP456-E1 | --- | HV CABLE LADDER RUNNING EARTH | MAIN PIPE RACK | F17-PP-456 | FLOTATION TAILINGS THICKENER UNDERFLOW PUMP 2 PUMP FRAME | FLOTATION TAILINGS THICKENER | 120 | 0.6/1 | 30 | 1C | Cu | PVC | Green/Yellow | Buried in Conduit | Primero | Primero | 170 | 0 |  | 3