## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | Length (m) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred colour) | Installation Method | Supplied By | Installed By | Area | Rev | Comments | Page
F16SW104-P3 | F16-GE-104 | FLOTATION ESSENTIAL SUPPLY 415V GENERATOR | FLOTATION ESSENTIAL 415V GENERATOR | F16-SW-104 | FLOTATION ESSENTIAL 415V SWITCHBOARD | FLOTATION 415V SWITCHROOM | 150 | 0.6/1 | 50 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 2
F16SW104-P4 | F16-GE-104 | FLOTATION ESSENTIAL SUPPLY 415V GENERATOR | FLOTATION ESSENTIAL 415V GENERATOR | F16-SW-104 | FLOTATION ESSENTIAL 415V SWITCHBOARD | FLOTATION 415V SWITCHROOM | 150 | 0.6/1 | 50 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 2
F16GE104CP-P1 | F16-DB-002 | FLOTATION 415V SWITCHROOM L&SP DISTRIBUTION BOARD | FLOTATION 415V SWITCHROOM | F16GE104-CP | FLOTATION ESSENTIAL SUPPLY 415V GENERATOR CONTROL PANEL | FLOTATION 415V SWITCHROOM AREA | 2.5 | 0.6/1 | 40 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 | Generator Battery Charger | 2
F16GE104CP-C1 | F16-DCS-408 | FLOTATION 415V SWITCHROOM DCS PANEL | FLOTATION 415V SWITCHROOM | F16GE104-CP | FLOTATION ESSENTIAL SUPPLY 415V GENERATOR CONTROL PANEL | FLOTATION 415V SWITCHROOM AREA | 1.5 | 0.6/1 | 40 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 | Generator Feedback to DCS | 2
F16GE104CP-C2 | F16-SW-104 | FLOTATION ESSENTIAL 415V SWITCHBOARD | FLOTATION 415V SWITCHROOM | F16GE104-CP | FLOTATION ESSENTIAL SUPPLY 415V GENERATOR CONTROL PANEL | FLOTATION 415V SWITCHROOM AREA | 1.5 | 0.6/1 | 40 | 2C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 | Generator Feedback to MCC | 2
F16GE104CP-D1 | F16-COM-002 | FLOTATION 415V SWITCHROOM COMMUNICATIONS RACK | FLOTATION 415V SWITCHROOM | F16GE104-CP | FLOTATION ESSENTIAL SUPPLY 415V GENERATOR CONTROL PANEL | FLOTATION 415V SWITCHROOM AREA | N/A | N/A | 40 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 | Generator to Comms | 2
F16RIO001-P1 | F16-DB-202 | FLOTATION 415V SWITCHROOM 415VAC UPS DISTRIBUTION BOARD | FLOTATION 415V SWITCHROOM | F16-RIO-001 | ROUGHER & SCAVENGER FLOTATION FIELD N-IO PANEL | FLOTATION AREA - ROUGHER FEED END | 25 | 0.6/1 | 170 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16RIO002-P1 | F16-DB-202 | FLOTATION 415V SWITCHROOM 415VAC UPS DISTRIBUTION BOARD | FLOTATION 415V SWITCHROOM | F16-RIO-002 | ROUGHER & SCAVENGER FLOTATION FIELD N-IO PANEL | FLOTATION AREA - SCAV DISCHARGE END | 25 | 0.6/1 | 180 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F17RIO001-P1 | F16-DB-202 | FLOTATION 415V SWITCHROOM 415VAC UPS DISTRIBUTION BOARD | FLOTATION 415V SWITCHROOM | F17-RIO-001 | FLOTATION TAILINGS THICKENING FIELD N-IO PANEL | FLOTATION TAILINGS THICKENER | 25 | 0.6/1 | 160 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 170 | 0 |  | 2
F17RIO002-P1 | F16-DB-202 | FLOTATION 415V SWITCHROOM 415VAC UPS DISTRIBUTION BOARD | FLOTATION 415V SWITCHROOM | F17-RIO-002 | FLOTATION TAILINGS THICKENING FIELD N-IO PANEL | FLOTATION TAILINGS THICKENER | 25 | 0.6/1 | 170 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 170 | 0 |  | 2
F18RIO001-P1 | F16-DB-202 | FLOTATION 415V SWITCHROOM 415VAC UPS DISTRIBUTION BOARD | FLOTATION 415V SWITCHROOM | F18-RIO-001 | CLEANER FLOTATION FIELD N-IO PANEL | CLEANER FLOTATION AREA | 25 | 0.6/1 | 150 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 180 | 0 |  | 2
F18RIO002-P1 | F16-DB-202 | FLOTATION 415V SWITCHROOM 415VAC UPS DISTRIBUTION BOARD | FLOTATION 415V SWITCHROOM | F18-RIO-002 | CLEANER FLOTATION FIELD N-IO PANEL | CLEANER FLOTATION AREA | 25 | 0.6/1 | 165 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 180 | 0 |  | 2
F24RIO001-P1 | F16-DB-202 | FLOTATION 415V SWITCHROOM 415VAC UPS DISTRIBUTION BOARD | FLOTATION 415V SWITCHROOM | F24-RIO-001 | AIR SERVICES FIELD N-IO PANEL | AIR COMPRESSOR SHED | 25 | 0.6/1 | 200 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 240 | 0 |  | 2
F24RIO002-P1 | F16-DB-202 | FLOTATION 415V SWITCHROOM 415VAC UPS DISTRIBUTION BOARD | FLOTATION 415V SWITCHROOM | F24-RIO-002 | WATER SERVICES FIELD N-IO PANEL | PROCESS WATER TANK AREA | 10 | 0.6/1 | 75 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 240 | 0 |  | 2
F16COM002/F16RIO001-FO1 | F16-COM-002 | FLOTATION 415V SWITCHROOM COMMUNICATIONS RACK | FLOTATION 415V SWITCHROOM | F16-RIO-001 | ROUGHER & SCAVENGER FLOTATION FIELD N-IO PANEL | FLOTATION AREA - ROUGHER FEED END | 9/125µm | N/A | 180 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | 160 | 0 |  | 2
F16RIO001/F16RIO002-FO1 | F16-RIO-001 | ROUGHER & SCAVENGER FLOTATION FIELD N-IO PANEL | FLOTATION AREA - ROUGHER FEED END | F16-RIO-002 | ROUGHER & SCAVENGER FLOTATION FIELD N-IO PANEL | FLOTATION AREA - SCAV DISCHARGE END | 9/125µm | N/A | 120 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | 160 | 0 |  | 2
F16RIO002/F17RIO001-FO1 | F16-RIO-002 | ROUGHER & SCAVENGER FLOTATION FIELD N-IO PANEL | FLOTATION AREA - SCAV DISCHARGE END | F17-RIO-001 | FLOTATION TAILINGS THICKENING FIELD N-IO PANEL | THICKENER FEED AREA - LOWER | 9/125µm | N/A | 50 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | 170 | 0 |  | 2
F17RIO001/F17RIO002-FO1 | F17-RIO-001 | FLOTATION TAILINGS THICKENING FIELD N-IO PANEL | THICKENER FEED AREA - LOWER | F17-RIO-002 | FLOTATION TAILINGS THICKENING FIELD N-IO PANEL | THICKENER FEED AREA - UPPER | 9/125µm | N/A | 40 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | 170 | 0 |  | 2
F17RIO002/F16COM002-FO1 | F17-RIO-002 | FLOTATION TAILINGS THICKENING FIELD N-IO PANEL | THICKENER FEED AREA - UPPER | F16-COM-002 | FLOTATION 415V SWITCHROOM COMMUNICATIONS RACK | FLOTATION 415V SWITCHROOM | 9/125µm | N/A | 160 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | 160 | 0 |  | 2
F16COM002/F24RIO002-FO1 | F16-COM-002 | FLOTATION 415V SWITCHROOM COMMUNICATIONS RACK | FLOTATION 415V SWITCHROOM | F24-RIO-002 | WATER SERVICES FIELD N-IO PANEL | PROCESS WATER TANK AREA | 9/125µm | N/A | 90 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | 240 | 0 |  | 2
F24RIO002/F18RIO001-FO1 | F24-RIO-002 | WATER SERVICES FIELD N-IO PANEL | PROCESS WATER TANK AREA | F18-RIO-001 | CLEANER FLOTATION FIELD N-IO PANEL | CLEANER FLOTATION AREA - LOWER | 9/125µm | N/A | 120 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | 180 | 0 |  | 2
F18RIO001/F18RIO002-FO1 | F18-RIO-001 | CLEANER FLOTATION FIELD N-IO PANEL | CLEANER FLOTATION AREA - LOWER | F18-RIO-002 | CLEANER FLOTATION FIELD N-IO PANEL | CLEANER FLOTATION AREA - UPPER | 9/125µm | N/A | 40 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | 180 | 0 |  | 2
F18RIO002/F24RIO001-FO1 | F18-RIO-002 | CLEANER FLOTATION FIELD N-IO PANEL | CLEANER FLOTATION AREA - UPPER | F24-RIO-001 | AIR SERVICES FIELD N-IO PANEL | AIR COMPRESSOR SHED | 9/125µm | N/A | 200 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | 240 | 0 |  | 2
F24RIO001/F16COM002-FO1 | F24-RIO-001 | AIR SERVICES FIELD N-IO PANEL | AIR COMPRESSOR SHED | F16-COM-002 | FLOTATION 415V SWITCHROOM COMMUNICATIONS RACK | FLOTATION 415V SWITCHROOM | 9/125µm | N/A | 230 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | 160 | 0 |  | 2
F16DB001-P1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F16-DB-001 | FLOTATION 11KV SWITCHROOM L&SP DISTRIBUTION BOARD | FLOTATION 11KV SWITCHROOM | 185 | 0.6/1 | 60 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 2
F16DB101-P1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F16-DB-101 | FLOTATION 11KV SWITCHROOM HV VSD AUXILIARY SUPPLIES DISTRIBUTION BOARD | FLOTATION 11KV SWITCHROOM | 95 | 0.6/1 | 60 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 2
F16DB301-P1 | F16-SW-104 | FLOTATION ESSENTIAL 415V SWITCHBOARD | FLOTATION 415V SWITCHROOM | F16-DB-301 | ROUGHER & SCAVENGER FLOTATION AREA L&SP DISTRIBUTION BOARD | FLOTATION TAILINGS THICKENER FEED | 185 | 0.6/1 | 170 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 2
F16PE301-P1 | F16-DB-301 | ROUGHER & SCAVENGER FLOTATION AREA L&SP DISTRIBUTION BOARD | FLOTATION TAILINGS THICKENER FEED | F16-PE-301 | ROUGHER & SCAVENGER FLOTATION AREA PHOTO-ELECTRIC CELL | FLOTATION TAILINGS THICKENER FEED | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 | PE Circuit for L&SP DB | 2
F16DB201-P1 | F16-DB-202 | FLOTATION 415V SWITCHROOM 415VAC UPS DISTRIBUTION BOARD | FLOTATION 415V SWITCHROOM | F16-DB-201 | FLOTATION 11KV SWITCHROOM 415VAC UPS DISTRIBUTION BOARD | FLOTATION 11KV SWITCHROOM | 16 | 0.6/1 | 60 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 2
F16BW401-P1 | F16BW401-VS | FLOTATION AIR BLOWER 1 LV VSD | FLOTATION 415V SWITCHROOM | F16-BW-401 | FLOTATION AIR BLOWER 1 | AIR SERVICES BUILDING | 185 | 0.6/1 | 180 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 2
F16BW401-P2 | F16BW401-VS | FLOTATION AIR BLOWER 1 LV VSD | FLOTATION 415V SWITCHROOM | F16-BW-401 | FLOTATION AIR BLOWER 1 | AIR SERVICES BUILDING | 185 | 0.6/1 | 180 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 2
F16HT548-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16-HT-548 | FLOTATION AIR BLOWER 1 SPACE HEATER | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 180 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16BW401LCS-C1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16BW401-LCS | FLOTATION AIR BLOWER 1 LOCAL CONTROL STATION | AIR SERVICES BUILDING | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16FN487-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-487 | FLOTATION AIR BLOWER 1 MOTOR COOLING FAN | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 180 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16FN487LCS-C1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16FN487-LCS | FLOTATION AIR BLOWER 1 MOTOR COOLING FAN LOCAL CONTROL STATION | AIR SERVICES BUILDING | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16FN493-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-493 | FLOTATION AIR BLOWER 1 VENTILATION FAN | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 180 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16FN493LCS-C1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16FN493-LCS | FLOTATION AIR BLOWER 1 VENTILATION FAN LOCAL CONTROL STATION | AIR SERVICES BUILDING | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16BW402-P1 | F16BW402-VS | FLOTATION AIR BLOWER 2 LV VSD | FLOTATION 415V SWITCHROOM | F16-BW-402 | FLOTATION AIR BLOWER 2 | AIR SERVICES BUILDING | 185 | 0.6/1 | 180 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 2
F16BW402-P2 | F16BW402-VS | FLOTATION AIR BLOWER 2 LV VSD | FLOTATION 415V SWITCHROOM | F16-BW-402 | FLOTATION AIR BLOWER 2 | AIR SERVICES BUILDING | 185 | 0.6/1 | 180 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 2
F16HT549-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16-HT-549 | FLOTATION AIR BLOWER 2 SPACE HEATER | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 180 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16BW402LCS-C1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16BW402-LCS | FLOTATION AIR BLOWER 2 LOCAL CONTROL STATION | AIR SERVICES BUILDING | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16FN488-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-488 | FLOTATION AIR BLOWER 2 MOTOR COOLING FAN | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 180 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16FN488LCS-C1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16FN488-LCS | FLOTATION AIR BLOWER 2 MOTOR COOLING FAN LOCAL CONTROL STATION | AIR SERVICES BUILDING | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16FN494-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-494 | FLOTATION AIR BLOWER 2 VENTILATION FAN | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 180 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 2
F16FN494LCS-C1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16FN494-LCS | FLOTATION AIR BLOWER 2 VENTILATION FAN LOCAL CONTROL STATION | AIR SERVICES BUILDING | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 2
F16BW403-P1 | F16BW403-VS | FLOTATION AIR BLOWER 3 LV VSD | FLOTATION 415V SWITCHROOM | F16-BW-403 | FLOTATION AIR BLOWER 3 | AIR SERVICES BUILDING | 185 | 0.6/1 | 180 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 2
F16BW403-P2 | F16BW403-VS | FLOTATION AIR BLOWER 3 LV VSD | FLOTATION 415V SWITCHROOM | F16-BW-403 | FLOTATION AIR BLOWER 3 | AIR SERVICES BUILDING | 185 | 0.6/1 | 180 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 3
F16HT550-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16-HT-550 | FLOTATION AIR BLOWER 3 SPACE HEATER | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 180 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16BW403LCS-C1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16BW403-LCS | FLOTATION AIR BLOWER 3 LOCAL CONTROL STATION | AIR SERVICES BUILDING | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16FN489-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-489 | FLOTATION AIR BLOWER 3 MOTOR COOLING FAN | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 180 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16FN489LCS-C1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16FN489-LCS | FLOTATION AIR BLOWER 3 MOTOR COOLING FAN LOCAL CONTROL STATION | AIR SERVICES BUILDING | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16FN495-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-495 | FLOTATION AIR BLOWER 3 VENTILATION FAN | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 180 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16FN495LCS-C1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16FN495-LCS | FLOTATION AIR BLOWER 3 VENTILATION FAN LOCAL CONTROL STATION | AIR SERVICES BUILDING | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16BW404-P1 | F16BW404-VS | FLOTATION AIR BLOWER 4 LV VSD | FLOTATION 415V SWITCHROOM | F16-BW-404 | FLOTATION AIR BLOWER 4 | AIR SERVICES BUILDING | 185 | 0.6/1 | 180 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 3
F16BW404-P2 | F16BW404-VS | FLOTATION AIR BLOWER 4 LV VSD | FLOTATION 415V SWITCHROOM | F16-BW-404 | FLOTATION AIR BLOWER 4 | AIR SERVICES BUILDING | 185 | 0.6/1 | 180 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 3
F16HT551-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16-HT-551 | FLOTATION AIR BLOWER 4 SPACE HEATER | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 180 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16BW404LCS-C1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16BW404-LCS | FLOTATION AIR BLOWER 4 LOCAL CONTROL STATION | AIR SERVICES BUILDING | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16FN490-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-490 | FLOTATION AIR BLOWER 4 MOTOR COOLING FAN | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 180 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16FN490LCS-C1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16FN490-LCS | FLOTATION AIR BLOWER 4 MOTOR COOLING FAN LOCAL CONTROL STATION | AIR SERVICES BUILDING | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16FN496-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-496 | FLOTATION AIR BLOWER 4 VENTILATION FAN | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 180 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16FN496LCS-C1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F16FN496-LCS | FLOTATION AIR BLOWER 4 VENTILATION FAN LOCAL CONTROL STATION | AIR SERVICES BUILDING | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16PP515-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16-PP-515 | FLOTATION CELLS DRAIN PUMP | FLOTATION AREA | 70 | 0.6/1 | 180 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 3
F16PP515-I1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16-PP-515 | FLOTATION CELLS DRAIN PUMP THERMISTOR | FLOTATION AREA | 1.5 | 0.11 | 180 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16PP515LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PP515-LCS | FLOTATION CELLS DRAIN PUMP LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16FN497-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-497 | ROUGHER FLOTATION CELL 1 GEARBOX COOLING FAN | FLOTATION AREA | 2.5 | 0.6/1 | 180 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16FN497LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16FN497-LCS | ROUGHER FLOTATION CELL 1 GEARBOX COOLING FAN LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16HT562JB-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16HT562-JB | ROUGHER FLOTATION CELL 1 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | 4 | 0.6/1 | 180 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16HT562-P1 | F16HT562-JB | ROUGHER FLOTATION CELL 1 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-562 | ROUGHER FLOTATION CELL 1 GEARBOX HEATER 1 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 3
F16HT563-P1 | F16HT562-JB | ROUGHER FLOTATION CELL 1 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-563 | ROUGHER FLOTATION CELL 1 GEARBOX HEATER 2 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 3
F16FN498-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-498 | ROUGHER FLOTATION CELL 2 GEARBOX COOLING FAN | FLOTATION AREA | 2.5 | 0.6/1 | 165 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16FN498LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16FN498-LCS | ROUGHER FLOTATION CELL 2 GEARBOX COOLING FAN LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 165 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16HT564JB-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16HT564-JB | ROUGHER FLOTATION CELL 2 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | 4 | 0.6/1 | 165 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16HT564-P1 | F16HT564-JB | ROUGHER FLOTATION CELL 2 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-564 | ROUGHER FLOTATION CELL 2 GEARBOX HEATER 1 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 3
F16HT565-P1 | F16HT564-JB | ROUGHER FLOTATION CELL 2 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-565 | ROUGHER FLOTATION CELL 2 GEARBOX HEATER 2 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 3
F16FN499-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-499 | ROUGHER FLOTATION CELL 3 GEARBOX COOLING FAN | FLOTATION AREA | 2.5 | 0.6/1 | 155 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16FN499LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16FN499-LCS | ROUGHER FLOTATION CELL 3 GEARBOX COOLING FAN LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 155 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16HT566JB-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16HT566-JB | ROUGHER FLOTATION CELL 3 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | 4 | 0.6/1 | 155 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16HT566-P1 | F16HT566-JB | ROUGHER FLOTATION CELL 3 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-566 | ROUGHER FLOTATION CELL 3 GEARBOX HEATER 1 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 3
F16HT567-P1 | F16HT566-JB | ROUGHER FLOTATION CELL 3 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-567 | ROUGHER FLOTATION CELL 3 GEARBOX HEATER 2 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 3
F16FN500-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-500 | SCAVENGER FLOTATION CELL 1 GEARBOX COOLING FAN | FLOTATION AREA | 2.5 | 0.6/1 | 140 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16FN500LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16FN500-LCS | SCAVENGER FLOTATION CELL 1 GEARBOX COOLING FAN LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 140 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16HT568JB-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16HT568-JB | SCAVENGER FLOTATION CELL 1 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | 4 | 0.6/1 | 140 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16HT568-P1 | F16HT568-JB | SCAVENGER FLOTATION CELL 1 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-568 | SCAVENGER FLOTATION CELL 1 GEARBOX HEATER 1 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 3
F16HT569-P1 | F16HT568-JB | SCAVENGER FLOTATION CELL 1 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-569 | SCAVENGER FLOTATION CELL 1 GEARBOX HEATER 2 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 3
F16FN501-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-501 | SCAVENGER FLOTATION CELL 2 GEARBOX COOLING FAN | FLOTATION AREA | 2.5 | 0.6/1 | 155 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16FN501LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16FN501-LCS | SCAVENGER FLOTATION CELL 2 GEARBOX COOLING FAN LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 155 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16HT570JB-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16HT570-JB | SCAVENGER FLOTATION CELL 2 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | 4 | 0.6/1 | 155 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16HT570-P1 | F16HT570-JB | SCAVENGER FLOTATION CELL 2 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-570 | SCAVENGER FLOTATION CELL 2 GEARBOX HEATER 1 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 3
F16HT571-P1 | F16HT570-JB | SCAVENGER FLOTATION CELL 2 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-571 | SCAVENGER FLOTATION CELL 2 GEARBOX HEATER 2 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 3
F16FN502-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-502 | SCAVENGER FLOTATION CELL 3 GEARBOX COOLING FAN | FLOTATION AREA | 2.5 | 0.6/1 | 165 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16FN502LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16FN502-LCS | SCAVENGER FLOTATION CELL 3 GEARBOX COOLING FAN LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 165 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 3
F16HT572JB-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16HT572-JB | SCAVENGER FLOTATION CELL 3 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | 4 | 0.6/1 | 165 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 3
F16HT572-P1 | F16HT572-JB | SCAVENGER FLOTATION CELL 3 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-572 | SCAVENGER FLOTATION CELL 3 GEARBOX HEATER 1 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 4
F16HT573-P1 | F16HT572-JB | SCAVENGER FLOTATION CELL 3 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-573 | SCAVENGER FLOTATION CELL 3 GEARBOX HEATER 2 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 4
F16FN503-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16-FN-503 | SCAVENGER FLOTATION CELL 4 GEARBOX COOLING FAN | FLOTATION AREA | 2.5 | 0.6/1 | 180 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 4
F16FN503LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16FN503-LCS | SCAVENGER FLOTATION CELL 4 GEARBOX COOLING FAN LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 4
F16HT574JB-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16HT574-JB | SCAVENGER FLOTATION CELL 4 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | 4 | 0.6/1 | 180 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 4
F16HT574-P1 | F16HT574-JB | SCAVENGER FLOTATION CELL 4 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-574 | SCAVENGER FLOTATION CELL 4 GEARBOX HEATER 1 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 4
F16HT575-P1 | F16HT574-JB | SCAVENGER FLOTATION CELL 4 GEARBOX HEATERS JUNCTION BOX | FLOTATION AREA | F16-HT-575 | SCAVENGER FLOTATION CELL 4 GEARBOX HEATER 2 | FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Final Run | Primero | Primero | 160 | 0 |  | 4
F16PP629-P1 | F16PP630-VS | ROUGHER 1 FINAL CONCENTRATE SAMPLE PUMP LV VSD | FLOTATION 415V SWITCHROOM | F16-PP-629 | ROUGHER 1 CONCENTRATE CLEANER FEED SAMPLE PUMP | FLOTATION AREA | 4 | 0.6/1 | 160 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 4
F16PP629LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PP629-LCS | ROUGHER 1 CONCENTRATE CLEANER FEED SAMPLE PUMP LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 160 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 4
F16PP630-P1 | F16PP630-VS | ROUGHER 1 FINAL CONCENTRATE SAMPLE PUMP LV VSD | FLOTATION 415V SWITCHROOM | F16-PP-630 | ROUGHER 1 FINAL CONCENTRATE SAMPLE PUMP | FLOTATION AREA | 4 | 0.6/1 | 160 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 4
F16PP630LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PP630-LCS | ROUGHER 1 FINAL CONCENTRATE SAMPLE PUMP LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 160 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 4
F16PP631-P1 | F16PP631-VS | ROUGHER 2 & 3 CONCENTRATE SAMPLE PUMP LV VSD | FLOTATION 415V SWITCHROOM | F16-PP-631 | ROUGHER 2 & 3 CONCENTRATE SAMPLE PUMP | CLEANER FLOTATION AREA | 4 | 0.6/1 | 150 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 4
F16PP631LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PP631-LCS | ROUGHER 2 & 3 CONCENTRATE SAMPLE PUMP LOCAL CONTROL STATION | CLEANER FLOTATION AREA | 1.5 | 0.6/1 | 150 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 4
F16PP632-P1 | F16PP632-VS | SCAVENGER CONCENTRATE SAMPLE PUMP LV VSD | FLOTATION 415V SWITCHROOM | F16-PP-632 | SCAVENGER CONCENTRATE SAMPLE PUMP | CLEANER FLOTATION AREA | 4 | 0.6/1 | 135 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 4
F16PP632LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PP632-LCS | SCAVENGER CONCENTRATE SAMPLE PUMP LOCAL CONTROL STATION | CLEANER FLOTATION AREA | 1.5 | 0.6/1 | 135 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 4
F16PP633-P1 | F16PP633-VS | SCAVENGER TAILS SAMPLE PUMP LV VSD | FLOTATION 415V SWITCHROOM | F16-PP-633 | SCAVENGER TAILS SAMPLE PUMP | FLOTATION AREA | 4 | 0.6/1 | 175 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 4
F16PP633LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PP633-LCS | SCAVENGER TAILS SAMPLE PUMP LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 175 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 4
F16PP634-P1 | F16PP634-VS | FINAL TAILS SAMPLE PUMP LV VSD | FLOTATION 415V SWITCHROOM | F16-PP-634 | FINAL TAILS SAMPLE PUMP | FLOTATION AREA | 4 | 0.6/1 | 175 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 160 | 0 |  | 4
F16PP634LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PP634-LCS | FINAL TAILS SAMPLE PUMP LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 175 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 4
F16PP638-P1 | F16PP638-VS | SAMPLE RETURN PUMP 1 LV VSD | FLOTATION 415V SWITCHROOM | F16-PP-638 | SAMPLE RETURN PUMP 1 | FLOTATION AREA | 25 | 0.6/1 | 175 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 160 | 0 |  | 4
F16PP638LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PP638-LCS | SAMPLE RETURN PUMP 1 LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 175 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 4
F16PP639-P1 | F16PP639-VS | SAMPLE RETURN PUMP 2 LV VSD | FLOTATION 415V SWITCHROOM | F16-PP-639 | SAMPLE RETURN PUMP 2 | FLOTATION AREA | 25 | 0.6/1 | 175 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 160 | 0 |  | 4
F16PP639LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PP639-LCS | SAMPLE RETURN PUMP 2 LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 175 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 4
F16PS411LCS-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PS411-LCS | FLOTATION AREA SUMP PUMP 1 LOCAL CONTROL STATION | FLOTATION AREA | 50 | 0.6/1 | 180 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 4
F16PS411-P1 | F16PS411-LCS | FLOTATION AREA SUMP PUMP 1 LOCAL CONTROL STATION | FLOTATION AREA | F16-PS-411 | FLOTATION AREA SUMP PUMP 1 | FLOTATION AREA | 50 | 0.6/1 | 10 | 3C+E | Cu | EPR/CSP | Black | Final Run | Primero | Primero | 160 | 0 |  | 4
F16PS411LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PS411-LCS | FLOTATION AREA SUMP PUMP 1 LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 180 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 4
F16PS412LCS-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PS412-LCS | FLOTATION AREA SUMP PUMP 2 LOCAL CONTROL STATION | FLOTATION AREA | 50 | 0.6/1 | 150 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 4
F16PS412-P1 | F16PS412-LCS | FLOTATION AREA SUMP PUMP 2 LOCAL CONTROL STATION | FLOTATION AREA | F16-PS-412 | FLOTATION AREA SUMP PUMP 2 | FLOTATION AREA | 50 | 0.6/1 | 10 | 3C+E | Cu | EPR/CSP | Black | Final Run | Primero | Primero | 160 | 0 |  | 4
F16PS412LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PS412-LCS | FLOTATION AREA SUMP PUMP 2 LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 150 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 4
F16PS413LCS-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PS413-LCS | FLOTATION AREA SUMP PUMP 3 LOCAL CONTROL STATION | FLOTATION AREA | 50 | 0.6/1 | 180 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 160 | 0 |  | 4
F16PS413-P1 | F16PS413-LCS | FLOTATION AREA SUMP PUMP 3 LOCAL CONTROL STATION | FLOTATION AREA | F16-PS-413 | FLOTATION AREA SUMP PUMP 3 | FLOTATION AREA | 50 | 0.6/1 | 10 | 3C+E | Cu | EPR/CSP | Black | Final Run | Primero | Primero | 160 | 0 |  | 4
F16PS413LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F16PS413-LCS | FLOTATION AREA SUMP PUMP 3 LOCAL CONTROL STATION | FLOTATION AREA | 1.5 | 0.6/1 | 180 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 160 | 0 |  | 4
F17DB301-P1 | F16-SW-104 | FLOTATION ESSENTIAL 415V SWITCHBOARD | FLOTATION 415V SWITCHROOM | F17-DB-301 | FLOTATION TAILINGS THICKENER AREA L&SP DISTRIBUTION BOARD | FLOTATION TAILINGS THICKENER | 185 | 0.6/1 | 165 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching | Primero | Primero | 170 | 0 |  | 4
F17PE301-P1 | F17-DB-301 | FLOTATION TAILINGS THICKENER AREA L&SP DISTRIBUTION BOARD | FLOTATION TAILINGS THICKENER | F17-PE-301 | FLOTATION TAILINGS THICKENER AREA PHOTO-ELECTRIC CELL | FLOTATION TAILINGS THICKENER | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 170 | 0 | PE Circuit for L&SP DB | 4
F17HU422-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F17-HU-422 | FLOTATION TAILINGS THICKENER FEED VALVE HYDRAULIC POWER UNIT | FLOTATION TAILINGS THICKENER FEED | 6 | 0.6/1 | 155 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 170 | 0 |  | 4
F17HU422LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F17HU422-LCS | FLOTATION TAILINGS THICKENER FEED VALVE HYDRAULIC POWER UNIT LOCAL CONTROL STATION | FLOTATION TAILINGS THICKENER FEED | 1.5 | 0.6/1 | 155 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 170 | 0 |  | 4
F17PS427LCS-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F17PS427-LCS | FLOTATION TAILINGS THICKENER AREA SUMP PUMP LOCAL CONTROL STATION | FLOTATION TAILINGS THICKENER UNDERFLOW | 70 | 0.6/1 | 170 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 170 | 0 |  | 4
F17PS427-P2 | F17PS427-LCS | FLOTATION TAILINGS THICKENER AREA SUMP PUMP LOCAL CONTROL STATION | FLOTATION TAILINGS THICKENER UNDERFLOW | F17-PS-427 | FLOTATION TAILINGS THICKENER AREA SUMP PUMP | FLOTATION TAILINGS THICKENER UNDERFLOW | 70 | 0.6/1 | 10 | 3C+E | Cu | EPR/CSP | Black | Final Run | Primero | Primero | 170 | 0 |  | 4
F17PS427LCS-C1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F17PS427-LCS | FLOTATION TAILINGS THICKENER AREA SUMP PUMP LOCAL CONTROL STATION | FLOTATION TAILINGS THICKENER UNDERFLOW | 1.5 | 0.6/1 | 170 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 170 | 0 |  | 4
F17PP459-P1 | F17PP459-VS | FLOTATION TAILINGS THICKENER P-DUC PUMP LV VSD | FLOTATION 415V SWITCHROOM | F17-PP-459 | FLOTATION TAILINGS THICKENER P-DUC PUMP | FLOTATION TAILINGS THICKENER | 25 | 0.6/1 | 175 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero | 170 | 0 |  | 4
F17PP459-I1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F17-PP-459 | FLOTATION TAILINGS THICKENER P-DUC PUMP BI-METALLIC TEMPERATURE SENSOR | FLOTATION TAILINGS THICKENER | 1.5 | 0.11 | 175 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 170 | 0 |  | 4
F17PP459LCS-C1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F17PP459-LCS | FLOTATION TAILINGS THICKENER P-DUC PUMP LOCAL CONTROL STATION | FLOTATION TAILINGS THICKENER | 1.5 | 0.6/1 | 175 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 170 | 0 |  | 4
F17PO408-P1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F17-PO-408 | FLOTATION TAILINGS THICKENER RAKE DRIVE PUMP | FLOTATION TAILINGS THICKENER | 25 | 0.6/1 | 200 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 170 | 0 |  | 4
F17PO408LCS-C1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F17PO408-LCS | FLOTATION TAILINGS THICKENER RAKE DRIVE PUMP LOCAL CONTROL STATION | FLOTATION TAILINGS THICKENER | 1.5 | 0.6/1 | 200 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 170 | 0 |  | 4
F17PO409-P1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F17-PO-409 | FLOTATION TAILINGS THICKENER RAKE LIFT PUMP | FLOTATION TAILINGS THICKENER | 2.5 | 0.6/1 | 200 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 170 | 0 |  | 5
F17PO409LCS-C1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F17PO409-LCS | FLOTATION TAILINGS THICKENER RAKE LIFT PUMP LOCAL CONTROL STATION | FLOTATION TAILINGS THICKENER | 1.5 | 0.6/1 | 200 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 170 | 0 |  | 5
F17HT539-P1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F17-HT-539 | FLOTATION TAILINGS THICKENER RAKE DRIVE OIL TANK HEATER | FLOTATION TAILINGS THICKENER | 10 | 0.6/1 | 200 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 170 | 0 |  | 5
F17HT540-P1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F17-HT-540 | FLOTATION TAILINGS THICKENER RAKE LIFT OIL TANK HEATER | FLOTATION TAILINGS THICKENER | 10 | 0.6/1 | 200 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 170 | 0 |  | 5
F17FN492-P1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F17-FN-492 | FLOTATION TAILINGS THICKENER RAKE DRIVE OIL COOLING FAN | FLOTATION TAILINGS THICKENER | 2.5 | 0.6/1 | 200 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 170 | 0 |  | 5
F17FN492LCS-C1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F17FN492-LCS | FLOTATION TAILINGS THICKENER RAKE DRIVE OIL COOLING FAN LOCAL CONTROL STATION | FLOTATION TAILINGS THICKENER | 1.5 | 0.6/1 | 200 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 170 | 0 |  | 5
F17FN504-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F17-FN-504 | FLOTATION TAILINGS THICKENER UNDERFLOW TUNNEL VENTILATION FAN | FLOTATION TAILINGS THICKENER | 4 | 0.6/1 | 200 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 170 | 0 |  | 5
F17FN504LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F17FN504-LCS | FLOTATION TAILINGS THICKENER UNDERFLOW TUNNEL VENTILATION FAN LOCAL CONTROL STATION | FLOTATION TAILINGS THICKENER | 1.5 | 0.6/1 | 200 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 170 | 0 |  | 5
F18DB301-P1 | F16-SW-104 | FLOTATION ESSENTIAL 415V SWITCHBOARD | FLOTATION 415V SWITCHROOM | F18-DB-301 | CLEANER FLOTATION AREA L&SP DISTRIBUTION BOARD | CLEANER FLOTATION AREA | 185 | 0.6/1 | 165 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching | Primero | Primero | 180 | 0 |  | 5
F18PE301-P1 | F18-DB-301 | CLEANER FLOTATION AREA L&SP DISTRIBUTION BOARD | CLEANER FLOTATION AREA | F18-PE-301 | CLEANER FLOTATION AREA PHOTO-ELECTRIC CELL | CLEANER FLOTATION AREA | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 180 | 0 | PE Circuit for L&SP DB | 5
F18PS501LCS-P1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18PS501-LCS | CLEANER AREA SUMP PUMP LOCAL CONTROL STATION | CLEANER FLOTATION AREA | 25 | 0.6/1 | 150 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 180 | 0 |  | 5
F18PS501-P2 | F18PS501-LCS | CLEANER AREA SUMP PUMP LOCAL CONTROL STATION | CLEANER FLOTATION AREA | F18-PS-501 | CLEANER AREA SUMP PUMP | CLEANER FLOTATION AREA | 25 | 0.6/1 | 10 | 3C+E | Cu | EPR/CSP | Black | Final Run | Primero | Primero | 180 | 0 | Flexible for decontactor to motor | 5
F18PS501LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18PS501-LCS | CLEANER AREA SUMP PUMP LOCAL CONTROL STATION | CLEANER FLOTATION AREA | 1.5 | 0.6/1 | 150 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 180 | 0 |  | 5
F18PP407-P1 | F18PP407-VS | FINAL CONCENTRATE PUMP 1 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-407 | FINAL CONCENTRATE PUMP 1 | CLEANER FLOTATION AREA | 70 | 0.6/1 | 150 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP407-P2 | F18PP407-VS | FINAL CONCENTRATE PUMP 1 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-407 | FINAL CONCENTRATE PUMP 1 | CLEANER FLOTATION AREA | 70 | 0.6/1 | 150 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP407-P4 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18-PP-407 | FINAL CONCENTRATE PUMP 1 SPACE HEATER | CLEANER FLOTATION AREA | 2.5 | 0.6/1 | 150 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP407-I1 | F18PP407-VS | FINAL CONCENTRATE PUMP 1 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-407 | FINAL CONCENTRATE PUMP 1 THERMISTOR | CLEANER FLOTATION AREA | 1.5 | 0.11 | 150 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP407LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18PP407-LCS | FINAL CONCENTRATE PUMP 1 LOCAL CONTROL STATION | CLEANER FLOTATION AREA | 1.5 | 0.6/1 | 150 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP408-P1 | F18PP408-VS | FINAL CONCENTRATE PUMP 2 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-408 | FINAL CONCENTRATE PUMP 2 | CLEANER FLOTATION AREA | 70 | 0.6/1 | 150 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP408-P2 | F18PP408-VS | FINAL CONCENTRATE PUMP 2 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-408 | FINAL CONCENTRATE PUMP 2 | CLEANER FLOTATION AREA | 70 | 0.6/1 | 150 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP408-P4 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18-PP-408 | FINAL CONCENTRATE PUMP 2 SPACE HEATER | CLEANER FLOTATION AREA | 2.5 | 0.6/1 | 150 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP408-I1 | F18PP408-VS | FINAL CONCENTRATE PUMP 2 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-408 | FINAL CONCENTRATE PUMP 2 THERMISTOR | CLEANER FLOTATION AREA | 1.5 | 0.11 | 150 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP408LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18PP408-LCS | FINAL CONCENTRATE PUMP 2 LOCAL CONTROL STATION | CLEANER FLOTATION AREA | 1.5 | 0.6/1 | 150 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP501-P1 | F18PP501-VS | CLEANER FLOTATION CELL RECIRCULATION PUMP 1 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-501 | CLEANER FLOTATION CELL RECIRCULATION PUMP 1 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 150 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP501-P2 | F18PP501-VS | CLEANER FLOTATION CELL RECIRCULATION PUMP 1 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-501 | CLEANER FLOTATION CELL RECIRCULATION PUMP 1 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 150 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP501-P3 | F18PP501-VS | CLEANER FLOTATION CELL RECIRCULATION PUMP 1 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-501 | CLEANER FLOTATION CELL RECIRCULATION PUMP 1 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 150 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP501-P4 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18-PP-501 | CLEANER FLOTATION CELL RECIRCULATION PUMP 1 SPACE HEATER | CLEANER FLOTATION AREA | 2.5 | 0.6/1 | 150 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP501-I1 | F18-RIO-001 | CLEANER FLOTATION FIELD N-IO PANEL | CLEANER FLOTATION AREA | F18-PP-501 | CLEANER FLOTATION CELL RECIRCULATION PUMP 1 RTD | CLEANER FLOTATION AREA | 1.5 | 0.11 | 75 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP501LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18PP501-LCS | CLEANER FLOTATION CELL RECIRCULATION PUMP 1 LOCAL CONTROL STATION | CLEANER FLOTATION AREA | 1.5 | 0.6/1 | 150 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP502-P1 | F18PP502-VS | CLEANER FLOTATION CELL RECIRCULATION PUMP 2 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-502 | CLEANER FLOTATION CELL RECIRCULATION PUMP 2 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 150 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP502-P2 | F18PP502-VS | CLEANER FLOTATION CELL RECIRCULATION PUMP 2 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-502 | CLEANER FLOTATION CELL RECIRCULATION PUMP 2 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 150 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP502-P3 | F18PP502-VS | CLEANER FLOTATION CELL RECIRCULATION PUMP 2 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-502 | CLEANER FLOTATION CELL RECIRCULATION PUMP 2 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 150 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP502-P4 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18-PP-502 | CLEANER FLOTATION CELL RECIRCULATION PUMP 2 SPACE HEATER | CLEANER FLOTATION AREA | 2.5 | 0.6/1 | 150 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP502-I1 | F18-RIO-001 | CLEANER FLOTATION FIELD N-IO PANEL | CLEANER FLOTATION AREA | F18-PP-502 | CLEANER FLOTATION CELL RECIRCULATION PUMP 2 RTD | CLEANER FLOTATION AREA | 1.5 | 0.11 | 75 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP502LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18PP502-LCS | CLEANER FLOTATION CELL RECIRCULATION PUMP 2 LOCAL CONTROL STATION | CLEANER FLOTATION AREA | 1.5 | 0.6/1 | 150 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP511-P1 | F18PP511-VS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 1 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-511 | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 1 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 185 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP511-P2 | F18PP511-VS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 1 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-511 | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 1 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 185 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP511-P3 | F18PP511-VS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 1 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-511 | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 1 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 185 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP511-P4 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18-PP-511 | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 1 SPACE HEATER | CLEANER FLOTATION AREA | 2.5 | 0.6/1 | 185 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP511-I1 | F18-RIO-002 | CLEANER FLOTATION FIELD N-IO PANEL | CLEANER FLOTATION AREA | F18-PP-511 | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 1 RTD | CLEANER FLOTATION AREA | 1.5 | 0.11 | 75 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP511LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18PP511-LCS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 1 LOCAL CONTROL STATION | CLEANER FLOTATION AREA | 1.5 | 0.6/1 | 185 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP512-P1 | F18PP512-VS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 2 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-512 | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 2 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 185 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP512-P2 | F18PP512-VS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 2 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-512 | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 2 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 185 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP512-P3 | F18PP512-VS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 2 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-512 | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 2 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 185 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP512-P4 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18-PP-512 | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 2 SPACE HEATER | CLEANER FLOTATION AREA | 2.5 | 0.6/1 | 185 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP512-I1 | F18-RIO-002 | CLEANER FLOTATION FIELD N-IO PANEL | CLEANER FLOTATION AREA | F18-PP-512 | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 2 RTD | CLEANER FLOTATION AREA | 1.5 | 0.11 | 75 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP512LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18PP512-LCS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 2 LOCAL CONTROL STATION | CLEANER FLOTATION AREA | 1.5 | 0.6/1 | 185 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 5
F18PP513-P1 | F18PP513-VS | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 1 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-513 | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 1 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 180 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 6
F18PP513-P2 | F18PP513-VS | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 1 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-513 | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 1 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 180 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 6
F18PP513-P3 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18-PP-513 | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 1 SPACE HEATER | CLEANER FLOTATION AREA | 2.5 | 0.6/1 | 180 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 180 | 0 |  | 6
F18PP513-I1 | F18-RIO-002 | CLEANER FLOTATION FIELD N-IO PANEL | CLEANER FLOTATION AREA | F18-PP-513 | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 1 RTD | CLEANER FLOTATION AREA | 1.5 | 0.11 | 60 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 6
F18PP513LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18PP513-LCS | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 1 LOCAL CONTROL STATION | CLEANER FLOTATION AREA | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 6
F18PP514-P1 | F18PP514-VS | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 2 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-514 | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 2 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 180 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 6
F18PP514-P2 | F18PP514-VS | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 2 LV VSD | FLOTATION 415V SWITCHROOM | F18-PP-514 | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 2 | CLEANER FLOTATION AREA | 240 | 0.6/1 | 180 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 180 | 0 |  | 6
F18PP514-P3 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18-PP-514 | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 2 SPACE HEATER | CLEANER FLOTATION AREA | 2.5 | 0.6/1 | 180 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 180 | 0 |  | 6
F18PP514-I1 | F18-RIO-002 | CLEANER FLOTATION FIELD N-IO PANEL | CLEANER FLOTATION AREA | F18-PP-514 | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 2 RTD | CLEANER FLOTATION AREA | 1.5 | 0.11 | 60 | 6TR | Cu | PVC/IOSCN/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 6
F18PP514LCS-C1 | F16-SW-004 | FLOTATION 415V MCC | FLOTATION 415V SWITCHROOM | F18PP514-LCS | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 2 LOCAL CONTROL STATION | CLEANER FLOTATION AREA | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 180 | 0 |  | 6
F24CM401-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F24-CM-401 | PLANT AIR COMPRESSOR 1 MOTOR 1 | AIR SERVICES BUILDING | 240 | 0.6/1 | 195 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24CM401-P2 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F24-CM-401 | PLANT AIR COMPRESSOR 1 MOTOR 2 | AIR SERVICES BUILDING | 240 | 0.6/1 | 195 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24CM402-P1 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F24-CM-402 | PLANT AIR COMPRESSOR 2 MOTOR 1 | AIR SERVICES BUILDING | 240 | 0.6/1 | 200 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24CM402-P2 | F16-SW-005 | FLOTATION BLOWERS & COMPRESSORS 415V MCC | FLOTATION 415V SWITCHROOM | F24-CM-402 | PLANT AIR COMPRESSOR 2 MOTOR 2 | AIR SERVICES BUILDING | 240 | 0.6/1 | 200 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24CM403-P1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F24-CM-403 | PLANT AIR COMPRESSOR 3 MOTOR 1 | AIR SERVICES BUILDING | 240 | 0.6/1 | 215 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24CM403-P2 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F24-CM-403 | PLANT AIR COMPRESSOR 3 MOTOR 2 | AIR SERVICES BUILDING | 240 | 0.6/1 | 215 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24FI421-P1 | F17-DB-301 | FLOTATION TAILINGS THICKENER AREA L&SP DISTRIBUTION BOARD | FLOTATION TAILINGS THICKENER | F24-FI-421 | PLANT AIR COMPRESSOR 1 DISCHARGE DUST FILTER | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 100 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24FI422-P1 | F17-DB-301 | FLOTATION TAILINGS THICKENER AREA L&SP DISTRIBUTION BOARD | FLOTATION TAILINGS THICKENER | F24-FI-422 | PLANT AIR COMPRESSOR 2 DISCHARGE DUST FILTER | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 100 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24FI423-P1 | F17-DB-301 | FLOTATION TAILINGS THICKENER AREA L&SP DISTRIBUTION BOARD | FLOTATION TAILINGS THICKENER | F24-FI-423 | PLANT AIR COMPRESSOR 3 DISCHARGE DUST FILTER | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 100 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24FI424-P1 | F17-DB-301 | FLOTATION TAILINGS THICKENER AREA L&SP DISTRIBUTION BOARD | FLOTATION TAILINGS THICKENER | F24-FI-424 | PLANT AIR COMPRESSOR 1 DISCHARGE COALESCING FILTER | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 100 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24FI425-P1 | F17-DB-301 | FLOTATION TAILINGS THICKENER AREA L&SP DISTRIBUTION BOARD | FLOTATION TAILINGS THICKENER | F24-FI-425 | PLANT AIR COMPRESSOR 2 DISCHARGE COALESCING FILTER | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 100 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24FI426-P1 | F17-DB-301 | FLOTATION TAILINGS THICKENER AREA L&SP DISTRIBUTION BOARD | FLOTATION TAILINGS THICKENER | F24-FI-426 | PLANT AIR COMPRESSOR 3 DISCHARGE COALESCING FILTER | AIR SERVICES BUILDING | 2.5 | 0.6/1 | 100 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24FN417-P1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F24-FN-417 | HIGH PRESSURE PROCESS WATER PUMP 1 GEARBOX FAN | PROCESS WATER TANK | 2.5 | 0.6/1 | 100 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24FN417LCS-C1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F24FN417-LCS | HIGH PRESSURE PROCESS WATER PUMP 1 GEARBOX FAN LOCAL CONTROL STATION | PROCESS WATER TANK | 1.5 | 0.6/1 | 105 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24FN418-P1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F24-FN-418 | HIGH PRESSURE PROCESS WATER PUMP 2 GEARBOX FAN | PROCESS WATER TANK | 2.5 | 0.6/1 | 105 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6
F24FN418LCS-C1 | F16-SW-008 | THICKENER EMERGENCY POWER 415V MCC | FLOTATION 415V SWITCHROOM | F24FN418-LCS | HIGH PRESSURE PROCESS WATER PUMP 2 GEARBOX FAN LOCAL CONTROL STATION | PROCESS WATER TANK | 1.5 | 0.6/1 | 105 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | 240 | 0 |  | 6