## Equipment list
Rev | Equip. Number | Equipment Name | Qty | Description | Make | Model | Supplied By | Installed By | Comments | Page
0 | F16-SR-001 | Flotation 11kV Switchroom | 1 | Transportable switchroom on structural steel baseframe complete with 1.8m legs and landings, transported to site 600kms on sealed roads. | Switchroom Vendor | VTA | Switchroom Vendor | Primero | Refer 2000-F00-DSH-EL-11001 | 2
0 | - | Flotation 11kV Switchroom Landings and stairs | 1 | Equipment Landing to be structural steel baseframe complete with 1.8m legs and landings, designed to support heaviest piece of equipment to be installed in room. | Switchroom Vendor | VTA | Switchroom Vendor | Primero |  | 2
0 | F16-SW-011 | Flotation 11kV Switchboard | 1 | Metal clad, partition metal, withdrawable AIS 11kV switchboard. 1250A bus, 25kA/3s fault rating. Internally arc fault contained AFLR. With top mount arc absorbing duct on top - no arc vent to outdoors. 1 x VT panel, 1 x Incomer panel, 1 x Generator Incomer panel, 1 x Bus Tie panel, 1 x Bus Riser & VT panel, 15 x Feeder panels | ABB | UniGear ZS1 | Primero | Switchroom Vendor | Refer 2000-EL003-B02-10006 (Panel Arrangement), 2000-EL003-B03-10002 (Section View), 2000-EL003-C01-10005 (Foundation Frame Detail), 2000- EL003-C03-10004 (Foundation Layout), 2000-EL003-D01-10002 (SLD) 2000-F00-DSH-EL-11003 11kV Datasheet Switchboard Dimensions (W = 13060mm, H = 2533mm, D = 1340mm) approx. weight 21,250kg | 2
0 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | 1 | 415V 3Ø 250A DB. Fitted with incoming isolator, PE Cell circuit (night/day), Auto / Manual selector, Emergency light test controller, Rapidtest RCD test units, Lighting Contactors, air conditioner Contactors and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom Vendor | Switchroom Vendor | In accordance to Drawing 2000-F00-STD-EL-10025 & 2000-F00-STD-EL- 10022; Switchroom Vendor to calculate number of required poles including the number of circuits for Air conditioners, 20% loaded Spare circuit breakers and 20% spare space. | 2
0 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | 1 | 415V 3Ø 250A DB. Fitted with incoming isolator, and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom Vendor | Switchroom Vendor | In accordance to Drawing 2000-F00-STD-EL-10023 and 2000-F00-STD-EL- 10026. Switchroom Vendor to calculate number of required poles including 20% loaded Spare circuit breakers and 20% spare space. | 2
0 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | 1 | 415V 3Ø 250A UPS DB. Fitted with incoming isolator and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom Vendor | Switchroom Vendor | In accordance to Drawing 2000-F00-STD-EL-10027. Switchroom Vendor to calculate number of required poles including 20% loaded Spare circuit breakers and 20% spare space. | 2
0 | F16AG421-VS | Rougher Flotation Cell 1 Agitator HV VSD | 1 | 500kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens | SINAMICS Perfect Harmony GH180 6SR55020NE380BH0-Z | Primero | Switchroom Vendor |  | 2
0 | F16AG422-VS | Rougher Flotation Cell 2 Agitator HV VSD | 1 | 500kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens | SINAMICS Perfect Harmony GH180 6SR55020NE380BH0-Z | Primero | Switchroom Vendor |  | 2
0 | F16AG423-VS | Rougher Flotation Cell 3 Agitator HV VSD | 1 | 500kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens | SINAMICS Perfect Harmony GH180 6SR55020NE380BH0-Z | Primero | Switchroom Vendor |  | 2
0 | F16AG424-VS | Scavenger Flotation Cell 1 Agitator HV VSD | 1 | 500kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens | SINAMICS Perfect Harmony GH180 6SR55020NE380BH0-Z | Primero | Switchroom Vendor |  | 2
0 | F16AG425-VS | Scavenger Flotation Cell 2 Agitator HV VSD | 1 | 500kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens | SINAMICS Perfect Harmony GH180 6SR55020NE380BH0-Z | Primero | Switchroom Vendor |  | 2
0 | F16AG426-VS | Scavenger Flotation Cell 3 Agitator HV VSD | 1 | 500kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens | SINAMICS Perfect Harmony GH180 6SR55020NE380BH0-Z | Primero | Switchroom Vendor |  | 2
0 | F16AG427-VS | Scavenger Flotation Cell 4 Agitator HV VSD | 1 | 500kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens | SINAMICS Perfect Harmony GH180 6SR55020NE380BH0-Z | Primero | Switchroom Vendor |  | 2
0 | F17PP455-VS | Flotation Tailings Thickener Underflow Pump 1 HV VSD | 1 | 800kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens | SINAMICS Perfect Harmony GH180 6SR55020NF412BH0-Z | Primero | Switchroom Vendor |  | 2
0 | F17PP456-VS | Flotation Tailings Thickener Underflow Pump 2 HV VSD | 1 | 800kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens | SINAMICS Perfect Harmony GH180 6SR55020NF412BH0-Z | Primero | Switchroom Vendor |  | 2
0 | F24PW401-VS | Mill Water Pump 1 HV VSD | 1 | 800kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens | SINAMICS Perfect Harmony GH180 6SR55020NF412BH0-Z | Primero | Switchroom Vendor |  | 2
0 | F24PW402-VS | Mill Water Pump 2 HV VSD | 1 | 800kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens | SINAMICS Perfect Harmony GH180 6SR55020NF412BH0-Z | Primero | Switchroom Vendor |  | 2
0 | F24PW417-VS | High Pressure Process Water Pump 1 HV VSD | 1 | 800kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens | SINAMICS Perfect Harmony GH180 6SR55020NF412BH0-Z | Primero | Switchroom Vendor |  | 2
0 | F24PW418-VS | High Pressure Process Water Pump 2 HV VSD | 1 | 800kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens | SINAMICS Perfect Harmony GH180 6SR55020NF412BH0-Z | Primero | Switchroom Vendor |  | 2
0 | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | 1 | 48V DC Tripping and Closing Supply, 800Ah battery bank. Free-standing industrial cabinet. | Magellan | 4 string of 4 x 12V, 200Ah VRLA batteries | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 1 x U220 Battery enclosure (W:800mm, D: 800mm, H: 2200mm). IP-42, Bottom cable entry, 5mm Aluminium gland plate complete with 4 strings of 4 X 12V 200Ah VRLA Batteries. And all associated accessories. | 2
0 | F16-BC-001 | Flotation 11kV Switchroom 48V Charger | 1 | 48V DC Tripping and Closing Supply, with 200A charger complete with integral DB. Free-standing industrial cabinet. | Magellan | 48MCRII3P100 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 1 x U220 Battery enclosure (W:800mm, D: 800mm, H: 2200mm). 200A MCRII 3 Phase input charger. Compete with: Alarm relay board (voltage free alarm relays, including Floating Earth Fault). Blocking Diode Communications Board (For Modbus TCP) Including Lifting lugs, battery test facility, 1 hour battery discharge test, and integrated DC DB with 8 off 2P, 20A MCBs and 1 spare MCB with shunt trip. | 3
0 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | 1 | Communications Rack, Free Standing 19", 42U, 1000mm deep, Mesh door, Lift Off Side Panels. Fitted with 10 way 240VAC plug power distribution panel, wire management covers, shelves and cage nuts. Fitted out with FOBOTs (vendor supplied), DIN rail adapter (vendor supplied), and network switches (free issued). | Rittal | TS IT Enclosure (P/N 5514.110) + Accessories | Switchroom Vendor | Switchroom Vendor | In accordance to Drawing 2000-F00-STD-IC-10101 | 3
1 | F16COM001-JB | Flotation 11kV Switchroom Communications Rack Communications Rack 240VAC UPS Junction Box | 1 | Junction box mounted on the rear of the communications rack. All 240VAC UPS powered non-RCD Protected outlets shall be red with a "Warning. Socket not RCD Protected" Warning label. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Junction box for PDU Rail | 3
0 | F16-FOB-001 | Flotation 11kV Switchroom Fibre Optic Breakout Tray | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | 3
0 | F16-FOB-002 | Flotation 11kV Switchroom Fibre Optic Breakout Tray | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | 3
0 | F16-RIO-100 | Flotation 11kV Switchroom N-IO Panel | 1 | Remote IO panel - Indoor, Mild Steel | Fabricated Panel | Custom | Primero | Switchroom Vendor |  | 3
0 | F16SR001-LCS | Flotation 11kV Switchroom Emergency Shutdown | 1 | Switchroom Emergency Shutdown C/w shroud or lift-up flap and labelling | Fabricated Panel | VTA | Switchroom Vendor | Switchroom Vendor | With E34 Red 40mm Mushroom pushbutton (P/N E34LB2), and 2 off 2 N/O Contact Blocks (10250T2). Refer 2000-F00-STS-EL-10011 Section 4.19. | 3
0 | F16-FIP-001 | Flotation 11kV Switchroom Fire Indicator Panel | 1 | Fire Indicator Panel c/w full installation, wiring, certification, testing and commissioning. HVAC trip upon alarm. FIP shall include SMOF modems for connection to site-wide fire system network. | Wormald | Vigilant 8 Zone F3200 Conventional SHCIE FIP | Switchroom Vendor | Switchroom Vendor | Rated to operate in 50C ambience temperature | 3
0 | F16FIP001-XE1 | Flotation 11kV Switchroom VESDA Panel | 1 | VESDA Panel c/w full installation, wiring, certification, testing and commissioning.Alarm and fault signals to fire panel. | Xtralis | VESDA LaserPlus Scanner 12 relay VLS300 ASD system | Switchroom Vendor | Switchroom Vendor | Rated to operate in 50C ambience temperature | 3
0 | F16FIP001-XE2 | Flotation 11kV Switchroom Manual Call Points | VTA | Fire system Manual Call points (internal and external) as required by Australian Standards | Wormald | Manual Call Points | Switchroom Vendor | Switchroom Vendor | Manual call points shall be tagged in sequential order | 3
0 | F16FIP001-XE3 | Flotation 11kV Switchroom Smoke Detector | VTA | Fire system smoke detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom Vendor | Switchroom Vendor | Detectors shall be tagged in sequential order | 3
0 | F16FIP001-XE4 | Flotation 11kV Switchroom Fire Detector | VTA | Fire system fire detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom Vendor | Switchroom Vendor | Detectors shall be tagged in sequential order | 3
0 | F16FIP001-UA | Flotation 11kV Switchroom External Alarm Bells | VTA | Fire system alarm sirens as required by Australian Standards | Wormald | External Sounder / Red Strobe | Switchroom Vendor | Switchroom Vendor | Alarm sirens shall be tagged in sequential order | 3
0 | F16FIP001-XE5 | Flotation 11kV Switchroom Gas Suppression System (Inergen) | 1 | Inergen gas suppression system incl. all valves and pipework and cabinet for gas cylinders to be placed within switchroom. | VTA | VTA | Switchroom Vendor | Switchroom Vendor |  | 3
0 | - | Flotation 11kV Switchroom Fire Extinguishers | VTA | 5kg dry powder fire extinguishers complete with wall mount and signage. | VTA | VTA | Switchroom Vendor | Switchroom Vendor |  | 3
0 | - | Flotation 11kV Switchroom Automatic External Defibrillator | 1 | Automatic external defibrillator complete with wall-mounted cabinet. | Physio Control | Lifepak Defibrillator CR2 Fully Automatic | Switchroom Vendor | Switchroom Vendor |  | 3
0 | - | Flotation 11kV Switchroom HV Rescue Kit | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom Vendor | Switchroom Vendor |  | 3
0 | - | Flotation 11kV Switchroom CPR Signage | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom Vendor | Switchroom Vendor |  | 3
2 | - | Flotation 11kV Switchroom HVAC Controller | VTA | Wall mounted Air Conditioner Controller | VTA | VTA | Switchroom Vendor | Switchroom Vendor | One wall mounted controller to control all A/C's per room (One per transformer room, LV room, HV room). Vendor to advise if actual control panel is required. | 3
0 | F16-AC-0XX | Flotation 11kV Switchroom HVAC Units | VTA | High Wall split system, single phase, MULTIPLE (N+1 reqd) with drip trays if necessary | VTA | VTA | Switchroom Vendor | Switchroom Vendor | Switchroom Vendor to provide the most cost effective HVAC solution for the heat loads including the failure of a single unit. Splits are preferred however may not be possible. AC units shall be tagged in numercial order (e.g. F16-AC-001, F16-AC-002 etc. ) | 3
0 | F16AC0XX-ISL | Flotation 11kV Switchroom Air Conditioner Isolators | VTA | Field isolator, one per split system AC | VTA | VTA | Switchroom Vendor | Switchroom Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Isolators shall be tagged with the respective AC equipment number (e.g. F16AC0xx-ISL etc) | 3
0 | - | Flotation 11kV Switchroom Normal Light Fittings | 1 lot | Lighting to meet National Construction Code | VTA | VTA | Switchroom Vendor | Switchroom Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | 3
0 | - | Flotation 11kV Switchroom Emergency Light Fittings | 1 lot | Lighting to meet National Construction Code; C/w built in battery pack. | VTA | VTA | Switchroom Vendor | Switchroom Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | 4
0 | UT16030 | F16-SR-001 Flotation 11kV Switchroom Temperature/Humidity Transmitter | 1 | Switchroom Temperature/Humidity Transmitter | VTA | VTA | Switchroom Vendor | Switchroom Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | 4
0 | F16-PE-001 | Flotation 11kV Switchroom Photo-electric Cell Photo-electric cell | 1 | Switchroom Photo-electric cell | VTA | VTA | Switchroom Vendor | Switchroom Vendor | PE Cell - 1 per building. Vendor to position | 4
1 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | 1 | IP65 Enclosure, hinged, lockable, clear perspex escutcheon cover over operator interfaces to prevent inadvertent/unauthorised operation. Remote Switching Local control station (visual mimic and control of CBs, VSD Contactors, earth switches) with door mounted selector switches providing open/close functionality for CBs, Contactors and earth switches, rack in/rack out functionality of circuit breakers and contactors and indication lights for status. Provided with the following for each panel type: Bus VT & Earth Switch Panels (1 off) • 1 off Earth Switch Indicator (RD/GN) • 1 off VT Rack Indicator (RD/GN) • 1 off 3-position Selector Switches • 1 off 2-position Selector Switches Fused Contactor Feeder Panels (13 off) • 3 off Contactor/Earth Switch Indicators (RD/GN) • 1 off Fused Contactor Racked In/Racked Out Indicators (RD/GN) • 3 off 3-position Selector Switches • 1 off 2-position Selector Switches Incomer & CB Feeder Panels (4 off) • 3 off Circuit Breaker/Earth Switch Indicators (RD/GN) • 1 off CB Racked In/Racked Out Indicators (RD/GN) • 3 off 3-position Selector Switches • 1 off 2-position Selector Switches Bus-Tie and Bus-Tie Riser (1 off) • 2 off Circuit Breaker/Earth Switch Indicators (RD/GN) • 2 off CB Racked In/Racked Out Indicators (RD/GN) • 3 off Selector Switches | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Typical Schematics & GA to be provided to Switchroom Vendor to design and fabricate panel. | 4
0 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | 1 | External to Room: 50 x 6.3mm Tinned Flat Copper Bus bar mounted on insulated standoffs under switchroom floor. Drilled/punch 12mm diameter holes suitable for connection of all internal equipment earth cables to meet requirements of cable schedule. To have spare capacity for connection of an additional 4 x 120mm2 conductors and 4 x 70mm2 conductors, as a minimum. | GVK or similar |  | Switchroom Vendor | Switchroom Vendor |  | 4
0 | F16SW011-EB01 | Flotation 11kV Switchboard Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on insulated standoffs inside Switchboard. | TBA | TBA | Primero | Switchroom Vendor |  | 4

## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred colour) | Installation | Supplied By | Installed By | Comments | Revision | Page
F16BC001-P1 | F16-DB-101 | FLOTATION 11KV SWITCHROOM HV VSD AUXILIARY SUPPLIES DISTRIBUTION BOARD | Flotation 11kV Switchroom | F16-BC-001 | Flotation 11kV Switchroom 48V Charger | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Charger Supply. 3ph | 1 | 5
F16BA001-P11-R | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P12-R | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P11-B | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P12-B | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P21-R | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P22-R | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P21-B | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P22-B | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P31-R | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P32-R | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P31-B | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P32-B | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P41-R | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P42-R | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P41-B | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16BA001-P42-B | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 25 | 0.6/1 | 1C | Cu | X-HF-110 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 5
F16SW011-P3 | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | 6 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Charger - 48VDC to switchboard | 0 | 5
F16SW011-P4 | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | 6 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Charger - 48VDC to switchboard | 0 | 5
F16SW011-P5 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V for panel anticondensation heaters. | 0 | 5
F16SW011LCS-P1 | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Charger - 48VDC to switchboard | 0 | 5
F16AG421VS-P1-R | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG421-VS | Rougher Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 5
F16AG421VS-P1-W | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG421-VS | Rougher Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 5
F16AG421VS-P1-B | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG421-VS | Rougher Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 5
F16AG421VS-P2 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | F16AG421-VS | Rougher Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 415V 3ph Auxiliary Supply | 1 | 5
F16AG421VS-P3 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F16AG421-VS | Rougher Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V UPS Supply | 0 | 5
F16AG422VS-P1-R | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG422-VS | Rougher Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 5
F16AG422VS-P1-W | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG422-VS | Rougher Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 5
F16AG422VS-P1-B | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG422-VS | Rougher Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 5
F16AG422VS-P2 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | F16AG422-VS | Rougher Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 415V 3ph Auxiliary Supply | 1 | 5
F16AG422VS-P3 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F16AG422-VS | Rougher Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V UPS Supply | 0 | 5
F16AG423VS-P1-R | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG423-VS | Rougher Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 5
F16AG423VS-P1-W | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG423-VS | Rougher Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 5
F16AG423VS-P1-B | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG423-VS | Rougher Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F16AG423VS-P2 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | F16AG423-VS | Rougher Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 415V 3ph Auxiliary Supply | 1 | 6
F16AG423VS-P3 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F16AG423-VS | Rougher Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V UPS Supply | 0 | 6
F16AG424VS-P1-R | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG424-VS | Scavenger Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F16AG424VS-P1-W | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG424-VS | Scavenger Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F16AG424VS-P1-B | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG424-VS | Scavenger Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F16AG424VS-P2 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | F16AG424-VS | Scavenger Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 415V 3ph Auxiliary Supply | 1 | 6
F16AG424VS-P3 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F16AG424-VS | Scavenger Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V UPS Supply | 0 | 6
F16AG425VS-P1-R | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG425-VS | Scavenger Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F16AG425VS-P1-W | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG425-VS | Scavenger Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F16AG425VS-P1-B | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG425-VS | Scavenger Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F16AG425VS-P2 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | F16AG425-VS | Scavenger Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 415V 3ph Auxiliary Supply | 1 | 6
F16AG425VS-P3 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F16AG425-VS | Scavenger Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V UPS Supply | 0 | 6
F16AG426VS-P1-R | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG426-VS | Scavenger Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F16AG426VS-P1-W | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG426-VS | Scavenger Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F16AG426VS-P1-B | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG426-VS | Scavenger Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F16AG426VS-P2 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | F16AG426-VS | Scavenger Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 415V 3ph Auxiliary Supply | 1 | 6
F16AG426VS-P3 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F16AG426-VS | Scavenger Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V UPS Supply | 0 | 6
F16AG427VS-P1-R | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG427-VS | Scavenger Flotation Cell 4 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F16AG427VS-P1-W | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG427-VS | Scavenger Flotation Cell 4 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F16AG427VS-P1-B | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG427-VS | Scavenger Flotation Cell 4 Agitator HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F16AG427VS-P2 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | F16AG427-VS | Scavenger Flotation Cell 4 Agitator HV VSD | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 415V 3ph Auxiliary Supply | 1 | 6
F16AG427VS-P3 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F16AG427-VS | Scavenger Flotation Cell 4 Agitator HV VSD | Flotation 11kV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V UPS Supply | 0 | 6
F17PP455VS-P1-R | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F17PP455-VS | Flotation Tailings Thickener Underflow Pump 1 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F17PP455VS-P1-W | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F17PP455-VS | Flotation Tailings Thickener Underflow Pump 1 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F17PP455VS-P1-B | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F17PP455-VS | Flotation Tailings Thickener Underflow Pump 1 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F17PP455VS-P2 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | F17PP455-VS | Flotation Tailings Thickener Underflow Pump 1 HV VSD | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 415V 3ph Auxiliary Supply | 1 | 6
F17PP455VS-P3 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F17PP455-VS | Flotation Tailings Thickener Underflow Pump 1 HV VSD | Flotation 11kV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V UPS Supply | 0 | 6
F17PP456VS-P1-R | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F17PP456-VS | Flotation Tailings Thickener Underflow Pump 2 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 6
F17PP456VS-P1-W | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F17PP456-VS | Flotation Tailings Thickener Underflow Pump 2 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F17PP456VS-P1-B | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F17PP456-VS | Flotation Tailings Thickener Underflow Pump 2 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F17PP456VS-P2 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | F17PP456-VS | Flotation Tailings Thickener Underflow Pump 2 HV VSD | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 415V 3ph Auxiliary Supply | 1 | 7
F17PP456VS-P3 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F17PP456-VS | Flotation Tailings Thickener Underflow Pump 2 HV VSD | Flotation 11kV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V UPS Supply | 0 | 7
F24PW401VS-P1-R | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW401-VS | Mill Water Pump 1 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F24PW401VS-P1-W | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW401-VS | Mill Water Pump 1 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F24PW401VS-P1-B | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW401-VS | Mill Water Pump 1 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F24PW401VS-P2 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | F24PW401-VS | Mill Water Pump 1 HV VSD | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 415V 3ph Auxiliary Supply | 1 | 7
F24PW401VS-P3 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F24PW401-VS | Mill Water Pump 1 HV VSD | Flotation 11kV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V UPS Supply | 0 | 7
F24PW402VS-P1-R | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW402-VS | Mill Water Pump 2 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F24PW402VS-P1-W | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW402-VS | Mill Water Pump 2 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F24PW402VS-P1-B | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW402-VS | Mill Water Pump 2 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F24PW402VS-P2 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | F24PW402-VS | Mill Water Pump 2 HV VSD | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 415V 3ph Auxiliary Supply | 1 | 7
F24PW402VS-P3 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F24PW402-VS | Mill Water Pump 2 HV VSD | Flotation 11kV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V UPS Supply | 0 | 7
F24PW417VS-P1-R | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW417-VS | High Pressure Process Water Pump 1 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F24PW417VS-P1-W | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW417-VS | High Pressure Process Water Pump 1 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F24PW417VS-P1-B | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW417-VS | High Pressure Process Water Pump 1 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F24PW417VS-P2 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | F24PW417-VS | High Pressure Process Water Pump 1 HV VSD | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 415V 3ph Auxiliary Supply | 1 | 7
F24PW417VS-P3 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F24PW417-VS | High Pressure Process Water Pump 1 HV VSD | Flotation 11kV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V UPS Supply | 0 | 7
F24PW418VS-P1-R | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW418-VS | High Pressure Process Water Pump 2 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F24PW418VS-P1-W | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW418-VS | High Pressure Process Water Pump 2 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F24PW418VS-P1-B | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW418-VS | High Pressure Process Water Pump 2 HV VSD | Flotation 11kV Switchroom | 50 | 11 | 1C | Cu | R-EP-90/EPR/XHD-90-PCP AS2802 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Protolon Part No. 5DK5 566 (11kV flexible 6D bending radius installed). In trefoil, SS cable tie on every rung. | 0 | 7
F24PW418VS-P2 | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | F24PW418-VS | High Pressure Process Water Pump 2 HV VSD | Flotation 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 415V 3ph Auxiliary Supply | 1 | 7
F24PW418VS-P3 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F24PW418-VS | High Pressure Process Water Pump 2 HV VSD | Flotation 11kV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 240V UPS Supply | 0 | 7
F16FIP001-P1 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16-FIP-001 | Flotation 11kV Switchroom Fire Indicator Panel | Flotation 11kV Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 7
F16FIP001XE1-P1 | F16-FIP-001 | Flotation 11kV Switchroom Fire Indicator Panel | Flotation 11kV Switchroom | F16FIP001-XE1 | Flotation 11kV Switchroom VESDA Panel | Flotation 11kV Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 7
F16COM001-P1 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 7
F16RIO100-P1 | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | F16-RIO-100 | Flotation 11kV Switchroom N-IO Panel | Flotation 11kV Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 7
F16DB001-R13 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC001-ISL | Flotation 11kV Switchroom Air Conditioner No. 1 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16AC001-P1 | F16AC001-ISL | Flotation 11kV Switchroom Air Conditioner No. 1 Isolator | Flotation 11kV Switchroom | F16-AC-001 | Flotation 11kV Switchroom Air Conditioner No. 1 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16DB001-W13 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC002-ISL | Flotation 11kV Switchroom Air Conditioner No. 2 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16AC002-P1 | F16AC002-ISL | Flotation 11kV Switchroom Air Conditioner No. 2 Isolator | Flotation 11kV Switchroom | F16-AC-002 | Flotation 11kV Switchroom Air Conditioner No. 2 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16DB001-B13 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC003-ISL | Flotation 11kV Switchroom Air Conditioner No. 3 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16AC003-P1 | F16AC003-ISL | Flotation 11kV Switchroom Air Conditioner No. 3 Isolator | Flotation 11kV Switchroom | F16-AC-003 | Flotation 11kV Switchroom Air Conditioner No. 3 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16DB001-R15 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC004-ISL | Flotation 11kV Switchroom Air Conditioner No. 4 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16AC004-P1 | F16AC004-ISL | Flotation 11kV Switchroom Air Conditioner No. 4 Isolator | Flotation 11kV Switchroom | F16-AC-004 | Flotation 11kV Switchroom Air Conditioner No. 4 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16DB001-W15 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC005-ISL | Flotation 11kV Switchroom Air Conditioner No. 5 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16AC005-P1 | F16AC005-ISL | Flotation 11kV Switchroom Air Conditioner No. 5 Isolator | Flotation 11kV Switchroom | F16-AC-005 | Flotation 11kV Switchroom Air Conditioner No. 5 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16DB001-B15 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC006-ISL | Flotation 11kV Switchroom Air Conditioner No. 6 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16AC006-P1 | F16AC006-ISL | Flotation 11kV Switchroom Air Conditioner No. 6 Isolator | Flotation 11kV Switchroom | F16-AC-006 | Flotation 11kV Switchroom Air Conditioner No. 6 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16DB001-R17 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC007-ISL | Flotation 11kV Switchroom Air Conditioner No. 7 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16AC007-P1 | F16AC007-ISL | Flotation 11kV Switchroom Air Conditioner No. 7 Isolator | Flotation 11kV Switchroom | F16-AC-007 | Flotation 11kV Switchroom Air Conditioner No. 7 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16DB001-W17 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC008-ISL | Flotation 11kV Switchroom Air Conditioner No. 8 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16AC008-P1 | F16AC008-ISL | Flotation 11kV Switchroom Air Conditioner No. 8 Isolator | Flotation 11kV Switchroom | F16-AC-008 | Flotation 11kV Switchroom Air Conditioner No. 8 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16DB001-B17 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC009-ISL | Flotation 11kV Switchroom Air Conditioner No. 9 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16AC009-P1 | F16AC009-ISL | Flotation 11kV Switchroom Air Conditioner No. 9 Isolator | Flotation 11kV Switchroom | F16-AC-009 | Flotation 11kV Switchroom Air Conditioner No. 9 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16DB001-R19 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC010-ISL | Flotation 11kV Switchroom Air Conditioner No. 10 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16AC010-P1 | F16AC010-ISL | Flotation 11kV Switchroom Air Conditioner No. 10 Isolator | Flotation 11kV Switchroom | F16-AC-010 | Flotation 11kV Switchroom Air Conditioner No. 10 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16DB001-W19 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC011-ISL | Flotation 11kV Switchroom Air Conditioner No. 11 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16AC011-P1 | F16AC011-ISL | Flotation 11kV Switchroom Air Conditioner No. 11 Isolator | Flotation 11kV Switchroom | F16-AC-011 | Flotation 11kV Switchroom Air Conditioner No. 11 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16DB001-B19 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC012-ISL | Flotation 11kV Switchroom Air Conditioner No. 12 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16AC012-P1 | F16AC012-ISL | Flotation 11kV Switchroom Air Conditioner No. 12 Isolator | Flotation 11kV Switchroom | F16-AC-012 | Flotation 11kV Switchroom Air Conditioner No. 12 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 8
F16DB001-R14 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC013-ISL | Flotation 11kV Switchroom Air Conditioner No. 13 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16AC013-P1 | F16AC013-ISL | Flotation 11kV Switchroom Air Conditioner No. 13 Isolator | Flotation 11kV Switchroom | F16-AC-013 | Flotation 11kV Switchroom Air Conditioner No. 13 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-W14 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC014-ISL | Flotation 11kV Switchroom Air Conditioner No. 14 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16AC014-P1 | F16AC014-ISL | Flotation 11kV Switchroom Air Conditioner No. 14 Isolator | Flotation 11kV Switchroom | F16-AC-014 | Flotation 11kV Switchroom Air Conditioner No. 14 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-B14 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC015-ISL | Flotation 11kV Switchroom Air Conditioner No. 15 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16AC015-P1 | F16AC015-ISL | Flotation 11kV Switchroom Air Conditioner No. 15 Isolator | Flotation 11kV Switchroom | F16-AC-015 | Flotation 11kV Switchroom Air Conditioner No. 15 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-R16 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC016-ISL | Flotation 11kV Switchroom Air Conditioner No. 16 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16AC016-P1 | F16AC016-ISL | Flotation 11kV Switchroom Air Conditioner No. 16 Isolator | Flotation 11kV Switchroom | F16-AC-016 | Flotation 11kV Switchroom Air Conditioner No. 16 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-W16 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC017-ISL | Flotation 11kV Switchroom Air Conditioner No. 17 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16AC017-P1 | F16AC017-ISL | Flotation 11kV Switchroom Air Conditioner No. 17 Isolator | Flotation 11kV Switchroom | F16-AC-017 | Flotation 11kV Switchroom Air Conditioner No. 17 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-B16 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC018-ISL | Flotation 11kV Switchroom Air Conditioner No. 18 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16AC018-P1 | F16AC018-ISL | Flotation 11kV Switchroom Air Conditioner No. 18 Isolator | Flotation 11kV Switchroom | F16-AC-018 | Flotation 11kV Switchroom Air Conditioner No. 18 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-R18 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC019-ISL | Flotation 11kV Switchroom Air Conditioner No. 19 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16AC019-P1 | F16AC019-ISL | Flotation 11kV Switchroom Air Conditioner No. 19 Isolator | Flotation 11kV Switchroom | F16-AC-019 | Flotation 11kV Switchroom Air Conditioner No. 19 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-W18 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC020-ISL | Flotation 11kV Switchroom Air Conditioner No. 20 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16AC020-P1 | F16AC020-ISL | Flotation 11kV Switchroom Air Conditioner No. 20 Isolator | Flotation 11kV Switchroom | F16-AC-020 | Flotation 11kV Switchroom Air Conditioner No. 20 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-B18 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | F16AC021-ISL | Flotation 11kV Switchroom Air Conditioner No. 21 Isolator | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16AC021-P1 | F16AC021-ISL | Flotation 11kV Switchroom Air Conditioner No. 21 Isolator | Flotation 11kV Switchroom | F16-AC-021 | Flotation 11kV Switchroom Air Conditioner No. 21 | Flotation 11kV Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-R09 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom |  | Lighting - Switchroom Internal 1 (Low Side of Roof) | Flotation 11kV Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-R09_ | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom |  | Lighting - Switchroom Internal 1 (Emergency) | Flotation 11kV Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-W09 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom |  | Lighting - Switchroom Internal 2 (High Side of Roof) | Flotation 11kV Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-W09_ | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom |  | Lighting - Switchroom Internal 2 (Emergency) | Flotation 11kV Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-B10 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom |  | Lighting - Switchroom External 1 | Flotation 11kV Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-B10_ | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom |  | Lighting - Switchroom External 1 (Emergency) | Flotation 11kV Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 9
F16DB001-W08 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom |  | Lighting - Switchroom External Junction Box (for site use) | Flotation 11kV Switchroom | 4 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 10
F16DB001-R03 | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom |  | General Power - Flotation 11kV Switchroom GPO's | Flotation 11kV Switchroom | 4 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor |  | 3 | 10
F16SW011-C25 | F16SR001-LCS | Flotation 11kV Switchroom Emergency Shutdown | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 09 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Emerg/ Shutdown Circuit. E-shut to trip incomer | 2 | 10
F16SW011-C26 | F16SR001-LCS | Flotation 11kV Switchroom Emergency Shutdown | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 15 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Emerg/ Shutdown Circuit. E-shut to trip incomer | 2 | 10
F16SW011-C2 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 01 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C24 | F16-RIO-100 | Flotation 11kV Switchroom N-IO Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 01 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DCS Bus/VT Signals | 1 | 10
F16SW011-C3 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 02 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C4 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 03 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C5 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 04 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C6 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 05 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C7 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 06 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C8 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 07 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C9 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 08 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C10 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 09 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C11 | F16-RIO-100 | Flotation 11kV Switchroom N-IO Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 09 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DCS incomer Open/Close | 1 | 10
F16SW011-C12 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 10 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C13 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 11 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C14 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 12 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C15 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 13 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C16 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 15 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C17 | F16-RIO-100 | Flotation 11kV Switchroom N-IO Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 15 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DCS incomer Open/Close | 1 | 10
F16SW011-C18 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 16 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C19 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 17 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C20 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 18 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C21 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 19 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C22 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 20 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 1 | 10
F16SW011-C23 | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel 21 | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 10
F16AG421VS-C1 | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG421-VS | Rougher Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 12C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 10
F16AG422VS-C1 | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG422-VS | Rougher Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 12C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 10
F16AG423VS-C1 | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG423-VS | Rougher Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 12C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16AG424VS-C1 | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG424-VS | Scavenger Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 12C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16AG425VS-C1 | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG425-VS | Scavenger Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 12C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16AG426VS-C1 | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG426-VS | Scavenger Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 12C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16AG427VS-C1 | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F16AG427-VS | Scavenger Flotation Cell 4 Agitator HV VSD | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 12C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F24PW401VS-C1 | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW401-VS | Mill Water Pump 1 HV VSD | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 12C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F24PW402VS-C1 | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW402-VS | Mill Water Pump 2 HV VSD | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 12C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F24PW417VS-C1 | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW417-VS | High Pressure Process Water Pump 1 HV VSD | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 12C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F24PW418VS-C1 | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F24PW418-VS | High Pressure Process Water Pump 2 HV VSD | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 12C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F17PP455VS-C1 | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F17PP455-VS | Flotation Tailings Thickener Underflow Pump 1 HV VSD | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 12C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F17PP456VS-C1 | F16-SW-011 | Flotation 11kV Switchboard | Flotation 11kV Switchroom | F17PP456-VS | Flotation Tailings Thickener Underflow Pump 2 HV VSD | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 12C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16DB001-C1 | F16-FIP-001 | Flotation 11kV Switchroom Fire Indicator Panel | Flotation 11kV Switchroom | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 2C | Cu | R-EP-110 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | HVAC trip. | 3 | 11
F16FIP001-C1 | F16-RIO-100 | Flotation 11kV Switchroom N-IO Panel | Flotation 11kV Switchroom | F16-FIP-001 | Flotation 11kV Switchroom Fire Indicator Panel | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16SR001LCS-C1 | F16-RIO-100 | Flotation 11kV Switchroom N-IO Panel | Flotation 11kV Switchroom | F16SR001-LCS | Flotation 11kV Switchroom Emergency Shutdown | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Emergency Shut-Down Status. 24VDC supply for Pilz Relay also included. | 2 | 11
F16DB001-C2 | F16-PE-001 | Flotation 11kV Switchroom Photo-electric Cell | Flotation 11kV Switchroom | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | 2.5 | 0.45/0.75 | 3C+E | Cu | Flat - PVC/PVC | White | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Lighting Control. Direct from PE | 3 | 11
UT16030-I1 | F16-RIO-100 | Flotation 11kV Switchroom N-IO Panel | Flotation 11kV Switchroom | UT16030 | F16-SR-001 Flotation 11kV Switchroom Temperature/Humidity Transmitter | Flotation 11kV Switchroom | 1.5 | 0.15 | 2 Pr | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 11
F16BC001-C1 | F16-RIO-100 | Flotation 11kV Switchroom N-IO Panel | Flotation 11kV Switchroom | F16-BC-001 | Flotation 11kV Switchroom 48VDC Charger | Flotation 11kV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Hardwire allowance | 0 | 11
F16FIP001-FO1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-FIP-001 | Flotation 11kV Switchroom Fire Indicator Panel | Flotation 11kV Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | Patching between communication rack and FIP. | 0 | 11
F16FIP001-FO2 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-FIP-001 | Flotation 11kV Switchroom Fire Indicator Panel | Flotation 11kV Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | Patching between communication rack and FIP. | 0 | 11
F16SW011-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A09 (Main Incomer) - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16SW011-D2 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A09 (Main Incomer) - SEL 735 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16SW011-D3 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A02 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16SW011-D4 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A03 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16SW011-D5 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A04 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16SW011-D6 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A05 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16SW011-D7 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A06 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16SW011-D8 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A07 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16SW011-D9 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A08 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16SW011-D10 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A10 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 11
F16SW011-D11 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A11 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16SW011-D12 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A12 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16SW011-D13 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A15 (Generator Incomer) - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16SW011-D14 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A15 (Generator Incomer) - SEL 700G | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16SW011-D15 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A16 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16SW011-D16 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A17 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16SW011-D17 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A18 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16SW011-D18 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A19 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16SW011-D19 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-SW-011 | Flotation 11kV Switchboard Panel A20 - SEL 751 | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16AG421VS-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16AG421-VS | Rougher Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16AG422VS-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16AG422-VS | Rougher Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16AG423VS-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16AG423-VS | Rougher Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16AG424VS-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16AG424-VS | Scavenger Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16AG425VS-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16AG425-VS | Scavenger Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16AG426VS-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16AG426-VS | Scavenger Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16AG427VS-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16AG427-VS | Scavenger Flotation Cell 4 Agitator HV VSD | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F24PW401VS-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F24PW401-VS | Mill Water Pump 1 HV VSD | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F24PW402VS-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F24PW402-VS | Mill Water Pump 2 HV VSD | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F24PW417VS-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F24PW417-VS | High Pressure Process Water Pump 1 HV VSD | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F24PW418VS-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F24PW418-VS | High Pressure Process Water Pump 2 HV VSD | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F17PP455VS-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F17PP455-VS | Flotation Tailings Thickener Underflow Pump 1 HV VSD | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F17PP456VS-D1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F17PP456-VS | Flotation Tailings Thickener Underflow Pump 2 HV VSD | Flotation 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16RIO100-FO1 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-RIO-100 | Flotation 11kV Switchroom N-IO Panel | Flotation 11kV Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | DCS Comms - NIU UPLINK (Optical ESB Bus Primary) | 0 | 12
F16RIO100-FO2 | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | F16-RIO-100 | Flotation 11kV Switchroom N-IO Panel | Flotation 11kV Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | DCS Comms - NIU UPLINK (Optical ESB Bus Secondary) | 0 | 12
F16SW011EB01-E2 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16SW011-EB01 | Flotation 11kV Switchboard Earth Bar | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Each end of HV switchboard earth bar to be bonded to switchroom earth bar. | 0 | 12
F16SW011EB01-E3 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16SW011-EB01 | Flotation 11kV Switchboard Earth Bar | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | Each end of HV switchboard earth bar to be bonded to switchroom earth bar. | 0 | 12
F16AG421VS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16AG421-VS | Rougher Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16AG422VS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16AG422-VS | Rougher Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16AG423VS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16AG423-VS | Rougher Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 12
F16AG424VS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16AG424-VS | Scavenger Flotation Cell 1 Agitator HV VSD | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 13
F16AG425VS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16AG425-VS | Scavenger Flotation Cell 2 Agitator HV VSD | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 13
F16AG426VS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16AG426-VS | Scavenger Flotation Cell 3 Agitator HV VSD | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 13
F16AG427VS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16AG427-VS | Scavenger Flotation Cell 4 Agitator HV VSD | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 13
F17PP455VS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F17PP455-VS | Flotation Tailings Thickener Underflow Pump 1 HV VSD | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 13
F17PP456VS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F17PP456-VS | Flotation Tailings Thickener Underflow Pump 2 HV VSD | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 13
F24PW401VS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F24PW401-VS | Mill Water Pump 1 HV VSD | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 13
F24PW402VS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F24PW402-VS | Mill Water Pump 2 HV VSD | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 13
F24PW417VS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F24PW417-VS | High Pressure Process Water Pump 1 HV VSD | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 13
F24PW418VS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F24PW418-VS | High Pressure Process Water Pump 2 HV VSD | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 0 | 13
F16BC001-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16-BC-001 | Flotation 11kV Switchroom 48V Charger | Flotation 11kV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
F16BA001-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16-BA-001 | Flotation 11kV Switchroom 48V Battery | Flotation 11kV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
F16SW011LCS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16SW011-LCS | Flotation 11kV Switchboard Remote Switching Panel | Flotation 11kV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
F16SR001LCS-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16SR001-LCS | Flotation 11kV Switchroom Emergency Shutdown | Flotation 11kV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
F16DB001-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16-DB-001 | Flotation 11kV Switchroom L&SP Distribution Board | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
F16DB101-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16-DB-101 | Flotation 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | Flotation 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
F16DB201-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16-DB-201 | Flotation 11kV Switchroom 415VAC UPS Distribution Board | Flotation 11kV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
F16FIP001-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16-FIP-001 | Flotation 11kV Switchroom Fire Indicator Panel | Flotation 11kV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
F16COM001-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16-COM-001 | Flotation 11kV Switchroom Communications Rack | Flotation 11kV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
F16RIO100-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16-RIO-100 | Flotation 11kV Switchroom N-IO Panel | Flotation 11kV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
F16SR001-E3 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16-SR-001 | Subfloor Cable Ladder | Flotation 11kV Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
F16SR001-E4 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16-SR-001 | Subfloor Cable Ladder | Flotation 11kV Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
Ladder Joint Bonds | F16-SR-001 | Subfloor Cable Ladder | Flotation 11kV Switchroom | F16-SR-001 | Subfloor Cable Ladder | Flotation 11kV Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
F16SR001-E1 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16-SR-001 | Switchroom Subframe | Flotation 11kV Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13
F16SR001-E2 | F16SR001-EB01 | Flotation 11kV Switchroom Earth Bar | Flotation 11kV Switchroom | F16-SR-001 | Switchroom Subframe | Flotation 11kV Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor |  | 3 | 13