## Equipment list
Rev | Equip. Number | Equipment Name | Qty | Description | Make | Model | Supplied By | Installed By | Comments | Page
0 | F16-SR-002 | Flotation 415V Switchroom | 1 | Transportable switchroom complete with 1.8m legs and landings, transported to site 600kms on sealed roads. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero | Refer 2000-F00-DSH-EL-11001 | 2
0 | - | Flotation 415V Switchroom Landings and stairs | 1 | Equipment Landing to be structural steel baseframe complete with 1.8m legs and landings, designed to support heaviest piece of equipment to be installed in room. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero |  | 2
0 | - | Flotation 415V MCC Transformer Enclosure Room | 1 | Separate dry transformer enclosure with removable wall panel and personnel access door Fortress key locked (Keyed alike) with 33kV feeder earth switch on F00-SW-010 33kV switchgear | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Access to transformer cubicle is only possible with 33kV Feeder isolated and earthed. Switchroom manufacturer to coordinate Fortress keys with TEKSAL. | 2
0 | - | Flotation Blowers and Compressors 415V MCC Transformer Enclosure Room | 1 | Separate dry transformer enclosure with removable wall panel and personnel access door Fortress key locked (Keyed alike) with 33kV feeder earth switch on F00-SW-010 33kV switchgear | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Access to transformer cubicle is only possible with 33kV Feeder isolated and earthed. Switchroom manufacturer to coordinate Fortress keys with TEKSAL. | 2
0 | - | Thickener Emergency Power 415V MCC Transformer Enclosure Room | 1 | Separate dry transformer enclosure with removable wall panel and personnel access door Fortress key locked (Keyed alike) with 11kV feeder earth switch on F16-SW-011 11kV switchgear | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Access to transformer cubicle is only possible with 11kV Feeder isolated and earthed. Switchroom manufacturer to coordinate Fortress keys with TEKSAL. | 2
0 | - | Flotation 415V MCC Transformer Enclosure Room Signage | 1 | TRANSFORMER ENCLOSURE F16-TR-004 33,000/433 VOLTS (Modify to suit) DANGER – HIGH VOLTAGE (with the lightning bolt sign) NO UNAUTHORISED ACCESS – ENSURE SUPPLY IS ISOLATED AND EARTHED PRIOR TO ENTRY ISOLATE AT F00-SW-010, PANEL BXX (BXX being the 33kV panel/tier number) | Switchroom Vendor |  | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Signage to be placed on outside of transformer enclosure | 2
0 | - | Flotation Blowers and Compressors 415V MCC Transformer Enclosure Room Signage | 1 | TRANSFORMER ENCLOSURE F16-TR-005 33,000/433 VOLTS (Modify to suit) DANGER – HIGH VOLTAGE (with the lightning bolt sign) NO UNAUTHORISED ACCESS – ENSURE SUPPLY IS ISOLATED AND EARTHED PRIOR TO ENTRY ISOLATE AT F00-SW-010, PANEL BXX (BXX being the 33kV panel/tier number) | Switchroom Vendor |  | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Signage to be placed on outside of transformer enclosure | 2
0 | - | Thickener Emergency Power 415V MCC Transformer Enclosure Room Signage | 1 | TRANSFORMER ENCLOSURE F16-TR-008 11,000/433 VOLTS (Modify to suit) DANGER – HIGH VOLTAGE (with the lightning bolt sign) NO UNAUTHORISED ACCESS – ENSURE SUPPLY IS ISOLATED AND EARTHED PRIOR TO ENTRY ISOLATE AT F16-SW-011 , PANEL AXX (AXX being the 11kV panel/tier number) | Switchroom Vendor |  | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Signage to be placed on outside of transformer enclosure | 2
0 | F16-TR-004 | Flotation 415V MCC Transformer | 1 | Dry Type Transformer, 33/0.433kV, 2500kVA Dyn11, AN/AF. | Siemens | 33/0.433kV 2500kVA | Primero | Switchroom/MCC Vendor | Vendor to remove wheels and secure transformer once installed. Wheels to be stored securely within the transformer room. Vendor to bolt down/brace for transport. Refer transformer GAs. | 2
0 | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | 1 | Dry Type Transformer, 33/0.433kV, 2500kVA Dyn11, AN/AF. | Siemens | 33/0.433kV 2500kVA | Primero | Switchroom/MCC Vendor | Vendor to remove wheels and secure transformer once installed. Wheels to be stored securely within the transformer room. Vendor to bolt down/brace for transport. Refer transformer GAs. | 2
0 | F16-TR-008 | Thickener Emergency Power 415V MCC Transformer | 1 | Dry Type Transformer, 11/0.433kV, 630kVA Dyn11, AN/AF. | Siemens | 11/0.433kV 630kVA | Primero | Switchroom/MCC Vendor | Vendor to remove wheels and secure transformer once installed. Wheels to be stored securely within the transformer room. Vendor to bolt down/brace for transport. Refer transformer GAs. | 2
0 | F16-SW-004 | Flotation 415V MCC | 1 | Demountable Form 4a double sided 415V Switchboard, 4000A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Vendor to install free issued network switches in MCC Refer datasheet 2000-F00-DSH-EL-11008 | 2
0 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | 1 | Demountable Form 4a double sided 415V Switchboard, 4000A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Vendor to install free issued network switches in MCC Refer datasheet 2000-F00-DSH-EL-11008 | 2
0 | F16-SW-008 | Thickener Emergency Power 415V MCC | 1 | Demountable Form 4a double sided 415V Switchboard, 960A bus 65kA/1s fault rating, internal arc fault containment. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Vendor to install free issued network switches in MCC Refer datasheet 2000-F00-DSH-EL-11008 | 2
0 | F16-SW-104 | Flotation Essential 415V Switchboard | 1 | Demountable Form 4a single sided 415V Essential Switchboard, 400A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Refer datasheet 2000-F00-DSH-EL-11012 | 2
0 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | 1 | 415V 3Ø 250A DB. Fitted with incoming isolator, PE Cell circuit (night/day), Auto / Manual selector, Emergency light test controller, Rapidtest RCD test units, Lighting Contactors, air conditioner Contactors and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-EL-10025 & 2000-F00-STD-EL-10022; Switchroom Vendor to calculate number of required poles including the number of circuits for Air conditioners, 20% loaded Spare circuit breakers and 20% spare space. | 2
0 | F16-DB-202 | Flotation 415V Switchroom 415VAC UPS Distribution Board | 1 | 415VAC 3Ø 250A UPS DB. Fitted with incoming isolator and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-EL-10027. Switchroom Vendor to calculate number of required poles including 20% loaded Spare circuit breakers and 20% spare space. | 2
0 | F16-UPS-002 | Flotation 415V Switchroom 415VAC UPS | 1 | LV Switchroom 415V AC, 30kVA UPS, free-standing. 8 hours autonomy time. 3-Phase in / 3-Phase Out. | Riello | S3T 30 XTD A0 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 30kVA/30kW Sentryum Xtend UPS 3Ph in/3Ph out Vendor to secure wheels once installed. Vendor to bolt down/brace for transport. W: 440mm, D: 840mm, H: 1320mm, Weight: 112Kg | 2
0 | F16-BA-002A | Flotation 415V Switchroom 415VAC UPS Battery Bank A | 1 | Floor Mount UPS Battery Cabinet, contains 1 string of 40 x 12V 90Ah long life batteries. | Riello | BB 1900 480-V3 CA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 480V Extension Battery Cabinet with 40 x 90Ah Long life batteries W: 860mm, D: 800mm, H: 1900mm, Weight: 1380Kg | 2
0 | F16-BA-002B | Flotation 415V Switchroom 415VAC UPS Battery Bank B | 1 | Floor Mount UPS Battery Cabinet, contains 1 string of 40 x 12V 90Ah long life batteries. | Riello | BB 1900 480-V3 CA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 480V Extension Battery Cabinet with 40 x 90Ah Long life batteries W: 860mm, D: 800mm, H: 1900mm, Weight: 1380Kg | 2
0 | - | Flotation 415V Switchroom 415VAC UPS Network Card | 1 | Netman UPS Ethernet Card | Riello | Netman 208 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Supplied and installed into UPS by Switchroom Vendor | 3
0 | - | Flotation 415V Switchroom 415VAC UPS Relay Contact Card | 1 | Multicom Configurable Slot In Relay Card, 3 Inputs & 8 Outputs | Riello | Mulitcom 392 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Supplied and installed into UPS by Switchroom Vendor | 3
0 | F16UPS002-ISL | Flotation 415V Switchroom 415VAC UPS Maintenance Bypass Switch | 1 | External Wall-mount UPS bypass switch. | Riello | WABS 0063A-33H | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Wall mounted rotary bypass switch. 3Ph in/3Ph out, 63A Dimensions: 400 x 400 x 300mm | 3
0 | F16-HF-004 | Flotation 415V MCC Active Harmonic Filter | 1 | Schneider AccuSine PCS+ 300A Active Harmonic Filter, 380-480VAC, IP54. | Schneider | PCSP300D5IP54 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Vendor to supply and install as per OEM recommendations including upstream breaker and CT's. | 3
0 | F16PP629-VS | Rougher 1 Concentrate Cleaner Feed Sample Pump LV VSD | 1 | Allen-Bradley 5.5 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC015JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F16PP630-VS | Rougher 1 Final Concentrate Sample Pump LV VSD | 1 | Allen-Bradley 5.5 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC015JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F16PP631-VS | Rougher 2 & 3 Concentrate Sample Pump LV VSD | 1 | Allen-Bradley 5.5 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC015JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F16PP632-VS | Scavenger Concentrate Sample Pump LV VSD | 1 | Allen-Bradley 5.5 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC015JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F16PP633-VS | Scavenger Tails Sample Pump LV VSD | 1 | Allen-Bradley 5.5 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC015JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F16PP634-VS | Final Tails Sample Pump LV VSD | 1 | Allen-Bradley 5.5 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC015JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F16PP638-VS | Sample Return Pump 1 LV VSD | 1 | Allen-Bradley 30 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F4, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC072JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F16PP639-VS | Sample Return Pump 2 LV VSD | 1 | Allen-Bradley 30 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F4, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC072JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F17PP459-VS | Flotation Tailings Thickener P-Duc Pump LV VSD | 1 | Allen-Bradley 37 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F5, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC085JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F18PP407-VS | Final Concentrate Pump 1 LV VSD | 1 | Allen-Bradley 132 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F7, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC302JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F18PP408-VS | Final Concentrate Pump 2 LV VSD | 1 | Allen-Bradley 132 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F7, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC302JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F18PP501-VS | Cleaner Flotation Cell Recirculation Pump 1 LV VSD | 1 | Allen-Bradley 450 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20- 750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G11BC1K0JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F18PP502-VS | Cleaner Flotation Cell Recirculation Pump 2 LV VSD | 1 | Allen-Bradley 450 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20- 750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G11BC1K0JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F18PP511-VS | Cleaner-Scavenger Flotation Cell Recirculation Pump 1 LV VSD | 1 | Allen-Bradley 450 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20- 750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G11BC1K0JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F18PP512-VS | Cleaner-Scavenger Flotation Cell Recirculation Pump 2 LV VSD | 1 | Allen-Bradley 450 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20- 750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G11BC1K0JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F18PP513-VS | Cleaner-Scavenger Flotation Cell Tails Pump 1 LV VSD | 1 | Allen-Bradley 315 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20- 750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G1ABC650JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F18PP514-VS | Cleaner-Scavenger Flotation Cell Tails Pump 2 LV VSD | 1 | Allen-Bradley 315 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20- 750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G1ABC650JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F16BW401-VS | Flotation Blower 1 LV VSD | 1 | Allen-Bradley 315 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20- 750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G1ABC650JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F16BW402-VS | Flotation Blower 2 LV VSD | 1 | Allen-Bradley 315 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20- 750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G1ABC650JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F16BW403-VS | Flotation Blower 3 LV VSD | 1 | Allen-Bradley 315 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20- 750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G1ABC650JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F16BW404-VS | Flotation Blower 4 LV VSD | 1 | Allen-Bradley 315 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20- 750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G1ABC650JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F16BW405-VS | Flotation Air Blower 5 LV VSD (FUTURE) | 1 | Switchroom builder to allocate switchroom floor space for future install (by Others) of Allen-Bradley Powerflex 755 Frame 8 Floor Mount VSD. | Allen-Bradley |  | N/A - Space Only | N/A - Space Only | Switchroom builder to allocate floor / wall space for future installation (by others) of this VSD. | 3
0 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | 1 | Communications Rack, Free Standing 19", 42U, 1000mm deep, Mesh door, Lift Off Side Panels. Fitted with 10 way 240VAC plug power distribution panel, wire management covers, shelves and cage nuts. Fitted out with FOBOTs (vendor supplied), DIN rail adapter (vendor supplied), and network switches (free issued). | Rittal | TS IT Enclosure (P/N 5514.110) + Accessories | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-IC-10101 | 3
1 | F16COM002-JB | Flotation 415V Switchroom Communications Rack Communications Rack 240VAC UPS Junction Box | 1 | Junction box mounted on the rear of the communications rack. All 240VAC UPS powered non-RCD Protected outlets shall be red with a "Warning. Socket not RCD Protected" Warning label. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Junction box for PDU Rail | 3
0 | F16-FOB-101 | Flotation 415V Switchroom Fibre Optic Breakout Tray | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | 3
0 | F16-FOB-102 | Flotation 415V Switchroom Fibre Optic Breakout Tray | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | 3
0 | F16-FOB-103A/B | Flotation 415V Switchroom RIO Circuit Fibre Optic Breakout Ring 1 Tray #1 | 1 | 2 X 12C SMOF Capacity FOBOT C/W Splice hardware & 1-6 LC Duplex Faceplate (LHS) + 1-6 LC Duplex Faceplate (RHS) | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. One FOBOT with two 12C faceplates. Vendor to label each side as per equipment number and name. | 3
0 | F16-FOB-104A/B | Flotation 415V Switchroom RIO Circuit Fibre Optic Breakout Ring 2 Tray #1 | 1 | 2 X 12C SMOF Capacity FOBOT C/W Splice hardware & 1-6 LC Duplex Faceplate (LHS) + 1-6 LC Duplex Faceplate (RHS) | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. One FOBOT with two 12C faceplates. Vendor to label each side as per equipment number and name. | 3
1 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | 1 | Custom Built Panel. Indoor, Mild Steel. Contains DCS hardware, power supply, MCBs and marshalling terminals. | Fabricated Panel | Custom | Primero | Switchroom/MCC Vendor |  | 4
0 | F16SR002-LCS | Flotation 415V Switchroom Emergency Shutdown | 1 | Switchroom Emergency Shutdown C/w shroud or lift-up flap and labelling | Fabricated Panel | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | With E34 Red 40mm Mushroom pushbutton (P/N E34LB2), and 4 off 2 N/O Contact Blocks (10250T2). Refer 2000-F00-STS-EL-10011 Section 4.19. | 4
0 | F16-FIP-002 | Flotation 415V Switchroom Fire Indicator Panel | 1 | Fire Indicator Panel c/w full installation, wiring, certification, testing and commissioning. HVAC trip upon alarm. FIP shall include SMOF modem(s) for connection to site-wide fire system network. | Wormald | Vigilant 8 Zone F3200 Conventional SHCIE FIP | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Rated to operate in 50C ambience temperature | 4
0 | F16FIP002-XE1 | Flotation 415V Switchroom VESDA Panel | 1 | VESDA Panel c/w full installation, wiring, certification, testing and commissioning.Alarm and fault signals to fire panel. | Xtralis | VESDA LaserPlus Scanner 12 relay VLS300 ASD system | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Rated to operate in 50C ambience temperature | 4
0 | F16FIP002-XE2 | Flotation 415V Switchroom Manual Call Points | VTA | Fire system Manual Call points (internal and external) as required by Australian Standards | Wormald | Manual Call Points | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Manual call points shall be tagged in sequential order | 4
0 | F16FIP002-XE3 | Flotation 415V Switchroom Smoke Detector | VTA | Fire system smoke detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order | 4
0 | F16FIP002-XE4 | Flotation 415V Switchroom Heat Detector | VTA | Fire system heat detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order | 4
0 | F16FIP002-UA | Flotation 415V Switchroom External Alarm Bells | VTA | Fire system alarm bells as required by Australian Standards | Wormald | External Sounder / Red Strobe | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Alarm sirens shall be tagged in sequential order | 4
0 | F16FIP002-XE5 | Flotation 415V Switchroom Gas Suppression System (Inergen) | 1 | Inergen gas suppression system incl. all valves and pipework, gas cylinders placed inside switchroom, refer to Switchroom General Arrangement | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | - | Flotation 415V Switchroom Fire Extinguishers | VTA | 5kg dry powder fire extinguishers complete with wall mount and signage. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | - | Flotation 415V Switchroom Automatic External Defibrillator | 1 | Automatic external defibrillator complete with wall-mounted cabinet. | Physio Control | Lifepak Defibrillator CR2 Fully Automatic | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | - | Flotation 415V Switchroom LV Rescue Kit | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | - | Flotation 415V Switchroom CPR Signage | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | - | Flotation 415V Switchroom HVAC Controller | VTA | Wall mounted Air Conditioner Controller, with relay contacts for Faulty & Healthy | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | One wall mounted controller to control all A/C's per room (One per transformer room, LV room, HV room). | 4
0 | F16-AC-1XX | Flotation 415V Switchroom Air Conditioners | VTA | High Wall split system, single phase, MULTIPLE (N+1 reqd) with drip trays if necessary | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. AC units shall be tagged in sequential order (e.g. F16-AC-100 for AC Unit 1, F16-AC-101 for AC Unit 2, etc. | 4
0 | F16AC1XX-ISL | Flotation 415V Switchroom Air Conditioner Isolators | VTA | Field isolator, one per split system AC | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Isolators shall be tagged with the respective AC equipment number (e.g. F16AC100-ISL etc) | 4
0 | - | Flotation 415V Switchroom Normal Light Fittings | 1 lot | Lighting to meet National Construction Code | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | 4
0 | - | Flotation 415V Switchroom Emergency Light Fittings | 1 lot | Lighting to meet National Construction Code; C/w built in battery pack. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | 4
0 | - | Flotation 415V Switchroom Exit Light Fittings | 1 lot | Lighting to meet National Construction Code | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | 4
0 | UT16031 | F16-SR-002 Flotation 415V Switchroom Temperature/Humidity Transmitter | 1 | 415V Switchroom Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | 4
0 | UT16032 | F16-SR-002 Flotation 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | 1 | F16-TR-004 Enclosure Room Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | 4
0 | UT16033 | F16-SR-002 Flotation 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | 1 | F16-TR-005 Enclosure Room Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | 4
0 | UT16034 | F16-SR-002 Flotation 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | 1 | F16-TR-008 Enclosure Room Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | 4
0 | F16-PE-002 | Flotation 415V Switchroom Photo-electric Cell | 1 | Switchroom Photo-electric cell | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | PE Cell - 1 per building. Vendor to position | 4
0 | F16SW004-LCS | Flotation 415V MCC Remote Switching Panel | 1 | LV MCC Incomer Remote Switching Panel | NHP | TemRack LCS | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | F16SW005-LCS | Flotation Blowers and Compressors 415V MCC Remote Switching Panel | 1 | LV MCC Incomer Remote Switching Panel | NHP | TemRack LCS | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | F16SW008-LCS | Thickener Emergency Power 415V MCC Remote Switching Panel | 1 | LV MCC Incomer Remote Switching Panel | Fabricated Panel | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Two buttons (Opened/Closed) and two indicator lamp (CB Opened/CB Closed) | 4
0 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | 1 | 50 x 6.3mm Tinned Flat Copper Bus bar mounted on standoffs on the subframe. Suitable for connection of earth cables to meet requirements of cable schedule. To have spare capacity for connection of an additional 4 x 120mm2 conductors and 4 x 70mm2 conductors, as a minimum. | GVK or similar |  | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | F16TR004-EB01 | Flotation 415V MCC Transformer Earth Bar | 1 | 50 x 6.3mm Tinned Flat Copper Bus bar mounted on standoffs on the Transformer. | Generic |  | Transformer Vendor | Transformer Vendor |  | 4
0 | F16TR005-EB01 | Flotation Blowers and Compressors 415V MCC Transformer Earth Bar | 1 | 50 x 6.3mm Tinned Flat Copper Bus bar mounted on standoffs on the Transformer. | Generic |  | Transformer Vendor | Transformer Vendor |  | 4
0 | F16TR008-EB01 | Thickener Emergency Power 415V MCC Transformer Earth Bar | 1 | 50 x 6.3mm Tinned Flat Copper Bus bar mounted on standoffs on the Transformer. | Generic |  | Transformer Vendor | Transformer Vendor |  | 4
0 | F16SW004-EB01 | Flotation 415V MCC Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on standoffs inside MCC. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 5
0 | F16SW005-EB01 | Flotation Blowers & Compressors 415V MCC Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on standoffs inside MCC. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 5
0 | F16SW008-EB01 | Thickener Emergency Power 415V MCC Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on standoffs inside MCC. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 5
0 | F16SW104-EB01 | Flotation Essential 415V Switchboard Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on standoffs inside MCC. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 5

## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred Colour) | Installation | Supplied By | Installed By | Revision | Comments | Page
F16SW004-P1-R | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-P1-W | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-P1-B | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-P2-R | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-P2-W | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-P2-B | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-P3-R | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-P3-W | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-P3-B | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-P4-R | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-P4-W | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-P4-B | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-N1 | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-N2 | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-N3 | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW004-N4 | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-P1-R | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-P1-W | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-P1-B | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-P2-R | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-P2-W | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-P2-B | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-P3-R | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-P3-W | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-P3-B | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-P4-R | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-P4-W | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-P4-B | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-N1 | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-N2 | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-N3 | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW005-N4 | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW008-P1-R | F16-TR-008 | Thickener Emergency Power 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW008-P1-W | F16-TR-008 | Thickener Emergency Power 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW008-P1-B | F16-TR-008 | Thickener Emergency Power 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW008-P2-R | F16-TR-008 | Thickener Emergency Power 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW008-P2-W | F16-TR-008 | Thickener Emergency Power 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW008-P2-B | F16-TR-008 | Thickener Emergency Power 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW008-N1 | F16-TR-008 | Thickener Emergency Power 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW008-N2 | F16-TR-008 | Thickener Emergency Power 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F16SW104-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16-SW-104 | Flotation Essential 415V Switchboard | Flotation 415V Switchroom | 120 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 7
F16SW104-P2 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16-SW-104 | Flotation Essential 415V Switchboard | Flotation 415V Switchroom | 120 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 7
F16PP629VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP629-VS | Rougher 1 Concentrate Cleaner Feed Sample Pump LV VSD | Flotation 415V Switchroom | 4 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F16PP630VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP630-VS | Rougher 1 Final Concentrate Sample Pump LV VSD | Flotation 415V Switchroom | 4 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F16PP631VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP631-VS | Rougher 2 & 3 Concentrate Sample Pump LV VSD | Flotation 415V Switchroom | 4 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F16PP632VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP632-VS | Scavenger Concentrate Sample Pump LV VSD | Flotation 415V Switchroom | 4 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F16PP633VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP633-VS | Scavenger Tails Sample Pump LV VSD | Flotation 415V Switchroom | 4 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F16PP634VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP634-VS | Final Tails Sample Pump LV VSD | Flotation 415V Switchroom | 4 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F16PP638VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP638-VS | Sample Return Pump 1 LV VSD | Flotation 415V Switchroom | 16 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F16PP639VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP639-VS | Sample Return Pump 2 LV VSD | Flotation 415V Switchroom | 16 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F17PP459VS-P1 | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | F17PP459-VS | Flotation Tailings Thickener P-Duc Pump LV VSD | Flotation 415V Switchroom | 25 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP407VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP407-VS | Final Concentrate Pump 1 LV VSD | Flotation 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP407VS-P2 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP407-VS | Final Concentrate Pump 1 LV VSD | Flotation 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP408VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP408-VS | Final Concentrate Pump 2 LV VSD | Flotation 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP408VS-P2 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP408-VS | Final Concentrate Pump 2 LV VSD | Flotation 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP501VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP501-VS | Cleaner Flotation Cell Recirculation Pump 1 LV VSD | Flotation 415V Switchroom | 185 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP501VS-P2 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP501-VS | Cleaner Flotation Cell Recirculation Pump 1 LV VSD | Flotation 415V Switchroom | 185 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP501VS-P3 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP501-VS | Cleaner Flotation Cell Recirculation Pump 1 LV VSD | Flotation 415V Switchroom | 185 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP502VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP502-VS | Cleaner Flotation Cell Recirculation Pump 2 LV VSD | Flotation 415V Switchroom | 185 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP502VS-P2 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP502-VS | Cleaner Flotation Cell Recirculation Pump 2 LV VSD | Flotation 415V Switchroom | 185 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP502VS-P3 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP502-VS | Cleaner Flotation Cell Recirculation Pump 2 LV VSD | Flotation 415V Switchroom | 185 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP511VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP511-VS | Cleaner-Scavenger Flotation Cell Recirculation Pump 1 LV VSD | Flotation 415V Switchroom | 185 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP511VS-P2 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP511-VS | Cleaner-Scavenger Flotation Cell Recirculation Pump 1 LV VSD | Flotation 415V Switchroom | 185 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP511VS-P3 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP511-VS | Cleaner-Scavenger Flotation Cell Recirculation Pump 1 LV VSD | Flotation 415V Switchroom | 185 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP512VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP512-VS | Cleaner-Scavenger Flotation Cell Recirculation Pump 2 LV VSD | Flotation 415V Switchroom | 185 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP512VS-P2 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP512-VS | Cleaner-Scavenger Flotation Cell Recirculation Pump 2 LV VSD | Flotation 415V Switchroom | 185 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP512VS-P3 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP512-VS | Cleaner-Scavenger Flotation Cell Recirculation Pump 2 LV VSD | Flotation 415V Switchroom | 185 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP513VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP513-VS | Cleaner-Scavenger Flotation Cell Tails Pump 1 LV VSD | Flotation 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP513VS-P2 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP513-VS | Cleaner-Scavenger Flotation Cell Tails Pump 1 LV VSD | Flotation 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP514VS-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP514-VS | Cleaner-Scavenger Flotation Cell Tails Pump 2 LV VSD | Flotation 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F18PP514VS-P2 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP514-VS | Cleaner-Scavenger Flotation Cell Tails Pump 2 LV VSD | Flotation 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F16BW401VS-P1 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16BW401-VS | Flotation Air Blower 1 LV VSD | Flotation 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F16BW401VS-P2 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16BW401-VS | Flotation Air Blower 1 LV VSD | Flotation 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F16BW402VS-P1 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16BW402-VS | Flotation Air Blower 2 LV VSD | Flotation 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F16BW402VS-P2 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16BW402-VS | Flotation Air Blower 2 LV VSD | Flotation 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F16BW403VS-P1 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16BW403-VS | Flotation Air Blower 3 LV VSD | Flotation 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F16BW403VS-P2 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16BW403-VS | Flotation Air Blower 3 LV VSD | Flotation 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F16BW404VS-P1 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16BW404-VS | Flotation Air Blower 4 LV VSD | Flotation 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F16BW404VS-P2 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16BW404-VS | Flotation Air Blower 4 LV VSD | Flotation 415V Switchroom | 240 | 0.6/1 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F16DB002-P1 | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | 150 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | 7
F16HF004-P1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16-HF-004 | Flotation 415V MCC Active Harmonic Filter | Flotation 415V Switchroom | 95 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F16HF004-P2 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16-HF-004 | Flotation 415V MCC Active Harmonic Filter | Flotation 415V Switchroom | 95 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F16UPS002ISL-P1 | F16-SW-104 | Flotation Essential 415V Switchboard | Flotation 415V Switchroom | F16UPS002-ISL | Flotation 415V Switchroom 415VAC UPS Maintenance Bypass Switch | Flotation 415V Switchroom | 25 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F16UPS002-P1 | F16UPS002-ISL | Flotation 415V Switchroom 415VAC UPS Maintenance Bypass Switch | Flotation 415V Switchroom | F16-UPS-002 | Flotation 415V Switchroom 415VAC UPS | Flotation 415V Switchroom | 25 | 0.6/1 | 4C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16UPS002ISL-P2 | F16-UPS-002 | Flotation 415V Switchroom 415VAC UPS | Flotation 415V Switchroom | F16UPS002-ISL | Flotation 415V Switchroom 415VAC UPS Maintenance Bypass Switch | Flotation 415V Switchroom | 25 | 0.6/1 | 4C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16DB202-P1 | F16UPS002-ISL | Flotation 415V Switchroom 415VAC UPS Maintenance Bypass Switch | Flotation 415V Switchroom | F16-DB-202 | Flotation 415V Switchroom 415VAC UPS Distribution Board | Flotation 415V Switchroom | 25 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F16BA002A-P1-B(+) | F16-UPS-002 | Flotation 415V Switchroom 415VAC UPS | Flotation 415V Switchroom | F16-BA-002A | Flotation 415V Switchroom 415VAC UPS Battery Bank A | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16BA002A-P1-P1-B(N) | F16-UPS-002 | Flotation 415V Switchroom 415VAC UPS | Flotation 415V Switchroom | F16-BA-002A | Flotation 415V Switchroom 415VAC UPS Battery Bank A | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16BA002A-P1-B(-) | F16-UPS-002 | Flotation 415V Switchroom 415VAC UPS | Flotation 415V Switchroom | F16-BA-002A | Flotation 415V Switchroom 415VAC UPS Battery Bank A | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16BA002A-P1-E | F16-UPS-002 | Flotation 415V Switchroom 415VAC UPS | Flotation 415V Switchroom | F16-BA-002A | Flotation 415V Switchroom 415VAC UPS Battery Bank A | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16BA002B-P1-B(+) | F16-BA-002A | Flotation 415V Switchroom 415VAC UPS | Flotation 415V Switchroom | F16-BA-002B | Flotation 415V Switchroom 415VAC UPS Battery Bank A | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16BA002B-P1-P1-B(N) | F16-BA-002A | Flotation 415V Switchroom 415VAC UPS | Flotation 415V Switchroom | F16-BA-002B | Flotation 415V Switchroom 415VAC UPS Battery Bank A | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16BA002B-P1-B(-) | F16-BA-002A | Flotation 415V Switchroom 415VAC UPS | Flotation 415V Switchroom | F16-BA-002B | Flotation 415V Switchroom 415VAC UPS Battery Bank A | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16BA002B-P1-E | F16-BA-002A | Flotation 415V Switchroom 415VAC UPS | Flotation 415V Switchroom | F16-BA-002B | Flotation 415V Switchroom 415VAC UPS Battery Bank A | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16FIP002-P1 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16-FIP-002 | Flotation 415V Switchroom Fire Indicator Panel | Flotation 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16FIP002XE1-P1 | F16-FIP-002 | Flotation 415V Switchroom Fire Indicator Panel | Flotation 415V Switchroom | F16FIP002-XE1 | Flotation 415V Switchroom VESDA Panel | Flotation 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16TR004-P1 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | Transformer fans 240V Supply | 8
F16TR005-P1 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | Transformer fans 240V Supply | 8
F16TR008-P1 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16-TR-008 | Thickener Emergency Power 415V MCC Transformer | Flotation 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | Transformer fans 240V Supply | 8
F16SW004-P5 | F16-DB-202 | Flotation 415V Switchroom 415VAC UPS Distribution Board | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Control Power - UPS Fed | 8
F16SW004-P6 | F16-DB-202 | Flotation 415V Switchroom 415VAC UPS Distribution Board | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Control Power - UPS Fed | 8
F16SW104-P6 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16-SW-104 | Flotation Essential 415V Switchboard | Flotation 415V Switchroom | 10 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | 24VDC Supply to Essential Board | 8
F16SW005-P5 | F16-DB-202 | Flotation 415V Switchroom 415VAC UPS Distribution Board | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Control Power - UPS Fed | 8
F16SW005-P6 | F16-DB-202 | Flotation 415V Switchroom 415VAC UPS Distribution Board | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Control Power - UPS Fed | 8
F16SW008-P5 | F16-DB-202 | Flotation 415V Switchroom 415VAC UPS Distribution Board | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Control Power - UPS Fed | 8
F16DCS408-P1 | F16-DB-202 | Flotation 415V Switchroom 415VAC UPS Distribution Board | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 8
F16COM002-P1 | F16-DB-202 | Flotation 415V Switchroom 415VAC UPS Distribution Board | Flotation 415V Switchroom | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 8
F16DB002-W08 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom |  | Lighting - Switchroom External Lighting Junction Box (for site use) | Flotation 415V Switchroom | 4 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16DB002-R13 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC101-ISL | Flotation 415V Switchroom Air Conditioner No. 1 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16AC101-P1 | F16AC101-ISL | Flotation 415V Switchroom Air Conditioner No. 1 Isolator | Flotation 415V Switchroom | F16-AC-101 | Flotation 415V Switchroom Air Conditioner No. 1 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16DB002-W13 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC102-ISL | Flotation 415V Switchroom Air Conditioner No. 2 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16AC102-P1 | F16AC102-ISL | Flotation 415V Switchroom Air Conditioner No. 2 Isolator | Flotation 415V Switchroom | F16-AC-102 | Flotation 415V Switchroom Air Conditioner No. 2 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16DB002-B13 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC103-ISL | Flotation 415V Switchroom Air Conditioner No. 3 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16AC103-P1 | F16AC103-ISL | Flotation 415V Switchroom Air Conditioner No. 3 Isolator | Flotation 415V Switchroom | F16-AC-103 | Flotation 415V Switchroom Air Conditioner No. 3 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16DB002-R15 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC104-ISL | Flotation 415V Switchroom Air Conditioner No. 4 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16AC104-P1 | F16AC104-ISL | Flotation 415V Switchroom Air Conditioner No. 4 Isolator | Flotation 415V Switchroom | F16-AC-104 | Flotation 415V Switchroom Air Conditioner No. 4 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16DB002-W15 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC105-ISL | Flotation 415V Switchroom Air Conditioner No. 5 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 8
F16AC105-P1 | F16AC105-ISL | Flotation 415V Switchroom Air Conditioner No. 5 Isolator | Flotation 415V Switchroom | F16-AC-105 | Flotation 415V Switchroom Air Conditioner No. 5 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-B15 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC106-ISL | Flotation 415V Switchroom Air Conditioner No. 6 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC106-P1 | F16AC106-ISL | Flotation 415V Switchroom Air Conditioner No. 6 Isolator | Flotation 415V Switchroom | F16-AC-106 | Flotation 415V Switchroom Air Conditioner No. 6 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-R17 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC107-ISL | Flotation 415V Switchroom Air Conditioner No. 7 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC107-P1 | F16AC107-ISL | Flotation 415V Switchroom Air Conditioner No. 7 Isolator | Flotation 415V Switchroom | F16-AC-107 | Flotation 415V Switchroom Air Conditioner No. 7 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-W17 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC108-ISL | Flotation 415V Switchroom Air Conditioner No. 8 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC108-P1 | F16AC108-ISL | Flotation 415V Switchroom Air Conditioner No. 8 Isolator | Flotation 415V Switchroom | F16-AC-108 | Flotation 415V Switchroom Air Conditioner No. 8 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-B17 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC109-ISL | Flotation 415V Switchroom Air Conditioner No. 9 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC109-P1 | F16AC109-ISL | Flotation 415V Switchroom Air Conditioner No. 9 Isolator | Flotation 415V Switchroom | F16-AC-109 | Flotation 415V Switchroom Air Conditioner No. 9 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-R19 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC110-ISL | Flotation 415V Switchroom Air Conditioner No. 10 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC110-P1 | F16AC110-ISL | Flotation 415V Switchroom Air Conditioner No. 10 Isolator | Flotation 415V Switchroom | F16-AC-110 | Flotation 415V Switchroom Air Conditioner No. 10 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-W19 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC111-ISL | Flotation 415V Switchroom Air Conditioner No. 11 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC111-P1 | F16AC111-ISL | Flotation 415V Switchroom Air Conditioner No. 11 Isolator | Flotation 415V Switchroom | F16-AC-111 | Flotation 415V Switchroom Air Conditioner No. 11 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-B19 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC112-ISL | Flotation 415V Switchroom Air Conditioner No. 12 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC112-P1 | F16AC112-ISL | Flotation 415V Switchroom Air Conditioner No. 12 Isolator | Flotation 415V Switchroom | F16-AC-112 | Flotation 415V Switchroom Air Conditioner No. 12 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-R14 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC113-ISL | Flotation 415V Switchroom Air Conditioner No. 13 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC113-P1 | F16AC113-ISL | Flotation 415V Switchroom Air Conditioner No. 13 Isolator | Flotation 415V Switchroom | F16-AC-113 | Flotation 415V Switchroom Air Conditioner No. 13 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-W14 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC114-ISL | Flotation 415V Switchroom Air Conditioner No. 14 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC114-P1 | F16AC114-ISL | Flotation 415V Switchroom Air Conditioner No. 14 Isolator | Flotation 415V Switchroom | F16-AC-114 | Flotation 415V Switchroom Air Conditioner No. 14 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-B14 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC115-ISL | Flotation 415V Switchroom Air Conditioner No. 15 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC115-P1 | F16AC115-ISL | Flotation 415V Switchroom Air Conditioner No. 15 Isolator | Flotation 415V Switchroom | F16-AC-115 | Flotation 415V Switchroom Air Conditioner No. 15 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-R16 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC116-ISL | Flotation 415V Switchroom Air Conditioner No. 16 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC116-P1 | F16AC116-ISL | Flotation 415V Switchroom Air Conditioner No. 16 Isolator | Flotation 415V Switchroom | F16-AC-116 | Flotation 415V Switchroom Air Conditioner No. 16 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-W16 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC117-ISL | Flotation 415V Switchroom Air Conditioner No. 17 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC117-P1 | F16AC117-ISL | Flotation 415V Switchroom Air Conditioner No. 17 Isolator | Flotation 415V Switchroom | F16-AC-117 | Flotation 415V Switchroom Air Conditioner No. 17 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-B16 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC118-ISL | Flotation 415V Switchroom Air Conditioner No. 18 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC118-P1 | F16AC118-ISL | Flotation 415V Switchroom Air Conditioner No. 18 Isolator | Flotation 415V Switchroom | F16-AC-118 | Flotation 415V Switchroom Air Conditioner No. 18 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-R18 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC119-ISL | Flotation 415V Switchroom Air Conditioner No. 19 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC119-P1 | F16AC119-ISL | Flotation 415V Switchroom Air Conditioner No. 19 Isolator | Flotation 415V Switchroom | F16-AC-119 | Flotation 415V Switchroom Air Conditioner No. 19 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-W18 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | F16AC120-ISL | Flotation 415V Switchroom Air Conditioner No. 20 Isolator | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16AC120-P1 | F16AC120-ISL | Flotation 415V Switchroom Air Conditioner No. 20 Isolator | Flotation 415V Switchroom | F16-AC-120 | Flotation 415V Switchroom Air Conditioner No. 20 | Flotation 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-R09 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom |  | Lighting - Swtichroom Internal 1 | Flotation 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-R09_ | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom |  | Lighting - Swtichroom Internal 1 (Emergency) | Flotation 415V Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-W09 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom |  | Lighting - Swtichroom Internal 2 | Flotation 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-W09_ | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom |  | Lighting - Swtichroom Internal 2 (Emergency) & Exit Lights | Flotation 415V Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-B10 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom |  | Lighting - Swtichroom External 1 | Flotation 415V Switchroom | 6 | 0.45/0.75 | 4C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16DB002-R03 | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom |  | General Power - Flotation 415V Switchroom GPO's | Flotation 415V Switchroom | 4 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F16SW004-C1 | F16SR002-LCS | Flotation 415V Switchroom Emergency Shutdown | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 1.5 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Emerg/ Shutdown Circuit. E-stop to trip incomer | 9
F16SW005-C1 | F16SR002-LCS | Flotation 415V Switchroom Emergency Shutdown | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 1.5 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Emerg/ Shutdown Circuit. E-stop to trip incomer | 9
F16SW008-C1 | F16SR002-LCS | Flotation 415V Switchroom Emergency Shutdown | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 1.5 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Emerg/ Shutdown Circuit. E-stop to trip incomer | 9
F16TR004-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Transformer Signals to MCC | 10
F16TR005-C1 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Transformer Signals to MCC | 10
F16TR008-C1 | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | F16-TR-008 | Thickener Emergency Power 415V MCC Transformer | Flotation 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Transformer Signals to MCC | 10
F16PP629VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP629-VS | Rougher 1 Concentrate Cleaner Feed Sample Pump LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F16PP630VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP630-VS | Rougher 1 Final Concentrate Sample Pump LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F16PP631VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP631-VS | ROUGHER 2 & 3 CONCENTRATE SAMPLE PUMP LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F16PP632VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP632-VS | SCAVENGER CONCENTRATE SAMPLE PUMP LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F16PP633VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP633-VS | SCAVENGER TAILS SAMPLE PUMP LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F16PP634VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP634-VS | FINAL TAILS SAMPLE PUMP LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F16PP638VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP638-VS | Sample Return Pump 1 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F16PP639VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16PP639-VS | Sample Return Pump 2 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F17PP459VS-C1 | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | F17PP459-VS | Flotation Tailings Thickener P-Duc Pump LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F18PP407VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP407-VS | Final Concentrate Pump 1 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F18PP408VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP408-VS | Final Concentrate Pump 2 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F18PP501VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP501-VS | CLEANER FLOTATION CELL RECIRCULATION PUMP 1 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F18PP502VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP502-VS | CLEANER FLOTATION CELL RECIRCULATION PUMP 2 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F18PP511VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP511-VS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 1 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F18PP512VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP512-VS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 2 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F18PP513VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP513-VS | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 1 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F18PP514VS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F18PP514-VS | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 2 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F16BW401VS-C1 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16BW401-VS | Flotation Air Blower 1 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F16BW402VS-C1 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16BW402-VS | Flotation Air Blower 2 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F16BW403VS-C1 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16BW403-VS | Flotation Air Blower 3 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F16BW404VS-C1 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16BW404-VS | Flotation Air Blower 4 LV VSD | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F16SW004-C2 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Incomer Signals to DCS. | 10
F16SW005-C2 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Incomer Signals to DCS. | 10
F16SW008-C2 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Incomer Signals to DCS. | 10
F16SW104-C1 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | F16-SW-104 | Flotation Essential 415V Switchboard | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | MCC Incomer Signals to DCS | 10
F16DB002-C1 | F16-FIP-002 | Flotation 415V Switchroom Fire Indicator Panel | Flotation 415V Switchroom | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | 1.5 | 0.6/1 | 2C | Cu | R-EP-110 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | HVAC trip. | 10
F16FIP002-C1 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | F16-FIP-002 | Flotation 415V Switchroom Fire Indicator Panel | Flotation 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 10
F16DB002-C2 | F16-PE-002 | Flotation 415V Switchroom Photo-electric Cell | Flotation 415V Switchroom | F16-DB-002 | Flotation 415V Switchroom L&SP Distribution Board | Flotation 415V Switchroom | 2.5 | 0.45/0.75 | 3C+E | Cu | PVC/PVC | White | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 10
UT16031-I1 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | UT16031 | F16-SR-002 Flotation 415V Switchroom Temperature/Humidity Transmitter | Flotation 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 10
UT16032-I1 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | UT16032 | F16-SR-002 Flotation 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | Flotation 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 10
UT16033-I1 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | UT16033 | F16-SR-002 Flotation 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | Flotation 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 10
UT16034-I1 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | UT16034 | F16-SR-002 Flotation 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | Flotation 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 10
ZSC16037-I1 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | ZSC16037 | F16-SR-002 Flotation 415V MCC Transformer Enclosure Door Position Switch Closed | Flotation 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Transformer Enclosure Door feedback | 10
ZSC16038-I1 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | ZSC16038 | F16-SR-002 Flotation Blowers and Compressors415V MCC Transformer Enclosure Door Position Switch Closed | Flotation 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Transformer Enclosure Door feedback | 10
ZSC16039-I1 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | ZSC16039 | F16-SR-002 Thickener Emergency 415V MCC Transformer Enclosure Door Position Switch Closed | Flotation 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Transformer Enclosure Door feedback | 10
F16UPS002-C1 | F16UPS002-ISl | Flotation 415V Switchroom 415VAC UPS Maintenance Bypass Switch | Flotation 415V Switchroom | F16-UPS-002 | Flotation 415V Switchroom 415VAC UPS | Flotation 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | By pass | 11
F16HF004-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16-HF-004 | Flotation 415V MCC Active Harmonic Filter | Flotation 415V Switchroom | 2.5 | 0.6/1 | 6C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | HF to MCC Incomer | 11
F16SW004LCS-C1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16SW004-LCS | Flotation 415V MCC Remote Switching Panel | Flotation 415V Switchroom | 1.5 | 0.6/1 | 20C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F16SW005LCS-C1 | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | F16SW005-LCS | Flotation Blowers and Compressors 415V MCC Remote Switching Panel | Flotation 415V Switchroom | 1.5 | 0.6/1 | 20C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F16SW008LCS-C1 | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | F16SW008-LCS | Thickener Emergency Power 415V MCC Remote Switching Panel | Flotation 415V Switchroom | 1.5 | 0.6/1 | 20C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F16SW004-C51 | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 11
F16SW004-C52 | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 11
F16SW004-C53 | F16-TR-004 | Flotation 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 11
F16SW005-C51 | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 11
F16SW005-C52 | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 11
F16SW005-C53 | F16-TR-005 | Flotation Blowers and Compressors 415V MCC Transformer | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 11
F16SW008-C51 | F16-TR-008 | Thickener Emergency Power 415V MCC Tansformer | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 11
F16SW008-C52 | F16-TR-008 | Thickener Emergency Power 415V MCC Tansformer | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 11
F16SW008-C53 | F16-TR-008 | Thickener Emergency Power 415V MCC Tansformer | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 11
F16SW004-C3 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | 24VDC PSU monitoring | 11
F16SW004-C4 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | 24VDC PSU monitoring | 11
F16SW005-C3 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | 24VDC PSU monitoring | 11
F16SW005-C4 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | 24VDC PSU monitoring | 11
F16SW008-C3 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | 24VDC PSU monitoring | 11
F16SR002LCS-C1 | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | F16SR002-LCS | Flotation 415V Switchroom Emergency Shutdown | Flotation 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | 24VDC Supply to PILZ Relay in Switchroom E-Shut. Plus E-shut status signal to DCS. | 11
F16FIP002-FO1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-FIP-002 | Flotation 415V Switchroom Fire Indicator Panel | Flotation 415V Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Site-Wide Fire network - patch to FIP. | 11
F16FIP002-FO2 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-FIP-002 | Flotation 415V Switchroom Fire Indicator Panel | Flotation 415V Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Site-Wide Fire network - patch to FIP. | 11
F16SW104-D1 | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | F16-SW-104 | Flotation Essential 415V Switchboard | Flotation 415V Switchroom | N/A | N/A | N/A | N/A | VAMP CAN Bus | Grey | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 3 | VAMP CAN Bus Cable. | 11
F16SW104-D2 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-SW-104 | Flotation Essential 415V Switchboard | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Ethernet allowance | 11
F16UPS002-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-UPS-002 | Flotation 415V Switchroom 415VAC UPS | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F16PP629VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16PP629-VS | Rougher 1 Concentrate Cleaner Feed Sample Pump LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F16PP630VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16PP630-VS | Rougher 1 Final Concentrate Sample Pump LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F16PP631VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16PP631-VS | ROUGHER 2 & 3 CONCENTRATE SAMPLE PUMP LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F16PP632VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16PP632-VS | SCAVENGER CONCENTRATE SAMPLE PUMP LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F16PP633VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16PP633-VS | SCAVENGER TAILS SAMPLE PUMP LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F16PP634VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16PP634-VS | FINAL TAILS SAMPLE PUMP LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F16PP638VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16PP638-VS | Sample Return Pump 1 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F16PP639VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16PP639-VS | Sample Return Pump 2 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F17PP459VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F17PP459-VS | Flotation Tailings Thickener P-Duc Pump LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F18PP407VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F18PP407-VS | Final Concentrate Pump 1 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F18PP408VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F18PP408-VS | Final Concentrate Pump 2 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F18PP501VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F18PP501-VS | CLEANER FLOTATION CELL RECIRCULATION PUMP 1 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 11
F18PP502VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F18PP502-VS | CLEANER FLOTATION CELL RECIRCULATION PUMP 2 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F18PP511VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F18PP511-VS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 1 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F18PP512VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F18PP512-VS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 2 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F18PP513VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F18PP513-VS | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 1 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F18PP514VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F18PP514-VS | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 2 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F16BW401VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16BW401-VS | Flotation Air Blower 1 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F16BW402VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16BW402-VS | Flotation Air Blower 2 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F16BW403VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16BW403-VS | Flotation Air Blower 3 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F16BW404VS-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16BW404-VS | Flotation Air Blower 4 LV VSD | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F16SW004-D11 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | Connected to local MCC ethernet switches. | 12
F16SW004-D12 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | Connected to local MCC ethernet switches. | 12
F16SW004-D13 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches. | 12
F16SW004-D14 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-SW-004 | Flotation 415V MCC | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches. | 12
F16SW005-D11 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | Connected to local MCC ethernet switches. | 12
F16SW005-D12 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | Connected to local MCC ethernet switches. | 12
F16SW005-D13 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-SW-005 | Flotation Blowers & Compressors 415V MCC | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches. | 12
F16SW008-D11 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | Connected to local MCC ethernet switches. | 12
F16SW008-D12 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-SW-008 | Thickener Emergency Power 415V MCC | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches. | 12
F16HF004-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-HF-004 | Flotation 415V MCC Active Harmonic Filter | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F16DCS408-D1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Orange | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms - CPU 1 PRIMARY | 12
F16DCS408-D2 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Orange | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms - CPU 1 SECONDARY | 12
F16DCS408-D3 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Purple | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms - CPU 2 PRIMARY | 12
F16DCS408-D4 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Purple | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms - CPU 2 SECONDARY | 12
F16DCS408-D5 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | DCS Comms - ALE CARD (AS REQUIRED) | 12
F16DCS408-D6 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | DCS Comms - ALE CARD (AS REQUIRED) | 12
F16DCS408-D7 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | DCS Comms - ALE CARD (AS REQUIRED) | 12
F16DCS408-D11 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | DCS Comms - ALE CARD (AS REQUIRED) | 12
F16DCS408-D12 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | DCS Comms - ALE CARD (AS REQUIRED) | 12
F16DCS408-FO1 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED). | 12
F16DCS408-FO2 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED). | 12
F16DCS408-FO11 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED). | 12
F16DCS408-FO12 | F16-COM-002 | Flotation 415V Switchroom Communications Rack | Flotation 415V Switchroom | F16-DCS-408 | Flotation 415V Switchroom DCS Panel | Flotation 415V Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED). | 12
F16TR004EB01-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16TR004-EB01 | Flotation 415V MCC Transformer Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F16TR004EB01-E2 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16TR004-EB01 | Flotation 415V MCC Transformer Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F16TR005EB01-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16TR005-EB01 | Flotation Blowers and Compressors 415V MCC Transformer Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F16TR005EB01-E2 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16TR005-EB01 | Flotation Blowers and Compressors 415V MCC Transformer Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F16TR008EB01-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16TR008-EB01 | Thickener Emergency Power 415V MCC Transformer Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F16TR008EB01-E2 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16TR008-EB01 | Thickener Emergency Power 415V MCC Transformer Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 12
F16SW004EB01-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16SW004-EB01 | Flotation 415V MCC Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16SW004EB01-E2 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16SW004-EB01 | Flotation 415V MCC Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16SW005EB01-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16SW005-EB01 | Flotation Blowers & Compressors 415V MCC Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16SW005EB01-E2 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16SW005-EB01 | Flotation Blowers & Compressors 415V MCC Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16SW008EB01-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16SW008-EB01 | Thickener Emergency Power 415V MCC Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16SW008EB01-E2 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16SW008-EB01 | Thickener Emergency Power 415V MCC Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16SW104EB01-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16SW104-EB01 | Flotation Essential 415V Switchboard Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16SW104EB01-E2 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16SW104-EB01 | Flotation Essential 415V Switchboard Earth Bar | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16HF004-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16-HF-004 | Flotation 415V MCC Active Harmonic Filter | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16PP629VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16PP629-VS | Rougher 1 Concentrate Cleaner Feed Sample Pump LV VSD | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16PP630VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16PP630-VS | ROUGHER 1 CONCENTRATE SAMPLE PUMP LV VSD | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16PP631VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16PP631-VS | ROUGHER 2 & 3 CONCENTRATE SAMPLE PUMP LV VSD | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16PP632VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16PP632-VS | SCAVENGER CONCENTRATE SAMPLE PUMP LV VSD | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16PP633VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16PP633-VS | SCAVENGER TAILS SAMPLE PUMP LV VSD | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16PP634VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16PP634-VS | FINAL TAILS SAMPLE PUMP LV VSD | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16PP638VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16PP638-VS | Sample Return Pump LV VSD | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16PP639VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16PP639-VS | Flotation Feed PSA Pump LV VSD | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F17PP459VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F17PP459-VS | Flotation Tailings Thickener P-Duc Pump LV VSD | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F18PP407VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F18PP407-VS | Final Concentrate Pump 1 LV VSD | Flotation 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F18PP408VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F18PP408-VS | Final Concentrate Pump 2 LV VSD | Flotation 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F18PP501VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F18PP501-VS | CLEANER FLOTATION CELL RECIRCULATION PUMP 1 LV VSD | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F18PP502VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F18PP502-VS | CLEANER FLOTATION CELL RECIRCULATION PUMP 2 LV VSD | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F18PP511VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F18PP511-VS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 1 LV VSD | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F18PP512VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F18PP512-VS | CLEANER-SCAVENGER FLOTATION CELL RECIRCULATION PUMP 2 LV VSD | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F18PP513VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F18PP513-VS | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 1 LV VSD | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F18PP514VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F18PP514-VS | CLEANER-SCAVENGER FLOTATION CELL TAILS PUMP 2 LV VSD | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16BW401VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16BW401-VS | Flotation Blower 1 LV VSD | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16BW402VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16BW402-VS | Flotation Blower 2 LV VSD | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16BW403VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16BW403-VS | Flotation Blower 3 LV VSD | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16BW404VS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16BW404-VS | Flotation Blower 4 LV VSD | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 13
F16SW004LCS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16SW004-LCS | FLOTATION 415V MCC REMOTE SWITCHING PANEL | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 13
F16SW005LCS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16SW005-LCS | FLOTATION BLOWERS AND COMPRESSORS 415V MCC REMOTE SWITCHING PANEL | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 13
F16SW008LCS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16SW008-LCS | THICKENER EMERGENCY POWER 415V MCC REMOTE SWITCHING PANEL | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 13
F16SR002LCS-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16SR002-LCS | FLOTATION 415V SWITCHROOM EMERGENCY SHUTDOWN | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 13
F16FIP002-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16-FIP-002 | FLOTATION 415V SWITCHROOM FIRE INDICATOR PANEL | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 13
F16DB002-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16-DB-002 | FLOTATION 415V SWITCHROOM L&SP DISTRIBUTION BOARD | Flotation 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 13
F16UPS002-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16-UPS-002 | FLOTATION 415V SWITCHROOM 415VAC UPS | Flotation 415V Switchroom | 25 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 13
F16UPS002ISL-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16UPS002-ISL | FLOTATION 415V SWITCHROOM 415VAC UPS MAINTENANCE BYPASS SWITCH | Flotation 415V Switchroom | 25 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 13
F16BA002A-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16-BA-002A | FLOTATION 415V SWITCHROOM 415VAC UPS BATTERY BANK A | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 13
F16BA002B-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16-BA-002B | FLOTATION 415V SWITCHROOM 415VAC UPS BATTERY BANK B | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 14
F16DB202-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16-DB-202 | FLOTATION 415V SWITCHROOM 415VAC UPS DISTRIBUTION BOARD | Flotation 415V Switchroom | 25 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 14
F16COM002-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16-COM-002 | FLOTATION 415V SWITCHROOM 415VAC UPS DISTRIBUTION BOARD | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 14
F16DCS408-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16-DCS-408 | FLOTATION 415V SWITCHROOM 415VAC UPS DISTRIBUTION BOARD | Flotation 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 14
F16SR002-E1 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16-SR-002 | Switchroom Subframe | Flotation 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 14
F16SR002-E2 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16-SR-002 | Switchroom Subframe | Flotation 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 14
F16SR002-E3 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16-SR-002 | Subfloor Cable Ladder | Flotation 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 14
F16SR002-E4 | F16SR002-EB01 | Flotation 415V Switchroom Earth Bar | Flotation 415V Switchroom | F16-SR-002 | Subfloor Cable Ladder | Flotation 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 14
Ladder Joint Bonds | F16-SR-002 | Subfloor Cable Ladder | Flotation 415V Switchroom | F16-SR-002 | Subfloor Cable Ladder | Flotation 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 14