## Equipment list
Connected Load (Name Plate) | Maximum Demand (15 minutes) | Transformer Utilisation | 24 Hour Average Demand (Plant Running) | Yearly Average Consumption | Equipment Name | Equipment Number | Transformer / Generator Rating (kVA) | Page
kW | kW | % | kW | MWh |  |  |  | 4
215 | 110 | 67% | 65 | 573 | Southlakes Booster Station LV Motor Control Centre | F175-SW-701 | 200 | 4
[5 empty] | Client: | NORTHERN STAR RESOURCES | SOUTHLAKES BOOSTER STATION ELECTRICAL LOAD LIST | 5
[5 empty] | Project: | KCGM FIM TSF PROJECT |  | 5
[5 empty] | Document Number: | 2000-F175-LST-EL-40001 |  | 5
[5 empty] | Revision: | 0 |  | 5
|  | Electrical Connection | Load Details |  | Equipment |  | Input Data | 5

## Load list
Equipment Number | Equipment Description | Nameplate (kW) | Voltage (V) | Load Type | Duty / Standby | MCC | Motor / Load Efficiency 75% Load | Motor / Load Power Factor 75% Load | Load Factor (LF) | Active Power (kW) | Apparent Power (kVA) | Plant Diversity Factor (PDF) | Reactive Power (kVAR) | Annual Run Hours | Annual Energy Consumption (MWh) | Data Source | Status | Rev | Page
F175-PW-701 | Southlakes Booster Pump 1 | 75 | 415 | 415V 45 TO 90kW VSD MOTOR | Duty | F175-SW-701 | 0.95 | 0.85 | 0.75 | 59 | 70 | 0.25 | 9 | 1.00 | 130 | MELH _ | Confirmed | 0 | 5
F175-PW-702 | Southlakes Booster Pump 2 | 75 | 415 | 415V 45 TO 90kW VSD MOTOR | Standby | F175-SW-701 | 0.95 | 0.85 | 0.75 | 0 | 0 | 0.25 | 0 | 1.00 | 0 | MELH _ | Confirmed | 0 | 5
F175-DB-701 | Southlakes Booster Station L&SP Distribution Board | 55 | 415 | 415V FEEDER 0.37 TO 110kW | Duty | F175-SW-701 | 0.90 | 0.80 | 0.70 | 43 | 53 | 1.00 | 32 | 1.00 | 375 | EEL | Estimated | C | 5
F175-UPS-701 | Southlakes Booster Station LV Switchroom 240V AC UPS | 10 | 415 | 415V FEEDER 0.37 TO 110kW | Duty | F175-SW-701 | 0.90 | 0.80 | 0.70 | 8 | 10 | 1.00 | 6 | 1.00 | 68 | EEL | Estimated | C | 5