## Cable schedule
Cable Number | Cable Origin Equip. Number | Equipment Name | Cable Destination Equip. Number | Length (m) | Cable Type / Size / Construction | Installation method | Cable Supplier | Cable Installer | Cable Terminator | Schematic / Termination Drawing | Comments | Status | Revision | Insulation (kV) | Conductor | No. of Cores / Pairs | Conductor Size (mm2) | Construction | Standard Installation Drawing Reference | Page
F175SW701-R1 | SMSB | Western Power Metering Cubicle | F175-SW-701 | 45 | 1C 185mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-SLD-EL-40001 | Main incomer | Confirmed | 2 | [6 empty] | 4
F175SW701-W1 | SMSB | Western Power Metering Cubicle | F175-SW-701 | 45 | 1C 185mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-SLD-EL-40001 | Main incomer | Confirmed | 2 | [6 empty] | 4
F175SW701-B1 | SMSB | Western Power Metering Cubicle | F175-SW-701 | 45 | 1C 185mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-SLD-EL-40001 | Main incomer | Confirmed | 2 | [6 empty] | 4
F175SW701-N1 | SMSB | Western Power Metering Cubicle | F175-SW-701 | 45 | 1C 185mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-SLD-EL-40001 | Main incomer | Confirmed | 2 | [6 empty] | 4
F175GE701DPS-P1 | F175-GE-701 | Southlakes Booster Station Generator | F175GE701-DPS | 15 | 4C+E 240mm² Cu 0.6/1kV EPR/CPE FLEXIBLE WITH 90◦ ANGLED PLUG | Loose | CN037-E&I | CN037-E&I | CN037-E&I (Plug only) | 2000-F175-SLD-EL-40001 | Refer Note 10 | Confirmed | 0 | [6 empty] | 4
F175SW701-P3 | F175GE701-DPS | Southlakes Booster Station Generator Decontactor Panel | F175-SW-701 | Note 8 | 4C+E 240mm² Cu 0.6/1kV EPR/CPE FLEXIBLE | Ladder | EL006 | EL006 | EL006 | 2000-F175-SLD-EL-40001 | Generator incomer | Confirmed | 0 | [6 empty] | 4
F175SR701EB-E1 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre Earth Bar | F175SR701-EB | Note 8 | 1C 120mm² Cu 0.6/1kV GnYe PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-SLD-EL-40001 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175HF701-P1 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre Incomer | F175-HF-701 | Note 8 | 4C+E 25mm² Cu 0.6/1kV XLPE/PVC | Ladder / Conduit |  |  |  | 2000-F175-SCM-EL-40015 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175HF701-C1 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre Incomer | F175-HF-701 | Note 8 | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-SCM-EL-40015 2000-F175-TER-EL-40001 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175HF701-C2 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre Incomer | F175-HF-701 | Note 8 | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-SCM-EL-40015 2000-F175-TER-EL-40001 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175HF701-C3 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre Incomer | F175-HF-701 | Note 8 | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-SCM-EL-40015 2000-F175-TER-EL-40001 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175AFD701-C1 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre Incomer | F175-AFD-701 | Note 8 | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TER-EL-40001 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175AFD701-C2 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre Incomer | F175-AFD-701 | Note 8 | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TER-EL-40001 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175AFD701-C3 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre Incomer | F175-AFD-701 | Note 8 | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TER-EL-40001 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175SR701LCS-C1 | F175-RTU-701 | Southlakes Booster Station LV Switchroom RTU Panel | F175SR701-LCS | Note 8 | 6C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TER-EL-40002 | Refer Note 8 | Confirmed | 1 | [6 empty] | 4
F175SR701LCS-C2 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre Incomer | F175SR701-LCS | Note 8 | 6C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TER-EL-40002 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175SW701-C1 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre Incomer | F175-RTU-701 | Note 8 | 15C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TER-EL-40001 | Refer Note 8 | Confirmed | 1 | [6 empty] | 4
F175PW701VS-P1 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre | F175PW701-VS | Note 8 | 3C+E 70mm² Cu 0.6/1kV XLPE/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-SCM-EL-40011 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175PW701-P1 | F175PW701-VS | Southlakes Booster Pump 1 Variable Speed Drive | F175-PW-701 | 25 | 3C+3E 70mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-SCM-EL-40011 |  | Confirmed | 0 | [6 empty] | 4
F175PW701VS-C1 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre | F175PW701-VS | Note 8 | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-SCM-EL-40011 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175PW701-C1 | F175-PW-701 | Southlakes Booster Station LV Motor Control Centre | F175PW701-LCS | 25 | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-SCM-EL-40011 |  | Confirmed | 0 | [6 empty] | 4
F175PW701-I1 | F175PW701-VS | Southlakes Booster Pump 1 Variable Speed Drive | F175-PW-701 | 25 | 1.5mm² 1 Pair O/S | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-SCM-EL-40011 |  | Confirmed | 1 | [6 empty] | 4
F175PW702VS-P1 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre | F175PW702-VS | Note 8 | 3C+E 70mm² Cu 0.6/1kV XLPE/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-SCM-EL-40012 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175PW702-P1 | F175PW701-VS | Southlakes Booster Pump 2 Variable Speed Drive | F175-PW-702 | 25 | 3C+3E 70mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-SCM-EL-40012 |  | Confirmed | 0 | [6 empty] | 4
F175PW702VS-C1 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre | F175PW702-VS | Note 8 | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-SCM-EL-40012 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175PW702-C1 | F175-PW-702 | Southlakes Booster Station LV Motor Control Centre | F175PW702-LCS | 25 | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-SCM-EL-40012 |  | Confirmed | 0 | [6 empty] | 4
F175PW702-I1 | F175PW702-VS | Southlakes Booster Pump 2 Variable Speed Drive | F175-PW-702 | 25 | 1.5mm² 1 Pair O/S | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-SCM-EL-40012 |  | Confirmed | 1 | [6 empty] | 4
F175DB701-P1 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre | F175-DB-701 | Note 8 | 4C+E 95mm² Cu 0.6/1kV XLPE/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40001 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175UPS701ISL-P1 | F175-SW-701 | Southlakes Booster Station LV Motor Control Centre | F175UPS701-ISL | Note 8 | 4C+E 16mm² Cu 0.6/1kV XLPE/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40002 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175UPS701-P1 | F175UPS701-ISL | Southlakes Booster Station LV Switchroom 240V AC UPS Bypass Switch | F175-UPS-701 | Note 8 | 4C+E 10mm² Cu 0.6/1kV R-EP-90 | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40002 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175UPS701ISL-P2 | F175-UPS-701 | Southlakes Booster Station LV Switchroom 240V AC UPS | F175UPS701-ISL | Note 8 | 2C+E 10mm² Cu 0.6/1kV R-EP-90 | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40002 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175UPS701-C1 | F175UPS701-ISL | Southlakes Booster Station LV Switchroom 240V AC UPS Bypass Switch | F175-UPS-701 | Note 8 | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40002 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
F175DB702-P1 | F175UPS701-ISL | Southlakes Booster Station LV Switchroom 240V AC UPS Bypass Switch | F175-DB-702 | Note 8 | 2C+E 16mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40002 | Refer Note 8 | Confirmed | 0 | [6 empty] | 4
Client: | NORTHERN STAR RESOURCES |  | SOUTHLAKES BOOSTER STATION CABLE SCHEDULE - LV CABLES | [16 empty] | 5
Project: Document Number: | KCGM 2000-F175-LST-EL-40003 | [18 empty] | 5
Revision: | 2 | [18 empty] | 5
F175SW701-P1 | F175-DB-702 | Southlakes Booster Station LV Switchroom 240V AC UPS DB | F175-SW-701 | Note 8 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40002 | Refer Note 8 | Confirmed | 0 | [6 empty] | 5
F175SW701-P2 | F175-DB-702 | Southlakes Booster Station LV Switchroom 240V AC UPS DB | F175-SW-701 | Note 8 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40002 | Refer Note 8 | Confirmed | 0 | [6 empty] | 5
F175RTU701-P1 | F175-DB-702 | Southlakes Booster Station LV Switchroom 240V AC UPS DB | F175-RTU-701 | Note 8 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40002 | Refer Note 8 | Confirmed | 0 | [6 empty] | 5
F175COM701-P1 | F175-DB-702 | Southlakes Booster Station LV Switchroom 240V AC UPS DB | F175-COM-701 | Note 8 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40002 | Refer Note 8 | Confirmed | 0 | [6 empty] | 5
F175FIP701-P1 | F175-DB-702 | Southlakes Booster Station LV Switchroom 240V AC UPS DB | F175-FIP-701 | Note 8 | 2C 1.5mm² Cu 0.45/0.75kV R-EP-110°C | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40002 | Refer Note 8 | Confirmed | 0 | [6 empty] | 5
F175FIP701-C1 | F175-RTU-701 | Southlakes Booster Station LV Switchroom RTU Panel | F175-FIP-701 | Note 8 | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TER-IC-40002 | Refer Note 8 | Confirmed | 1 | [6 empty] | 5
F175DB701-R2 | F175-DB-701 | Southlakes Booster Station LV Switchroom and Area L&SP DB |  | 30 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-TLD-EL-40001 |  | Confirmed | 1 | [6 empty] | 5
F175DB701-W2 | F175-DB-701 | Southlakes Booster Station LV Switchroom and Area L&SP DB |  | Note 8 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40001 | Refer Note 8 | Confirmed | 0 | [6 empty] | 5
F175DB701-B2 | F175-DB-701 | Southlakes Booster Station LV Switchroom and Area L&SP DB |  | Note 8 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40001 | Refer Note 8 | Confirmed | 0 | [6 empty] | 5
F175DB701-RWB4 | F175-DB-701 | Southlakes Booster Station LV Switchroom and Area L&SP DB |  | 30 | 4C+E 16mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-TLD-EL-40001 |  | Confirmed | 1 | [6 empty] | 5
F175DB701-R5 | F175-DB-701 | Southlakes Booster Station LV Switchroom and Area L&SP DB |  | 30 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-TLD-EL-40001 |  | Confirmed | 0 | [6 empty] | 5
F175DB701-W5 | F175-DB-701 | Southlakes Booster Station LV Switchroom and Area L&SP DB |  | 20 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-TLD-EL-40001 |  | Confirmed | 0 | [6 empty] | 5
F175DB701-R6 | F175-DB-701 | Southlakes Booster Station LV Switchroom and Area L&SP DB |  | Note 8 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40001 | Refer Note 8 | Confirmed | 0 | [6 empty] | 5
F175DB701-B5 | F175-DB-701 | Southlakes Booster Station LV Switchroom and Area L&SP DB |  | Note 8 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40001 | Refer Note 8 | Confirmed | 0 | [6 empty] | 5
F175DB701-B6 | F175-DB-701 | Southlakes Booster Station LV Switchroom and Area L&SP DB |  | Note 8 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40001 | Refer Note 8 | Confirmed | 0 | [6 empty] | 5
F175DB701-R7 | F175-DB-701 | Southlakes Booster Station LV Switchroom and Area L&SP DB |  | Note 8 | Note 8 | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40001 | Refer Note 8 | Preliminary | 0 | [6 empty] | 5
F175DB701-W7 | F175-DB-701 | Southlakes Booster Station LV Switchroom and Area L&SP DB |  | Note 8 | Note 8 | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40001 | Refer Note 8 | Preliminary | 0 | [6 empty] | 5
F175DB701-B7 | F175-DB-701 | Southlakes Booster Station LV Switchroom and Area L&SP DB |  | Note 8 | Note 8 | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40001 | Refer Note 8 | Preliminary | 0 | [6 empty] | 5
F175DB701-R8 | F175-DB-701 | Southlakes Booster Station LV Switchroom and Area L&SP DB |  | Note 8 | Note 8 | Ladder / Conduit | EL006 | EL006 | EL006 | 2000-F175-TLD-EL-40001 | Refer Note 8 | Preliminary | 0 | [6 empty] | 5
Client: | NORTHERN STAR RESOURCES |  | SOUTHLAKES BOOSTER STATION CABLE SCHEDULE - COMMS CABLES | [16 empty] | 6
Project: Document Number: | KCGM 2000-F175-LST-EL-40003 | [18 empty] | 6
Revision: | 2 | [18 empty] | 6
F175ETH701-FO1 | F175-ETH-702 | Southlakes Booster Station LV Switchroom Ethernet Switch 2 (PCN Switch) | F175-ETH-701 | Note 8 | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 0 | [6 empty] | 6
F175FIP701-FO1 | F175-ETH-702 | Southlakes Booster Station LV Switchroom Ethernet Switch 2 (PCN Switch) | F175-FIP-701 | Note 8 | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 0 | [6 empty] | 6
F175ETH703-FO1 | F175-ETH-702 | Southlakes Booster Station LV Switchroom Ethernet Switch 2 (PCN Switch) | F175-ETH-703 | Note 8 | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 0 | [6 empty] | 6
F175SD701-D1 | F175-ETH-703 | Southlakes Booster Station LV Switchroom Ethernet Switch 3 (CCTV Switch) | F175-SD-701 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 1 | [6 empty] | 6
F175PW701VS-D1 | F175-ETH-701 | Southlakes Booster Station LV Switchroom Ethernet Switch 1 (PCN Switch) | F175PW701-VS | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 0 | [6 empty] | 6
F175PW702VS-D1 | F175-ETH-701 | Southlakes Booster Station LV Switchroom Ethernet Switch 1 (PCN Switch) | F175PW702-VS | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 0 | [6 empty] | 6
F175AFD701-D1 | F175-ETH-701 | Southlakes Booster Station LV Switchroom Ethernet Switch 1 (PCN Switch) | F175-AFD-701 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 0 | [6 empty] | 6
F175PM701-D1 | F175-ETH-701 | Southlakes Booster Station LV Switchroom Ethernet Switch 1 (PCN Switch) | F175-PM-701 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 0 | [6 empty] | 6
F175SW701-D1 | F175-ETH-701 | Southlakes Booster Station LV Switchroom Ethernet Switch 1 (PCN Switch) | F175-SW-701 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 0 | [6 empty] | 6
F175SW701-D2 | F175-GWY-701 | Southlakes Booster Station LV Motor Control Centre Incomer Gateway | F175-SW-701 | Note 8 | RS485 | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 0 | [6 empty] | 6
F175RTU701-D1 | F175-ETH-701 | Southlakes Booster Station LV Switchroom Ethernet Switch 1 (PCN Switch) | F175-RTU-701 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 0 | [6 empty] | 6
F175HF701-D1 | F175-ETH-701 | Southlakes Booster Station LV Switchroom Ethernet Switch 1 (PCN Switch) | F175-HF-701 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 0 | [6 empty] | 6
F175UPS701-D1 | F175-ETH-701 | Southlakes Booster Station LV Switchroom Ethernet Switch 1 (PCN Switch) | F175-UPS-701 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 0 | [6 empty] | 6
F175RTU701-N1 | F175-RTU-701 | Southlakes Booster Station LV Switchroom RTU Panel ACE 3600 Serial Port 1 | F175-RTU-701_Radio | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 | Cable on DCS Equipment List, 2000- F175-LST-IC-40003 | Confirmed | 0 | [6 empty] | 6
F175RTU701A-C1 | F175-RTU-701_Radio | Southlakes Booster Station LV Switchroom RTU Panel Data Radio | F175-SS-701A | Note 8 | CNT-400 | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 | Low Loss 5ohm Cable | Confirmed | 0 | [6 empty] | 6
F175RTU701A-C2 | F175-SS-701A | Southlakes Booster Station LV Switchroom RTU Panel Surge Supressor 1 | F175-ANT-701A | 40 | CNT-400 | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-BLK-IC-40001 | Low Loss 5ohm Cable | Confirmed | 0 | [6 empty] | 6
F175RTU701-N2 | F175-RTU-701 | Southlakes Booster Station LV Switchroom RTU Panel ACE 3600 Serial Port 2 | F175-RTU-701_Modem | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 | Cable on DCS Equipment List, 2000- F175-LST-IC-40003 | Confirmed | 0 | [6 empty] | 6
F175RTU701B-C1 | F175-RTU-701_Modem | Southlakes Booster Station LV Switchroom RTU Panel Radio Modem 4G | F175-SS-701B | Note 8 | CNT-400 | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 | Low Loss 5ohm Cable | Confirmed | 0 | [6 empty] | 6
F175RTU701B-C2 | F175-SS-701B | Southlakes Booster Station LV Switchroom RTU Panel Surge Supressor 2 | F175-ANT-701B | Note 8 | CNT-400 | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 | Low Loss 5ohm Cable | Confirmed | 0 | [6 empty] | 6
F175RTU701-N3 | F175-RTU-701 | Southlakes Booster Station LV Switchroom RTU Panel ACE 3600 Ethernet Port 1 | F175-RTU-701 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 | 2000-F175-BLK-IC-40001 |  | Confirmed | 0 | [6 empty] | 6
Client: | NORTHERN STAR RESOURCES |  | SOUTHLAKES BOOSTER STATION CABLE SCHEDULE - INSTRUMENT CABLES | [16 empty] | 7
Project: Document Number: | KCGM 2000-F175-LST-EL-40003 | [18 empty] | 7
Revision: | 2 | [18 empty] | 7
PIT17520-I1 | F175-RTU-701 | Southlakes Booster Station LV Switchroom RTU Panel | PIT17520 | 40 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder / Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-TER-IC-40003 |  | Confirmed | 0 | 0.11 | Cu | 1PR | 1.5 | PVC/OSCN/PVC |  | 7
PIT17521-I1 | F175-RTU-701 | Southlakes Booster Station LV Switchroom RTU Panel | PIT17521 | 35 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder / Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-TER-IC-40003 |  | Confirmed | 0 | 0.11 | Cu | 1PR | 1.5 | PVC/OSCN/PVC |  | 7
FIT17522-I1 | F175-RTU-701 | Southlakes Booster Station LV Switchroom RTU Panel | FIT17522 | 25 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Ladder / Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-TER-IC-40001 2000-F175-TER-IC-40003 |  | Confirmed | 0 | 0.11 | Cu | 2PR | 1.5 | PVC/IOSCN/PVC |  | 7
FIT17522-P1 | F175-RTU-701 | Southlakes Booster Station LV Switchroom RTU Panel | FIT17522 | 25 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder / Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F175-SCM-IC-40002 2000-F175-TER-IC-40003 |  | Confirmed | 0 | 0.6/1 | Cu | 2C+E | 1.5 | PVC/PVC |  | 7
UT17523-I1 | F175-RTU-701 | Southlakes Booster Station LV Switchroom RTU Panel | UT17523 | 20 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit | EL006 | EL006 | EL006 | 2000-F175-TER-IC-40003 |  | Confirmed | 1 | 0.11 | Cu | 2PR | 1.5 | PVC/IOSCN/PVC |  | 7
F175SW701PS-I1 | F175-RTU-701 | Southlakes Booster Station LV Switchroom RTU Panel | F175SW701-PS | Note 8 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit | EL006 | EL006 | EL006 | 2000-F175-TER-IC-40001 2000-F175-SCM-EL-40004 |  | Confirmed | 0 | 0.11 | Cu | 2PR | 1.5 | PVC/OSCN/PVC |  | 7
F175COM701PS-I1 | F175-RTU-701 | Southlakes Booster Station LV Switchroom RTU Panel | F175COM701-PS | Note 8 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit | EL006 | EL006 | EL006 | 2000-F175-TER-IC-40002 2000-F175-SCM-IC-40001 |  | Confirmed | 0 | 0.11 | Cu | 2PR | 1.5 | PVC/OSCN/PVC |  | 7
FIT17503-P1 | SEBDT01SW | Eastern Borefield Dam Switchboard | FIT-17503 | 90 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 175\E\3045-002 175\E\3038_5 | Not on model Contractor to provide, install and wire a 2A (DTCB6202D) circuit breaker into the existing SEBDT01DB01A distribution board. The flow transmitter power cable will be wired to this circuit breaker. | Confirmed | 1 | 0.6/1 | Cu | 2C+E | 2.5 | PVC/PVC | 2000-F00-STD-EL-10015 | 7
FIT17503-I1 | SEBDT01SW | Eastern Borefield Dam Switchboard | FIT-17503 | 90 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 175\E\3045-002 175\E\3043-002 | Not on model Contractor to provide, install and wire in a new IO Module Card (Slot 4 -V562) c/w 52 terminals (weidmuller -W2 wC il_l 4 b_eD wT ir) e, dw h toic oh . the FIT signals | Confirmed | 1 | 0.11 | Cu | 2PR | 1.5 | PVC/IOSCN/PVC | 2000-F00-STD-EL-10015 | 7
PIT17504-I1 | SEBDT01SW | Eastern Borefield Dam Switchboard | PIT-17504 | 90 | 1PR 1.5mm² Cu 0.6/1kV PVC/OSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 175\E\3045-003 175\E\3043_002 | Not on model Contractor to provide, install and wire a 2A (DTCB6202D) circuit breaker into the existing SEBDT01DB01A distribution board. The flow transmitter power cable will be wired to this circuit breaker. | Confirmed | 1 | 0.6/1 | Cu | 1PR | 1.5 | PVC/OSCN/PVC |  | 7
PCV17504-P1 | SEBDT01SW | Eastern Borefield Dam Switchboard | PCV-17504 | 80 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 175\E\3045-003 175\E\3038_5 | Not on model Contractor to provide, install and wire a 2A (DTCB6202D) circuit breaker into the existing SEBDT01DB01A distribution board. The flow transmitter power cable will be wired to this circuit breaker. | Confirmed | 1 | 0.6/1 | Cu | 2C+E | 2.5 | PVC/PVC |  | 7
PCV17504-I1 | SEBDT01SW | Eastern Borefield Dam Switchboard | PCV-17504 | 80 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 175\E\3045-003 175\E\3043-002 | Not on model Contractor to provide, install and wire in a new IO Module Card (Slot 4 -V562) c/w 52 terminals (weidmul sle igr n-W als2 C w_ill4 b_eD T w) ir, ew dh ti oc oh the valve . | Confirmed | 1 | 0.11 | Cu | 2PR | 1.5 | PVC/IOSCN/PVC |  | 7
FIT75794-P1 | SEBDT01SW | Eastern Borefield Dam Switchboard | FIT-75794 | 30 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 175\E\3045-002 175\E\3038_5 | Not on model Contractor to provide, install and wire a 2A (DTCB6202D) circuit breaker into the existing SEBDT01DB01A distribution board. The flow transmitter power cable will be wired to this circuit breaker. | Confirmed | 1 | 0.6/1 | Cu | 2C+E | 2.5 | PVC/PVC | 2000-F00-STD-EL-10015 | 7
FIT75794-I1 | SEBDT01SW | Eastern Borefield Dam Switchboard | FIT-75794 | 30 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 175\E\3045-002 175\E\3043-002 | Not on model Contractor to provide, install and wire in a new IO Module Card (Slot 4 -V562) c/w 52 terminals (weidmuller -W2 wC il_l 4 b_eD wT ir) e, dw h toic oh . the FIT signals | Confirmed | 1 | 0.11 | Cu | 2PR | 1.5 | PVC/IOSCN/PVC | 2000-F00-STD-EL-10015 | 7

## Equipment list
Cable Supplier | Cable Installer | Cable Terminator | Page
EL006 | EL006 | EL006 | 4