## MCC schedule
Sort | Equipment Number | Module No. | Schematic Drawing No. | Name Plate kW | Approx. Full Load Current (A) | MCC No | Make / Model | Rating (A) | Circuit Breaker Model - Verify Against Nameplate (Terasaki) | Rated Current (In, A) | Long Time Trip (lr, xln) | Instantaneous Trip (Ii, xln) | Long Time Trip 1 (Ir, A) | Long Time Trip 2 (Ir, A) | Long Time Delay (tr, s) | Short Time Trip (Isd, A) | Short Time Delay (tsd, s) | Short Time Delay (I²t) | Instantaneous Setting (Ii, A) | Long Time Trip (Ir, A) | Characteristic Curve No. | Internal Ground Fault (Ig, A) | Internal Ground Fault Delay (tg,s) | ELR Make/Model | ELR Threshold IΔn (A) | ELR Delay (s) | Frequency Response | Page
1 | F175-DB-701 | 01R-21 | 2000-F175-SCM-EL-40013 | 46 | 80.0 | F175-SW-701 | IPD / NHG1-250 (TBC) | 250 (TBC) | P160-H-2-3-160-TM | 160 A | 0.63 (100.8 A) | 6 (960 A) | - | - | - | - | - | - | - | - | - | - | - | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | 8
2 | F175-HF-701 | 01R-17 | 2000-F175-SCM-EL-40015 | - | 60 | F175-SW-701 | - | - | P160-H-2-3-100-TM | 160 A | 0.63 (100.8 A) | 6 (960 A) | - | - | - | - | - | - | - | - | - | - | - | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | 8
3 | F175UPS701-ISL | 01R-05 | 2000-F175-SCM-EL-40014 | 10 | 17.4 | F175-SW-701 | - | - | P160-H-2-3-63-TM | 63 A | 0.63 (39.7 A) | 6 (378 A) | - | - | - | - | - | - | - | - | - | - | - | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | 8
4 | F175-PW-701 | 01R-09 | 2000-F175-SCM-EL-40011 | 75 | 131.0 | F175-SW-701 | - | - | P250-H-2-3-250-BE | 250 A | - | - | 0.64 (160 A) | 1 (160 A) | 0.5 | 1.5 (240A) | 0.05 | - | 4 (1000 A) | - | - | - | - | AmpControl ELV (P/N 170447) | 1.0 (Sw. Posn. 'C') | 0.25 (Sw. Posn. '4') | Weighted Mode (Default) | 8
5 | F175-PW-702 | 01R-13 | 2000-F175-SCM-EL-40012 | 75 | 131.0 | F175-SW-701 | - | - | P250-H-2-3-250-BE | 251 A | - | - | 0.64 (160 A) | 1 (160 A) | 0.5 | 1.5 (240A) | 0.05 | - | 4 (1000 A) | - | - | - | - | AmpControl ELV (P/N 170447) | 1.0 (Sw. Posn. 'C') | 0.25 (Sw. Posn. '4') | Weighted Mode (Default) | 8
[7 empty] | Equipment Number | F175-PW-701 | F175-PW-702 | [18 empty] | 9
[7 empty] | Description | Southlakes Booster Pump 1 | Southlakes Booster Pump 2 | [18 empty] | 9
[7 empty] | VVVF Model Number | 20F1ANC170JA0NNNNN+20- 750-S+20-750-20COMM+20- HIM-A6+20-750-APS | 20F1ANC170JA0NNNNN+20- 750-S+20-750-20COMM+20- HIM-A6+20-750-APS | [18 empty] | 9
[7 empty] | VVVF Input Current (A) | TBA | TBA | [18 empty] | 9
[7 empty] | Rating (kW) | 75 | 75 | [18 empty] | 9
[7 empty] | No of Motors | 1 | 1 | [18 empty] | 9
[7 empty] | FLC (A) | 131.00 | 131.00 | [18 empty] | 9
[7 empty] | Schematic Drawing | 2000-F175-SCM-EL-40011 | 2000-F175-SCM-EL-40012 | [18 empty] | 9
[7 empty] | VVVF Datasheet | N/A | N/A | [18 empty] | 9
[7 empty] | VVVF Website Cutsheet | https://configurator.rockwellaut | https://configurator.rockwellaut | [18 empty] | 9
[8 empty] | omation.com/api/Product/20f1a | omation.com/api/Product/20f1a | [18 empty] | 9
[8 empty] | nc170ja0nnnnn/cutsheet | nc170ja0nnnnn/cutsheet | [18 empty] | 9
[7 empty] | Motor Datasheet | 2000-ME015-F14- 40001 B IFI _ _ | 2000-ME015-F14- 40001 B IFI _ _ | [18 empty] | 9
[7 empty] | IP Address | 10.10.221.16 (Note 5) | 10.10.221.16 (Note 5) | [18 empty] | 9
[7 empty] | Circuit Breaker | P250-H-2-3-250-BE | P250-H-2-3-250-BE | [18 empty] | 9
[7 empty] | Nominal Rating of Trip Unit (A) | 250 | 250 | [18 empty] | 9
[7 empty] | Ir (xIn) | - | - | [18 empty] | 9
[7 empty] | Ii (xIn) | - | - | [18 empty] | 9
[7 empty] | Long Time - Ir1 | 0.64 (160 A) | 0.64 (160 A) | [18 empty] | 9
[7 empty] | Long Time - Ir2 | 1 (160 A) | 1 (160 A) | [18 empty] | 9
[7 empty] | Long Time Delay - tr (sec) | 0.5 | 0.5 | [18 empty] | 9
[7 empty] | Short Time - Isd | 1.5 (240 A) | 1.5 (240 A) | [18 empty] | 9
[7 empty] | Short Time Delay - tsd (sec) | 0.05 | 0.05 | [18 empty] | 9
[7 empty] | Short Time Delay I²t | - | - | [18 empty] | 9
[7 empty] | Instantaneous - Ii | 4 (1000 A) | 4 (1000 A) | [18 empty] | 9
[7 empty] | Characteristic No. | - | - | [18 empty] | 9
[7 empty] | TOL | - | - | [18 empty] | 9
[7 empty] | TOL Setting (A) | - | - | [18 empty] | 9
File / Group | Port | No. | Display Name | Data Type | Setting Notes | [22 empty] | 9
MOTOR CONTROL - Motor Data | 0 | 25 | Motor NP Volts | Real | 400V |  |  | 415V | 415V | [18 empty] | 10
MOTOR CONTROL - Motor Data | 0 | 26 | Motor NP Amps | Real | Lookup |  |  | 131 | 131 | [18 empty] | 10
MOTOR CONTROL - Motor Data | 0 | 27 | Motor NP Hertz | Real | 50 |  |  | 50 | 50 | [18 empty] | 10
MOTOR CONTROL - Motor Data | 0 | 28 | Motor NP RPM | Real | Datasheet |  |  | 1483 | 1483 | [18 empty] | 10
MOTOR CONTROL - Motor Data | 0 | 29 | Mtr NP Pwr Units | 32-bit Integer | 1 – kW |  |  | 1 = kW | 1 = kW | [18 empty] | 10
MOTOR CONTROL - Motor Data | 0 | 30 | Motor NP Power | Real | Lookup |  |  | 75 | 75 | [18 empty] | 10
MOTOR CONTROL - Motor Data | 0 | 31 | Motor Poles | 32-bit Integer | Lookup |  |  | 4 | 4 | [18 empty] | 10
MOTOR CONTROL - Mtr Ctrl Options | 0 | 35 | Motor Ctrl Mode | 32-bit Integer | 1 – Induction SV | Note 1 |  | 1 - Induction SV | 1 - Induction SV | [18 empty] | 10
MOTOR CONTROL - Mtr Ctrl Options | 0 | 36 | Maximum Voltage | Real | 415 |  |  | 415 | 415 | [18 empty] | 10
MOTOR CONTROL - Mtr Ctrl Options | 0 | 37 | Maximum Freq | Real | 50 |  |  | 50 | 50 | [18 empty] | 10
MOTOR CONTROL - Mtr Ctrl Options | 0 | 38 | PWM Frequency | Real | Default, Dependant on Frame size |  |  | Default, Dependant on Frame size | Default, Dependant on Frame size | [18 empty] | 10
MOTOR CONTROL - Mtr Ctrl Options | 0 | 41 | Common Mode Type | 32-bit Integer | 0 – CMV |  |  | 0 – CMV | 0 – CMV | [18 empty] | 10
MOTOR CONTROL - Volts per Hertz | 0 | 60 | Start Acc Boost | Real | Default |  |  | Default | Default | [18 empty] | 10
MOTOR CONTROL - Volts per Hertz | 0 | 61 | Run Boost | Real | Default |  |  | Default | Default | [18 empty] | 10
MOTOR CONTROL - Volts per Hertz | 0 | 62 | Break Voltage | Real | Default |  |  | Default | Default | [18 empty] | 10
MOTOR CONTROL - Volts per Hertz | 0 | 63 | Break Frequency | Real | Default |  |  | Default | Default | [18 empty] | 10
MOTOR CONTROL - Volts per Hertz | 0 | 65 | VHz Curve | 32-bit Integer | Default |  |  | Default | Default | [18 empty] | 10
MOTOR CONTROL - Autotune | 0 | 70 | Autotune | 32-bit Integer | 1 – Calculate |  |  | 1 – Calculate | 1 – Calculate | [18 empty] | 10
MOTOR CONTROL - Autotune | 0 | 71 | Autotune Torque | Real | 50% |  |  | 50% | 50% | [18 empty] | 10
MOTOR CONTROL - Autotune | 0 | 73 | IR Voltage Drop | Real | Set By Autotune |  |  | Set By Autotune | Set By Autotune | [18 empty] | 10
MOTOR CONTROL - Autotune | 0 | 74 | Ixo Voltage Drop | Real | Set By Autotune |  |  | Set By Autotune | Set By Autotune | [18 empty] | 10
MOTOR CONTROL - Autotune | 0 | 75 | Flux Current Ref | Real | Set By Autotune |  |  | Set By Autotune | Set By Autotune | [18 empty] | 10
MOTOR CONTROL - Autotune | 0 | 76 | Total Inertia | Real | Set By Autotune |  |  | Set By Autotune | Set By Autotune | [18 empty] | 10
FEEDBACK & I/O - Digin Functions | 0 | 150 | Digital In Cfg | 32-bit Integer | 0 – Run Edge |  |  | 0 – Run Edge | 0 – Run Edge | [18 empty] | 10
FEEDBACK & I/O - Digin Functions | 0 | 155 | DI Enable | 32-bit Integer | Default |  |  | Default | Default | [18 empty] | 10
FEEDBACK & I/O - Digin Functions | 0 | 156 | DI Clear Fault | 32-bit Integer | Default |  |  | Default | Default | [18 empty] | 10
FEEDBACK & I/O - Digin Functions | 0 | 157 | DI Aux Fault | 32-bit Integer | Default |  |  | Default | Default | [18 empty] | 10
FEEDBACK & I/O - Digin Functions | 0 | 158 | DI Stop | 32-bit Integer | Default |  |  | Default | Default | [18 empty] | 10
FEEDBACK & I/O - Digin Functions | 0 | 159 | DI Cur Lmt Stop | 32-bit Integer | Default |  |  | Default | Default | [18 empty] | 10
FEEDBACK & I/O - Digin Functions | 0 | 160 | DI Coast Stop | 32-bit Integer | Default |  |  | Default | Default | [18 empty] | 10
FEEDBACK & I/O - Digin Functions | 0 | 161 | DI Start | 32-bit Integer | Default |  |  | Default | Default | [18 empty] | 10
FEEDBACK & I/O - Digin Functions | 0 | 162 | DI Fwd Reverse | 32-bit Integer | Default |  |  | Default | Default | [18 empty] | 10
FEEDBACK & I/O - Digin Functions | 0 | 163 | DI Run | 32-bit Integer | Default |  |  | Port 0: Dig In Sts.Input 1 | Port 0: Dig In Sts.Input 1 | [18 empty] | 10
FEEDBACK & I/O - Digin Functions | 0 | 164 | DI Run Forward | 32-bit Integer | Default |  |  | Default | Default | [18 empty] | 10
FEEDBACK & I/O - Digin Functions | 0 | 165 | DI Run Reverse | 32-bit Integer | Default |  |  | Default | Default | [18 empty] | 10
FEEDBACK & I/O - Digout Functions | 0 | 230 | RO0 Sel | 32-bit Integer | 0 |  |  | Default | Default | [18 empty] | 10
DRIVE CFG - Control Cfg | 0 | 306 | Duty Rating | 32-bit Integer | 0 normally, 1 for HD |  |  | 1 = “Heavy Duty” | 1 = “Heavy Duty” | [18 empty] | 10
DRIVE CFG - Control Cfg | 0 | 308 | Direction Mode | 32-bit Integer | 0 = “Unipolar” 1 = “Reversing" |  |  | 0 = “Unipolar” | 0 = “Unipolar” | [18 empty] | 10
DRIVE CFG - Control Cfg | 0 | 325 | Auto Mask | - | 00000000 01000000 |  |  | 00000000 01000000 | 00000000 01000000 | [18 empty] | 10
DRIVE CFG - Control Cfg | 0 | 326 | Manual Cmd Mask | - | 00000000 00000100 |  |  | 00000000 00000100 | 00000000 00000100 | [18 empty] | 10
Protection - Motor Overload | 0 | 410 | Motor OL Actn | 32-bit Integer | 3 = “FltCoastStop” |  |  | 3 = “FltCoastStop” | 3 = “FltCoastStop” | [18 empty] | 11
Protection - Motor Overload | 0 | 411 | Mtr OL at Pwr | 32-bit Integer | 0 = “Assume Cold” |  |  | 0 = “Assume Cold” | 0 = “Assume Cold” | [18 empty] | 11
Protection - Motor Overload | 0 | 412 | Mtr OL Alarm Lvl | Real | N/A |  |  | N/A | N/A | [18 empty] | 11
Protection - Motor Overload | 0 | 413 | Mtr OL Factor | Real | 1 |  |  | 1 | 1 | [18 empty] | 11
Protection - Motor Overload | 0 | 414 | Mtr OL Hertz | Real | 20 |  |  | 20 | 20 | [18 empty] | 11
Protection - Motor Overload | 0 | 415 | Mtr OL Reset Lvl | Real | Default |  |  | Default | Default | [18 empty] | 11
Protection - Load Limits | 0 | 420 | Drive OL Mode | 32-bit Integer | 3 = “Both PWM 1st” |  |  | 3 = “Both PWM 1st” | 3 = “Both PWM 1st” | [18 empty] | 11
Protection - Load Limits | 0 | 421 | Current Lmt Sel | 32-bit Integer | 422 |  |  | 422 | 422 | [18 empty] | 11
Protection - Load Limits | 0 | 422 423 | Current Limit 1 Current Limit 2 | Real | Default |  |  | Default | Default | [18 empty] | 11
Protection - Load Limits | 0 | 425 | Current Rate Lmt | Real | 400 |  |  | 400 | 400 | [18 empty] | 11
Speed Control - Speed Limits | 0 | 520 | Max Fwd Speed | Real | Default |  |  | 50 Hz | 50 Hz | [18 empty] | 11
Speed Control - Speed Limits | 0 | 521 | Max Rev Speed | Real | Default |  |  | 0 Hz | 0 Hz | [18 empty] | 11
Speed Control - Speed Limits | 0 | 522 | Min Fwd Speed | Real | 0 |  |  | 10 Hz | 10 Hz | [18 empty] | 11
Speed Control - Speed Limits | 0 | 523 | Min Rev Speed | Real | 0 |  |  | 0 Hz | 0 Hz | [18 empty] | 11
Speed Control - Speed Limits | 0 | 524 | Overspeed Limit | Real | Default |  |  | Default | Default | [18 empty] | 11
Speed Control - Speed Limits | 0 | 525 | Zero Speed Limit | Real | Default |  |  | Default | Default | [18 empty] | 11
Speed Control - Speed Ramp Rates | 0 | 535 536 | Accel Time 1 Accel Time 2 | Real | 10, or 20 for Heavy Duty |  |  | 20 | 20 | [18 empty] | 11
Speed Control - Speed Ramp Rates | 0 | 537 538 | Decel Time 1 Decel Time 2 | Real | 10, or 20 for Heavy Duty |  |  | 20 | 20 | [18 empty] | 11
Speed Control - Speed Reference | 0 | 545 | Spd Ref A Sel Spd Ref B Sel | 32-bit Integer | Default |  |  | Port 0: P876 - Port 6 Reference | Port 0: P876 - Port 6 Reference | [18 empty] | 11
Communication - DPI Datalinks | 0 | 905 | Data Out A1 | Real | 0 - Disabled |  |  | Port 0: Mtr Vel Fdbk | Port 0: Mtr Vel Fdbk | [18 empty] | 11
Communication - DPI Datalinks | 0 | 906 | Data Out A2 | Real | 0 - Disabled |  |  | Port 0: Output Current | Port 0: Output Current | [18 empty] | 11
Communication - DPI Datalinks | 0 | 907 | Data Out B1 | Real | 0 - Disabled |  |  | Port 0: Torque Cur Fdbk | Port 0: Torque Cur Fdbk | [18 empty] | 11
Communication - DPI Datalinks | 0 | 908 | Data Out B2 | Real | 0 - Disabled |  |  | Port 0: Output Voltage | Port 0: Output Voltage | [18 empty] | 11
Communication - DPI Datalinks | 0 | 909 | Data Out C1 | Real | 0 - Disabled |  |  | Port 0: Output Power | Port 0: Output Power | [18 empty] | 11
Communication - DPI Datalinks | 0 | 910 | Data Out C2 | Real | 0 - Disabled |  |  | Port 0: Elapsed Run Time | Port 0: Elapsed Run Time | [18 empty] | 11
Communication - DPI Datalinks | 0 | 911 | Data Out D1 | Real | 0 - Disabled |  |  | Port 0: Last Fault Code | Port 0: Last Fault Code | [18 empty] | 11
22-Series I/O Analog Outputs | 4 | 10 | RO0 Sel | 32-bit Integer |  |  |  | N/A | N/A | [18 empty] | 11
22-Series I/O Analog Outputs | 4 | 6 | Dig Out Invert | 32-bit Integer |  |  |  | N/A | N/A | [18 empty] | 11
Port 6 (20-750-20COMM) | 6 | 3 | BOOTP |  | Disabled |  |  | Disabled | Disabled | [18 empty] | 11
Port 6 (20-750-20COMM) | 6 | 4 | IP Addr Cfg 1 |  | 10 |  |  | 10 | 10 | [18 empty] | 11
Port 6 (20-750-20COMM) | 6 | 5 | IP Addr Cfg 2 |  | 10 |  |  | 10 | 10 | [18 empty] | 11
Port 6 (20-750-20COMM) | 6 | 6 | IP Addr Cfg 3 |  | 145 |  |  | 221 | 221 | [18 empty] | 11
Port 6 (20-750-20COMM) | 6 | 7 | IP Addr Cfg 4 |  | Specific to drive |  |  | 16 | 17 | [18 empty] | 11
Port 6 (20-750-20COMM) | 6 | 8 | Subnet Cfg 1 |  | 255 |  |  | 255 | 255 | [18 empty] | 11
Port 6 (20-750-20COMM) | 6 | 9 | Subnet Cfg 2 |  | 255 |  |  | 255 | 255 | [18 empty] | 11
Port 6 (20-750-20COMM) | 6 | 10 | Subnet Cfg 3 |  | 255 |  |  | 255 | 255 | [18 empty] | 12
Port 6 (20-750-20COMM) | 6 | 11 | Subnet Cfg 4 |  | 0 |  |  | 0 | 0 | [18 empty] | 12
Port 6 (20-750-20COMM) | 6 | 12 | Gateway Cfg 1 |  | 10 |  |  | 10 | 10 | [18 empty] | 12
Port 6 (20-750-20COMM) | 6 | 12 | Gateway Cfg 2 |  | 10 |  |  | 10 | 10 | [18 empty] | 12
Port 6 (20-750-20COMM) | 6 | 13 | Gateway Cfg 3 |  | 142 |  |  | 221 | 221 | [18 empty] | 12
Port 6 (20-750-20COMM) | 6 | 14 | Gateway Cfg 4 |  | 1 |  |  | 1 | 1 | [18 empty] | 12
Port 6 (20-750-20COMM) | 6 | 19 | Msg I/O Timer |  | 60 |  |  | 60 | 60 | [18 empty] | 12
Port 6 (20-750-20COMM) | 6 | 23 | Comm Flt Action | Real | 1 = Stop |  |  | 1 = Stop | 1 = Stop | [18 empty] | 12
Port 6 (20-750-20COMM) | 6 | 38 | Indirect Par #1 |  | 220 (PF753) or 14001 (PF755) |  |  | 220 | 220 | [18 empty] | 12
Port 6 (20-750-20COMM) | 6 | 39 | Indirect Par #2 |  | 933 |  |  | 933 | 933 | [18 empty] | 12
Port 6 (20-750-20COMM) | 6 | 40 | Indirect Par #3 |  | 724 |  |  | 724 | 724 | [18 empty] | 12
Port 6 (20-750-20COMM) | 6 | 41 | Indirect Par #4 |  | 937 |  |  | 937 | 937 | [18 empty] | 12

## Equipment list
Sort | Make / Model | Rating (A) | Equipment Number | Page
LV VVVF SETTINGS Notes: 1. All Settings to be verified during pre-commissioning. 2. Motor load current values and RPM are to be confirmed against motor nameplate data on site. 3. Parameters given for all protection settings on this list, not all functions enabled. 4. Long Time Setting Check - thermal / long time setting is higher than VVVF input current. 5. Refer to RTU Communications document for IP Address Register for details. 6. Motor RTDs wired to DCS, not VVVF. 7. STO implementation is "out-of-the-box" and "hardwired", refer Rockwell Automation Publication 750-UM002O-EN-P - January 2025. Note, PowerFlex 755 drives (frames 8...10) control boards do not have a SAFETY enable jumper. PowerFlex 753 do have a SAFETY enable jumber that is required to be removed from the Main Control Board to ensure the drive does does not fault. Refer <https://www.rockwellautomation.com/en-us/products/details.20-750-S.html> and extract below. | Allen-Bradley PowerFlex Series | PF 753 Series |  | 9
Equipment Number |  |  | F175-HF-701 | 13
Description |  |  | Southlakes Booster Station 415V Switchroom Active Harmonic Filter | 13
Make/Model |  |  | Schneider AccuSine PCS+ PCSP060D5IP31 | 13
Motor Control Centre |  |  | F175-SW-701 | 13
IP Address |  |  | 10.10.221.15 | 13
System Rating |  |  | 60A | 13
Nominal Voltage ¦ Frequency |  |  | 415V 50Hz | 13
External Transformer |  |  | No | 13
Wiring Type |  |  | 3P3W | 13
CT Configuration |  |  | 3 CTs | 13
CT Position |  |  | Source | 13
Total Capacity |  |  | 60 Amps | 13
CT Setting |  |  | 400:1, Positive | 13
Harmonic Mode |  |  | On | 13
PF Mode |  |  | On | 13
Optimised PF Mode |  |  | On | 13
Load Balancing |  |  | Off | 13
Power On Mode |  |  | Manual (Pre-commissioning) Autostart Enable (Post-commissioning) | 13
Output Enabled |  |  | On | 13
5th |  |  | On | 13
7th |  |  | On | 13
11th |  |  | On | 13
13th |  |  | On | 13
17th |  |  | On | 13
19th |  |  | On | 13
23rd |  |  | On | 13
25th |  |  | On | 13
All other Harmonics |  |  | Off | 13
Inductive or Capacitive |  |  | Inductive | 13
Target PF |  |  | 0.96 | 13
OTHER SETTINGS |  |  | Factory Default | 13
General Notes |  |  | Refer harmonics calculation for details of sizing requirement 2000-F175-CAL-EL-2000-F175-LST- EL-40001. | 13