## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | To Equip. Number | To Equipment Name | Conductor Size (mm2) | Insulation (kV) | Length (m) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred colour) | Installation | Supplied By | Installed By | Reference Drawing | Area | Rev | Comments | Page
F19CP401-P1 | F19-SW-61 | SUB 60 - 19-SW-61 Switchboard | F19-CP-401 | Ball Charger Rectifier Control Panel | 25 | 0.6/1 | 165 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Enabling Works Contractor | Enabling Works Contractor | 2000-F19-SLD-EL-10103 2000-F19-SCM-EL-10001 | 19 | 0 |  | 2
F19CP402-P1 | F19-CP-401 | Ball Charger Rectifier Control Panel | F19-CP-402 | Ball Charger Hoist Control Panel | 10 | 0.6/1 | 45 | 3C+E | Cu | Flexible Multicore Catenary Cable | Black | CATENARY | ME067 ERIEZ | Enabling Works Contractor | 2000-ME067-D02-10005 | 19 | 0 | 415V Supply to Hoist/Trolley Control Panel. | 2
F19CR401-P1 | F19-CP-401 | Ball Charger Rectifier Control Panel | F19-CR-401 | Ball Charger Magnet Cable Reeler | 25 | 0.6/1 | 45 | 1C | Cu | Flexible Single Core Catenary Cable | Black | CATENARY | ME067 ERIEZ | Enabling Works Contractor | 2000-ME067-D02-10005 | 19 | 0 | Cable from Magnet Control Panel to Cable Reeler. | 2
F19CR401-P2 | F19-CP-401 | Ball Charger Rectifier Control Panel | F19-CR-401 | Ball Charger Magnet Cable Reeler | 25 | 0.6/1 | 45 | 1C | Cu | Flexible Single Core Catenary Cable | Black | CATENARY | ME067 ERIEZ | Enabling Works Contractor | 2000-ME067-D02-10005 | 19 | 0 | Cable from Magnet Control Panel to Cable Reeler. | 2
F19CR401-P3 | F19-CP-401 | Ball Charger Rectifier Control Panel | F19-CR-401 | Ball Charger Magnet Cable Reeler | 25 | 0.6/1 | 45 | 1C | Cu | Flexible Earth Catenary Cable | Green/Yellow | CATENARY | ME067 ERIEZ | Enabling Works Contractor | 2000-ME067-D02-10005 | 19 | 0 | Cable from Magnet Control Panel to Cable Reeler. | 2
F19BLC401-P1 | F19-CR-401 | Ball Charger Magnet Cable Reeler | F19-BLC-401 | Ball Charger Magnet | 25 | 0.6/1 | 45 | 2C+E | Cu | Flexible Reeler Cable | Black | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10005 | 19 | 0 | Vendor Install | 2
F19LMP401-P1 | F19-DB-60 | Emergency Power Distribution Board | F19-LMP-401 | Ball Charger LED Lamp | 4 | 0.6/1 | TBC | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Enabling Works Contractor | Enabling Works Contractor | 2000-F19-TLD-EL-10005 | 19 | 0 | TBC - Contractor to determine if circuit is adequate | 2
F19COM401-P1 | F19-DB-62 | Substation 60 - 240V Instrument Distribution Board No.62 | F19-COM-401 | Ball Charger CCTV Control Panel | 4 | 0.6/1 | 165 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Enabling Works Contractor | Enabling Works Contractor | 2000-F19-TLD-EL-10002 | 19 | 0 |  | 2
F19CP402-C1 | F19-CP-401 | Ball Charger Rectifier Control Panel | F19-CP-402 | Ball Charger Hoist Control Panel | 1.5 | 0.6/1 | 45 | 12C | Cu | Flexible Reeling Cable | Black | CATENARY | ME067 ERIEZ | Enabling Works Contractor | 2000-ME067-D02-10004 | 19 | 0 |  | 2
F19CP402-C2 | F19-CP-401 | Ball Charger Rectifier Control Panel | F19-CP-402 | Ball Charger Hoist Control Panel | 1.5 | 0.6/1 | 45 | 12C | Cu | Flexible Reeling Cable | Black | CATENARY | ME067 ERIEZ | Enabling Works Contractor | 2000-ME067-D02-10004 | 19 | 0 |  | 2
F19CP403-C1 | F19-CP-401 | Ball Charger Rectifier Control Panel | F19-CP-403 | Ball Charger Instrument Control Panel | 1.5 | 0.6/1 | 45 | 12C | Cu | Flexible Reeling Cable | Black | CATENARY | ME067 ERIEZ | Enabling Works Contractor | 2000-ME067-D02-10004 | 19 | 0 |  | 2
F19CP403-J1 | F19-CP-401 | Ball Charger Rectifier Control Panel | F19-CP-403 | Ball Charger Instrument Control Panel | 1.5 | 0.6/1 | 45 | 6PR | Cu | Flexible Reeling Cable | Black | CATENARY | ME067 ERIEZ | Enabling Works Contractor | 2000-ME067-D02-10004 | 19 | 0 |  | 2
F19CP403-J2 | F19-CP-402 | Ball Charger Hoist Control Panel | F19-CP-403 | Ball Charger Instrument Control Panel | 1.5 | Vendor | Vendor | Vendor | Cu | Vendor Cable | Vendor | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10004 | 19 | 0 | Vendor Install | 2
ZS19401-C1 | F19-CP-403 | Ball Charger Instrument Control Panel | ZS19401 | F19-BN-61A Ball Charging Bin No.1 Position Switch (LS3) | 1.5 | Vendor | Vendor | Vendor | Vendor | Vendor Cable | Black | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10004 | 19 | 0 | Vendor supplied and installed to LS3. | 2
ZS19402-C1 | F19-CP-403 | Ball Charger Instrument Control Panel | ZS19402 | F19-BN-61B Ball Charging Bin No.2 Position Switch (LS4) | 1.5 | Vendor | Vendor | Vendor | Vendor | Vendor Cable | Black | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10004 | 19 | 0 | Vendor supplied and installed to LS4. | 2
ZS19403-C1 | F19-CP-403 | Ball Charger Instrument Control Panel | ZS19403 | F19-BN-61C Ball Charging Bin No.3 Position Switch (LS6) | 1.5 | Vendor | Vendor | Vendor | Vendor | Vendor Cable | Black | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10004 | 19 | 0 | Vendor supplied and installed to LS6. | 2
ZS19404-C1 | F19-CP-402 | Ball Charger Hoist Control Panel | ZS19404 | F19-BLC-401 Ball Charger Trolley Over-Travel North Position Switch (LS1) | 1.5 | 0.6/1 | 5 | 6 | Cu | Vendor Cable | Black | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10004 | 19 | 0 | Vendor supplied and installed to LS1. | 2
ZS19405-C1 | F19-CP-402 | Ball Charger Hoist Control Panel | ZS19405 | F19-BLC-401 Ball Charger Trolley Over-Travel South Position Switch (LS8) | 1.5 | 0.6/1 | 5 | 6 | Cu | Vendor Cable | Black | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10004 | 19 | 0 | Vendor supplied and installed to LS8. | 2
ZS19406-C1 | F19-CP-403 | Ball Charger Instrument Control Panel | ZS19406 | F19-BLC-401 Ball Charger Trolley Maintenance Position Switch | 1.5 | Vendor | Vendor | Vendor | Vendor | Vendor Cable | Black | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10004 | 19 | 0 | Vendor suplied and installed to LS7. | 2
ZS19408-C1 | F19-CP-403 | Ball Charger Instrument Control Panel | ZS19408 | F19-BLC-401 Ball Charger Trolley 25mm Ball Bunker Position Switch (LS5) | 1.5 | Vendor | Vendor | Vendor | Vendor | Vendor Cable | Black | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10004 | 19 | 0 | Vendor supplied and installed to LS5. | 2
ZS19409-C1 | F19-CP-403 | Ball Charger Instrument Control Panel | ZS19409 | F19-BLC-401 Ball Charger Trolley 125mm Ball Bunker Position | 1.5 | Vendor | Vendor | Vendor | Vendor | Vendor Cable | Black | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10004 | 19 | 0 | Vendor supplied and installed to LS2. | 2
ZS19410-C1 | F19-CP-402 | Ball Charger Hoist Control Panel | ZS19410 | F19-BLC-401 Ball Charger Hoist Position Limit Switch (S103) | 1.5 | 0.6/1 | 5 | 8C | Cu | Vendor Cable | Black | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10004 | 19 | 0 | Vendor supplied and installed to S103. | 2
WE19401-C1 | F19-CP-402 | Ball Charger Hoist Control Panel | WE19401 | F19-BLC-401 Ball Charger Magnet Load Cell (B101) | 1.5 | TBC | TBC | 4C | Cu | Vendor Cable | Black | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10004 | 19 | 0 | Vendor supplied and installed to B101. | 2
ZE19411-C1 | F19-CP-403 | Ball Charger Instrument Control Panel | ZE19411 | F19-BLC-401 Ball Charger Hoist Position Encoder (A801) | 1.5 | TBC | TBC | 8C | Cu | Vendor Cable | Black | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10004 | 19 | 0 | Vendor supplied and installed to A801. | 2
ZE19412-C1 | F19-CP-403 | Ball Charger Instrument Control Panel | ZE19412 | F19-BLC-401 Ball Charger Trolley Position Encoder (A802) | 1.5 | TBC | TBC | 8C | Cu | Vendor Cable | Black | Final Run | ME067 ERIEZ | ME067 ERIEZ | 2000-ME067-D02-10004 | 19 | 0 | Vendor supplied and installed to A802. | 2
ZI19408-C1 | F19-CP-401 | Ball Charger Rectifier Control Panel | ZI19408 | F19-BLC-401 Ball Charger Magnet 25mm Ball Bunker Traffic Light | 1.5 | 0.6/1 | 15 | 4C+E | Cu | PVC/PVC Control | Black | Ladder / Conduit | Enabling Works Contractor | Enabling Works Contractor | 2000-ME067-D02-10004 | 19 | 0 |  | 2
ZI19409-C1 | F19-CP-401 | Ball Charger Rectifier Control Panel | ZI19409 | F19-BLC-401 Ball Charger Magnet 125mm Ball Bunker Traffic Light | 1.5 | 0.6/1 | 15 | 4C+E | Cu | PVC/PVC Control | Black | Ladder / Conduit | Enabling Works Contractor | Enabling Works Contractor | 2000-ME067-D02-10004 | 19 | 0 |  | 2
LT19755-I1 | F19-CP-401 | Ball Charger Rectifier Control Panel | LT19755 | F19-BN-61A Ball Charging Bin No.1 Level Transmitter | 1.5 | 0.11/0.15 | 20 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder / Conduit | Enabling Works Contractor | Enabling Works Contractor | 2000-ME067-D02-10004 | 19 | 0 |  | 2
LI19755-I1 | LT19755 | F19-BN-61A Ball Charging Bin No.1 Level Transmitter | LI19755 | F19-BN-61A Ball Charging Bin No.1 Level Indicator | 1.5 | 0.11/0.15 | 10 | 1PR | Cu | PVC/OSCN/PVC | Black | Final Run | Level Transmitter Vendor | Enabling Works Contractor | 2000-ME067-D02-10004 | 19 | 0 | TBC - Flying lead | 2
LT19756-I1 | F19-CP-401 | Ball Charger Rectifier Control Panel | LT19756 | F19-BN-61B Ball Charging Bin No.3 Level Transmitter | 1.5 | 0.11/0.15 | 20 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder / Conduit | Enabling Works Contractor | Enabling Works Contractor | 2000-ME067-D02-10004 | 19 | 0 |  | 2
LI19756-I1 | LT19756 | F19-BN-61B Ball Charging Bin No.3 Level Transmitter | LI19756 | F19-BN-61B Ball Charging Bin No.2 Level Indicator | 1.5 | 0.11/0.15 | 10 | 1PR | Cu | PVC/OSCN/PVC | Black | Final Run | Level Transmitter Vendor | Enabling Works Contractor | 2000-ME067-D02-10004 | 19 | 0 | TBC - Flying lead | 2
LT19757-I1 | F19-CP-401 | Ball Charger Rectifier Control Panel | LT19757 | F19-BN-61A Ball Charging Bin No.1 Level Transmitter | 1.5 | 0.11/0.15 | 20 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder / Conduit | Enabling Works Contractor | Enabling Works Contractor | 2000-ME067-D02-10004 | 19 | 0 |  | 2
LI19757-I1 | LT19757 | F19-BN-61A Ball Charging Bin No.1 Level Transmitter | LI19757 | F19-BN-61C Ball Charging Bin No.3 Level Sensor | 1.5 | 0.11/0.15 | 10 | 1PR | Cu | PVC/OSCN/PVC | Black | Final Run | Level Transmitter Vendor | Enabling Works Contractor | 2000-ME067-D02-10004 | 19 | 0 | TBC - Flying lead | 2
F19COM01-D401 | F19PC61-AR | 19-PC-61 AR Section - FCS202 - ALE111 Ethernet Communications Module | F19-COM-01 | 19-COM-01 Communications Panel - Existing D-Link Switch | - | - | 30 | 4PR | Cu | Cat6 SF/UTP Indoor Cable | Grey | Ladder | Enabling Works Contractor | Enabling Works Contractor | N/A | 19 | A |  | 2
F19COM01-D402 | F19-COM-02 | 19-COM-02 Communications Panel - SWITCH-SUB60CAM CCTV Switch | F19-COM-01 | 19-COM-01 Communications Panel - Existing D-Link Switch | - | - | 10 | 4PR | Cu | Cat6 SF/UTP Indoor Cable | Grey | Ladder | Enabling Works Contractor | Enabling Works Contractor | N/A | 19 | A |  | 2
F19COM02-FO401 | F19-COM-01 | 19-COM-01 Communications Panel - Existing D-Link Switch | F19-COM-02 | 19-COM-02 Communications Panel - New Ball Charger FOBOT | - | - | 10 | 2C | OS2 Single Mode Fiber | LC-LC Patch Lead | Yellow | Ladder | Enabling Works Contractor | Enabling Works Contractor | N/A | 19 | A | LC-LC SMOF OS2 Patch Leads. Note 3 | 2
F19COM02-FO402 | F19-COM-01 | 19-COM-01 Communications Panel - Existing D-Link Switch | F19-COM-02 | 19-COM-02 Communications Panel - New Ball Charger FOBOT | - | - | 10 | 2C | OS2 Single Mode Fiber | LC-LC Patch Lead | Yellow | Ladder | Enabling Works Contractor | Enabling Works Contractor | N/A | 19 | A | LC-LC SMOF OS2 Patch Leads. Note 3 | 2
F19COM401-FO1 | F19-COM-02 | 19-COM-02 Communications Panel - New Ball Charger FOBOT | F19-COM-401 | Ball Charger CCTV Control Panel | - | - | 175 | 12C | OS2 Single Mode Fiber | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, PE sheath | Black | Ladder | Enabling Works Contractor | Enabling Works Contractor | 2000-F19-DRG-EL-10101 | 19 | A | Note 5 | 2
F19CAM401JB-D1 | F19-COM-401 | Ball Charger CCTV Control Panel | F19CAM401-JB | Ball Charger CCTV Camera Junction Box | - | - | 30 | 4PR | Cu | Cat6 SF/UTP Outdoor Cable | Black | Ladder | Enabling Works Contractor | Enabling Works Contractor | 2000-F19-DRG-EL-10101 | 19 | A | RJ45-CAT6A, Shielded (STP). Note 5 | 2
F19CP401-D1 | F19-COM-401 | Ball Charger CCTV Control Panel | F19-CP-401 | Ball Charger Rectifier Control Panel | - | - | 10 | 4PR | Cu | Cat6 SF/UTP Outdoor Cable | Black | Ladder | Enabling Works Contractor | Enabling Works Contractor | 2000-F19-DRG-EL-10101 2000-ME067-D02-10002 | 19 | A | RJ45-CAT6A, Shielded (STP). Note 5 | 2