## Equipment list
Rev | Equip. Number | Equipment Name | Qty | Description | Make | Model | Supplied By | Installed By | Comments | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred Colour) | Installation | Revision | Equipment Type | Applicable Switchroom(s) | Dimensions Height x Width x Depth (mm) | Weight (kg) | Mounting | Cable Entry | Page
0 | F21-SR-001 | CIL4 415V Switchroom | 1 | Transportable switchroom complete with 1.8m legs and landings, transported to site 600kms on sealed roads. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero | Refer 2000-F00-DSH-EL-11001 | [20 empty] | 2
0 | - | CIL4 415V Switchroom Landing & Stairs | 1 | Equipment Landing to be structural steel baseframe complete with 1.8m legs, designed to support heaviest piece of equipment to be installed in room. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero | [21 empty] | 2
0 | - | CIL4 415V MCC No.1 Transformer Enclosure Room | 1 | Separate dry transformer enclosure with removable wall panel and personnel access door Fortress key locked (Keyed alike) with 33kV feeder earth switch on F00-SW-010 33kV switchgear | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Access to transformer cubicle is only possible with 33kV Feeder isolated and earthed. Switchroom manufacturer to coordinate Fortress keys with TEKSAL. | [20 empty] | 2
0 | - | CIL4 415V MCC No.2 Transformer Enclosure Room | 1 | Separate dry transformer enclosure with removable wall panel and personnel access door Fortress key locked (Keyed alike) with 33kV feeder earth switch on F00-SW-010 33kV switchgear | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Access to transformer cubicle is only possible with 33kV Feeder isolated and earthed. Switchroom manufacturer to coordinate Fortress keys with TEKSAL. | [20 empty] | 2
0 | - | CIL4 415V MCC No.1 Transformer Enclosure Room Signage | 1 | TRANSFORMER ENCLOSURE FXX-TR-XXX 33,000/433 VOLTS (Modify to suit) DANGER – HIGH VOLTAGE (with the lightning bolt sign) NO UNAUTHORISED ACCESS – ENSURE SUPPLY IS ISOLATED AND EARTHED PRIOR TO ENTRY ISOLATE AT F00-SW-010, PANEL BXX (BXX being the 33kV panel/tier number) | Switchroom Vendor |  | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Signage to be placed on outside of transformer enclosure | [20 empty] | 2
0 | - | CIL4 415V MCC No.2 Transformer Enclosure Room Signage | 1 | TRANSFORMER ENCLOSURE FXX-TR-XXX 33,000/433 VOLTS (Modify to suit) DANGER – HIGH VOLTAGE (with the lightning bolt sign) NO UNAUTHORISED ACCESS – ENSURE SUPPLY IS ISOLATED AND EARTHED PRIOR TO ENTRY ISOLATE AT F00-SW-010, PANEL BXX (BXX being the 33kV panel/tier number) | Switchroom Vendor |  | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Signage to be placed on outside of transformer enclosure | [20 empty] | 2
0 | F21-TR-006 | CIL4 415V MCC 1 Transformer | 1 | Dry Type Transformer, 33/0.433kV, 2500kVA, AN/AF | Siemens | 33/0.433kV 2500kVA | Primero | Switchroom/MCC Vendor | Vendor to remove wheels and secure transformer once installed. Wheels to be stored securely within the transformer room. Vendor to bolt down/brace for transport. Refer transformer GAs. | [20 empty] | 2
0 | F21-TR-007 | CIL4 415V MCC 2 Transformer | 1 | Dry Type Transformer, 33/0.433kV, 2500kVA, AN/AF | Siemens | 33/0.433kV 2500kVA | Primero | Switchroom/MCC Vendor | Vendor to remove wheels and secure transformer once installed. Wheels to be stored securely within the transformer room. Vendor to bolt down/brace for transport. Refer transformer GAs. | [20 empty] | 2
0 | F21-SW-006 | CIL4 415V MCC 1 | 1 | Demountable Form 4a double sided 415V Switchboard, 4000A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom/MCC Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Vendor to install free issued network switches in MCC Refer datasheet 2000-F00-DSH-EL-11008. Complete with Mechnical interlock between Generator and Mains incomers. | [20 empty] | 2
0 | F21-SW-007 | CIL4 415V MCC 2 | 1 | Demountable Form 4a double sided 415V Switchboard, 4000A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom/MCC Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Vendor to install free issued network switches in MCC Refer datasheet 2000-F00-DSH-EL-11008. Complete with Mechnical interlock between Generator and Mains incomers. | [20 empty] | 2
Del-0 | F21-SW-106 | CIL4 Essential 415V Switchboard | 1 | Demountable Form 4a single sided 415V Essential Switchboard, 630A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Refer datasheet 2000-F00-DSH-EL-11012 | [20 empty] | 2
Del-0 | F21-SW-107 | CIL4 Emergency 415V MCC | 1 | Demountable Form 4a single sided 415V Emergency Switchboard, 960A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Refer datasheet 2000-F00-DSH-EL-11012 | [20 empty] | 2
0 | F21-DB-001 | CIL4 415V Switchroom L&SP Distribution Board | 1 | 415V 3Ø 250A DB. Fitted with incoming isolator, PE Cell circuit (night/day), Auto / Manual selector, Emergency light test controller, Rapidtest RCD test units, Lighting Contactors, air conditioner Contactors and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-EL-10025 & 2000-F00-STD-EL- 10022; Switchroom Vendor to calculate number of required poles including the number of circuits for Air conditioners, 20% loaded Spare circuit breakers and 20% spare space. | [20 empty] | 2
0 | F21-DB-201 | CIL4 415V Switchroom 240V UPS Distribution Board | 1 | 240VAC 250A UPS DB. Fitted with incoming isolator and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-EL-10027. Switchroom Vendor to calculate number of required poles including 20% loaded Spare circuit breakers and 20% spare space. | [20 empty] | 2
0 | F21-UPS-001 | CIL4 415V Switchroom 240VAC UPS | 1 | LV Switchroom 240V AC, 10kVA UPS, free-standing. 8 hours autonomy time. 3-Phase in / 1-Phase Out. | Riello | S3M 10 XTD A0 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 10kVA/10kW Sentryum Xtend UPS - 3 Phase in- 1 out. Vendor to secure wheels once installed. Vendor to bolt down/brace for transport. W: 440mm, D: 840mm, H: 1320mm, Weight: 103Kg | [20 empty] | 2
0 | F21-BA-001 | CIL4 415V Switchroom 240VAC UPS Battery Bank | 1 | UPS Battery Cabinet w/ 40 x 55Ah batteries | Riello | BB 1900 480-V5 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 480V Extension Battery Cabinet with 40 x 55Ah Long life batteries. Cabinet shipped empty with the batteries packed separately W: 860mm, D: 800mm, H: 1900mm, Weight: 900Kg | [20 empty] | 2
0 | - | CIL4 415V Switchroom 240VAC UPS Ethernet Card | 1 | Netman UPS Ethernet Card | Riello | Netman 208 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Supplied and installed into UPS by Switchroom Vendor | [20 empty] | 2
0 | - | CIL4 415V Switchroom 240VAC UPS Dry Contact Relay Card | 1 | Multicom Configurable Slot In Relay Card, 3 Inputs & 8 Outputs | Riello | Mulitcom 392 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Supplied and installed into UPS by Switchroom Vendor | [20 empty] | 2
0 | F21UPS001-ISL | CIL4 415V Switchroom 240VAC UPS Maintenance Bypass Switch | 1 | External Wall-mount UPS bypass switch. | Riello | WABS 0063A-31H | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Wall mounted rotary style bypass switch. 3Ph in/1Ph out, 10kVA. Dimensions: 400 x 300 x 210mm | [20 empty] | 3
0 | F21PP470-VS | CIL4 Loaded Carbon Pump LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
0 | F21PP471-VS | CIL4 Carbon Transfer Pump 1 LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
0 | F21PP478-VS | CIL4 Tank 1 Oxygen Injection Pump LV VSD | 1 | Allen-Bradley 250 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20- 750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G1ABC650JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
0 | F21PP491-VS | CIL4 Tank 2 Oxygen Injection Pump LV VSD | 1 | Allen-Bradley 250 kW Heavy Duty, 415VAC, IP20 Floor mount. Accessories supplied loose: , 20-HIM-C6S, , 20-750-S, 20- 750-20COMM + 20-COMM-M, 20-750-2262C-2R, 0 | Allen-Bradley | 20G1ABC650JN0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
0 | F21SA431-VS | CIL4 Tails Primary Sampler LV VSD | 1 | Allen-Bradley 2.2 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM- A6, 20-750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC8P7JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
Del-0 | F72PP681-VS | Lead Nitrate Dosing Pump 1 LV VSD | 1 | Allen-Bradley 1.5 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose. | Allen-Bradley | Frame 2 - Model TBC | Primero | Switchroom/MCC Vendor | Note 5. Stage 2 VSDs TBC. Refer free issued list for sizing. Vendor to install all loose supplied accessories | [20 empty] | 3
Del-0 | F72PP682-VS | Lead Nitrate Dosing Pump 2 LV VSD | 1 | Allen-Bradley 1.5 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose. | Allen-Bradley | Frame 2 - Model TBC | Primero | Switchroom/MCC Vendor | Note 5. Stage 2 VSDs TBC. Refer free issued list for sizing. Vendor to install all loose supplied accessories | [20 empty] | 3
Del-0 | F72FS411-VS | Lime Silo Screw Feeder LV VSD | 1 | Allen-Bradley 5.5 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose. | Allen-Bradley | Frame 3 - Model TBC | Primero | Switchroom/MCC Vendor | Note 5. Stage 2 VSDs TBC. Refer free issued list for sizing. Vendor to install all loose supplied accessories | [20 empty] | 3
Del-0 | F72PP655-VS | Slaked Lime Transfer Pump LV VSD | 1 | Allen-Bradley 11 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose. | Allen-Bradley | Frame 3 - Model TBC | Primero | Switchroom/MCC Vendor | Note 5. Stage 2 VSDs TBC. Refer free issued list for sizing. Vendor to install all loose supplied accessories | [20 empty] | 3
0 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | 1 | Communications Rack, Free Standing 19", 42U, 1000mm deep, Mesh door, Lift Off Side Panels. Fitted with 10 way 240VAC plug power distribution panel, wire management covers, shelves and cage nuts. Fitted out with FOBOTs (vendor supplied), DIN rail adapter (vendor supplied), and network switches (free issued). | Rittal | TS IT Enclosure (P/N 5514.110) + Accessories | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-IC-10101 | [20 empty] | 3
0 | F21COM001-JB | CIL4 415V Switchroom Communications Rack 240VAC UPS Junction Box | 1 | Junction box mounted on the rear of the communications rack. All 240VAC UPS powered non-RCD Protected outlets shall be red with a "Warning. Socket not RCD Protected" Warning label. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Junction box for PDU Rail | [20 empty] | 3
0 | F21-FOB-001 | CIL4 415V Switchroom Fibre Optic Breakout Tray | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | [20 empty] | 3
0 | F21-FOB-002 | CIL4 415V Switchroom Fibre Optic Breakout Tray | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | [20 empty] | 3
0 | F21-FOB-003A/B | CIL4 415V Switchroom RIO Circuit Fibre Optic Breakout Ring 1 Tray #1 (SP 2) | 1 | 2 X 12C SMOF Capacity FOBOT C/W Splice hardware & 1-6 LC Duplex Faceplate (LHS) + 1-6 LC Duplex Faceplate (RHS) | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. One FOBOT with two 12C faceplates. Vendor to label each side as per equipment number and name. | [20 empty] | 3
0 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | 1 | Custom Built Panel. Indoor, Mild Steel. Contains DCS hardware, power supply, MCBs and marshalling terminals. | Fabricated Panel | Custom | Primero | Switchroom/MCC Vendor | [21 empty] | 3
0 | F21SR001-LCS | CIL4 415V Switchroom Emergency Shutdown | 1 | Switchroom Emergency Shutdown C/w shroud or lift-up flap and labelling | Fabricated Panel | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | With E34 Red 40mm Mushroom pushbutton (P/N E34LB2), and 4 off 2 N/O Contact Blocks (10250T2). Refer 2000-F00-STS-EL-10011 Section 4.19. | [20 empty] | 3
0 | F21-FIP-001 | CIL4 415V Switchroom Fire Indicator Panel | 1 | Fire Indicator Panel c/w full installation, wiring, certification, testing and commissioning. HVAC trip upon alarm. FIP shall include SMOF modem(s) for connection to site-wide fire system network. | Wormald | Vigilant 8 Zone F3200 Conventional SHCIE FIP | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Rated to operate in 50C ambience temperature | [20 empty] | 3
0 | F21FIP001-XE1 | CIL4 415V Switchroom VESDA Panel | 1 | VESDA Panel c/w full installation, wiring, certification, testing and commissioning.Alarm and fault signals to fire panel. | Xtralis | VESDA LaserPlus Scanner 12 relay VLS300 ASD system | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Rated to operate in 50C ambience temperature | [20 empty] | 3
0 | F21FIP001-XE2 | CIL4 415V Switchroom Manual Call Points | VTA | Fire system Manual Call points (internal and external) as required by Australian Standards | Wormald | Manual Call Points | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Manual call points shall be tagged in sequential order | [20 empty] | 3
0 | F21FIP001-XE3 | CIL4 415V Switchroom Smoke Detector | VTA | Fire system smoke detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order | [20 empty] | 3
0 | F21FIP001-XE4 | CIL4 415V Switchroom Heat Detector | VTA | Fire system heat detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order | [20 empty] | 3
0 | F21FIP001-UA | CIL4 415V Switchroom External Alarm Bells | VTA | Fire system alarm bells as required by Australian Standards | Wormald | External Sounder / Red Strobe | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Alarm sirens shall be tagged in sequential order | [20 empty] | 3
0 | F21FIP001-XE5 | CIL4 415V Switchroom Gas Suppression System (Inergen) | 1 | Inergen gas suppression system incl. all valves and pipework, gas cylinders placed inside switchroom, refer to Switchroom General Arrangement | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 3
0 | - | CIL4 415V Switchroom Fire Extinguishers | VTA | 5kg dry powder fire extinguishers complete with wall mount and signage. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 3
0 | - | CIL4 415V Switchroom Automatic External Defibrillator | 1 | Automatic external defibrillator complete with wall-mounted cabinet. | Physio Control | Lifepak Defibrillator CR2 Fully Automatic | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 3
0 | - | CIL4 415V Switchroom LV Rescue Kit | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 3
0 | - | CIL4 415V Switchroom CPR Signage | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 3
0 | - | CIL4 415V Switchroom HVAC Controller | 1 | Wall mounted Air Conditioner Controller, with relay contacts for Faulty & Healthy | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | One wall mounted controller to control all A/C's per room (One per transformer room, LV room, HV room). | [20 empty] | 4
0 | F21-AC-0XX | CIL4 415V Switchroom Air Conditioners | VTA | High Wall split system, single phase, MULTIPLE (N+1 reqd) with drip trays if necessary | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. AC units shall be tagged in Numerical Order eg. F21-AC-001, F21-AC-002 etc | [20 empty] | 4
0 | F21AC0XX-ISL | CIL4 415V Switchroom Air Conditioner Isolators | VTA | Field isolator, one per split system AC | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Isolators shall be tagged with the respective AC equipment number (e.g. F21AC0xx- ISL etc) | [20 empty] | 4
0 | - | CIL4 415V Switchroom Normal Light Fittings | 1 lot | Lighting to meet National Construction Code | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | [20 empty] | 4
0 | - | CIL4 415V Switchroom Emergency Light Fittings | 1 lot | Lighting to meet National Construction Code; C/w built in battery pack. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | [20 empty] | 4
0 | - | CIL4 415V Switchroom Exit Light Fittings | 1 lot | Lighting to meet National Construction Code | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | [20 empty] | 4
0 | UT21016 | F21-SR-001 CIL4 415V Switchroom 415V Switchroom Temperature/Humidity Transmitter | 1 | 415V Switchroom Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | [20 empty] | 4
0 | UT21017 | F21-SR-001 CIL4 415V Switchroom 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | 1 | Transformer Room Temperature/Humidity Transmitter (F21-TR-006) | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | [20 empty] | 4
0 | UT21018 | F21-SR-001 CIL4 415V Switchroom 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | 1 | Transformer Room Temperature/Humidity Transmitter (F21-TR-007) | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | [20 empty] | 4
0 | F21-PE-001 | CIL4 415V Switchroom Photo-electric Cell | 1 | Switchroom Photo-electric cell | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | PE Cell - 1 per building. Vendor to position | [20 empty] | 4
0 | F21SW006-LCS01 | CIL4 415V MCC 1 Mains Incomer Remote Switching Panel | 1 | LV MCC Incomer Remote Switching Panel | NHP | TemRack LCS | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 4
0 | F21SW006-LCS02 | CIL4 415V MCC 1 Generator Incomer Remote Switching Panel | 1 | LV MCC Generator Incomer Remote Switching Panel | NHP | TemRack LCS | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 4
0 | F21SW007-LCS01 | CIL4 415V MCC 2 Mains Incomer Remote Switching Panel | 1 | LV MCC Incomer Remote Switching Panel | NHP | TemRack LCS | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 4
0 | F21SW007-LCS02 | CIL4 415V MCC 2 Generator Incomer Remote Switching Panel | 1 | LV MCC Generator Incomer Remote Switching Panel | NHP | TemRack LCS | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 4
0 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | 1 | External to Room: 50 x 6.3mm Tinned Flat Copper Bus bar mounted on insulated standoffs under switchroom floor. Drilled/punch 12mm diameter holes suitable for connection of all internal equipment earth cables to meet requirements of cable schedule. To have spare capacity for connection of an additional 4 x 120mm2 conductors and 4 x 70mm2 conductors, as a minimum. | GVK or similar |  | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 4
0 | F21TR006-EB01 | CIL4 LV MCC 1 Transformer Earth Bar | 1 | 50 x 6.3mm Tinned Flat Copper Bus bar mounted on standoffs on the Transformer. | Generic |  | Transformer Vendor | Transformer Vendor | [21 empty] | 4
0 | F21TR007-EB01 | CIL4 LV MCC 2 Transformer Earth Bar | 1 | 50 x 6.3mm Tinned Flat Copper Bus bar mounted on standoffs on the Transformer. | Generic |  | Transformer Vendor | Transformer Vendor | [21 empty] | 4
0 | F21SW006-EB01 | CIL4 415V MCC 1 Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on standoffs inside MCC. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 4
0 | F21SW007-EB01 | CIL4 415V MCC 1 Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on standoffs inside MCC. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 4
Del-0 | F21SW106-EB01 | CIL4 Essential 415V Switchboard Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on standoffs inside MCC. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 4
Del-0 | F21SW107-EB01 | CIL4 Emergency 415V MCC Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on standoffs inside MCC. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 4
[7 empty] | Switchroom Vendor | Switchroom Vendor | Earth bonding conductors shall be equal to the larger of 16mm2 or equipment phase conductor size, but no greater than 120mm2. | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | Multiple | Each UPS, DB, switching panel, or other electrical panels. | CIL4 LV Switchroom | Note 6. | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 0 | [6 empty] | 9
[7 empty] | Switchroom Vendor | Switchroom Vendor | Ladder to be bonded to earth bar in two places and bonded across each fish plate. | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom |  | Subfloor cable ladder. | CIL4 LV Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 0 | [6 empty] | 9
[7 empty] | Switchroom Vendor | Switchroom Vendor | Switchroom subframe to be bonded to switchroom earth bar. Earth bonds to be at two opposing corners. | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom |  | Switchroom subframe. | CIL4 LV Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 0 | [6 empty] | 9
[5 empty] | Allen-Bradley | Frame 2 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 1.5kW | 415V Switchrooms | 500 x 134 x 212 | 8 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 2 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 4kW | 415V Switchrooms | 500 x 134 x 212 | 8 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 2 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 5.5kW | 415V Switchrooms | 500 x 134 x 212 | 8 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 2 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 7.5kW | 415V Switchrooms | 500 x 134 x 212 | 8 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 3 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 11kW | 415V Switchrooms | 531 x 190 x 223.1 | 11 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 3 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 15kW | 415V Switchrooms | 531 x 190 x 223.1 | 11 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 4 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 30kW | 415V Switchrooms | 565.2 x 222 x 222.7 | 16 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 5 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 37kW | 415V Switchrooms | 666.1 x 270 x 222.7 | 24 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 5 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 45kW | 415V Switchrooms | 666.1 x 270 x 222.7 | 24 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 5 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 45kW AFE | 415V Switchrooms | 1127 x 334 x 357 | 125 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 6 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 55kW | 415V Switchrooms | 945.1 x 308 x 346.7 | 39 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 6 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 55kW AFE | 415V Switchrooms | 1876 x 405 x 432 | 145 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 6 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 75kW | 415V Switchrooms | 945.1 x 308 x 346.7 | 39 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 6 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 90kW | 415V Switchrooms | 945.1 x 308 x 346.7 | 39 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 7 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 132kW | 415V Switchrooms | 1271 x 430 x 561 | 106 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 8 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 250kW | 415V Switchrooms | 2453 x 600 x 600 | 644 | Floor Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 8 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 250kW AFE | 415V Switchrooms | 2132 x 1200 x 676 | 900 | Floor Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 8 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 315kW | 415V Switchrooms | 2453 x 600 x 600 | 644 | Floor Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 8 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 355kW | 415V Switchrooms | 2453 x 600 x 600 | 644 | Floor Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 9 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 500kW | 415V Switchrooms | 2453 x 1200 x 600 | 1287 | Floor Mount | Bottom Entry | 10
[5 empty] | Fabricated Panel | Custom | Primero | Switchroom Vendor | Top entry for communication wiring, bottom entry for power and control. | [14 empty] | Switchroom DCS Panel | 415V Switchrooms | 2000x800x400 | 400kg est. | Floor Mount | Top & Bottom Entry | 10
[5 empty] | Fabricated Panel | Custom | Primero | Switchroom Vendor | Top entry for communication wiring, bottom entry for power and control. | [14 empty] | Switchroom Remote I/O Panel | F00-SR-001, F16-SR-001 | 2000x800x400 | 400kg est. | Floor Mount | Top & Bottom Entry | 10
[5 empty] | Siemens | 11/0.433kV 2500kVA | Primero | Switchroom Vendor | Installed on rails to roll transformer in/out. Refer 2000-EL004-B02- 10001 | [14 empty] | 415V Transformer 11/0.433kV 2500kVA | F12-SR-002 | 1968 x 1280 x 2400 | 5100 | Floor Mount | Bottom Entry | 10
[5 empty] | Siemens | 33/0.433kV 2500kVA | Primero | Switchroom Vendor | Installed on rails to roll transformer in/out. Refer 2000-EL004-B02- 10001 | [14 empty] | 415V Transformer 33/0.433kV 2500kVA | 415V Switchrooms | 2248 x 1280 x 2760 | 6300 | Floor Mount | Bottom Entry | 10
[5 empty] | Siemens | 11/0.433kV 630kVA | Primero | Switchroom Vendor | Installed on rails to roll transformer in/out. Refer 2000-EL004-B02- 10001 | [14 empty] | 415V Transformer 11/0.433kV 630kVA | F16-SR-002 | 1408 x 820 x 1850 | 1950 | Floor Mount | Bottom Entry | 10
[5 empty] | Siemens | 33/0.433kV 1000kVA | Primero | Switchroom Vendor | Installed on rails to roll transformer in/out. Refer 2000-EL004-B02- 10001 | [14 empty] | 415V Transformer 33/0.433kV 1000kVA | F23-SR-002, F28-SR-002 | 1828 x 990 x 2350 | 3420 | Floor Mount | Bottom Entry | 10
[5 empty] | ABB | ZX2 | Primero | Switchroom Vendor | HV Cables - Bottom Entry 48VDC/Control/Comms - Bottom Entry | [14 empty] | 33kV Switchboard Incomer Panel | F00-SR-001 | 800mm W x 1860mm D x 2600mm H | 2000 | Floor Mount | Bottom & Top Entry | 10
[5 empty] | ABB | ZX2 | Primero | Switchroom Vendor | HV Cables - Bottom Entry 48VDC/Control/Comms - Bottom Entry | [14 empty] | 33kV Switchboard Feeder Panel | F00-SR-001 | 600mm W x 1860mm D x 2600mm H | 1400 | Floor Mount | Bottom & Top Entry | 10
[5 empty] | ABB | ZX2 | Primero | Switchroom Vendor | HV Cables - Bottom Entry 48VDC/Control/Comms - Bottom Entry | [14 empty] | 33kV Switchboard Bus Tie Panel | F00-SR-001 | 800mm W x 1860mm D x 2600mm H | 2400 | Floor Mount | Bottom & Top Entry | 10
[5 empty] | ABB | ZS1 | Primero | Switchroom Vendor | HV Cables - Bottom Entry 48VDC/Control/Comms - Bottom Entry | [14 empty] | 11kV Switchboard Incomer Panel | 11kV Switchrooms | 650mm W x 1340mm D x 2533mm H | 850 | Floor Mount | Bottom & Top Entry | 10
[5 empty] | ABB | ZS1 | Primero | Switchroom Vendor | HV Cables - Bottom Entry 48VDC/Control/Comms - Bottom Entry | [14 empty] | 11kV Switchboard Feeder Panel | 11kV Switchrooms | 650mm W x 1340mm D x 2533mm H | 850 | Floor Mount | Bottom & Top Entry | 10
[5 empty] | ABB | ZS1 | Primero | Switchroom Vendor | HV Cables - Bottom Entry 48VDC/Control/Comms - Bottom Entry | [14 empty] | 11kV Switchboard VT Panel | 11kV Switchrooms | 650mm W x 1340mm D x 2533mm H | 850 | Floor Mount | Bottom & Top Entry | 10
[5 empty] | Siemens | SINAMICS Pefect Harmony GH180 6SR55020NE380BH0-Z | Primero | Switchroom Vendor | [15 empty] | 800kVA, 200A HV VSD (Heavy Duty) | F16-SR-001, F23-SR-001 | H=2223mm, W=2905mm, D=1143mm | 3100 | Floor Mount | Bottom Entry | 10
[5 empty] | Siemens | SINAMICS Pefect Harmony GH180 6SR55020NF412BH0-Z | Primero | Switchroom Vendor | [15 empty] | 1250kVA, 260A HV VSD (Heavy Duty) | F16-SR-001, F23-SR-001 | H=2223mm, W=2905mm, D=1143mm | 4950 | Floor Mount | Bottom Entry | 10
[5 empty] | Siemens | SINAMICS Pefect Harmony GH180 6SR55020NG412BH0-Z | Primero | Switchroom Vendor | [15 empty] | 1250kVA, 340A HV VSD (Heavy Duty) | F12-SR-001 | H=2380mm, W=3400mm, D=1230mm | 4141.6 | Floor Mount | Bottom Entry | 10

## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred Colour) | Installation | Supplied By | Installed By | Revision | Comments | Page
F21SW006-P1-R | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-P1-W | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-P1-B | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-P2-R | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-P2-W | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-P2-B | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-P3-R | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-P3-W | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-P3-B | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-P4-R | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-P4-W | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-P4-B | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-N-1 | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-N-2 | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-N-3 | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW006-N-4 | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-P1-R | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-P1-W | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-P1-B | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-P2-R | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-P2-W | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-P2-B | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-P3-R | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-P3-W | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-P3-B | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-P4-R | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-P4-W | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-P4-B | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-N-1 | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-N-2 | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-N-3 | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW007-N-4 | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 500 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21SW106-P3 | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | F21-SW-106 | CIL4 Essential 415V Switchboard | CIL4 LV Switchroom | 120 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 5
F21SW107-P1-R | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 5
F21SW107-P1-W | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 5
F21SW107-P1-B | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 5
F21SW107-P2-R | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 5
F21SW107-P2-W | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 5
F21SW107-P2-B | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 5
F21SW107-N-1 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 5
F21SW107-N-2 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 5
F21PP470VS-P1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21PP470-VS | CIL4 Loaded Carbon Pump LV VSD | CIL4 LV Switchroom | 50 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F21PP471VS-P1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21PP471-VS | CIL4 Carbon Transfer Pump 1 LV VSD | CIL4 LV Switchroom | 50 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Was P2 | 6
F21PP478VS-P1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21PP478-VS | CIL4 Tank 1 Oxygen Injection Pump LV VSD | CIL4 LV Switchroom | 150 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Was 120, upsized due to pump size increase | 6
F21PP478VS-P2 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21PP478-VS | CIL4 Tank 1 Oxygen Injection Pump LV VSD | CIL4 LV Switchroom | 150 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Was 120, upsized due to pump size increase | 6
F21PP491VS-P1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21PP491-VS | CIL4 Tank 2 Oxygen Injection Pump LV VSD | CIL4 LV Switchroom | 150 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Was 120, upsized due to pump size increase | 6
F21PP491VS-P2 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21PP491-VS | CIL4 Tank 2 Oxygen Injection Pump LV VSD | CIL4 LV Switchroom | 150 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Was 120, upsized due to pump size increase | 6
F21SA431VS-P1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21SA431-VS | CIL4 Tails Primary Sampler LV VSD | CIL4 LV Switchroom | 4 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Cable added as F21-SA-431 is now supplied from a VSD | 6
F72FS411VS-P1 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F72FS411-VS | Lime Silo Screw Feeder LV VSD | CIL4 LV Switchroom | 6 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 6
F72PP655VS-P1 | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | F72PP655-VS | Slaked Lime Transfer Pump LV VSD | CIL4 LV Switchroom | 10 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 6
F72PP681VS-P1 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F72PP681-VS | Lead Nitrate Dosing Pump 1 LV VSD | CIL4 LV Switchroom | 6 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 6
F72PP682VS-P1 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F72PP682-VS | Lead Nitrate Dosing Pump 2 LV VSD | CIL4 LV Switchroom | 6 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 6
F21DB001-P1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21-DB-001 | CIL4 415V SWITCHROOM L&SP DISTRIBUTION BOARD | CIL4 LV Switchroom | 150 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Flexible cable. Was 95 | 6
F21UPS001ISL-P1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21UPS001-ISL | CIL4 415V SWITCHROOM 240VAC UPS MAINTENANCE BYPASS SWITCH | CIL4 LV Switchroom | 16 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC to Bypass Switch. Was 10mm2 | 6
F21UPS001-P1 | F21UPS001-ISL | CIL4 415V Switchroom 240VAC UPS Maintenance Bypass Switch | CIL4 LV Switchroom | F21-UPS-001 | CIL4 415V SWITCHROOM 240VAC UPS | CIL4 LV Switchroom | 10 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Bypass Switch to UPS. Was 16mm2 | 6
F21UPS001ISL-P2 | F21-UPS-001 | CIL4 415V Switchroom 240VAC UPS | CIL4 LV Switchroom | F21UPS001-ISL | CIL4 415V SWITCHROOM 240VAC UPS MAINTENANCE BYPASS SWITCH | CIL4 LV Switchroom | 10 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | UPS to Bypass Switch | 6
F21DB201-P1 | F21UPS001-ISL | CIL4 415V Switchroom 240VAC UPS Maintenance Bypass Switch | CIL4 LV Switchroom | F21-DB-201 | CIL4 415V SWITCHROOM 240V UPS DISTRIBUTION BOARD | CIL4 LV Switchroom | 50 | 0.6/1 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | TBC cabling between UPS and battery. | 6
F21BA001-P1 | F21-UPS-001 | CIL4 415V Switchroom 240VAC UPS | CIL4 LV Switchroom | F21-BA-001 | CIL4 415V SWITCHROOM 240VAC UPS BATTERY BANK | CIL4 LV Switchroom | 16 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Bypass Switch to UPS DB | 6
F21FIP001-P1 | F21-DB-001 | CIL4 415V Switchroom L&SP Distribution Board | CIL4 LV Switchroom | F21-FIP-001 | CIL4 415V Switchroom Fire Indicator Panel | CIL4 LV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F21FIP001XE1-P1 | F21-FIP-001 | CIL4 415V Switchroom Fire Indicator Panel | CIL4 LV Switchroom | F21FIP001-XE1 | CIL4 415V Switchroom VESDA Panel | CIL4 LV Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F21TR006-P1 | F21-DB-001 | CIL4 415V Switchroom L&SP Distribution Board | CIL4 LV Switchroom | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 240V for transformer cooling fans | 6
F21TR007-P1 | F21-DB-001 | CIL4 415V Switchroom L&SP Distribution Board | CIL4 LV Switchroom | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 240V for transformer cooling fans | 6
F21SW006-P5 | F21-DB-201 | CIL4 415V Switchroom 240V UPS Distribution Board | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 4 | 0.6/1 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC PSU 1 | 6
F21SW006-P6 | F21-DB-201 | CIL4 415V Switchroom 240V UPS Distribution Board | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 4 | 0.6/1 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC PSU 2 | 6
F21SW007-P5 | F21-DB-201 | CIL4 415V Switchroom 240V UPS Distribution Board | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 4 | 0.6/1 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC PSU 1 | 6
F21SW007-P6 | F21-DB-201 | CIL4 415V Switchroom 240V UPS Distribution Board | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 4 | 0.6/1 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC PSU 2 | 6
F21SW106-P5 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21-SW-106 | CIL4 Essential 415V Switchboard | CIL4 LV Switchroom | 10 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 | 24VDC Supply to Essential Board | 6
F21SW107-P6 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | 10 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 | 24VDC Supply to Essential Board | 6
F21DCS411-P1 | F21-DB-201 | CIL4 415V Switchroom 240V UPS Distribution Board | CIL4 LV Switchroom | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F21COM001-P1 | F21-DB-201 | CIL4 415V Switchroom 240V UPS Distribution Board | CIL4 LV Switchroom | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F21SW006-C1 | F21SR001-LCS | CIL4 415V Switchroom Emergency Shutdown | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Emerg/ Shutdown Circuit. E-stop to trip incomer | 6
F21SW007-C1 | F21SR001-LCS | CIL4 415V Switchroom Emergency Shutdown | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Emerg/ Shutdown Circuit. E-stop to trip incomer | 6
F21SW106-C1 | F21SR001-LCS | CIL4 415V Switchroom Emergency Shutdown | CIL4 LV Switchroom | F21-SW-106 | CIL4 Essential 415V Switchboard | CIL4 LV Switchroom | 1.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 | Emerg/ Shutdown Circuit. E-stop to trip incomer | 6
F21SW107-C1 | F21SR001-LCS | CIL4 415V Switchroom Emergency Shutdown | CIL4 LV Switchroom | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | 1.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 | Emerg/ Shutdown Circuit. E-stop to trip incomer | 6
F21TR006-C1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Transformer Signals to MCC | 6
F21TR007-C1 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Transformer Signals to MCC | 6
F21PP470VS-C1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21PP470-VS | CIL4 Loaded Carbon Pump LV VSD | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F21PP471VS-C1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21PP471-VS | CIL4 Carbon Transfer Pump 1 LV VSD | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F21PP478VS-C1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21PP478-VS | CIL4 Tank 1 Oxygen Injection Pump LV VSD | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F21PP491VS-C1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21PP491-VS | CIL4 Tank 2 Oxygen Injection Pump LV VSD | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F21SA431VS-C1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21SA431-VS | CIL4 Tails Primary Sampler LV VSD | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Cable added as F21-SA-431 is now supplied from a VSD | 6
F72PP681VS-C1 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F72PP681-VS | Lead Nitrate Dosing Pump 1 LV VSD | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 7
F72PP682VS-C1 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F72PP682-VS | Lead Nitrate Dosing Pump 2 LV VSD | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 7
F72FS411VS-C1 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F72FS411-VS | Lime Silo Screw Feeder LV VSD | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 7
F72PP655VS-C1 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F72PP655-VS | Slaked Lime Transfer Pump LV VSD | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 7
F21SW006-C2 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | Mains Incomer | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Incomer Signals to DCS | 7
F21SW006-C6 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | Generator Incomer | 1.5 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Incomer Signals to DCS. Generator Incomer signals | 7
F21SW007-C2 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | Mains Incomer | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Incomer Signals to DCS | 7
F21SW007-C6 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | Generator Incomer | 1.5 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Incomer Signals to DCS. Generator Incomer signals | 7
F21SW106-C2 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | F21-SW-106 | CIL4 Essential 415V Switchboard | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 | MCC Incomer Signals to DCS | 7
F21SW107-C2 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | DEL-0 | MCC Incomer Signals to DCS | 7
F21DB001-C1 | F21-FIP-001 | CIL4 415V Switchroom Fire Indicator Panel | CIL4 LV Switchroom | F21-DB-001 | CIL4 415V Switchroom L&SP Distribution Board | CIL4 LV Switchroom | 1.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder | Switchroom Vendor | Switchroom Vendor | 0 | HVAC trip. | 7
F21FIP001-C1 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | F21-FIP-001 | CIL4 415V Switchroom Fire Indicator Panel | CIL4 LV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F21DCS411-C2 | - | - | CIL4 LV Switchroom | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Healthy/Fault feedback from wall mounted A/C Controller | 7
UT21016-I1 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | UT21016 | F21-SR-001 CIL4 415V Switchroom 415V Switchroom Temperature/Humidity Transmitter | CIL4 LV Switchroom | 1.5 | 0.15 | 2pr | Cu | PVC/OS/PVC | Black | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
UT21017-I1 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | UT21017 | F21-SR-001 CIL4 415V Switchroom 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | CIL4 LV Switchroom | 1.5 | 0.15 | 2pr | Cu | PVC/OS/PVC | Black | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
UT21018-I1 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | UT21018 | F21-SR-001 CIL4 415V Switchroom 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | CIL4 LV Switchroom | 1.5 | 0.15 | 2pr | Cu | PVC/OS/PVC | Black | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F21DB001-C2 | F21-PE-001 | CIL4 415V Switchroom Photo-electric Cell | CIL4 LV Switchroom | F21-DB-001 | CIL4 415V Switchroom L&SP Distribution Board | CIL4 LV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Lighting Control. Direct from PE | 7
F21UPS001-C1 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | F21-UPS-001 | CIL4 415V Switchroom 240VAC UPS | CIL4 LV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | UPS Feedback allowance | 7
F21UPS001-C2 | F21UPS001-ISl | CIL4 415V Switchroom 240VAC UPS Maintenance Bypass Switch | CIL4 LV Switchroom | F21-UPS-001 | CIL4 415V Switchroom 240VAC UPS | CIL4 LV Switchroom | 1.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | By pass | 7
F21SR001LCS-C1 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | F21SR001-LCS | CIL4 415V Switchroom Emergency Shutdown | CIL4 LV Switchroom | 2.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
ZSC21019-C2 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | ZSC21019 | F21-TR-006 CIL4 415V MCC 1 Transformer Enclosure Door Position Switch Closed | CIL4 LV Switchroom | 1.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
ZSC21020-C2 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | ZSC21020 | F21-TR-007 CIL4 415V MCC 2 Transformer Enclosure Door Position Switch Closed | CIL4 LV Switchroom | 1.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F21SW006LCS01-C1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21SW006-LCS01 | CIL4 415V MCC 1 Mains Incomer Remote Switching Panel | CIL4 LV Switchroom | 1.5 | 0.6/1 | 20C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F21SW006LCS02-C1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21SW006-LCS02 | CIL4 415V MCC 1 Generator Incomer Remote Switching Panel | CIL4 LV Switchroom | 1.5 | 0.6/1 | 20C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F21SW007LCS01-C1 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F21SW007-LCS01 | CIL4 415V MCC 2 Mains Incomer Remote Switching Panel | CIL4 LV Switchroom | 1.5 | 0.6/1 | 20C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F21SW007LCS02-C1 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F21SW007-LCS02 | CIL4 415V MCC 2 Generator Incomer Remote Switching Panel | CIL4 LV Switchroom | 1.5 | 0.6/1 | 20C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F21SW006-C5 | F21-TR-006 | CIL4 415V MCC 1 Transformer | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 6 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | AFD CT Cable | 7
F21SW007-C5 | F21-TR-007 | CIL4 415V MCC 2 Transformer | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 6 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | AFD CT Cable | 7
F21SW006-C3 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 24VDC PSU monitoring | 7
F21SW006-C4 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 24VDC PSU monitoring | 7
F21SW007-C3 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 24VDC PSU monitoring | 7
F21SW007-C4 | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 24VDC PSU monitoring | 7
F21FIP001-FO1 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-FIP-001 | CIL4 415V Switchroom Fire Indicator Panel | CIL4 LV Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Site-Wide Fire network - patch to FIP. | 7
F21FIP001-F02 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-FIP-001 | CIL4 415V Switchroom Fire Indicator Panel | CIL4 LV Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Site-Wide Fire network - patch to FIP. | 7
F21UPS001-D1 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-UPS-001 | CIL4 415V Switchroom 240VAC UPS | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F21SW106-D1 | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | F21-SW-106 | CIL4 Essential 415V Switchboard | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | DEL-0 | VAMP CAN Bus Cable. | 7
F21SW106-D2 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-SW-106 | CIL4 Essential 415V Switchboard | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | DEL-0 | Ethernet allowance | 7
F21SW107-D1 | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | DEL-0 | VAMP CAN Bus Cable. | 7
F21SW107-D2 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-SW-107 | CIL4 Emergency 415V MCC | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | DEL-0 | Ethernet allowance | 8
F21PP470VS-D1 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21PP470-VS | CIL4 Loaded Carbon Pump LV VSD | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F21PP471VS-D1 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21PP471-VS | CIL4 Carbon Transfer Pump 1 LV VSD | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F21PP478VS-D1 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21PP478-VS | CIL4 Tank 1 Oxygen Injection Pump LV VSD | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F21PP491VS-D1 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21PP491-VS | CIL4 Tank 2 Oxygen Injection Pump LV VSD | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F21SA431VS-D1 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21SA431-VS | CIL4 Tails Primary Sampler LV VSD | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72FS411VS-D1 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F72FS411-VS | Lime Silo Screw Feeder LV VSD | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 8
F72PP655VS-D1 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F72PP655-VS | Slaked Lime Transfer Pump LV VSD | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 8
F72PP681VS-D1 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F72PP681-VS | Lead Nitrate Dosing Pump 1 LV VSD | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 8
F72PP682VS-D1 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F72PP682-VS | Lead Nitrate Dosing Pump 2 LV VSD | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 8
F21SW006-D11 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Connected to local MCC ethernet switches | 8
F21SW006-D12 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Connected to local MCC ethernet switches | 8
F21SW006-D13 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Connected to local MCC ethernet switches | 8
F21SW006-D14 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Connected to local MCC ethernet switches | 8
F21SW006-D15 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-SW-006 | CIL4 415V MCC 1 | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Connected to local MCC ethernet switches | 8
F21SW007-D11 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Connected to local MCC ethernet switches | 8
F21SW007-D12 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Connected to local MCC ethernet switches | 8
F21SW007-D13 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Connected to local MCC ethernet switches | 8
F21SW007-D14 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Connected to local MCC ethernet switches | 8
F21SW007-D15 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-SW-007 | CIL4 415V MCC 2 | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Connected to local MCC ethernet switches | 8
F21DCS411-D1 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Orange | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 1 PRIMARY | 8
F21DCS411-D2 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Orange | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 1 SECONDARY | 8
F21DCS411-D3 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Purple | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 2 PRIMARY | 8
F21DCS411-D4 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Purple | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 2 SECONDARY | 8
F21DCS411-D5 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - ALE CARD (AS REQUIRED) | 8
F21DCS411-D6 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - ALE CARD (AS REQUIRED) | 8
F21DCS411-D7 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Orange | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - ALE CARD (AS REQUIRED) | 8
F21DCS411-F01 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED). | 8
F21DCS411-F02 | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | F21-DCS-411 | CIL4 415V Switchroom DCS Panel | CIL4 LV Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED). | 8
F21COM001-FOx | F21-COM-001 | CIL4 415V Switchroom Communications Rack | CIL4 LV Switchroom | Multiple | Misc SMOF Patch leads in Panel | CIL4 LV Switchroom | N/A | N/A | 2C |  | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | 1 lot; Qty TBC | 8
F21TR006EB01-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21TR006-EB01 | CIL4 LV MCC 1 Transformer Earth Bar | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F21TR006EB01-E2 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21TR006-EB01 | CIL4 LV MCC 1 Transformer Earth Bar | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F21TR007EB01-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21TR007-EB01 | CIL4 LV MCC 2 Transformer Earth Bar | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F21TR007EB01-E2 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21TR007-EB01 | CIL4 LV MCC 2 Transformer Earth Bar | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F21SW006EB01-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21SW006-EB01 | CIL4 415V MCC 1 Earth Bar | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F21SW006EB01-E2 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21SW006-EB01 | CIL4 415V MCC 1 Earth Bar | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F21SW007EB01-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21SW007-EB01 | CIL4 415V MCC 1 Earth Bar | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F21SW007EB01-E2 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21SW007-EB01 | CIL4 415V MCC 1 Earth Bar | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F21SW106EB01-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21SW106-EB01 | CIL4 Essential 415V Switchboard Earth Bar | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 8
F21SW106EB01-E2 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21SW106-EB01 | CIL4 Essential 415V Switchboard Earth Bar | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 8
F21SW107EB01-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21SW107-EB01 | CIL4 Emergency 415V MCC Earth Bar | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 9
F21SW107EB01-E2 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21SW107-EB01 | CIL4 Emergency 415V MCC Earth Bar | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 9
F21PP470VS-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21PP470-VS | CIL4 Loaded Carbon Pump LV VSD | CIL4 LV Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F21PP471VS-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21PP471-VS | CIL4 Carbon Transfer Pump 1 LV VSD | CIL4 LV Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F21PP478VS-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21PP478-VS | CIL4 Tank 1 Oxygen Injection Pump LV VSD | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F21PP491VS-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21PP491-VS | CIL4 Tank 2 Oxygen Injection Pump LV VSD | CIL4 LV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F21SA431VS-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F21SA431-VS | CIL4 Tails Primary Sampler LV VSD | CIL4 LV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F72FS411VS-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F72FS411-VS | Lime Silo Screw Feeder LV VSD | CIL4 LV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 9
F72PP655VS-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F72PP655-VS | Slaked Lime Transfer Pump LV VSD | CIL4 LV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 9
F72PP681VS-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F72PP681-VS | Lead Nitrate Dosing Pump 1 LV VSD | CIL4 LV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 9
F72PP682VS-E1 | F21SR001-EB01 | CIL4 415V Switchroom Earth Bar | CIL4 LV Switchroom | F72PP682-VS | Lead Nitrate Dosing Pump 2 LV VSD | CIL4 LV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | DEL-0 |  | 9