## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | Length (m) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred colour) | Installation Method | Supplied By | Installed By | Reference Drawing (SLD/SCM/TER) | Area | Rev | Comments | Page
F22SW131-P3 | F22-GE-131 | CARBON TREATMENT AND ELUTION EMERGENCY SUPPLY 415V GENERATOR | CARBON REGEN & ELUTION 415V GENERATOR | F22-SW-131 | CARBON TREATMENT AND ELUTION EMERGENCY 415V MCC | CARBON REGEN & ELUTION SWITCHROOM | 150 | 0.6/1 | 40 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SLD-EL-10261 | 220 | 0 |  | 2
F22SW131-P4 | F22-GE-131 | CARBON TREATMENT AND ELUTION EMERGENCY SUPPLY 415V GENERATOR | CARBON REGEN & ELUTION 415V GENERATOR | F22-SW-131 | CARBON TREATMENT AND ELUTION EMERGENCY 415V MCC | CARBON REGEN & ELUTION SWITCHROOM | 150 | 0.6/1 | 40 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SLD-EL-10261 | 220 | 0 |  | 2
F22GE131CP-P1 | F22-DB-001 | CARBON TREATMENT AND ELUTION 415V SWITCHROOM L&SP DISTRIBUTION BOARD | CARBON REGEN & ELUTION SWITCHROOM | F22GE131-CP | CARBON TREATMENT AND ELUTION EMERGENCY SUPPLY 415V GENERATOR CONTROL PANEL | CARBON REGEN & ELUTION 415V GENERATOR | 2.5 | 0.6/1 | 50 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-TLD-EL-10051 | 220 | 0 | Genset Battery Charger | 2
F22GE131CP-C1 | F22-DCS-412 | CARBON TREATMENT AND ELUTION 415V SWITCHROOM DCS PANEL | CARBON REGEN & ELUTION SWITCHROOM | F22GE131-CP | CARBON TREATMENT AND ELUTION EMERGENCY SUPPLY 415V GENERATOR CONTROL PANEL | CARBON REGEN & ELUTION 415V GENERATOR | 1.5 | 0.6/1 | 50 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-TER-IC-10013 | 220 | 0 | Generator Feedback to DCS | 2
F22GE131CP-C2 | F22-SW-131 | CARBON TREATMENT AND ELUTION EMERGENCY 415V MCC | CARBON REGEN & ELUTION SWITCHROOM | F22GE131-CP | CARBON TREATMENT AND ELUTION EMERGENCY SUPPLY 415V GENERATOR CONTROL PANEL | CARBON REGEN & ELUTION 415V GENERATOR | 1.5 | 0.6/1 | 50 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-SCM-EL-10272 | 220 | 0 | Generator Signals to MCC | 2
F22GE131CP-D1 | F22-COM-001 | CARBON TREATMENT AND ELUTION 415V SWITCHROOM COMMUNICATIONS RACK | CARBON REGEN & ELUTION SWITCHROOM | F22GE131-CP | CARBON TREATMENT AND ELUTION EMERGENCY SUPPLY 415V GENERATOR CONTROL PANEL | CARBON REGEN & ELUTION 415V GENERATOR | N/A | N/A | 50 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-TER-IC-10003 | 220 | 0 | Generator to Comms | 2
F22RIO001-P1 | F22-DB-201 | CARBON TREATMENT AND ELUTION 415V SWITCHROOM 240V UPS DISTRIBUTION BOARD | CARBON REGEN AND ELUTION SWITCHROOM | F22-RIO-001 | ELUTION FIELD N-IO PANEL | ELUTION BUILDING | 16 | 0.6/1 | 50 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-TLD-EL-10052 | 220 | 0 |  | 2
F22RIO002-P1 | F22-DB-201 | CARBON TREATMENT AND ELUTION 415V SWITCHROOM 240V UPS DISTRIBUTION BOARD | CARBON REGEN AND ELUTION SWITCHROOM | F22-RIO-002 | ELUTION FIELD N-IO PANEL | ELUTION BUILDING | 16 | 0.6/1 | 50 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-TLD-EL-10052 | 220 | 0 |  | 2
F22COM001/F22RIO001-FO1 | F22-COM-001 | CARBON TREATMENT AND ELUTION 415V SWITCHROOM COMMUNICATIONS RACK | CARBON REGEN AND ELUTION SWITCHROOM | F22-RIO-001 | ELUTION FIELD N-IO PANEL | ELUTION BUILDING | 9/125µm | N/A | 50 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | 2000-F22-TER-IC-10002 | 220 | 0 |  | 2
F22RIO001/F22RIO002-FO1 | F22-RIO-001 | ELUTION FIELD N-IO PANEL | ELUTION BUILDING | F22-RIO-002 | ELUTION FIELD N-IO PANEL | ELUTION BUILDING | 9/125µm | N/A | 15 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | 2000-F22-TER-IC-10200 | 220 | 0 |  | 2
F22RIO002/F22COM001-FO1 | F22-RIO-002 | ELUTION FIELD N-IO PANEL | ELUTION BUILDING | F22-COM-001 | CARBON TREATMENT AND ELUTION 415V SWITCHROOM COMMUNICATIONS RACK | CARBON REGEN AND ELUTION SWITCHROOM | 9/125µm | N/A | 50 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | 2000-F22-TER-IC-10230 | 220 | 0 |  | 2
F22KN411CP-D1 | F22-RIO-001 | ELUTION FIELD N-IO PANEL | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | N/A | N/A | 20 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Comms | Primero | Primero | 2000-F22-TER-IC-10200 | 220 | 0 | Comms | 2
F22FIP401-P1 | F22-DB-301 | CARBON TREATMENT AND ELUTION AREA L&SP DISTRIBUTION BOARD | ELUTION BUILDING | F22-FIP-401 | F22-SC-421 CIL4 LOADED CARBON SCREEN FIRE INDICATOR PANEL | CARBON SCREEN PLATFORM | 2.5 | 0.6/1 | 80 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 2000-F22-TLD-EL-10201 | 220 | 0 |  | 2
F72PP698-P1 | F22-DB-301 | CARBON TREATMENT AND ELUTION AREA L&SP DISTRIBUTION BOARD | ELUTION BUILDING | F72-PP-698 | ANTISCALANT DOSING PUMP 2 | ELUTION AREA | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | Fly Lead to GPO | VENDOR | Primero | 2000-F22-TLD-EL-10201 | 720 | 0 |  | 2
F72PP699-P1 | F22-DB-301 | CARBON TREATMENT AND ELUTION AREA L&SP DISTRIBUTION BOARD | ELUTION BUILDING | F72-PP-699 | ANTISCALANT DOSING PUMP 3 | ELUTION AREA | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | Fly Lead to GPO | VENDOR | Primero | 2000-F22-TLD-EL-10201 | 720 | 0 |  | 2
F72PP700-P1 | F22-DB-301 | CARBON TREATMENT AND ELUTION AREA L&SP DISTRIBUTION BOARD | ELUTION BUILDING | F72-PP-700 | ANTISCALANT DOSING PUMP 4 | ELUTION AREA | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | Fly Lead to GPO | VENDOR | Primero | 2000-F22-TLD-EL-10201 | 720 | 0 |  | 2
F22CR442ISL-P1 | F22-SW-131 | CARBON TREATMENT AND ELUTION EMERGENCY 415V MCC | CARBON REGEN AND ELUTION SWITCHROOM | F22CR442-ISL | CIL4 CARBON HOIST FIELD ISOLATOR | KILN PLATFORM | 10 | 0.6/1 | 40 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10231 | 220 | 0 |  | 2
F22CR442-P1 | F22-SW-131 | CARBON TREATMENT AND ELUTION EMERGENCY 415V MCC | CARBON REGEN AND ELUTION SWITCHROOM | F22-CR-442 | CIL4 CARBON HOIST | KILN PLATFORM | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | 2000-F22-SCM-EL-10231 | 220 | 0 |  | 2
F22KN411CP-P1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | 25 | 0.6/1 | 35 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10206 | 220 | 0 | Kiln main power supply | 2
F22KN411-P1 | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | F22-KN-411 | CIL4 CARBON REGENERATION KILN MAIN DRIVE | KILN | 4 | 0.6/1 | 15 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-ME017-D01-10001 | 220 | 0 | Kiln Main Drive | 2
F22KN411-P2 | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | F22-KN-411 | CIL4 CARBON REGENERATION KILN 24VDC EMERGENCY DRIVE | KILN | 25 | 0.6/1 | 15 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-ME017-D01-10001 | 220 | 0 | Kiln 24VDC Emergency Drive. 0.75kW motor | 2
F22FS413-P1 | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | F22-FS-413 | CIL4 CARBON REGENERATION KILN SCREW FEEDER | KILN | 2.5 | 0.6/1 | 15 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-ME017-D01-10001 | 220 | 0 | Kiln Screw Feeder | 2
F22FN443-P1 | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | F22-FN-443 | CIL4 CARBON REGENERATION KILN HEATER TERMINAL COOLING FAN 1 | KILN | 2.5 | 0.6/1 | 35 | 3C+E | Cu | ÖLFLEX ® HEAT 125 MC #1024335 | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-ME017-D01-10001 | 220 | 0 | Kiln Heater Terminal Cooling Fans | 2
F22FN444-P1 | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | F22-FN-444 | CIL4 CARBON REGENERATION KILN HEATER TERMINAL COOLING FAN 2 | KILN | 2.5 | 0.6/1 | 35 | 3C+E | Cu | ÖLFLEX ® HEAT 125 MC #1024335 | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-ME017-D01-10001 | 220 | 0 | Kiln Heater Terminal Cooling Fans | 2
F22FN445-P1 | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | F22-FN-445 | CIL4 CARBON REGENERATION KILN HEATER TERMINAL COOLING FAN 3 | KILN | 2.5 | 0.6/1 | 35 | 3C+E | Cu | ÖLFLEX ® HEAT 125 MC #1024335 | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-ME017-D01-10001 | 220 | 0 | Kiln Heater Terminal Cooling Fans | 2
F22FN446-P1 | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | F22-FN-446 | CIL4 CARBON REGENERATION KILN HEATER TERMINAL COOLING FAN 4 | KILN | 2.5 | 0.6/1 | 35 | 3C+E | Cu | ÖLFLEX ® HEAT 125 MC #1024335 | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-ME017-D01-10001 | 220 | 0 | Kiln Heater Terminal Cooling Fans | 2
F22FN447-P1 | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | F22-FN-447 | CIL4 CARBON REGENERATION KILN HEATER TERMINAL COOLING FAN 5 | KILN | 2.5 | 0.6/1 | 35 | 3C+E | Cu | ÖLFLEX ® HEAT 125 MC #1024335 | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-ME017-D01-10001 | 220 | 0 | Kiln Heater Terminal Cooling Fans | 2
F22FN448-P1 | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | F22-FN-448 | CIL4 CARBON REGENERATION KILN HEATER TERMINAL COOLING FAN 6 | KILN | 2.5 | 0.6/1 | 35 | 3C+E | Cu | ÖLFLEX ® HEAT 125 MC #1024335 | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-ME017-D01-10001 | 220 | 0 | Kiln Heater Terminal Cooling Fans | 2
F22FN449-P1 | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | F22-FN-449 | CIL4 CARBON REGENERATION KILN HEATER TERMINAL COOLING FAN 7 | KILN | 2.5 | 0.6/1 | 35 | 3C+E | Cu | ÖLFLEX ® HEAT 125 MC #1024335 | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-ME017-D01-10001 | 220 | 0 | Kiln Heater Terminal Cooling Fans | 2
F22FN450-P1 | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | F22-FN-450 | CIL4 CARBON REGENERATION KILN HEATER TERMINAL COOLING FAN 8 | KILN | 2.5 | 0.6/1 | 35 | 3C+E | Cu | ÖLFLEX ® HEAT 125 MC #1024335 | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-ME017-D01-10001 | 220 | 0 | Kiln Heater Terminal Cooling Fans | 2
F22KN411CP-C1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | 1.5 | 0.6/1 | 30 | 30C+E | Cu | PVC/PVC | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-TER-EL-10203 | 220 | 0 |  | 2
F22KN411CP-C2 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | 1.5 | 0.6/1 | 30 | 30C+E | Cu | PVC/PVC | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-TER-EL-10203 | 220 | 0 |  | 2
F22KN411CP-I1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | 1.5 | 0.11 | 30 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-TER-EL-10203 | 220 | 0 |  | 2
F22KN411CP-I2 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | 1.5 | 0.11 | 30 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-TER-EL-10253 | 220 | 0 |  | 2
F22KN411CP-I3 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-CP | CIL4 CARBON REGENERATION KILN CONTROL PANEL | KILN PLATFORM | 1.5 | 0.11 | 30 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-TER-EL-10253 | 220 | 0 |  | 2
F22KN411JB11-P1-R | F22KN411A-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 1 BANK 1 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB11 | CARBON REGENERATION KILN ZONE 1 BANK 1 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10207 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB11-P1-W | F22KN411A-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 1 BANK 1 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB11 | CARBON REGENERATION KILN ZONE 1 BANK 1 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10207 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB11-P1-B | F22KN411A-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 1 BANK 1 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB11 | CARBON REGENERATION KILN ZONE 1 BANK 1 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10207 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB12-P1-R | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB12 | CARBON REGENERATION KILN ZONE 1 BANK 2 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10208 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB12-P1-W | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB12 | CARBON REGENERATION KILN ZONE 1 BANK 2 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10208 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB12-P1-B | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB12 | CARBON REGENERATION KILN ZONE 1 BANK 2 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10208 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB13-P1-R | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB13 | CARBON REGENERATION KILN ZONE 1 BANK 3 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10209 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB13-P1-W | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB13 | CARBON REGENERATION KILN ZONE 1 BANK 3 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10209 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB13-P1-B | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB13 | CARBON REGENERATION KILN ZONE 1 BANK 3 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10209 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB14-P1-R | F22KN411D-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 1 BANK 4 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB14 | CARBON REGENERATION KILN ZONE 1 BANK 4 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10210 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB14-P1-W | F22KN411D-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 1 BANK 4 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB14 | CARBON REGENERATION KILN ZONE 1 BANK 4 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10210 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB14-P1-B | F22KN411D-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 1 BANK 4 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB14 | CARBON REGENERATION KILN ZONE 1 BANK 4 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10210 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB15-P1-R | F22KN411E-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 1 BANK 5 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB15 | CARBON REGENERATION KILN ZONE 1 BANK 5 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10211 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB15-P1-W | F22KN411E-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 1 BANK 5 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB15 | CARBON REGENERATION KILN ZONE 1 BANK 5 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10211 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB15-P1-B | F22KN411E-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 1 BANK 5 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB15 | CARBON REGENERATION KILN ZONE 1 BANK 5 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10211 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB16-P1-R | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB16 | CARBON REGENERATION KILN ZONE 1 BANK 6 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10212 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB16-P1-W | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB16 | CARBON REGENERATION KILN ZONE 1 BANK 6 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10212 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB16-P1-B | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB16 | CARBON REGENERATION KILN ZONE 1 BANK 6 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10212 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB17-P1-R | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB17 | CARBON REGENERATION KILN ZONE 1 BANK 7 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10213 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 2
F22KN411JB17-P1-W | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB17 | CARBON REGENERATION KILN ZONE 1 BANK 7 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10213 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB17-P1-B | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB17 | CARBON REGENERATION KILN ZONE 1 BANK 7 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10213 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB18-P1-R | F22KN411H-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 1 BANK 8 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB18 | CARBON REGENERATION KILN ZONE 1 BANK 8 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10214 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB18-P1-W | F22KN411H-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 1 BANK 8 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB18 | CARBON REGENERATION KILN ZONE 1 BANK 8 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10214 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB18-P1-B | F22KN411H-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 1 BANK 8 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB18 | CARBON REGENERATION KILN ZONE 1 BANK 8 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10214 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB21-P1-R | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB21 | CARBON REGENERATION KILN ZONE 2 BANK 1 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10260 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB21-P1-W | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB21 | CARBON REGENERATION KILN ZONE 2 BANK 1 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10260 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB21-P1-B | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB21 | CARBON REGENERATION KILN ZONE 2 BANK 1 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10260 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB22-P1-R | F22KN411J-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 2 BANK 2 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB22 | CARBON REGENERATION KILN ZONE 2 BANK 2 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10261 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB22-P1-W | F22KN411J-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 2 BANK 2 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB22 | CARBON REGENERATION KILN ZONE 2 BANK 2 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10261 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB22-P1-B | F22KN411J-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 2 BANK 2 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB22 | CARBON REGENERATION KILN ZONE 2 BANK 2 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10261 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB23-P1-R | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB23 | CARBON REGENERATION KILN ZONE 2 BANK 3 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10262 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB23-P1-W | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB23 | CARBON REGENERATION KILN ZONE 2 BANK 3 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10262 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB23-P1-B | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB23 | CARBON REGENERATION KILN ZONE 2 BANK 3 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10262 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB24-P1-R | F22KN411L-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 2 BANK 4 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB24 | CARBON REGENERATION KILN ZONE 2 BANK 4 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10263 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB24-P1-W | F22KN411L-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 2 BANK 4 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB24 | CARBON REGENERATION KILN ZONE 2 BANK 4 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10263 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB24-P1-B | F22KN411L-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 2 BANK 4 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB24 | CARBON REGENERATION KILN ZONE 2 BANK 4 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10263 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB25-P1-R | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB25 | CARBON REGENERATION KILN ZONE 2 BANK 5 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10264 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB25-P1-W | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB25 | CARBON REGENERATION KILN ZONE 2 BANK 5 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10264 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB25-P1-B | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB25 | CARBON REGENERATION KILN ZONE 2 BANK 5 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10264 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB26-P1-R | F22KN411N-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 2 BANK 6 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB26 | CARBON REGENERATION KILN ZONE 2 BANK 6 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10265 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB26-P1-W | F22KN411N-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 2 BANK 6 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB26 | CARBON REGENERATION KILN ZONE 2 BANK 6 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10265 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB26-P1-B | F22KN411N-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 2 BANK 6 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB26 | CARBON REGENERATION KILN ZONE 2 BANK 6 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10265 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB31-P1-R | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB31 | CARBON REGENERATION KILN ZONE 3 BANK 1 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10266 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB31-P1-W | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB31 | CARBON REGENERATION KILN ZONE 3 BANK 1 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10266 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB31-P1-B | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB31 | CARBON REGENERATION KILN ZONE 3 BANK 1 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10266 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB32-P1-R | F22KN411P-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 3 BANK 2 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB32 | CARBON REGENERATION KILN ZONE 3 BANK 2 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10267 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB32-P1-W | F22KN411P-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 3 BANK 2 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB32 | CARBON REGENERATION KILN ZONE 3 BANK 2 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10267 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB32-P1-B | F22KN411P-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 3 BANK 2 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB32 | CARBON REGENERATION KILN ZONE 3 BANK 2 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10267 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB33-P1-R | F22KN411Q-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 3 BANK 3 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB33 | CARBON REGENERATION KILN ZONE 3 BANK 3 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10274 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB33-P1-W | F22KN411Q-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 3 BANK 3 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB33 | CARBON REGENERATION KILN ZONE 3 BANK 3 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10274 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22KN411JB33-P1-B | F22KN411Q-XE | CIL 4 CARBON REGEN KILN HEATERS ZONE 3 BANK 3 CONTROLLER | CARBON REGEN AND ELUTION SWITCHROOM | F22KN411-JB33 | CARBON REGENERATION KILN ZONE 3 BANK 3 JUNCTION BOX | KILN | 150 | 0.6/1 | 35 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Trefoil, Spaced 1D, Grouped up to 6 | Primero | Primero | 2000-F22-SCM-EL-10274 | 220 | 0 | REFER TO RESISTOR WIRING DIAGRAM FOR INTER- RESISTOR CONNECTIONS | 3
F22DB301-P1 | F22-SW-131 | CARBON TREATMENT AND ELUTION EMERGENCY 415V MCC | CARBON REGEN AND ELUTION SWITCHROOM | F22-DB-301 | CARBON TREATMENT AND ELUTION AREA L&SP DISTRIBUTION BOARD | ELUTION BUILDING | 185 | 0.6/1 | 50 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10257 | 220 | 0 |  | 3
F22PE301-P1 | F22-DB-301 | CARBON TREATMENT AND ELUTION AREA L&SP DISTRIBUTION BOARD | ELUTION BUILDING | F22-PE-301 | CARBON TREATMENT AND ELUTION AREA PHOTO-ELECTRIC CELL | ELUTION BUILDING | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-TLD-EL-10201 | 220 | 0 | PE Circuit for L&SP DB | 3
F22SC421-P1 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22-SC-421 | CIL4 LOADED CARBON SCREEN | ELUTION TOP DECK | 6 | 0.6/1 | 85 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10233 | 220 | 0 |  | 3
F22SC421-P2 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22-SC-421 | CIL4 LOADED CARBON SCREEN | ELUTION TOP DECK | 6 | 0.6/1 | 85 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10233 | 220 | 0 |  | 3
F22SC421LCS-C1 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22SC421-LCS | CIL4 LOADED CARBON SCREEN LOCAL CONTROL STATION | ELUTION TOP DECK | 1.5 | 0.6/1 | 85 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-SCM-EL-10233 | 220 | 0 | LCS | 3
F22SC423-P1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22-SC-423 | CIL4 REGEN KILN DEWATERING SCREEN | ELUTION TOP DECK | 6 | 0.6/1 | 80 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10229 | 220 | 0 |  | 3
F22SC423-P2 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22-SC-423 | CIL4 REGEN KILN DEWATERING SCREEN | ELUTION TOP DECK | 6 | 0.6/1 | 80 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10229 | 220 | 0 |  | 3
F22SC423LCS-C1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22SC423-LCS | CIL4 REGEN KILN DEWATERING SCREEN LOCAL CONTROL STATION | ELUTION TOP DECK | 1.5 | 0.6/1 | 80 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-SCM-EL-10229 | 220 | 0 | LCS | 3
F22FN401-P1 | F22-SW-131 | CARBON TREATMENT AND ELUTION EMERGENCY 415V MCC | CARBON REGEN AND ELUTION SWITCHROOM | F22-FN-401 | KILN MERCURY ABATEMENT EXHAUST FAN | MERCURY ABATEMENT | 4 | 0.6/1 | 65 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10258 | 220 | 0 |  | 3
F22FN401LCS-C1 | F22-SW-131 | CARBON TREATMENT AND ELUTION EMERGENCY 415V MCC | CARBON REGEN AND ELUTION SWITCHROOM | F22FN401-LCS | KILN MERCURY ABATEMENT EXHAUST FAN LCS | MERCURY ABATEMENT | 1.5 | 0.6/1 | 65 | 4C+E | Cu | PVC/PVC | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10258 | 220 | 0 | LCS | 3
F22HT401CP-P1 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22HT401-CP | KILN MERCURY ABATEMENT EXHAUST HEATER CONTROL PANEL | MERCURY ABATEMENT | 16 | 0.6/1 | 60 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10225 | 220 | 0 |  | 3
F22HT401-C1 | F22HT401-CP | KILN MERCURY ABATEMENT EXHAUST HEATER CONTROL PANEL | CARBON REGEN AND ELUTION SWITCHROOM | F22-HT-401 | KILN MERCURY ABATEMENT EXHAUST HEATER | MERCURY ABATEMENT | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | VENDOR | Ladder - Single Layer Touching | Vendor - ME080 | Primero | 2000-ME080-D02-10001 | 220 | 0 |  | 3
F22HT411CP-P1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22HT411-CP | CIL4 ELUTION HEATER CONTROL PANEL | ELUTION BUILDING | 16 | 0.6/1 | 50 | 3C+E | Cu | PVC/PVC | Orange | Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10206 | 220 | 0 |  | 3
F22HT411CP-C1 | F22PP460-LCS | CIL4 ELUTION HEATER THERMAL OIL PUMP 1 LCS | ELUTION BUILDING | F22HT411-CP | CIL4 ELUTION HEATER CONTROL PANEL | ELUTION BUILDING | 1.5 | 0.6/1 | 10 | 2C+E | Cu | PVC/PVC | Black | Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10223 | 220 | 0 | E-Stop from Control Panel | 3
F22HT411CP-I1 | F22-RIO-001 | ELUTION FIELD N-IO PANEL | ELUTION BUILDING | F22HT411-CP | CIL4 ELUTION HEATER CONTROL PANEL | ELUTION BUILDING | 1.5 | 0.11 | 80 | 12PR | Cu | PVC/OSCN/PVC | Black | Buried in Conduit/Ladder - Bunched Ctrl/Instro | Primero | Primero | 2000-F22-TER-IC-10207 | 220 | 0 |  | 3
F22HT411CP-I2 | F22-RIO-001 | ELUTION FIELD N-IO PANEL | ELUTION BUILDING | F22HT411-CP | CIL4 ELUTION HEATER CONTROL PANEL | ELUTION BUILDING | 1.5 | 0.11 | 80 | 8PR | Cu | PVC/IOSCN/PVC | Black | Buried in Conduit/Ladder - Bunched Ctrl/Instro | Primero | Primero | 2000-F22-TER-IC-10212 | 220 | 0 |  | 3
F22FN411-P1 | F22HT411-CP | CIL4 ELUTION HEATER CONTROL PANEL | ELUTION BUILDING | F22-FN-411 | CIL4 ELUTION HEATER COMBUSTION FAN | ELUTION BUILDING | 4 | 0.6/1 | VENDOR | 3C+E | Cu | XLPE/PVC | Orange | VENDOR | Vendor - ME016 (TPE) | Vendor - ME016 (TPE) | 2000-ME016-D02-10001 | 220 | 0 |  | 3
F22PP460-P1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22-PP-460 | CIL4 ELUTION HEATER THERMAL OIL PUMP | ELUTION BUILDING | 95 | 0.6/1 | 50 | 3C+E | Cu | XLPE/PVC | Orange | Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10223 | 220 | 0 |  | 3
F22PP460-I1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22-PP-460 | CIL4 ELUTION HEATER THERMAL OIL PUMP THERMISTOR | ELUTION BUILDING | 1.5 | 0.11 | 50 | 1PR | Cu | PVC/OSCN/PVC | Black | Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10223 | 220 | 0 | Thermistor | 3
F22PP460LCS-C1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22PP460-LCS | CIL4 ELUTION HEATER THERMAL OIL PUMP LCS | ELUTION BUILDING | 1.5 | 0.6/1 | 60 | 4C+E | Cu | PVC/PVC | Black | Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10223 | 220 | 0 | LCS | 3
F22PP490-P1 | F22PP490-VS | CIL4 BARREN CARBON PUMP LV VSD | CARBON REGEN AND ELUTION SWITCHROOM | F22-PP-490 | CIL4 BARREN CARBON PUMP | ELUTION BUILDING | 25 | 0.6/1 | 40 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10224 | 220 | 0 |  | 3
F22PP490LCS-C1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22PP490-LCS | CIL4 BARREN CARBON PUMP LCS | ELUTION BUILDING | 1.5 | 0.6/1 | 40 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-SCM-EL-10224 | 220 | 0 | LCS | 3
F22PS451LCS-P1 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22PS451-LCS | CIL4 ELUTION AREA SUMP PUMP LOCAL CONTROL STATION | ELUTION BUILDING | 25 | 0.6/1 | 40 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10268 | 220 | 0 |  | 3
F22PS451-P2 | F22PS451-LCS | CIL4 ELUTION AREA SUMP PUMP LOCAL CONTROL STATION | ELUTION BUILDING | F22-PS-451 | CIL4 ELUTION AREA SUMP PUMP | ELUTION BUILDING | 25 | 0.6/1 | 10 | 3C+E | Cu | EPR/CSP | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10268 | 220 | 0 | Flexible for decontactor to motor | 4
F22PS451LCS-C1 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22PS451-LCS | CIL4 ELUTION AREA SUMP PUMP LOCAL CONTROL STATION | ELUTION BUILDING | 1.5 | 0.6/1 | 40 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-SCM-EL-10268 | 220 | 0 | LCS | 4
F22PS452LCS-P1 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22PS452-LCS | REGEN KILN AREA SUMP PUMP LOCAL CONTROL STATION | ELUTION BUILDING | 25 | 0.6/1 | 45 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10269 | 220 | 0 |  | 4
F22PS452-P2 | F22PS452-LCS | REGEN KILN AREA SUMP PUMP LOCAL CONTROL STATION | ELUTION BUILDING | F22-PS-452 | REGEN KILN AREA SUMP PUMP | ELUTION BUILDING | 25 | 0.6/1 | 10 | 3C+E | Cu | EPR/CSP | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10269 | 220 | 0 | Flexible for decontactor to motor | 4
F22PS452LCS-C1 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22PS452-LCS | REGEN KILN AREA SUMP PUMP LOCAL CONTROL STATION | ELUTION BUILDING | 1.5 | 0.6/1 | 45 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-SCM-EL-10269 | 220 | 0 | LCS | 4
F22PS453LCS-P1 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22PS453-LCS | MERCURY ABATEMENT AREA SUMP PUMP LOCAL CONTROL STATION | MERCURY ABATEMENT AREA | 25 | 0.6/1 | 50 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10270 | 220 | 0 |  | 4
F22PS453-P2 | F22PS453-LCS | MERCURY ABATEMENT AREA SUMP PUMP LOCAL CONTROL STATION | MERCURY ABATEMENT AREA | F22-PS-453 | MERCURY ABATEMENT AREA SUMP PUMP | MERCURY ABATEMENT AREA | 25 | 0.6/1 | 10 | 3C+E | Cu | EPR/CSP | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10270 | 220 | 0 | Flexible for decontactor to motor | 4
F22PS453LCS-C1 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22PS453-LCS | MERCURY ABATEMENT AREA SUMP PUMP LOCAL CONTROL STATION | MERCURY ABATEMENT AREA | 1.5 | 0.6/1 | 50 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-SCM-EL-10270 | 220 | 0 | LCS | 4
F22PW403-P1 | F22PW403-VS | CIL4 CARBON EDUCTOR PUMP LV VSD | CARBON REGEN AND ELUTION SWITCHROOM | F22-PW-403 | CIL4 CARBON EDUCTOR PUMP | ELUTION TANKS AREA | 10 | 0.6/1 | 100 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10226 | 220 | 0 |  | 4
F22PW403LCS-C1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22PW403-LCS | CIL4 CARBON EDUCTOR PUMP LCS | ELUTION TANKS AREA | 1.5 | 0.6/1 | 100 | 4C+E | Cu | PVC/PVC | Black | Burited in Conduit - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-SCM-EL-10226 | 220 | 0 | LCS | 4
F22PW441-P1 | F22PW441-VS | CIL4 ELUTION PUMP 1 LV VSD | CARBON REGEN AND ELUTION SWITCHROOM | F22-PW-441 | CIL4 ELUTION WATER PUMP 1 | ELUTION TANKS AREA | 35 | 0.6/1 | 100 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10227 | 220 | 0 |  | 4
F22PW441-I1 | F22PW441-VS | CIL4 ELUTION PUMP 1 LV VSD | CARBON REGEN AND ELUTION SWITCHROOM | F22-PW-441 | CIL4 ELUTION WATER PUMP 1 THERMISTOR | ELUTION TANKS AREA | 1.5 | 0.11 | 100 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10227 | 220 | 0 | Thermistor | 4
F22PW441LCS-C1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22PW441-LCS | CIL4 ELUTION WATER PUMP 1 LCS | ELUTION TANKS AREA | 1.5 | 0.6/1 | 100 | 4C+E | Cu | PVC/PVC | Black | Burited in Conduit - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-SCM-EL-10227 | 220 | 0 | LCS | 4
F22PW444-P1 | F22PW444-VS | CIL4 ELUTION PUMP 2 LV VSD | CARBON REGEN AND ELUTION SWITCHROOM | F22-PW-444 | CIL4 ELUTION WATER PUMP 2 | ELUTION TANKS AREA | 35 | 0.6/1 | 100 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10228 | 220 | 0 |  | 4
F22PW444-I1 | F22PW444-VS | CIL4 ELUTION PUMP 2 LV VSD | CARBON REGEN AND ELUTION SWITCHROOM | F22-PW-444 | CIL4 ELUTION WATER PUMP 2 THERMISTOR | ELUTION TANKS AREA | 1.5 | 0.11 | 100 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10228 | 220 | 0 | Thermistor | 4
F22PW444LCS-C1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22PW444-LCS | CIL4 ELUTION WATER PUMP 2 LCS | ELUTION TANKS AREA | 1.5 | 0.6/1 | 100 | 4C+E | Cu | PVC/PVC | Black | Burited in Conduit - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-SCM-EL-10228 | 220 | 0 | LCS | 4
F22PW591-P1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22-PW-591 | KILN ABATEMENT SYSTEM COOLING WATER PUMP 1 | CHILLER SKID | 4 | 0.6/1 | 100 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10222 | 220 | 0 |  | 4
F22PW591LCS-C1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22PW591-LCS | KILN ABATEMENT SYSTEM COOLING WATER PUMP 1 LCS | CHILLER SKID | 1.5 | 0.6/1 | 100 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-SCM-EL-10222 | 220 | 0 | LCS | 4
F22PW592-P1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22-PW-592 | KILN ABATEMENT SYSTEM COOLING WATER PUMP 2 | CHILLER SKID | 4 | 0.6/1 | 100 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F22-SCM-EL-10256 | 220 | 0 |  | 4
F22PW592LCS-C1 | F22-SW-030 | CARBON TREATMENT AND ELUTION 415V MCC 1 | CARBON REGEN AND ELUTION SWITCHROOM | F22PW592-LCS | KILN ABATEMENT SYSTEM COOLING WATER PUMP 2 LCS | CHILLER SKID | 1.5 | 0.6/1 | 100 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-SCM-EL-10256 | 220 | 0 | LCS | 4
F22CU406-P1 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22-CU-406 | KILN MERCURY ABATEMENT CHILLER | KILM MERCURY ABATEMENT CHILLER SKID | 95 | 0.6/1 | 100 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10232 | 220 | 0 |  | 4
F22CU406-P2 | F22-SW-031 | CARBON TREATMENT AND ELUTION 415V MCC 2 | CARBON REGEN AND ELUTION SWITCHROOM | F22-CU-406 | KILN MERCURY ABATEMENT CHILLER | KILM MERCURY ABATEMENT CHILLER SKID | 95 | 0.6/1 | 100 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero | 2000-F22-SCM-EL-10232 | 220 | 0 |  | 4
F22CU406-I1 | F22-RIO-002 | ELUTION FIELD N-IO PANEL | ELUTION BUILDING | F22-CU-406 | KILN MERCURY ABATEMENT CHILLER | KILM MERCURY ABATEMENT CHILLER SKID | 1.5 | 0.11 | 90 | 8PR | Cu | PVC/OSCN/PVC | Black | Buried in Conduit/Ladder - Bunched Ctrl/Instro | Primero | Primero | 2000-F22-TER-IC-10234 | 220 | 0 |  | 4
F22CAM001-D1 | F22-RIO-002 | ELUTION FIELD N-IO PANEL | ELUTION BUILDING | F22-CAM-001 | CARBON SCREEN CCTV CAMERA | ELUTION BUILDING | N/A | N/A | 70 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-TER-IC-10230 | 220 | 0 | CCTV | 4
F22CAM002-D1 | F22-RIO-002 | ELUTION FIELD N-IO PANEL | ELUTION BUILDING | F22-CAM-002 | ELUTION COLUMN UPPER CCTV CAMERA | ELUTION BUILDING | N/A | N/A | 50 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-TER-IC-10230 | 220 | 0 | CCTV | 4
F22CAM003-D1 | F22-RIO-002 | ELUTION FIELD N-IO PANEL | ELUTION BUILDING | F22-CAM-003 | ELUTION COLUMN LOWER CCTV CAMERA | ELUTION BUILDING | N/A | N/A | 40 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-TER-IC-10230 | 220 | 0 | CCTV | 4
F22CAM004-D1 | F22-RIO-002 | ELUTION FIELD N-IO PANEL | ELUTION BUILDING | F22-CAM-004 | KILN ACCESS CCTV CAMERA | ELUTION BUILDING | N/A | N/A | 40 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F22-TER-IC-10230 | 220 | 0 | CCTV | 4