## Cable schedule
Cable Number | Equip. Number - From | Equip. Number - To | nductor Size (mm | Insula:on(kV) | Length | o. of Cores / Pai | Conductor | Construction | eath(Preferred colou | r Installation Method | Supplied By | Installed By | Comments | Rev | Equipment Name - From | Equipment Name - To | Location - To | Location - From | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | Length (m) | No. of Cores / Pairs | Sheath (Preferred colour) | Page
F23TR016-C1 | F23-SW-016 | F23-TR-016 | 1.5 | 0.6/1 | 40 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | Transformer trips to protection relay | 0 | [15 empty] | 2
F23NR016-P1 | F23-DB-001 | F23-NR-016 | 2.5 | 0.6/1 | 50 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched Ctrl/Inst | Primero | Primero | NER Anti-condensation heater | 0 | [15 empty] | 2
F23NR016-C1 | F23-SW-016 | F23-NR-016 | 4 | 0.6/1 | 40 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | NER CT + Sensing Resistor to protection relay | 0 | [15 empty] | 2
F23PP466-P2 | F23PP466-VS | F23-PP-466 | 2.5 | 0.6/1 | 120 | 2C+E | Cu | PVC/PVC | Orange |  | Primero | Primero |  | 0 | FINAL TAILS PUMP 1 HV VSD | FINAL TAILS PUMP 1 SPACE HEATER | F23 Field | [12 empty] | 2
F23PP466-I1 | F23PP466-VS | F23-PP-466 | 1.5 | 0.11 | 120 | 12TR | Cu | PVC/IOSCN/PVC | Black |  | Primero | Primero |  | 0 | FINAL TAILS PUMP 1 HV VSD | FINAL TAILS PUMP 1 RTDs | F23 Field | [12 empty] | 2
F23PP466LCS-C1 | F23PP466-VS | F23PP466-LCS | 1.5 | 0.6/1 | 125 | 6C+E | Cu | PVC/PVC | Black |  | Primero | Primero |  | 0 | FINAL TAILS PUMP 1 HV VSD | FINAL TAILS PUMP 1 LOCAL CONTROL STATION | F23 Field | [12 empty] | 2
F23PP467-P2 | F23PP467-VS | F23-PP-467 | 2.5 | 0.6/1 | 115 | 2C+E | Cu | PVC/PVC | Orange |  | Primero | Primero |  | 0 | FINAL TAILS PUMP 2 HV VSD | FINAL TAILS PUMP 2 SPACE HEATER | F23 Field | [12 empty] | 2
F23PP467-I1 | F23PP467-VS | F23-PP-467 | 1.5 | 0.11 | 115 | 12TR | Cu | PVC/IOSCN/PVC | Black |  | Primero | Primero |  | 0 | FINAL TAILS PUMP 2 HV VSD | FINAL TAILS PUMP 2 RTDs | F23 Field | [12 empty] | 2
F23PP467LCS-C1 | F23PP467-VS | F23PP467-LCS | 1.5 | 0.6/1 | 110 | 6C+E | Cu | PVC/PVC | Black |  | Primero | Primero |  | 0 | FINAL TAILS PUMP 2 HV VSD | FINAL TAILS PUMP 2 LOCAL CONTROL STATION | F23 Field | [12 empty] | 2
F23PP468-P2 | F23PP468-VS | F23-PP-468 | 2.5 | 0.6/1 | 130 | 2C+E | Cu | PVC/PVC | Orange |  | Primero | Primero |  | 0 | FINAL TAILS PUMP 3 HV VSD | FINAL TAILS PUMP 3 SPACE HEATER | F23 Field | [12 empty] | 2
F23PP468-I1 | F23PP468-VS | F23-PP-468 | 1.5 | 0.11 | 130 | 12TR | Cu | PVC/IOSCN/PVC | Black |  | Primero | Primero |  | 0 | FINAL TAILS PUMP 3 HV VSD | FINAL TAILS PUMP 3 RTDs | F23 Field | [12 empty] | 2
F23PP468LCS-C1 | F23PP468-VS | F23PP468-LCS | 1.5 | 0.6/1 | 125 | 6C+E | Cu | PVC/PVC | Black |  | Primero | Primero |  | 0 | FINAL TAILS PUMP 3 HV VSD | FINAL TAILS PUMP 3 LOCAL CONTROL STATION | F23 Field | [12 empty] | 2
F23PP469-P2 | F23PP469-VS | F23-PP-469 | 2.5 | 0.6/1 | 130 | 2C+E | Cu | PVC/PVC | Orange |  | Primero | Primero |  | 0 | FINAL TAILS PUMP 4 HV VSD | FINAL TAILS PUMP 4 SPACE HEATER | F23 Field | [12 empty] | 2
F23PP469-I1 | F23PP469-VS | F23-PP-469 | 1.5 | 0.11 | 130 | 12TR | Cu | PVC/IOSCN/PVC | Black |  | Primero | Primero |  | 0 | FINAL TAILS PUMP 4 HV VSD | FINAL TAILS PUMP 4 RTDs | F23 Field | [12 empty] | 2
F23PP469LCS-C1 | F23PP469-VS | F23PP469-LCS | 1.5 | 0.6/1 | 135 | 6C+E | Cu | PVC/PVC | Black |  | Primero | Primero |  | 0 | FINAL TAILS PUMP 4 HV VSD | FINAL TAILS PUMP 4 LOCAL CONTROL STATION | F23 Field | [12 empty] | 2
F72PK405-FO1 | F23-COM-001 | F72-PK-405 | 9/125µm | N/A | 70 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | Primero | Primero | Allowed for a 30m coil at the piperack | 0 | FINAL TAILS PUMPS 415V SWITCHROOM COMMUNICATIONS RACK | OXYGEN PLANT | F72 Field | Final Tails Pumps 415V Switchroom | [11 empty] | 2
F72SW072-C10 | F23-SW-016 | F72-SW-072 | 6 | 0.6/1 | 300 | 2C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | AF/ELR/SWRM E-Stop trip signals. | 0 | FINAL TAILS PUMPS 11KV SWITCHBOARD | REAGENTS 415V MCC | Reagents 415V Switchroom | Final Tails Pumps 11kV Switchroom | [11 empty] | 2
F00PS464LCS-P1 | F23-SW-023 | F00PS464-LCS | 185 | 0.6/1 | 250 | 3C+E | Cu | XLPE/PVC | Orange |  | Primero | Primero | 2000-F00-LST-EL-25013. Stage 2 Enabling Works | 0 |  | EVENT POND SUBMERSIBLE PUMP LCS / DECONTACTOR UNIT | Event Pond Area | Final Tails 415V Switchroom | [11 empty] | 2
F00PS464-P2 | F00PS464-LCS | F00-PS-464 | 70 | 0.6/1 | 15 | 3C+E | Cu | EPR/CSP | Black |  | NSR Enabling Works | NSR Enabling Works | 2000-F00-LST-EL-25013. Stage 2 Enabling Works | 0 |  | EVENT POND SUBMERSIBLE PUMP | Event Pond Area | Event Pond Area | [11 empty] | 2
F00PS464LCS-C1 | F23-SW-023 | F00PS464-LCS | 1.5 | 0.6/1 | 250 | 4C+E | Cu | PVC/PVC | Black |  | Primero | Primero | 2000-F00-LST-EL-25013. Stage 2 Enabling Works | 0 |  | EVENT POND SUBMERSIBLE PUMP LCS / DECONTACTOR UNIT | Event Pond Area | Final Tails 415V Switchroom | [11 empty] | 2
F00PS465LCS-P1 | F23-SW-023 | F00PS465-LCS | 185 | 0.6/1 | 235 | 3C+E | Cu | XLPE/PVC | Orange |  | Primero | Primero | 2000-F00-LST-EL-25013. Stage 2 Enabling Works | 0 |  | SILT TRAP SUBMERSIBLE PUMP LCS / DECONTACTOR UNIT | Event Pond Area | Final Tails 415V Switchroom | [11 empty] | 2
F00PS465-P2 | F00PS465-LCS | F00-PS-465 | 70 | 0.6/1 | 10 | 3C+E | Cu | EPR/CSP | Black |  | NSR Enabling Works | NSR Enabling Works | 2000-F00-LST-EL-25013. Stage 2 Enabling Works | 0 |  | SILT TRAP SUBMERSIBLE PUMP | Event Pond Area | Event Pond Area | [11 empty] | 2
F00PS465LCS-C1 | F23-SW-023 | F00PS465-LCS | 1.5 | 0.6/1 | 235 | 4C+E | Cu | PVC/PVC | Black |  | Primero | Primero | 2000-F00-LST-EL-25013. Stage 2 Enabling Works | 0 |  | SILT TRAP SUBMERSIBLE PUMP LCS / DECONTACTOR UNIT | Event Pond Area | Final Tails 415V Switchroom | [11 empty] | 2
F00DB401-P1 | F23-SW-123 | F00-DB-401 | 25 | 0.6/1 | 230 | 4C+E | Cu | XLPE/PVC | Orange |  | Primero | Primero | 2000-F00-LST-EL-25013. Stage 2 Enabling Works | 0 |  | EVENT POND AREA L&SP DISTRIBUTION BOARD | Event Pond Area | Final Tails 415V Switchroom | [11 empty] | 2
F00DB401R3-P1 | F00-DB-401 | F00DB401-R3 | 2.5 | 0.6/1 | 5 | 2C+E | Cu | PVC/PVC | Orange |  | NSR Enabling Works | NSR Enabling Works | 2000-F00-LST-EL-25013. Stage 2 Enabling Works | 0 |  | SILT TRAP AREA 15A 1-PH OUTLET | Event Pond Area | Event Pond Area | [11 empty] | 2
F00DB401R4-P1 | F00-DB-401 | F00DB401-R4 | 2.5 | 0.6/1 | 50 | 2C+E | Cu | PVC/PVC | Orange |  | NSR Enabling Works | NSR Enabling Works | 2000-F00-LST-EL-25013. Stage 2 Enabling Works | 0 |  | EVENT POND AREA SAFETY SHOWER LIGHTING | Event Pond Area | Event Pond Area | [11 empty] | 2
F00DB401W4-P1 | F00-DB-401 | F00DB401-W4 | 2.5 | 0.6/1 | 50 | 2C+E | Cu | PVC/PVC | Orange |  | NSR Enabling Works | NSR Enabling Works | 2000-F00-LST-EL-25013. Stage 2 Enabling Works | 0 |  | EVENT POND AREA EXTERNAL GANTRY LIGHTING | Event Pond Area | Event Pond Area | [11 empty] | 2
F00DB401B4-P1 | F00-DB-401 | F00DB401-B4 | 2.5 | 0.6/1 | 20 | 2C+E | Cu | PVC/PVC | Orange |  | NSR Enabling Works | NSR Enabling Works | 2000-F00-LST-EL-25013. Stage 2 Enabling Works | 0 |  | SILT TRAP AREA EXTERNAL LIGHTING | Event Pond Area | Event Pond Area | [11 empty] | 2
F00DB401RWB5-P1 | F00-DB-401 | F00DB401-RWB5 | 6 | 0.6/1 | 50 | 4C+E | Cu | PVC/PVC | Orange |  | NSR Enabling Works | NSR Enabling Works | 2000-F00-LST-EL-25013. Stage 2 Enabling Works | 0 |  | EVENT POND SUMP PUMP HOIST / MONORAIL UNIT | Event Pond Area | Event Pond Area | [11 empty] | 2
F00DB401RWB6-P1 | F00-DB-401 | F00DB401-RWB6 | 6 | 0.6/1 | 20 | 4C+E | Cu | PVC/PVC | Orange |  | NSR Enabling Works | NSR Enabling Works | 2000-F00-LST-EL-25013. Stage 2 Enabling Works | 0 |  | SILT TRAP SUMP PUMP HOIST / MONORAIL UNIT | Event Pond Area | Event Pond Area | [11 empty] | 2
F23SW123-P4 | F23-GE-123 | F23-SW-123 | 185 | 0.6/1 | 55 | 4C+E | Cu |  | Orange |  | Primero | Primero |  | 0 |  |  | Final Tails 415V Switchroom | Final Tails Switchroom Area | [11 empty] | 2
F23SW123-P5 | F23-GE-123 | F23-SW-123 | 185 | 0.6/1 | 55 | 4C+E | Cu |  | Orange |  | Primero | Primero |  | 0 |  |  | Final Tails 415V Switchroom | Final Tails Switchroom Area | [11 empty] | 2
F23SW123-P6 | F23-GE-123 | F23-SW-123 | 185 | 0.6/1 | 55 | 4C+E | Cu |  | Orange |  | Primero | Primero |  | 0 |  |  | Final Tails 415V Switchroom | Final Tails Switchroom Area | [11 empty] | 2
F23GE123CP-P1 | F23-DB-001 | F23GE123-CP | 2.5 | 0.6/1 | 60 | 2C+E | Cu |  | Orange |  | Primero | Primero |  | 0 |  |  | Final Tails Switchroom Area | Final Tails 415V Switchroom | [11 empty] | 2
F23GE123CP-C1 | F23-DCS-409 | F23GE123-CP | 1.5 | 0.6/1 | 60 | 6C+E | Cu |  | Black |  | Primero | Primero |  | 0 |  |  | Final Tails Switchroom Area | Final Tails 415V Switchroom | [11 empty] | 2
F23GE123CP-C2 | F23-SW-123 | F23GE123-CP | 1.5 | 0.6/1 | 60 | 10C+E | Cu |  | Black |  | Primero | Primero |  | 0 |  |  | Final Tails Switchroom Area | Final Tails 415V Switchroom | [11 empty] | 2
F23GE123CP-D1 | F23-COM-001 | F23GE123-CP | N/A | N/A | 60 | 4PR | Cu |  | Black |  | Primero | Primero |  | 0 |  |  | Final Tails Switchroom Area | Final Tails 415V Switchroom | [11 empty] | 2
F23DB301-P1 | F23-SW-123 | F23-DB-301 | 185 | 0.6/1 | 140 | 4C+E | Cu |  | Orange |  | Primero | Primero |  | 0 |  |  | Final Tails Area | Final Tails 415V Switchroom | [11 empty] | 2
F23PE301-P1 | F23-DB-301 | F23-PE-301 | 2.5 | 0.6/1 | 10 | 3C+E | Cu |  | Orange |  | Primero | Primero |  | 0 |  |  | Final Tails Area | Final Tails Area | [11 empty] | 2
F23RIO001-P1 | F23-DB-201 | F23-RIO-001 | 25 | 0.6/1 | 140 | 2C+E | Cu |  | Orange |  | Primero | Primero |  | 0 |  |  | Final Tails Area | Final Tails 415V Switchroom | [11 empty] | 2
F23COM001/F23RIO001-FO1 | F23-COM-001 | F23-RIO-001 | 9/125µm | N/A | 150 | 12C | OS2 SMOF |  | Black |  | Primero | Primero |  | 0 |  |  | Final Tails Area | Final Tails 415V Switchroom | [11 empty] | 2
F23RIO001/F23COM001-FO1 | F23-RIO-001 | F23-COM-001 | 9/125µm | N/A | 150 | 12C | OS2 SMOF |  | Black |  | Primero | Primero |  | 0 |  |  | Final Tails 415V Switchroom | Final Tails Area | [11 empty] | 2
F23AG404-P1 | F23AG404-VS | F23-AG-404 | 35 | 0.6/1 | 120 | 3C+3E | Cu |  | Black |  | Primero | Primero |  | 0 |  |  | Final Tails Area | Final Tails 415V Switchroom | [11 empty] | 2
F23AG404-I1 | F23AG404-VS | F23-AG-404 | 1.5 | 0.11 | 120 | 1PR | Cu |  | Black |  | Primero | Primero |  | 0 |  |  | Final Tails Area | Final Tails 415V Switchroom | [11 empty] | 2
F23AG404LCS-C1 | F23-SW-123 | F23AG404-LCS | 1.5 | 0.6/1 | 125 | 4C+E | Cu |  | Black |  | Primero | Primero |  | 0 |  |  | Final Tails Area | Final Tails 415V Switchroom | [11 empty] | 2
F23FN462-P1 | F23-SW-023 | F23-FN-462 | 4 | 0.6/1 | 140 | 3C+E | Cu |  | Orange |  | Primero | Primero |  | 0 |  |  | Final Tails Area | Final Tails 415V Switchroom | [11 empty] | 2
F23FN462LCS-C1 | F23-SW-023 | F23FN462-LCS | 1.5 | 0.6/1 | 140 | 4C+E | Cu |  | Black |  | Primero | Primero |  | 0 |  |  | Final Tails Area | Final Tails 415V Switchroom | [11 empty] | 2
F23FN463-P1 | F23-SW-023 | F23-FN-463 | 4 | 0.6/1 | 135 | 3C+E | Cu |  | Orange |  | Primero | Primero |  | 0 |  |  | Final Tails Area | Final Tails 415V Switchroom | [11 empty] | 2
F23FN463LCS-C1 | F23-SW-023 | F23FN463-LCS | 1.5 | 0.6/1 | 120 | 4C+E | Cu |  | Black |  | Primero | Primero |  | 0 |  |  | Final Tails Area | Final Tails 415V Switchroom | [11 empty] | 2
F23FN464-P1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | FINAL TAILS PUMPS 415V MCC | Final Tails 415V Switchroom | F23-FN-464 | FINAL TAILS PUMP 3 MOTOR COOLING FAN | Final Tails Area | 4 | 0.6/1 | 160 | 3C+E | Orange | 3
F23FN464LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | FINAL TAILS PUMPS 415V MCC | Final Tails 415V Switchroom | F23FN464-LCS | FINAL TAILS PUMP 3 MOTOR FAN LOCAL CONTROL STATION | Final Tails Area | 1.5 | 0.6/1 | 160 | 4C+E | Black | 3
F23FN465-P1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | FINAL TAILS PUMPS 415V MCC | Final Tails 415V Switchroom | F23-FN-465 | FINAL TAILS PUMP 4 MOTOR COOLING FAN | Final Tails Area | 4 | 0.6/1 | 160 | 3C+E | Orange | 3
F23FN465LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | FINAL TAILS PUMPS 415V MCC | Final Tails 415V Switchroom | F23FN465-LCS | FINAL TAILS PUMP 4 MOTOR FAN LOCAL CONTROL STATION | Final Tails Area | 1.5 | 0.6/1 | 165 | 4C+E | Black | 3
F23FN466-P1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F23-FN-466 | FINAL TAILS PUMP 1 GEARBOX OIL AIR COOLING FAN | Final Tails Area | 2.5 | 0.6/1 | 140 | 3C+E | Orange | 3
F23FN466LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F23FN466-LCS | FINAL TAILS PUMP 1 GEARBOX FAN LOCAL CONTROL STATION | Final Tails Area | 1.5 | 0.6/1 | 140 | 4C+E | Black | 3
F23FN467-P1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F23-FN-467 | FINAL TAILS PUMP 2 GEARBOX OIL AIR COOLING FAN | Final Tails Area | 2.5 | 0.6/1 | 135 | 3C+E | Orange | 3
F23FN467LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F23FN467-LCS | FINAL TAILS PUMP 2 GEARBOX FAN LOCAL CONTROL STATION | Final Tails Area | 1.5 | 0.6/1 | 120 | 4C+E | Black | 3
F23FN468-P1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F23-FN-468 | FINAL TAILS PUMP 3 GEARBOX OIL AIR COOLING FAN | Final Tails Area | 2.5 | 0.6/1 | 160 | 3C+E | Orange | 3
F23FN468LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F23FN468-LCS | FINAL TAILS PUMP 3 GEARBOX FAN LOCAL CONTROL STATION | Final Tails Area | 1.5 | 0.6/1 | 160 | 4C+E | Black | 3
F23FN469-P1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F23-FN-469 | FINAL TAILS PUMP 4 GEARBOX OIL AIR COOLING FAN | Final Tails Area | 2.5 | 0.6/1 | 160 | 3C+E | Orange | 3
F23FN469LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F23FN469-LCS | FINAL TAILS PUMP 4 GEARBOX FAN LOCAL CONTROL STATION | Final Tails Area | 1.5 | 0.6/1 | 165 | 4C+E | Black | 3
F24PW406-P1 | [6 empty] | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails 415V Switchroom | F24-PW-406 | RAW WATER PUMP 1 | Raw Water Area | 120 | 0.6/1 | 85 | 3C+E | Orange | 3
F24PW406-P2 | [6 empty] | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails 415V Switchroom | F24-PW-406 | RAW WATER PUMP 1 | Raw Water Area | 120 | 0.6/1 | 85 | 3C+E | Orange | 3
F24PW406-P3 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails 415V Switchroom | F24-PW-406 | RAW WATER PUMP 1 SPACE HEATER | Raw Water Area | 2.5 | 0.6/1 | 85 | 2C+E | Orange | 3
F24PW406-I1 | [6 empty] | Cu | PVC/OSCN/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails 415V Switchroom | F24-PW-406 | RAW WATER PUMP 1 THERMISTOR | Raw Water Area | 1.5 | 0.11 | 85 | 1PR | Black | 3
F24PW406LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails 415V Switchroom | F24PW406-LCS | RAW WATER PUMP 1 LOCAL CONTROL STATION | Raw Water Area | 1.5 | 0.6/1 | 85 | 4C+E | Black | 3
F24PW407-P1 | [6 empty] | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails 415V Switchroom | F24-PW-407 | RAW WATER PUMP 2 | Raw Water Area | 120 | 0.6/1 | 85 | 3C+E | Orange | 3
F24PW407-P2 | [6 empty] | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails 415V Switchroom | F24-PW-407 | RAW WATER PUMP 2 | Raw Water Area | 120 | 0.6/1 | 85 | 3C+E | Orange | 3
F24PW407-P3 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails 415V Switchroom | F24-PW-407 | RAW WATER PUMP 2 SPACE HEATER | Raw Water Area | 2.5 | 0.6/1 | 85 | 2C+E | Orange | 3
F24PW407-I1 | [6 empty] | Cu | PVC/OSCN/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails 415V Switchroom | F24-PW-407 | RAW WATER PUMP 2 THERMISTOR | Raw Water Area | 1.5 | 0.11 | 85 | 1PR | Black | 3
F24PW407LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails 415V Switchroom | F24PW407-LCS | RAW WATER PUMP 2 LOCAL CONTROL STATION | Raw Water Area | 1.5 | 0.6/1 | 85 | 4C+E | Black | 3
F24PW408-P1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F24-PW-408 | LP GLAND SEAL WATER PUMP 1 | Raw Water Area | 16 | 0.6/1 | 100 | 3C+E | Orange | 3
F24PW408LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F24PW408-LCS | LP GLAND SEAL WATER PUMP 1 LOCAL CONTROL STATION | Raw Water Area | 1.5 | 0.6/1 | 100 | 4C+E | Black | 3
F24PW409-P1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F24-PW-409 | LP GLAND SEAL WATER PUMP 2 | Raw Water Area | 16 | 0.6/1 | 100 | 3C+E | Orange | 3
F24PW409LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F24PW409-LCS | LP GLAND SEAL WATER PUMP 2 LOCAL CONTROL STATION | Raw Water Area | 1.5 | 0.6/1 | 100 | 4C+E | Black | 3
F24PW419-P1 | [6 empty] | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F24-PW-419 | HP GLAND SEAL WATER PUMP 1 | Raw Water Area | 120 | 0.6/1 | 95 | 3C+E | Orange | 3
F24PW419-P2 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F24-PW-419 | HP GLAND SEAL WATER PUMP 1 SPACE HEATER | Raw Water Area | 2.5 | 0.6/1 | 95 | 2C+E | Orange | 3
F24PW419-I1 | [6 empty] | Cu | PVC/OSCN/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F24-PW-419 | HP GLAND SEAL WATER PUMP 1 THERMISTOR | Raw Water Area | 1.5 | 0.11 | 95 | 1PR | Black | 3
F24PW419LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F24PW419-LCS | HP GLAND SEAL WATER PUMP 1 LOCAL CONTROL STATION | Raw Water Area | 1.5 | 0.6/1 | 95 | 4C+E | Black | 3
F24PW420-P1 | [6 empty] | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F24-PW-420 | HP GLAND SEAL WATER PUMP 2 | Raw Water Area | 120 | 0.6/1 | 95 | 3C+E | Orange | 3
F24PW420-P2 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F24-PW-420 | HP GLAND SEAL WATER PUMP 2 SPACE HEATER | Raw Water Area | 2.5 | 0.6/1 | 95 | 2C+E | Orange | 3
F24PW420-I1 | [6 empty] | Cu | PVC/OSCN/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F24-PW-420 | HP GLAND SEAL WATER PUMP 2 THERMISTOR | Raw Water Area | 1.5 | 0.11 | 95 | 1PR | Black | 3
F24PW420LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-123 | FINAL TAILS PUMPS EMERGENCY 415V MCC | Final Tails 415V Switchroom | F24PW420-LCS | HP GLAND SEAL WATER PUMP 2 LOCAL CONTROL STATION | Raw Water Area | 1.5 | 0.6/1 | 95 | 4C+E | Black | 3
F24PW451-P1 | [6 empty] | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | FINAL TAILS PUMPS 415V MCC | Final Tails 415V Switchroom | F24-PW-451 | RAW WATER FEED BOOSTER PUMP 1 | Event Pond Area | 95 | 0.6/1 | 175 | 3C+E | Orange | 3
F24PW451-I1 | [6 empty] | Cu | PVC/OSCN/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | FINAL TAILS PUMPS 415V MCC | Final Tails 415V Switchroom | F24-PW-451 | RAW WATER FEED BOOSTER PUMP 1 THERMISTOR | Event Pond Area | 1.5 | 0.11 | 175 | 1PR | Black | 3
F24PW451LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | FINAL TAILS PUMPS 415V MCC | Final Tails 415V Switchroom | F24PW451-LCS | RAW WATER FEED BOOSTER PUMP 1 LOCAL CONTROL STATION | Event Pond Area | 1.5 | 0.6/1 | 175 | 4C+E | Black | 3
F24PW452-P1 | [6 empty] | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | FINAL TAILS PUMPS 415V MCC | Final Tails 415V Switchroom | F24-PW-452 | RAW WATER FEED BOOSTER PUMP 2 | Event Pond Area | 95 | 0.6/1 | 175 | 3C+E | Orange | 3
F24PW452-I1 | [6 empty] | Cu | PVC/OSCN/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | FINAL TAILS PUMPS 415V MCC | Final Tails 415V Switchroom | F24-PW-452 | RAW WATER FEED BOOSTER PUMP 2 THERMISTOR | Event Pond Area | 1.5 | 0.11 | 175 | 1PR | Black | 3
F24PW452LCS-C1 | [6 empty] | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 |  |  |  |  | F23-SW-023 | FINAL TAILS PUMPS 415V MCC | Final Tails 415V Switchroom | F24PW452-LCS | RAW WATER FEED BOOSTER PUMP 2 LOCAL CONTROL STATION | Event Pond Area | 1.5 | 0.6/1 | 175 | 4C+E | Black | 3