## Equipment list
Rev | Equip. Number | Equipment Name | Qty | Description | Make | Model | Supplied By | Installed By | Comments | Page
0 0 | F23-SR-001 - | Final Tails Pumps 11kV Switchroom Final Tails Pumps 11kV / 415V Switchroom Landings and Stairs | 1 1 | Transportable switchroom complete with 1.8m legs and landings, transported to site 600kms on sealed roads. Equipment Landing to be structural steel baseframe complete with 1.8m legs and landings, designed to support heaviest piece of equipment to be installed in room. | Switchroom Vendor Switchroom Vendor | VTA VTA | Switchroom/MCC Vendor Switchroom/MCC Vendor | Primero Primero | F23-SR-001, F23-SR-002, Transformer room(s) and Air Lock are all part of the same building | 2
0 | F23-SW-016 | Final Tails Pumps 11kV Switchboard | 1 | Metal clad, partition metal, 11kV switchboard. 1250A bus, 25kA/3s fault rating. Internally arc fault contained AFLR. With top mount arc absorbing duct on top - no arc vent to outdoors. 1 x VT & Earth Switch panel, 1 x Incomer panel, 8 x Feeder panels | ABB | UniGear ZS1 | Primero | Switchroom/MCC Vendor | Refer 2000-EL003-B02-10009 (Panel Arrangement), 2000-EL003-B03- 10003 (Section View), 2000-EL003-C01-10008 (Foundation Frame Detail), 2000-EL003-C03-10007 (Foundation Layout), 2000-EL003-D01- 10003 (SLD) 2000-F00-DSH-EL-11003 11kV Datasheet Switchboard Dimensions (W = 6560mm, H = 2533mm, D = 1340mm) approx. weight 8500kg | 2
1 | F23-DB-101 | Final Tails Pumps 11kV Switchroom HV VSD Auxiliary Supplies Distribution Board | 1 | 415V 3Ø 250A DB. Fitted with incoming isolator, and DB Legend. selector. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-EL-10025 & 2000-F00-STD-EL- 10022; Switchroom Vendor to calculate number of required poles including the number of circuits for Air conditioners, 20% loaded Spare circuit breakers and 20% spare space. | 2
0 | F23PP466-VS | Final Tails Pump 1 HV VSD | 1 | 800kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens |  | Primero |  |  | 2
0 | F23PP467-VS | Final Tails Pump 2 HV VSD | 1 | 800kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens |  | Primero |  |  | 2
0 | F23PP468-VS | Final Tails Pump 3 HV VSD | 1 | 800kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens |  | Primero |  |  | 2
0 | F23PP469-VS | Final Tails Pump 4 HV VSD | 1 | 800kW, 11kV input, 3.3kV output Variable Speed Drive. | Siemens |  | Primero |  |  | 2
0 0 | F23-BA-001 F23-BC-001 | Final Tails Pumps 11kV Switchroom 48VDC Battery Final Tails Pumps 11kV Switchroom 48VDC Charger | 1 1 | 48V DC Tripping and Closing Supply, 400Ah battery bank. Free-standing industrial cabinet. 48V DC Tripping and Closing Supply, with 100A charger complete with integral DB. Free-standing industrial cabinet. | Magellan Magellan | 2 string of 4 x 12V, 200Ah VRLA batteries 48MCRII3P100 | Switchroom/MCC Vendor Switchroom/MCC Vendor | Switchroom/MCC Vendor Switchroom/MCC Vendor | 1 x U220 Battery enclosure (W:800mm, D: 800mm, H: 2200mm). IP-42, Bottom cable entry, 5mm Aluminium gland plate complete with 2 strings of 4 X 12V 200Ah VRLA Batteries. And all associated accessories. 1 x U220 Battery enclosure (W:800mm, D: 800mm, H: 2200mm). 100A MCRII 3 Phase input charger. Compete with: Alarm relay board (voltage free alarm relays, including Floating Earth Fault). Blocking Diode Communications Board (For Modbus TCP) Including Lifting lugs, battery test facility, 1 hour battery discharge test, and integrated DC DB with 8 off 2P, 20A MCBs and 1 spare MCB with shunt trip | 2
0 | F23FIP001-XE2 |  | VTA |  | Wormald | Manual Call Points |  |  | Manual call points shall be tagged in sequential order (e.g. F23FIP001- | 2
0 | F23FIP001-XE3 |  | VTA |  | Wormald | Addressable Optical |  |  | XE11, F23FIP001-XE12, etc.) | 2
0 | F23FIP001-XE4 |  | VTA |  | Wormald | Addressable Optical |  |  | Detectors shall be tagged in sequential order (e.g. F23FIP001-XE21, | 2
0 | F23FIP001-UA |  | VTA |  | Wormald | External Sounder / Red Strobe |  |  | F23FIP001-XE22, etc.) | 2
0 | - |  | VTA |  | VTA | VTA |  |  | Detectors shall be tagged in sequential order (e.g. F23FIP001-XE31, | 2
0 | - |  | 1 |  | Physio Control | Lifepak Defibrillator CR2 Fully Automatic |  |  | F23FIP001-XE32, etc.) | 2
0 | - |  | 1 |  | VTA | VTA |  |  | Alarm sirens shall be tagged in sequential order (e.g. F23FIP001-UA01, | 2
0 | - |  | 1 |  | VTA | VTA |  |  | F23FIP001-UA02, etc.) | 2
0 |  |  | VTA | Wall mounted Air Conditioner Controller, with relay contacts for Faulty & Healthy | VTA | VTA |  |  |  | 3
2 |  |  | VTA | High Wall split system, single phase, MULTIPLE (N+1 reqd) with drip trays if necessary | VTA | VTA |  |  |  | 3
2 |  |  | VTA | Field isolator, one per split system Air Conditioner | VTA | VTA |  |  |  | 3
0 |  |  | 1 lot | Lighting to meet National Construction Code | VTA | VTA |  |  |  | 3
0 |  |  | 1 lot | Lighting to meet National Construction Code; C/w built in battery pack. | VTA | VTA |  |  |  | 3
0 |  |  | 1 lot | Lighting to meet National Construction Code | VTA | VTA |  |  |  | 3
0 |  |  | 1 | Switchroom Temperature/Humidity Transmitter | VTA | VTA |  |  |  | 3
1 | F23SW016-LCS | Final Tails Pumps 11kV Switchboard Remote Switching Panel | 1 | IP65 Enclosure, hinged, lockable, clear perspex escutcheon cover over operator interfaces to prevent inadvertent/unauthorised operation. Remote Switching Local control station (visual mimic and control of CBs, VSD Contactors, earth switches) with door mounted selector switches providing open/close functionality for CBs, Contactors and earth switches, rack in/rack out functionality of circuit breakers and contactors and indication lights for status. Provided with the following for each panel type: Bus VT & Earth Switch Panels (1 off) • 1 off Earth Switch Indicator (RD/GN) • 1 off VT Rack Indicator (RD/GN) • 1 off 3-position Selector Switches • 1 off 2-position Selector Switches Fused Contactor Feeder Panels (5 off) • 3 off Contactor/Earth Switch Indicators (RD/GN) • 1 off Fused Contactor Racked In/Racked Out Indicators (RD/GN) • 3 off 3-position Selector Switches • 1 off 2-position Selector Switches Incomer & CB Feeder Panels (4 off) • 3 off Circuit Breaker/Earth Switch Indicators (RD/GN) • 1 off CB Racked In/Racked Out Indicators (RD/GN) • 3 off 3-position Selector Switches • 1 off 2-position Selector Switches | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Typical Schematics & GA to be provided to Switchroom Vendor to design and fabricate panel. | 3
0 | F23SW016-EB01 | Final Tails Pumps 11kV Switchboard Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on insulated standoffs inside Switchboard. | TBC | TBC | Primero | Switchroom/MCC Vendor |  | 3

## Cable schedule
Cable Number | From Equip. Number | To Equip. Number | ductor Size (m | nsulaNon(kV) | No. of Cores / Pair | s Conductor | Sheath (Preferred colour) | Installation | Supplied By | Installed By | Revision | To Equipment Name | Construction | From Equipment Name | Conductor Size (mm2) | Insulation (kV) | No. of Cores / Pairs | Conductor | Sheath (Preferred Colour) | Page
F23BC001-P1 | F23-DB-001 | F23-BC-001 | 6 | 0.6/1 | 4C+E | Cu | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | [8 empty] | 4
F23BA001-P1-R | F23-BC-001 | F23-BA-001 | 35 | 0.6/1 | 1C | Cu | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | [8 empty] | 4
F23BA001-P1-B | F23-BC-001 | F23-BA-001 | 35 | 0.6/1 | 1C | Cu | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | [8 empty] | 4
F23SW016-P2 | F23-BC-001 | F23-SW-016 | 6 | 0.6/1 | 2C+E | Cu | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | [8 empty] | 4
F23SW016LCS-P1 | F23-BC-001 | F23SW016-LCS | 4 | 0.6/1 | 2C+E | Cu | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | [8 empty] | 4
F23SW016-P3 | F23-DB-001 | F23-SW-016 | 4 | 0.6/1 | 2C+E | Cu | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | [8 empty] | 4
F23DB101-P1 | F23-SW-023 | F23-DB-101 | 95 | 0.6/1 | 4C+E | Cu | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | [8 empty] | 4
F23PP466VS-P1-R | F23-SW-016 | F23PP466-VS | 50 | 11 | 1C | Cu | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | [8 empty] | 4
F23PP466VS-P1-W | F23-SW-016 | F23PP466-VS | 50 | 11 | 1C | Cu | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | [8 empty] | 4
F23PP466VS-P1-B | F23-SW-016 | F23PP466-VS | 50 | 11 | 1C | Cu | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | [8 empty] | 4
F23PP466VS-P2 | F23-DB-101 | F23PP466-VS | 6 | 0.6/1 | 4C+E | Cu | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | [8 empty] | 4
F23PP466VS-P3 | F23-DB-201 | F23PP466-VS | 2.5 | 0.6/1 | 2C+E | Cu | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | [8 empty] | 4
F23PP467VS-P1-R | F23-SW-016 | F23PP467-VS | 50 | 11 | 1C | Cu | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | [8 empty] | 4
F23PP467VS-P1-W | F23-SW-016 | F23PP467-VS | 50 | 11 | 1C | Cu | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | [8 empty] | 4
F23PP467VS-P1-B | F23-SW-016 | F23PP467-VS | 50 | 11 | 1C | Cu | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | [8 empty] | 4
F23PP467VS-P2 | F23-DB-101 | F23PP467-VS | 6 | 0.6/1 | 4C+E | Cu | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | [8 empty] | 4
F23PP467VS-P3 | F23-DB-201 | F23PP467-VS | 2.5 | 0.6/1 | 2C+E | Cu | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | [8 empty] | 4
F23PP468VS-P1-R | F23-SW-016 | F23PP468-VS | 50 | 11 | 1C | Cu | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | [8 empty] | 4
F23PP468VS-P1-W | F23-SW-016 | F23PP468-VS | 50 | 11 | 1C | Cu | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | [8 empty] | 4
F23PP468VS-P1-B | F23-SW-016 | F23PP468-VS | 50 | 11 | 1C | Cu | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | [8 empty] | 4
F23PP468VS-P2 | F23-DB-101 | F23PP468-VS | 6 | 0.6/1 | 4C+E | Cu | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | [8 empty] | 4
F23PP468VS-P3 | F23-DB-201 | F23PP468-VS | 2.5 | 0.6/1 | 2C+E | Cu | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | [8 empty] | 4
F23PP469VS-P1-R | F23-SW-016 | F23PP469-VS | 50 | 11 | 1C | Cu | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | [8 empty] | 4
F23PP469VS-P1-W | F23-SW-016 | F23PP469-VS | 50 | 11 | 1C | Cu | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | [8 empty] | 4
F23PP469VS-P1-B | F23-SW-016 | F23PP469-VS | 50 | 11 | 1C | Cu | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | [8 empty] | 4
F23PP469VS-P2 | F23-DB-101 | F23PP469-VS | 6 | 0.6/1 | 4C+E | Cu | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | [8 empty] | 4
F23PP469VS-P3 | F23-DB-201 | F23PP469-VS | 2.5 | 0.6/1 | 2C+E | Cu | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | [8 empty] | 4
F23SW016-C12 | F23SR001-LCS | F23-SW-016 | 1.5 | 0.15 | 4C+E | Cu | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pumps 11kV Switchboard Panel 04 | PVC/PVC | [6 empty] | 4
F23SW016-C1 | F23SW016-LCS | F23-SW-016 | 1.5 | 0.6/1 | 15C+E | Cu | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Final Tails Pumps 11kV Switchboard Panel 01 | PVC/PVC | [6 empty] | 4
F23SW016-C13 | F23-DCS-409 | F23-SW-016 | 1.5 | 0.6/1 | 10C+E | Cu | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | Final Tails Pumps 11kV Switchboard Panel 01 | PVC/PVC | [6 empty] | 4
F23SW016-C2 | F23SW016-LCS | F23-SW-016 | 1.5 | 0.6/1 | 30C+E | Cu | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Final Tails Pumps 11kV Switchboard Panel 02 | PVC/PVC | [6 empty] | 4
F23SW016-C3 | F23SW016-LCS | F23-SW-016 | 1.5 | 0.6/1 | 30C+E | Cu | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Final Tails Pumps 11kV Switchboard Panel 03 | PVC/PVC | [6 empty] | 4
F23SW016-C4 | F23SW016-LCS | F23-SW-016 | 1.5 | 0.6/1 | 30C+E | Cu | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Final Tails Pumps 11kV Switchboard Panel 04 | PVC/PVC | [6 empty] | 4
F23SW016-C5 | F23-DCS-409 | F23-SW-016 | 1.5 | 0.6/1 | 4C+E | Cu | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pumps 11kV Switchboard Panel 04 | PVC/PVC | [6 empty] | 4
F23SW016-C6 | F23SW016-LCS | F23-SW-016 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | PVC/PVC | Final Tails Pumps 11kV Switchboard Remote Switching Panel | 1.5 | 0.6/1 | 30C+E | Cu | Black | 5
F23SW016-C7 | F23SW016-LCS | F23-SW-016 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | PVC/PVC | Final Tails Pumps 11kV Switchboard Remote Switching Panel | 1.5 | 0.6/1 | 30C+E | Cu | Black | 5
F23SW016-C8 | F23SW016-LCS | F23-SW-016 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | PVC/PVC | Final Tails Pumps 11kV Switchboard Remote Switching Panel | 1.5 | 0.6/1 | 30C+E | Cu | Black | 5
F23SW016-C9 | F23SW016-LCS | F23-SW-016 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | PVC/PVC | Final Tails Pumps 11kV Switchboard Remote Switching Panel | 1.5 | 0.6/1 | 30C+E | Cu | Black | 5
F23SW016-C10 | F23SW016-LCS | F23-SW-016 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | PVC/PVC | Final Tails Pumps 11kV Switchboard Remote Switching Panel | 1.5 | 0.6/1 | 30C+E | Cu | Black | 5
F23SW016-C11 | F23SW016-LCS | F23-SW-016 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | PVC/PVC | Final Tails Pumps 11kV Switchboard Remote Switching Panel | 1.5 | 0.6/1 | 30C+E | Cu | Black | 5
F23PP466VS-C1 | F23-SW-016 | F23PP466-VS | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | PVC/PVC | Final Tails Pumps 11kV Switchboard | 1.5 | 0.6/1 | 10C+E | Cu | Black | 5
F23PP467VS-C1 | F23-SW-016 | F23PP467-VS | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | PVC/PVC | Final Tails Pumps 11kV Switchboard | 1.5 | 0.6/1 | 10C+E | Cu | Black | 5
F23PP468VS-C1 | F23-SW-016 | F23PP468-VS | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | PVC/PVC | Final Tails Pumps 11kV Switchboard | 1.5 | 0.6/1 | 10C+E | Cu | Black | 5
F23PP469VS-C1 | F23-SW-016 | F23PP469-VS | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | PVC/PVC | Final Tails Pumps 11kV Switchboard | 1.5 | 0.6/1 | 10C+E | Cu | Black | 5
UT23500-I1 | F23-DCS-409 | UT23500 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | PVC/IOSCN/PVC | Final Tails Pumps 415V Switchroom DCS Panel | 1.5 | 0.15 | 2 pr | Cu | Black | 5
F23BC001-C1 | F23-DCS-409 | F23-BC-001 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | PVC/PVC | Final Tails Pumps 415V Switchroom DCS Panel | 1.5 | 0.6/1 | 4C+E | Cu | Black | 5
F23SW016-D1 | F23-COM-001 | F23-SW-016 | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pumps 11kV Switchboard Panel 04 (Incomer) - SEL 751 | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23SW016-D2 | F23-COM-001 | F23-SW-016 | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pumps 11kV Switchboard Panel 04 (Incomer) - SEL 735 | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23SW016-D3 | F23-COM-001 | F23-SW-016 | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pumps 11kV Switchboard Panel 02 - SEL 751 | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23SW016-D4 | F23-COM-001 | F23-SW-016 | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pumps 11kV Switchboard Panel 03 - SEL 751 | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23SW016-D5 | F23-COM-001 | F23-SW-016 | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pumps 11kV Switchboard Panel 05 - SEL 751 | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23SW016-D6 | F23-COM-001 | F23-SW-016 | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pumps 11kV Switchboard Panel 06 - SEL 751 | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23SW016-D7 | F23-COM-001 | F23-SW-016 | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pumps 11kV Switchboard Panel 07 - SEL 751 | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23SW016-D8 | F23-COM-001 | F23-SW-016 | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pumps 11kV Switchboard Panel 08 - SEL 751 | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23SW016-D9 | F23-COM-001 | F23-SW-016 | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pumps 11kV Switchboard Panel 09 - SEL 751 | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23SW016-D10 | F23-COM-001 | F23-SW-016 | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pumps 11kV Switchboard Panel 10 - SEL 751 | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23PP466VS-D1 | F23-COM-001 | F23PP466-VS | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pump 1 HV VSD | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23PP467VS-D1 | F23-COM-001 | F23PP467-VS | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pump 2 HV VSD | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23PP468VS-D1 | F23-COM-001 | F23PP468-VS | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pump 3 HV VSD | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23PP469VS-D1 | F23-COM-001 | F23PP469-VS | [6 empty] | Switchroom Vendor | Switchroom Vendor | 0 | Final Tails Pump 4 HV VSD | CAT6A (Shielded) | Final Tails Pumps 415V Switchroom Communications Rack | N/A | N/A | 4 pr | Cu | Green | 5
F23SW016EB01-E1 | F23SR001-EB01 | F23SW016-EB01 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 120 | 0.6 | 1C | Cu | Green/Yellow | 5
F23SW016EB01-E2 | F23SR001-EB01 | F23SW016-EB01 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 120 | 0.6 | 1C | Cu | Green/Yellow | 5
F23PP466VS-E1 | F23SR001-EB01 | F23PP466-VS | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 120 | 0.6 | 1C | Cu | Green/Yellow | 5
F23PP467VS-E1 | F23SR001-EB01 | F23PP467-VS | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 120 | 0.6 | 1C | Cu | Green/Yellow | 5
F23PP468VS-E1 | F23SR001-EB01 | F23PP468-VS | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 120 | 0.6 | 1C | Cu | Green/Yellow | 5
F23PP469VS-E1 | F23SR001-EB01 | F23PP469-VS | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 120 | 0.6 | 1C | Cu | Green/Yellow | 5
F23BA001-E1 | F23SR001-EB01 | F23-BA-001 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 16 | 0.6 | 1C | Cu | Green/Yellow | 5
F23BC001-E1 | F23SR001-EB01 | F23-BC-001 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 16 | 0.6 | 1C | Cu | Green/Yellow | 5
F23DB101-E1 | F23SR001-EB01 | F23-DB-101 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 95 | 0.6 | 1C | Cu | Green/Yellow | 5
F23SW016LCS-E1 | F23SR001-EB01 | F23SW016-LCS | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 16 | 0.6 | 1C | Cu | Green/Yellow | 5
F23SR001-E3 | F23SR001-EB01 | F23-SR-001 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 35 | 0.6 | 1C | Cu | Green/Yellow | 5
F23SR001-E4 | F23SR001-EB01 | F23-SR-001 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | Subfloor Cable Ladder | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 35 | 0.6 | 1C | Cu | Green/Yellow | 6
Ladder Joint Bonds | F23-SR-001 | F23-SR-001 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | Subfloor Cable Ladder | PVC | Subfloor Cable Ladder | 35 | 0.6 | 1C | Cu | Green/Yellow | 6
F23SR001-E1 | F23SR001-EB01 | F23-SR-001 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | Switchroom Subframe | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 70 | 0.6 | 1C | Cu | Green/Yellow | 6
F23SR001-E2 | F23SR001-EB01 | F23-SR-001 | [5 empty] | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | Switchroom Subframe | PVC | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 70 | 0.6 | 1C | Cu | Green/Yellow | 6