## Equipment list
Rev | Equip. Number | Equipment Name | Qty | Description | Make | Model | Supplied By | Installed By | Comments | Page
0 | F23-SR-002 | Final Tails Pumps 415V Switchroom | 1 | Transportable switchroom complete with 1.8m legs and landings, transported to site 600kms on sealed roads. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero | F23-SR-001, F23-SR-002, Transformer room(s) and Air Lock are all part of the same building Refer 2000-F00-DSH-EL-11001 | 2
0 | - | Final Tails Pumps 415V MCC Transformer Enclosure Room | 1 | Separate dry transformer enclosure with removable wall panel and personnel access door. Personnel entry door shall be fortress key locked (keyed alike) with upstream feeder earth switch on F00-SW-010 33kV Switchboard. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero | Access to transformer cubicle is only possible with 33kV Feeder isolated and earthed. Switchroom manufacturer to coordinate Fortress keys with TEKSAL. | 2
0 | - | Final Tails Pumps 415V MCC Transformer Enclosure Room Signage | 1 | TRANSFORMER ENCLOSURE F23-TR-023 33,000/433 VOLTS (Modify to suit) DANGER – HIGH VOLTAGE (with the lightning bolt sign) NO UNAUTHORISED ACCESS – ENSURE SUPPLY IS ISOLATED AND EARTHED PRIOR TO ENTRY ISOLATE AT F00-SW-010, PANEL BXX (BXX being the 33kV panel/tier number) | Switchroom Vendor |  | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Signage to be placed on outside of transformer enclosure | 2
0 | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | 1 | 33/0.433kV, 1000kVA, ANAF | Siemens | 33/0.433kV 1000kVA | Primero | Switchroom/MCC Vendor | Vendor to remove wheels and secure transformer once installed. Wheels to be stored securely within the transformer room. Vendor to bolt down/brace for transport. Refer transformer GAs. | 2
0 | F23-SW-023 | Final Tails Pumps 415V MCC | 1 | Demountable Form 4a double sided 415V Switchboard, 1600A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Vendor to install free issued network switches in MCC Refer datasheet 2000-F00-DSH-EL-11008 | 2
0 | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | 1 | Demountable Form 4a single sided 415V Emergency Switchboard, 630A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Refer datasheet 2000-F00-DSH-EL-11012 | 2
0 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | 1 | 415V 3Ø 250A DB. Fitted with incoming isolator, PE Cell circuit (night/day), Auto / Manual selector, Emergency light test controller, Rapidtest RCD test units, Lighting Contactors, air conditioner Contactors and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-EL-10025 & 2000-F00-STD-EL-10022; Switchroom Vendor to calculate number of required poles including the number of circuits for Air conditioners, 20% loaded Spare circuit breakers and 20% spare space. | 2
0 | F23-DB-201 | Final Tails Pumps 415V Switchroom 240V UPS Distribution Board | 1 | 240V DC 250A UPS DB. Fitted with incoming isolator and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-EL-10027. Switchroom Vendor to calculate number of required poles including 20% loaded Spare circuit breakers and 20% spare space. | 2
0 | F23-UPS-002 | Final Tails Pumps 415V Switchroom 240VAC UPS | 1 | LV Switchroom 240V AC, 10kVA UPS, free-standing. 8 hours autonomy time. 3-Phase in / 1-Phase Out. | Riello | S3M 10 XTD A0 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 10kVA/10kW Sentryum Xtend UPS - 3 Phase in- 1 out. Vendor to secure wheels once installed. Vendor to bolt down/brace for transport. W: 440mm, D: 840mm, H: 1320mm, Weight: 103Kg | 2
0 | F23-BA-002 | Final Tails Pumps 415V Switchroom 240VAC UPS Battery Bank | 1 | UPS Battery Cabinet w/ 40 x 55Ah batteries | Riello | BB 1900 480-V5 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 480V Extension Battery Cabinet with 40 x 55Ah Long life batteries. Cabinet shipped empty with the batteries packed separately W: 860mm, D: 800mm, H: 1900mm, Weight: 900Kg | 2
0 | - | Final Tails Pumps 415V Switchroom 240VAC UPS Ethernet Card | 1 | Netman UPS Ethernet Card | Riello | Netman 208 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Supplied and installed into UPS by Switchroom Vendor | 2
0 | - | Final Tails Pumps 415V Switchroom 240VAC UPS Dry Contact Relay Card | 1 | Multicom Configurable Slot In Relay Card, 3 Inputs & 8 Outputs | Riello | Mulitcom 392 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Supplied and installed into UPS by Switchroom Vendor | 2
0 | F23UPS002-ISL | Final Tails Pumps 415V Switchroom 240VAC UPS Maintenance Bypass Switch | 1 | External Wall-mount UPS bypass switch. | Riello | WABS 0063A-31H | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Wall mounted rotary bypass switch. 3Ph in/1Ph out, 10kVA. Dimensions: 400 x 300 x 210mm | 2
0 | F23AG404-VS | Final Tails Tank Agitator LV VSD | 1 | Allen-Bradley 45 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: IP20, 20-HIM-A6, 20-750-APS, 20-750-S, 20-750- 20COMM + 20-COMM-M, , | Allen-Bradley | 20F11NC104JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | 1 | Communications Rack, Free Standing 19", 42U, 1000mm deep, Mesh door, Lift Off Side Panels. Fitted with 10 way 240VAC plug power distribution panel, wire management covers, shelves and cage nuts. Fitted out with FOBOTs (vendor supplied), DIN rail adapter (vendor supplied), and network switches (free issued). | Rittal | TS IT Enclosure (P/N 5514.110) + Accessories | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-IC-10101 | 2
1 | F23COM001-JB | Final Tails Pumps 415V Switchroom Communications Rack 240VAC UPS Junction Box | 1 | Junction box mounted on the rear of the communications rack. All 240VAC UPS powered non-RCD Protected outlets shall be red with a "Warning. Socket not RCD Protected" Warning label. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Junction box for PDU Rail | 2
0 | F23-FOB-001 | Final Tails Pumps 415V Switchroom Fibre Optic Breakout Tray (SP1) | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | 2
0 | F23-FOB-002 | Final Tails Pumps 415V Switchroom Fibre Optic Breakout Tray (SP1) | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | 2
0 | F23-FOB-003 | Final Tails Pumps 415V Switchroom Fibre Optic Breakout Tray (SP2) | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | 2
0 | F23-FOB-004A/B | Final Tails Pumps 415V Switchroom RIO Circuit Fibre Optic Breakout Ring 1 Tray #1 (SP 1) | 1 | 2 X 12C SMOF Capacity FOBOT C/W Splice hardware & 1-6 LC Duplex Faceplate (LHS) + 1-6 LC Duplex Faceplate (RHS) | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. One FOBOT with two 12C faceplates. Vendor to label each side as per equipment number and name. | 2
0 | F23-FOB-005A/B | Final Tails Pumps 415V Switchroom RIO Circuit Fibre Optic Breakout Ring 1 Tray #2 (SP 2) | 1 | 2 X 12C SMOF Capacity FOBOT C/W Splice hardware & 1-6 LC Duplex Faceplate (LHS) + 1-6 LC Duplex Faceplate (RHS) | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. One FOBOT with two 12C faceplates. Vendor to label each side as per equipment number and name. | 2
0 | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | 1 | Custom Built Panel. Contains DCS hardware, power supply, MCBs and marshalling terminals. | Fabricated Panel | Custom | Primero | Switchroom Vendor |  | 2
0 | F23SR001-LCS | Final Tails Pumps 11kV / 415V Switchroom Emergency Shutdown | 1 | Switchroom Emergency Shutdown C/w shroud or lift-up flap and labelling | Fabricated Panel | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | With E34 Red 40mm Mushroom pushbutton (P/N E34LB2), and 4 off 2 N/O Contact Blocks (10250T2). Refer 2000-F00-STS-EL-10011 Section 4.19. | 2
0 | F23-FIP-001 | Final Tails Pumps 11kV / 415V Switchroom Fire Indicator Panel | 1 | Fire Indicator Panel c/w full installation, wiring, certification, testing and commissioning. HVAC trip upon alarm. FIP shall include SMOF modem(s) for connection to site-wide fire system network. | Wormald | Vigilant 8 Zone F3200 Conventional SHCIE FIP | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Rated to operate in 50C ambience temperature | 3
0 | F23FIP001-XE1 | Final Tails Pumps 11kV / 415V Switchroom VESDA Panel | 1 | VESDA Panel c/w full installation, wiring, certification, testing and commissioning. Alarm and fault signals to fire panel. | Xtralis | VESDA LaserPlus Scanner 12 relay VLS300 ASD system | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Rated to operate in 50C ambience temperature | 3
0 | F23FIP001-XE2 | Final Tails Pumps 415V Switchroom Manual Call Points | VTA | Fire system Manual Call points (internal and external) as required by Australian Standards | Wormald | Manual Call Points | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Manual call points shall be tagged in sequential order (e.g. F23FIP001-XE11, F23FIP001-XE12, etc.) | 3
0 | F23FIP001-XE3 | Final Tails Pumps 415V Switchroom Smoke Detectors | VTA | Fire system smoke detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order (e.g. F23FIP001-XE21, F23FIP001-XE22, etc.) | 3
0 | F23FIP001-XE4 | Final Tails Pumps 415V Switchroom Heat Detectors | VTA | Fire system heat detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order (e.g. F23FIP001-XE31, F23FIP001-XE32, etc.) | 3
0 | F23FIP001-UA | Final Tails Pumps 415V Switchroom External Alarm Bell(s) | VTA | Fire system alarm bells as required by Australian Standards | Wormald | External Sounder / Red Strobe | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Alarm sirens shall be tagged in sequential order (e.g. F23FIP001-UA01, F23FIP001-UA02, etc.) | 3
0 | F23FIP001-XE5 | Final Tails Pumps 415V Switchroom Gas Suppression System (Inergen) | 1 | Inergen gas suppression system incl. all valves and pipework, gas cylinders placed inside switchroom, refer to Switchroom General Arrangement | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Final Tails Pumps 415V Switchroom Fire Extinguishers | VTA | 5kg carbon dioxide fire extinguishers complete with wall mount and signage. External Fire extinguishers to have UV resistant cover. | Physio Control | Lifepak Defibrillator CR2 Fully Automatic | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Final Tails Pumps 415V Switchroom Automatic External Defibrillator | 1 | Automatic external defibrillator complete with wall-mounted cabinet. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Final Tails Pumps 415V Switchroom LV Rescue Kit | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Final Tails Pumps 415V Switchroom CPR Signage | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Final Tails Pumps 11kV / 415V Switchroom HVAC Controller | VTA | Wall mounted Air Conditioner Controller, with relay contacts for Faulty & Healthy | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | One wall mounted controller to control all A/C's per room (One per transformer room, LV room, HV room). | 3
2 | F23-AC-0XX | Final Tails Pumps 415V Switchroom Air Conditioners | VTA | High Wall split system, single phase, MULTIPLE (N+1 reqd) with drip trays if necessary | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. AC units shall be tagged in numerical order (e.g. F23- AC-101, F23-AC-102 etc) | 3
2 | F23AC0XX-ISL | Final Tails Pumps 415V Switchroom Air Conditioner Isolators | VTA | Field isolator, one per split system Air Conditioner | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. AC units shall be tagged in numerical order (e.g. F23AC1XX-ISL, etc) | 3
0 | - | Final Tails Pumps 415V Switchroom Normal Light Fittings | 1 lot | Lighting to meet National Construction Code | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | 3
0 | - | Final Tails Pumps 415V Switchroom Emergency Light Fittings | 1 lot | Lighting to meet National Construction Code; C/w built in battery pack. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | 3
0 | - | Final Tails Pumps 415V Switchroom Exit Light Fittings | 1 lot | Lighting to meet National Construction Code | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | 3
0 | UT23501 | F23-SR-002 Final Tails Pumps 415V Switchroom Temperature/Humidity Transmitter | 1 | 415V Switchroom Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | 3
0 | UT23502 | F23-SR-002 Final Tails Pumps 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | 1 | Transformer Room Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | 3
0 | F23-PE-001 | Final Tails Pumps 11kV / 415V Switchroom Photo-electric Cell | 1 | Switchroom Photo-electric cell | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | PE Cell - 1 per building. Vendor to position | 3
0 | F23SW023-LCS | Final Tails Pumps 415V MCC Remote Switching Panel | 1 | LV MCC Incomer Remote Switching Panel | NHP | TemRack LCS | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | 1 | External to Room: 50 x 6.3mm Tinned Flat Copper Bus bar mounted on insulated standoffs under switchroom floor. Drilled/punch 12mm diameter holes suitable for connection of all internal equipment earth cables to meet requirements of cable schedule. To have spare capacity for connection of an additional 4 x 120mm2 conductors and 4 x 70mm2 conductors, as a minimum. | GVK or similar | - | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | F23TR023-EB01 | Final Tails Pumps 415V MCC Transformer Earth Bar Earth Bar | 1 | 50 x 6.3mm Tinned Flat Copper Bus bar mounted on standoffs on the Transformer. | Generic |  | Transformer Vendor | Transformer Vendor |  | 3
0 | F23SW023-EB01 | Final Tails Pumps 415V MCC Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on insulated standoffs inside MCC. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | F23SW123-EB01 | Final Tails Pumps Emergency 415V MCC Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on insulated standoffs inside MCC. | VTA | VTA | Switchroom Vendor | Switchroom Vendor |  | 3

## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred Colour) | Installation | Supplied By | Installed By | Revision | Comments | Page
F23SW023-P1-R | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F23SW023-P1-W | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F23SW023-P1-B | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F23SW023-P2-R | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F23SW023-P2-W | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F23SW023-P2-B | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F23SW023-P3-R | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F23SW023-P3-W | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F23SW023-P3-B | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe, in Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F23SW023-N1 | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 4
F23SW023-N2 | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 4
F23SW023-N3 | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 4
F23SW123-P1 | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | Final Tails Pumps 415V Switchroom | 95 | 0.6/1 | 1C | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23SW123-P2 | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | Final Tails Pumps 415V Switchroom | 95 | 0.6/1 | 1C | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23SW123-P3 | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | Final Tails Pumps 415V Switchroom | 95 | 0.6/1 | 1C | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23SW123-P4 | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | Final Tails Pumps 415V Switchroom | 95 | 0.6/1 | 1C | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23AG404VS-P1 | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | Final Tails Pumps 415V Switchroom | F23AG404-VS | Final Tails Tank Agitator LV VSD | Final Tails Pumps 415V Switchroom | 35 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | 4
F23DB001-P1 | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | Final Tails Pumps 415V Switchroom | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | 150 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | Flexible cable. Was 120mm2, change to 150mm2 based on 250A breaker. | 4
F23UPS002ISL-P1 | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | Final Tails Pumps 415V Switchroom | F23UPS002-ISL | Final Tails Pumps 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Final Tails Pumps 415V Switchroom | 16 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | MCC to Bypass Switch. | 4
F23UPS002-P1 | F23UPS002-ISL | Final Tails Pumps 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Final Tails Pumps 415V Switchroom | F23-UPS-002 | Final Tails Pumps 415V Switchroom 240VAC UPS | Final Tails Pumps 415V Switchroom | 10 | 0.6/1 | 4C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | Bypass Switch to UPS. | 4
F23UPS002ISL-P2 | F23-UPS-002 | Final Tails Pumps 415V Switchroom 240VAC UPS | Final Tails Pumps 415V Switchroom | F23UPS002-ISL | Final Tails Pumps 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Final Tails Pumps 415V Switchroom | 10 | 0.6/1 | 2C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | UPS to Bypass Switch | 4
F23BA002-P1 | F23-UPS-002 | Final Tails Pumps 415V Switchroom 240VAC UPS | Final Tails Pumps 415V Switchroom | F23-BA-002 | Final Tails Pumps 415V Switchroom 240VAC UPS Battery Bank | Final Tails Pumps 415V Switchroom | 10 | 0.6/1 | 3C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23DB201-P1 | F23UPS002-ISL | Final Tails Pumps 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Final Tails Pumps 415V Switchroom | F23-DB-201 | Final Tails Pumps 415V Switchroom 240V UPS Distribution Board | Final Tails Pumps 415V Switchroom | 16 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Bypass Switch to UPS DB | 4
F23DCS409-P1 | F23-DB-201 | Final Tails Pumps 415V Switchroom 240V UPS Distribution Board | Final Tails Pumps 415V Switchroom | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | 4
F23COM001-P1 | F23-DB-201 | Final Tails Pumps 415V Switchroom 240V UPS Distribution Board | Final Tails Pumps 415V Switchroom | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | PDU | 4
F23SW023-P4 | F23-DB-201 | Final Tails Pumps 415V Switchroom 240V UPS Distribution Board | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | MCC PSU 1 | 4
F23SW023-P5 | F23-DB-201 | Final Tails Pumps 415V Switchroom 240V UPS Distribution Board | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | MCC PSU 2 | 4
F23TR023-P2 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | 240V for transformer cooling fans. | 4
F23FIP001-P1 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP DB | Final Tails Pumps 415V Switchroom | F23-FIP-001 | Final Tails Pumps 11kV / 415V Switchroom Fire Indicator Panel | Final Tails Pumps 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23FIP001XE1-P1 | F23-FIP-001 | Final Tails Pumps 11kV / 415V Switchroom Fire Indicator Panel | Final Tails Pumps 415V Switchroom | F23FIP001-XE1 | Final Tails Pumps 11kV / 415V Switchroom VESDA Panel | Final Tails Pumps 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23DB001-R13 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC001-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 1 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23AC001-P1 | F23AC001-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 1 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-001 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 1 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23DB001-W13 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC002-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 2 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23AC002-P1 | F23AC002-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 2 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-002 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 2 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23DB001-B13 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC003-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 3 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23AC003-P1 | F23AC003-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 3 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-003 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 3 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23DB001-R15 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC004-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 4 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F23AC004-P1 | F23AC004-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 4 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-004 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 4 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-W15 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC005-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 5 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23AC005-P1 | F23AC005-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 5 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-005 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 5 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-B15 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC006-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 6 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23AC006-P1 | F23AC006-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 6 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-006 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 6 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-R17 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC007-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 7 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23AC007-P1 | F23AC007-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 7 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-007 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 7 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-W17 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC008-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 8 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23AC008-P1 | F23AC008-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 8 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-008 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 8 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-B17 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC009-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 9 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23AC009-P1 | F23AC009-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 9 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-009 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 9 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-R14 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC010-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 10 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23AC010-P1 | F23AC010-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 10 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-010 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 10 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-W14 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC011-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 11 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23AC011-P1 | F23AC011-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 11 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-011 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 11 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-B14 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC012-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 12 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23AC012-P1 | F23AC012-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 12 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-012 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 12 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-R16 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC013-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 13 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23AC013-P1 | F23AC013-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 13 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-013 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 13 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-W16 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC014-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 14 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23AC014-P1 | F23AC014-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 14 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-014 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 14 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-B16 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC015-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 15 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23AC015-P1 | F23AC015-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 15 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-015 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 15 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-R18 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | F23AC016-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 16 Isolator | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23AC016-P1 | F23AC016-ISL | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 16 Isolator | Final Tails Pumps 415V Switchroom | F23-AC-016 | Final Tails Pumps 11kV / 415V Switchroom Air Conditioner No. 16 | Final Tails Pumps 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-R11 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom |  | Lighting - Switchroom Internal 1 (Low Side of Roof) | Final Tails Pumps 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-R11_ | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom |  | Lighting - Switchroom Internal 1 (Emergency) | Final Tails Pumps 415V Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-W11 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom |  | Lighting - Switchroom Internal 2 (High Side of Roof) | Final Tails Pumps 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-W11_ | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom |  | Lighting - Switchroom Internal 2 (Emergency) | Final Tails Pumps 415V Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-W12 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom |  | Lighting - Switchroom External 1 | Final Tails Pumps 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-W12_ | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom |  | Lighting - Switchroom External 1 (Emergency) | Final Tails Pumps 415V Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-R03 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom |  | General Power - Switchroom GPO's | Final Tails Pumps 415V Switchroom | 4 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23DB001-B10 | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom |  | Lighting - Switchroom External Lighting Junction Box | Final Tails Pumps 415V Switchroom | 4 | 0.6/1 | 4C+E | Cu | PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F23SW023-C1 | F23SR001-LCS | Final Tails Pumps 11kV / 415V Switchroom Emergency Shutdown | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 11kV Switchroom | 1.5 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Emerg/ Shutdown Circuit. E-stop to trip incomer | 5
F23SW123-C2 | F23SR001-LCS | Final Tails Pumps 11kV / 415V Switchroom Emergency Shutdown | Final Tails Pumps 415V Switchroom | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | Final Tails Pumps 11kV Switchroom | 1.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | Emerg/ Shutdown Circuit. E-stop to trip incomer | 5
F23TR023-C1 | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Transformer Signals to MCC | 5
F23AG404VS-C1 | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | Final Tails Pumps 415V Switchroom | F23AG404-VS | Final Tails Tank Agitator LV VSD | Final Tails Pumps 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F23DB001-C1 | F23-FIP-001 | Final Tails Pumps 11kV / 415V Switchroom Fire Indicator Panel | Final Tails Pumps 415V Switchroom | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | 1.5 | 0.6/1 | 2C | Cu | R-EP-110 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | HVAC trip. | 5
F23SW023-C2 | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | MCC Incomer Signals to DCS. | 6
F23SW123-C1 | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | Final Tails Pumps 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Incomer Signals to DCS. | 6
F23SW123-C3 | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | Final Tails Pumps 415V Switchroom | 1.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F23FIP001-C1 | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | F23-FIP-001 | Final Tails Pumps 11kV / 415V Switchroom Fire Indicator Panel | Final Tails Pumps 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | FIP Alarm/Fault/Isolate Signals | 6
F23DB001-C2 | F23-PE-001 | Final Tails Pumps 11kV / 415V Switchroom Photo-electric Cell | Final Tails Pumps 415V Switchroom | F23-DB-001 | Final Tails Pumps 11kV / 415V Switchroom L&SP Distribution Board | Final Tails Pumps 415V Switchroom | 2.5 | 0.45/0.75 | 4C+E | Cu | Flat - PVC/PVC | White | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
UT23501-I1 | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | UT23501 | F23-SR-002 Final Tails Pumps 415V Switchroom Temperature/Humidity Transmitter | Final Tails Pumps 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
UT23502-I1 | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | UT23502 | F23-SR-002 Final Tails Pumps 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | Final Tails Pumps 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F23SR001LCS-C1 | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | F23SR001-LCS | Final Tails Pumps 11kV / 415V Switchroom Emergency Shutdown | Final Tails Pumps 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | 24VDC supply to PILZ relay in Switchroom E-shut | 6
ZSC23504-I1 | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | ZSC23504 | F23-SR-002 Final Tails Pumps 415V MCC Transformer Enclosure Door Position Switch Closed | Final Tails Pumps 415V Switchroom | 1.5 | 0.15 | 1PR | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | Transformer Enclosure Door feedback | 6
F23SW023LCS-C1 | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | F23SW023-LCS | Final Tails Pumps 415V MCC Remote Switching Panel | Final Tails Pumps 415V Switchroom | 1.5 | 0.6/1 | 20C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F23UPS002-C1 | F23UPS002-ISL | Final Tails Pumps 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Final Tails Pumps 415V Switchroom | F23-UPS-002 | Final Tails Pumps 415V Switchroom 240VAC UPS | Final Tails Pumps 415V Switchroom | 1.5 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | Bypass. | 6
F23SW023-C51 | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 6
F23SW023-C52 | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 6
F23SW023-C53 | F23-TR-023 | Final Tails Pumps 415V MCC Transformer | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 6
F23SW023-C3 | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 24VDC PSU monitoring | 6
F23SW023-C4 | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 24VDC PSU monitoring | 6
F23FIP001-FO1 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-FIP-001 | Final Tails Pumps 11kV / 415V Switchroom Fire Indicator Panel | Final Tails Pumps 415V Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Site-Wide Fire network - patch to FIP. | 6
F23FIP001-FO2 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-FIP-001 | Final Tails Pumps 11kV / 415V Switchroom Fire Indicator Panel | Final Tails Pumps 415V Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Site-Wide Fire network - patch to FIP. | 6
F23UPS002-D1 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-UPS-002 | Final Tails Pumps 415V Switchroom 240VAC UPS | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F23AG404VS-D1 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23AG404-VS | Final Tails Tank Agitator LV VSD | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F23SW023-D11 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switch F23-ETH- 021. | 6
F23SW023-D12 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switch F23-ETH- 022. | 6
F23SW023-D13 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switch F23-ETH- 023. | 6
F23-SW123-COM4 | F23-SW-023 | Final Tails Pumps 415V MCC | Final Tails Pumps 415V Switchroom | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | Final Tails Pumps 415V Switchroom | N/A | N/A | N/A | N/A | VAMP CAN Bus | Grey | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 3 | VAMP CAN Bus Cable. | 6
F23SW123-D11 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-SW-123 | Final Tails Pumps Emergency 415V MCC | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | Connected to local MCC ethernet switch F23-ETH- 024. | 6
F23DCS409-D1 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Orange | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 1 PRIMARY | 6
F23DCS409-D2 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Orange | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 1 SECONDARY | 6
F23DCS409-D3 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Purple | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 2 PRIMARY | 6
F23DCS409-D4 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Purple | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 2 SECONDARY | 6
F23DCS409-D5 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | DCS Comms Allowance - ALE CARD (AS REQUIRED) | 6
F23DCS409-D6 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | DCS Comms Allowance - ALE CARD (AS REQUIRED) | 6
F23DCS409-D7 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 3 | SPARE | 6
F23DCS409-D8 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 3 | SPARE | 6
F23DCS409-F01 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED). | 6
F23DCS409-F02 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom | F23-DCS-409 | Final Tails Pumps 415V Switchroom DCS Panel | Final Tails Pumps 415V Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED). | 6
F23SR002GN001-D1 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom |  | Final Tails Pumps 11kV / 415V Switchroom Data Points | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F23SR002GN001-D2 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom |  | Final Tails Pumps 11kV / 415V Switchroom Data Points | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F23SR002GN002-D1 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom |  | Final Tails Pumps 11kV / 415V Switchroom Data Points | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F23SR002GN002-D2 | F23-COM-001 | Final Tails Pumps 415V Switchroom Communications Rack | Final Tails Pumps 415V Switchroom |  | Final Tails Pumps 11kV / 415V Switchroom Data Points | Final Tails Pumps 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F23TR023EB01-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23TR023-EB01 | Final Tails Pumps 415V MCC Transformer Earth Bar Earth Bar | Final Tails Pumps 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | 7
F23TR023EB01-E2 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23TR023-EB01 | Final Tails Pumps 415V MCC Transformer Earth Bar Earth Bar | Final Tails Pumps 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | 7
F23SW023EB01-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23SW023-EB01 | Final Tails Pumps 415V MCC Earth Bar | Final Tails Pumps 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | 7
F23SW023EB01-E2 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23SW023-EB01 | Final Tails Pumps 415V MCC Earth Bar | Final Tails Pumps 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | 7
F23SW123EB01-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23SW123-EB01 | Final Tails Pumps Emergency 415V MCC Earth Bar | Final Tails Pumps 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | 7
F23SW123EB01-E2 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23SW123-EB01 | Final Tails Pumps Emergency 415V MCC Earth Bar | Final Tails Pumps 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | 7
F23AG404VS-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23AG404-VS | Final Tails Tank Agitator LV VSD | Final Tails Pumps 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F23SR001LCS-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23SR001-LCS | FINAL TAILS PUMPS 11KV / 415V SWITCHROOM EMERGENCY SHUTDOWN | Final Tails Pumps 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F23COM001-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23-COM-001 | FINAL TAILS PUMPS 415V SWITCHROOM COMMUNICATIONS RACK | Final Tails Pumps 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F23DCS409-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23-DCS-409 | FINAL TAILS PUMPS 415V SWITCHROOM DCS PANEL | Final Tails Pumps 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F23UPS002-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23-UPS-002 | FINAL TAILS PUMPS 415V SWITCHROOM 240VAC UPS | Final Tails Pumps 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F23UPS002ISL-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23UPS002-ISL | FINAL TAILS PUMPS 415V SWITCHROOM 240VAC UPS MAINTENANCE BYPASS SWITCH | Final Tails Pumps 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F23BA002-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23-BA-002 | FINAL TAILS PUMPS 415V SWITCHROOM 240VAC UPS BATTERY BANK | Final Tails Pumps 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F23DB201-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23-DB-201 | FINAL TAILS PUMPS 415V SWITCHROOM 240V UPS DISTRIBUTION BOARD | Final Tails Pumps 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F23SW023LCS-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23SW023-LCS | FINAL TAILS PUMPS 415V MCC REMOTE SWITCHING PANEL | Final Tails Pumps 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F23FIP001-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23-FIP-001 | FINAL TAILS PUMPS 11KV / 415V SWITCHROOM FIRE INDICATOR PANEL | Final Tails Pumps 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7
F23DB001-E1 | F23SR001-EB01 | Final Tails Pumps 11kV / 415V Switchroom Earth Bar | Final Tails Pumps 415V Switchroom | F23-DB-001 | FINAL TAILS PUMPS 11KV / 415V SWITCHROOM L&SP DISTRIBUTION BOARD | Final Tails Pumps 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 7