## Equipment list
Connected Load (Name Plate) | Maximum Demand (15 minutes) | Transformer Utilisation | 24 Hour Average Demand (Plant Running) | Yearly Average Consumption | Equipment Name | Load Description | Equipment Number | Transformer Rating (kVA) | Page
kW | kW | % | kW | MWh |  |  |  |  | 4
800 | 805 | N/A | 805 | 5,992 | FIM III Booster Pump 1 | FIM TSF | F23-PP-651 | N/A | 4
800 | 727 | N/A | 727 | 5,413 | FIM III Booster Pump 2 | FIM TSF | F23-PP-652 | N/A | 4
1,724 | 1,050 | 72% | 997 | 7,424 | FIM III Booster Station LV Motor Control Centre | FIM TSF | F23-SW-602 | 1600 | 4
3,324 | 2,582 | 54% | 2,529 | 18,828 | Total | FIM TSF | F23-SW-601 | 5,000 | 4
[5 empty] | Client: | NORTHERN STAR RESOURCES | FIM III BOOSTER STATION ELECTRICAL LOAD LIST |  | 5
[5 empty] | Project: | KCGM FIM TSF PROJECT |  |  | 5
[5 empty] | Document Number: | 2000-F23-LST-EL-40001 |  |  | 5
[5 empty] | Revision: | 2 |  |  | 5
|  | Load Details |  | 24 Hour Average Demand (Plant Running) Annual Consumption | Equipment |  | Input Data |  | 5

## Load list
Nameplate (kW) | Active Power (kW) | Apparent Power (kVA) | Reactive Power (kVAR) | Annual Energy Consumption (MWh) | Equipment Number | Equipment Description | Voltage (V) | Load Type | Duty / Standby | MCC | Motor / Load Efficiency 75% Load | Motor / Load Power Factor 75% Load | Load Factor (LF) | Plant Diversity Factor (PDF) | Annual Run Hours | Schematic Diagram | Single Line Diagram | Load Stage | Data Source | Status | Rev | Page
3324 | 2582 | 2712 | 667 | 18829 | [17 empty] | 5
800 | 805 | 821 | 163 | 5992 | F23-PP-651 | FIM III Booster Pump 1 | 3300 | 3.3kV 800kW VSD MOTOR | Duty | F23-SW-601 | 0.96 | 0.84 | 0.93 | 1.00 | 0.85 | 2000-EL006-B02-40023 | 2000-F23-SLD-EL-40001 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 1 | 5
800 | 727 | 742 | 148 | 5413 | F23-PP-652 | FIM III Booster Pump 2 | 3300 | 3.3kV 800kW VSD MOTOR | Duty | F23-SW-601 | 0.96 | 0.84 | 0.84 | 1.00 | 0.85 | 2000-EL006-B02-40023 | 2000-F23-SLD-EL-40001 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 1 | 5
4 | 3 | 4 | 3 | 25 | F23-FN-653 | FIM III Booster Pump 1 Motor Fan | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F23-SW-602 | 0.90 | 0.76 | 0.75 | 1.00 | 0.85 | 2000-F23-SCM-EL-40026 | 2000-F23-SLD-EL-40012 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
4 | 3 | 4 | 3 | 25 | F23-FN-654 | FIM III Booster Pump 2 Motor Fan | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F23-SW-602 | 0.90 | 0.76 | 0.75 | 1.00 | 0.85 | 2000-F23-SCM-EL-40027 | 2000-F23-SLD-EL-40012 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
0.18 | 0 | 0 | 0 | 2 | F23-FN-651 | FIM III Booster Pump 1 Gearbox Fan | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F23-SW-602 | 0.63 | 0.61 | 0.75 | 1.00 | 0.85 | 2000-F23-SCM-EL-40028 | 2000-F23-SLD-EL-40012 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
0.18 | 0 | 0 | 0 | 2 | F23-FN-652 | FIM III Booster Pump 2 Gearbox Fan | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F23-SW-602 | 0.63 | 0.61 | 0.75 | 1.00 | 0.85 | 2000-F23-SCM-EL-40029 | 2000-F23-SLD-EL-40012 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
1.5 | 1 | 1 | 0 | 9 | F23-PW-651 | FIM III Booster Pump 1 Seal Water Pump 1 | 415 | 415V 0.18 TO 37kW VSD MOTOR | Duty | F23-SW-602 | 0.86 | 0.67 | 0.70 | 1.00 | 0.85 | 2000-F23-SCM-EL-40020 | 2000-F23-SLD-EL-40011 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
1.5 | 0 | 0 | 0 | 0 | F23-PW-652 | FIM III Booster Pump 1 Seal Water Pump 2 | 415 | 415V 0.18 TO 37kW VSD MOTOR | Standby | F23-SW-602 | 0.86 | 0.67 | 0.70 | 1.00 | 0.85 | 2000-F23-SCM-EL-40021 | 2000-F23-SLD-EL-40011 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
1.5 | 1 | 1 | 0 | 9 | F23-PW-653 | FIM III Booster Pump 2 Seal Water Pump 1 | 415 | 415V 0.18 TO 37kW VSD MOTOR | Duty | F23-SW-602 | 0.86 | 0.67 | 0.70 | 1.00 | 0.85 | 2000-F23-SCM-EL-40022 | 2000-F23-SLD-EL-40011 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
1.5 | 0 | 0 | 0 | 0 | F23-PW-654 | FIM III Booster Pump 2 Seal Water Pump 2 | 415 | 415V 0.18 TO 37kW VSD MOTOR | Standby | F23-SW-602 | 0.86 | 0.67 | 0.70 | 1.00 | 0.85 | 2000-F23-SCM-EL-40023 | 2000-F23-SLD-EL-40011 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
1.0 | 0 | 0 | 0 | 2 | F75-FL-600 | FIM III Booster Pumps Seal Water Self-Cleaning Filter | 415 | 415V FEEDER 0.37 TO 110kW | Duty | F23-SW-602 | 0.82 | 0.65 | 0.19 | 1.00 | 0.85 | 2000-F23-SCM-EL-40024 | 2000-F23-SLD-EL-40011 | FIM TSF | 2000-F00-LST-ME-40001_0 | Preliminary | 0 | 5
7.5 | 7 | 8 | 0 | 5 | F23-HY-420 | FIM III Hydraulic Power Pack | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F23-SW-602 | 0.92 | 0.81 | 0.80 | 0.10 | 0.85 | 2000-F23-SCM-EL-40025 | 2000-F23-SLD-EL-40011 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 1 | 5
2.2 | 2 | 3 | 1 | 12 | F23-SE-431 | FIM III Booster Station Safety Shower | 415 | 415V FEEDER 0.37 TO 110kW | Duty | F23-SW-602 | 0.88 | 0.73 | 0.80 | 0.80 | 0.85 | 2000-F23-SCM-EL-40030 | 2000-F23-SLD-EL-40011 | FIM TSF | 2000-F00-LST-ME-40001_0 | Preliminary | 0 | 5
1.5 | 1 | 2 | 0 | 2 | F75-PW-665 | FIM III Booster Station Washdown Pump | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F23-SW-602 | 0.86 | 0.67 | 0.80 | 0.20 | 0.85 | 2000-F75-SCM-EL-40005 | 2000-F23-SLD-EL-40012 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
450 | 357 | 364 | 72 | 2657 | F75-PW-606 | Decant Dam 4 Return Pump 1 | 415 | 415V 220 TO 450kW VSD MOTOR | Duty | F23-SW-602 | 0.97 | 0.88 | 0.75 | 1.00 | 0.85 | 2000-F75-SCM-EL-40001 | 2000-F23-SLD-EL-40012 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
450 | 357 | 364 | 72 | 2657 | F75-PW-607 | Decant Dam 4 Return Pump 2 | 415 | 415V 220 TO 450kW VSD MOTOR | Duty | F23-SW-602 | 0.97 | 0.88 | 0.75 | 1.00 | 0.85 | 2000-F75-SCM-EL-40002 | 2000-F23-SLD-EL-40012 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
450 | 0 | 0 | 0 | 0 | F75-PW-608 | Decant Dam 4 Return Pump 3 | 415 | 415V 220 TO 450kW VSD MOTOR | Standby | F23-SW-602 | 0.97 | 0.88 | 0.50 | 1.00 | 0.85 | 2000-F75-SCM-EL-40003 | 2000-F23-SLD-EL-40012 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
2.2 | 2 | 2 | 0 | 1 | F75-PV-414 | Decant Dam 4 Vacuum Pump | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F23-SW-602 | 0.88 | 0.73 | 0.70 | 0.10 | 0.85 | 2000-F75-SCM-EL-40004 | 2000-F23-SLD-EL-40012 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
0.02 | 0 | 0 | 0 | 0 | F75-PP-482 | Decant Dam 4 Antiscalant Dosing Pump 1 | 240 | 240V FEEDER (1 PHASE) | Duty | F23-DB-601 | 0.90 | 0.80 | 0.70 | 1.00 | 0.85 | - | 2000-F23-TLD-EL-40011 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
0.02 | 0 | 0 | 0 | 0 | F75-PP-483 | Decant Dam 4 Antiscalant Dosing Pump 2 | 240 | 240V FEEDER (1 PHASE) | Duty | F23-DB-601 | 0.90 | 0.80 | 0.70 | 1.00 | 0.85 | - | 2000-F23-TLD-EL-40011 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
0.02 | 0 | 0 | 0 | 0 | F75-PP-484 | Decant Dam 4 Antiscalant Dosing Pump 3 | 240 | 240V FEEDER (1 PHASE) | Duty | F23-DB-601 | 0.90 | 0.80 | 0.70 | 1.00 | 0.85 | - | 2000-F23-TLD-EL-40011 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
9 | 10 | 13 | 8 | 74 | F23PP651-VSD | FIM III Booster Pump 1 Variable Speed Drive Auxiliary Supply | 415 | 415V FEEDER (WITHOUT E/L) | Duty | F23-SW-602 | 0.90 | 0.80 | 1.00 | 1.00 | 0.85 | 2000-F23-SCM-EL-40018 | 2000-F23-SLD-EL-40011 | FIM TSF | EEL | Confirmed | 2 | 5
9 | 10 | 13 | 8 | 74 | F23PP652-VSD | FIM III Booster Pump 2 Variable Speed Drive Auxiliary Supply | 415 | 415V FEEDER (WITHOUT E/L) | Duty | F23-SW-602 | 0.90 | 0.80 | 1.00 | 1.00 | 0.85 | 2000-F23-SCM-EL-40019 | 2000-F23-SLD-EL-40011 | FIM TSF | EEL | Confirmed | 2 | 5
30 | 33 | 42 | 25 | 248 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board | 415 | 415V FEEDER (WITHOUT E/L) | Duty | F23-SW-602 | 0.90 | 0.80 | 1.00 | 1.00 | 0.85 | 2000-F75-SCM-EL-40015 | 2000-F23-SLD-EL-40011 | FIM TSF | EEL | Confirmed | 2 | 5
250 | 222 | 278 | 133 | 1324 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC Distribution Board | 415 | 415V FEEDER (WITHOUT E/L) | Duty | F23-SW-602 | 0.90 | 0.80 | 0.80 | 0.80 | 0.85 | 2000-F75-SCM-EL-40016 | 2000-F23-SLD-EL-40011 | FIM TSF | EEL | Confirmed | 2 | 5
7.2 | 8 | 10 | 6 | 60 | F23-DB-603 | FIM III Booster Station Switchroom 240V UPS Distribution Board | 240 | 240V FEEDER (1 PHASE) | Duty | F23-SW-602 | 0.90 | 0.80 | 1.00 | 1.00 | 0.85 | 2000-F75-SCM-EL-40017 | 2000-F23-SLD-EL-40011 | FIM TSF | EEL | Confirmed | 2 | 5
40 | 32 | 39 | 22 | 235 | F75-SW-557 | FIM III TSF Switchboard 2 | 415 | 415V FEEDER (WITHOUT E/L) | Duty | F23-SW-602 | 0.95 | 0.82 | 0.75 | 1.00 | 0.85 | 2000-F75-SCM-EL-40006 | 2000-F23-SLD-EL-40012 | FIM TSF | 2000-F00-LST-ME-40001_0 | Confirmed | 2 | 5