## Equipment list
Equip. Number | Equipment Name | Type | Manufacturer | Model | Location | Fed From | Supplier | Installer | Comments | Standard Specification | Datasheet | Reference Drawing/Document | Status | Rev | Page
F23-TR-601 | FIM III Booster Station 33/11kV Transformer | Transformer | Tyree Transformers | 5000M6XX | FIM III Booster Station | FIM III TSF HV DISTRIBUTION 33kV POWERLINE POLE TSF3-2 | EL007 | CN037-E&I | 33/11 kV, 5MVA, Dyn11, Sealed type, KNAN (FM3990 Fluid (FR3 Cargill), FM Global approved (with certificate) Pad Mount Transformer | 2000-F00-STS-EL-10003 | 2000-F23-DSH-EL-40001 | 2000-F23-DRG-EL-40021 2000-F23-SLD-EL-40001 | Confirmed | 1 | 4
F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | Transformer | Siemens Energy | Cast resin dry type - Vendor to advise model number | F23-SR-601 Transformer Room | F23-SW-601 | EL006 | EL006 | 11/0.433 kV, 1600 kVA, Dyn11, fully assembled dry type transformer in IP00 enclosure. Installed inside switchroom, in Fortress key locked room | 2000-F00-STS-EL-10017 | 2000-F23-DSH-EL-40002 | 2000-F23-SLD-EL-40011 | Confirmed | 0 | 4
F23-NR-601 | FIM III Booster Station 33/11kV Transformer 11kV Neutral Earthing Resistor | NER | Fortress | 25A 10 Sec with NER Monitor (Loose) | F23-TR-601 |  | EL006 | CN037-E&I |  |  | 2000-F23-DSH-EL-40007 | 2000-F23-SLD-EL-40001 | Confirmed | 1 | 4
F23-SR-601 | FIM III Booster Station Switchroom | HV/LV Switchroom | Fabricated | Transportable Switchroom with 11kV Switchboard and 11/3.3kV VSDs w/ split system AC units and Fire suppression system | FIM III Booster Station |  | EL006 | CN037-E&I |  | 2000-F00-STS-EL-10011 | 2000-F23-DSH-EL-40003 | 2000-F23-DRG-EL-40021 | Confirmed | 0 | 4
F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | Earth Bar |  |  | F23-SR-601 |  | EL006 | EL006 |  | 2000-F00-STS-EL-10011 | 2000-F23-DSH-EL-40003 |  | Confirmed | 0 | 4
F23-EB-601 | FIM III Booster Station Seal Water Area Field Earth Bar | Earth Bar |  |  | Seal Water Pumps Area |  | CN037-E&I | CN037-E&I |  |  |  | 2000-F23-DRG-EL-40024 | Confirmed | 1 | 4
F75-EB-606 | Decant Dam 4 Field Earth Bar | Earth Bar |  |  | Decant Dam 4 |  | CN037-E&I | CN037-E&I |  |  |  | 2000-F23-DRG-EL-40024 | Confirmed | 1 | 4
F23-SW-601 | FIM III Booster Station HV Switchboard | HV Switchboard | Fabricated | Fabricated Panel | F23-SR-601 HV Switchroom | F23-TR-601 | EL006 | EL006 |  | 2000-F00-STS-EL-10015 | 2000-F23-DSH-EL-40004 | 2000-F23-SLD-EL-40001 2000-F23-SLD-EL-40002 | Confirmed | 0 | 4
F23-SW-602 | FIM III Booster Station LV Motor Control Centre | MCC | Fabricated | Fabricated Panel | F23-SR-601 LV Switchroom | F23-TR-602 | EL006 | EL006 |  | 2000-F00-STS-EL-10016 | 2000-F23-DSH-EL-40005 | 2000-F23-SLD-EL-40011 2000-F23-SLD-EL-40012 | Confirmed | 0 | 4
F23SW601-LCS | FIM III Booster Station HV Switchboard Remote Switching Panel | Remote Switching Panel | Fabricated | Fabricated Panel | F23-SR-601 Airlock |  | EL006 | EL006 |  | 2000-F00-STS-EL-10008 | 2000-F23-DSH-EL-40003 | 2000-F23-DRG-EL-40002 | Confirmed | 0 | 4
F23SW602-LCS | FIM III Booster Station LV Motor Control Centre Remote Switching Panel | Remote Switching Panel | Fabricated | Fabricated Panel | F23-SR-601 Airlock |  | EL006 | EL006 |  | 2000-F00-STS-EL-10008 | 2000-F23-DSH-EL-40003 | 2000-F23-SCM-EL-40012 2000-F23-TER-EL-40011 | Confirmed | 0 | 4
F23SR601-LCS01 | FIM III Booster Station Switchroom E-Shut 1 | E-SHUT | Eaton Cutler Hammer | E34 series 30.5mm pushbutton ¦ Enclosure PB2SS6 | F23-SR-601 Airlock | F23-DCS-601 | EL006 | EL006 |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 | 2000-F23-DSH-EL-40003 | 2000-F23-SLD-EL-40011 | Confirmed | 0 | 4
F23SR601-LCS02 | FIM III Booster Station Switchroom E-Shut 2 | E-SHUT | Eaton Cutler Hammer | E34 series 30.5mm pushbutton ¦ Enclosure PB2SS6 ¦ Sunshade | F23-SR-601 Outside HV Switchroom | F23-DCS-601 | EL006 | EL006 |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 | 2000-F23-DSH-EL-40003 | 2000-F23-SLD-EL-40011 | Confirmed | 0 | 4
F23-FIP-601 | FIM III Booster Station Switchroom Fire Indicator Panel | Fire Indicator Panel | Tyco | Vigilant MX1 | F23-SR-601 Airlock | F23-DB-603 | EL006 | EL006 | With Moxa EDS-405A-SS-SC ethernet switch | 2000-F00-STS-EL-10011 | 2000-F23-DSH-EL-40003 |  | Confirmed | 0 | 4
F23FIP601-XE1 | FIM III Booster Station Switchroom VESDA Panel | VESDA | Xtralis | VESDA-E VEP-A00P | F23-SR-601 Airlock | F23-FIP-601 | EL006 | EL006 |  | 2000-F00-STS-EL-10011 | 2000-F23-DSH-EL-40003 |  | Confirmed | 0 | 4
F23FIP601-XE2 | FIM III Booster Station Switchroom Gas Suppression System - Control Panel | Gas system | VTA | VTA | F23-SR-601 HV Switchroom | F23-FIP-601 | EL006 | EL006 |  | 2000-F00-STS-EL-10011 | 2000-F23-DSH-EL-40003 |  | Confirmed | 0 | 4
| FIM III Booster Station Switchroom Gas Suppression System - Gas Cylinders | Gas system | VTA | IG541 (Frike Pro Inert) | F23-SR-601 HV Switchroom |  | EL006 | EL006 |  | 2000-F00-STS-EL-10011 | 2000-F23-DSH-EL-40003 |  | Confirmed | 0 | 4
F23-HF-601 | FIM III Booster Station LV MCC Active Harmonic Filter | Active Harmonic Filter | Schneider | PCSP300D5IP31 | F23-SR-601 LV Switchroom | F23-SW-602 | EL006 | EL006 | Schneider AccuSine PCS+ 380-480V Active Harmonic Filter VAC IP31. | 2000-F00-STS-EL-10011 | 2000-F23-DSH-EL-40003 | 2000-F23-SCM-EL-40031 | Confirmed | 0 | 4
F23-DB-601 | FIM III Booster Station Switchroom and Area 415V L&SP DB | LV DB | NHP | Concept Premier | F23-SR-601 Airlock | F23-SW-602 | EL006 | EL006 | Indoor - 250A, 60 pole fully fitted with lighting timers, RCD testing | 2000-F00-STS-EL-10007 | 2000-F23-DSH-EL-40003 | 2000-F23-DRG-EL-40011 2000-F23-TLD-EL-40011 | Confirmed | 0 | 4
F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB | 240V DC UPS DB | NHP | Concept Premier | F23-SR-601 Airlock | F23-SW-602 | EL006 | EL006 | Indoor - 400A, 48 pole fully fitted with HVAC controls, RCD testing | 2000-F00-STS-EL-10007 | 2000-F23-DSH-EL-40003 | 2000-F23-DRG-EL-40012 2000-F23-TLD-EL-40012 | Confirmed | 0 | 4
F23-DB-603 | FIM III Booster Station Switchroom 240V AC UPS DB | 240V DC UPS DB | NHP | Concept Premier | F23-SR-601 LV Switchroom | F23-UPS-601 | EL006 | EL006 | 24 pole fully fitted, 160A, wall mounted DB | 2000-F00-STS-EL-10007 | 2000-F23-DSH-EL-40003 | 2000-F23-TLD-EL-40013 | Confirmed | 0 | 4
F23-BA-601 | FIM III Booster Station Switchroom 48V DC Battery | 48V Battery | Magellan | MKFT12-200 | F23-SR-601 HV Switchroom | F23-BC-601 | EL006 | EL006 | 200Ah, 48V | 2000-F00-STS-EL-10011 2000-F00-STS-EL-10014 | 2000-F23-DSH-EL-40003 | 2000-F23-TLD-EL-40001 | Confirmed | 0 | 4
F23-BC-601 | FIM III Booster Station Switchroom 48V DC Battery Charger | 48V Charger | Magellan | 48MCRII3P100 | F23-SR-601 HV Switchroom |  | EL006 | EL006 | 48V, 100A | 2000-F00-STS-EL-10011 2000-F00-STS-EL-10014 | 2000-F23-DSH-EL-40003 | 2000-F23-TLD-EL-40001 | Confirmed | 0 | 4
F23SW601-KEB | FIM III Booster Station Switchroom Key Exchange Box | Key Exchange Box |  |  | F23-SR-601 HV Switchroom |  | EL006 | EL006 |  |  | 2000-F23-DSH-EL-40003 |  | Deleted | 1 | 4
F23-UPS-601 | FIM III Booster Station Switchroom 240V AC UPS | UPS | Riello | S3M 10 XTD T5 LL CA | F23-SR-601 LV Switchroom |  | EL006 | EL006 | 10kVA/10kW Sentryum Xtend UPS - 3 or 1-phase out with 9Ah Long life Batteries | 2000-F00-STS-EL-10011 2000-F00-STS-EL-10014 | 2000-F23-DSH-EL-40003 | 2000-F23-TLD-EL-40013 | Confirmed | 0 | 4
F23UPS601-ISL | FIM III Booster Station Switchroom 240V AC UPS Bypass Switch | Bypass Switch | Riello | WABS 0063A-31H SI | F23-SR-601 LV Switchroom |  | EL006 | EL006 | External Maintenance Bypass Switch 3Ph/1Ph, 10 kVA, w/o Sep. bypass input 63A, mech/elec interlock | 2000-F00-STS-EL-10011 2000-F00-STS-EL-10014 | 2000-F23-DSH-EL-40003 | 2000-F23-TLD-EL-40013 | Confirmed | 0 | 4
F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | DCS Panel | Fabricated Panel |  | F23-SR-601 LV Switchroom |  | EL006 | EL006 | For Yokogowa DCS | 2000-F00-STS-EL-10008 | 2000-F23-DSH-EL-40003 | 2000-F23-DRG-IC-40002 2000-F23-SCM-IC-40002 | Confirmed | 0 | 4
F75-RTU-606 | FIM III Booster Station Switchroom RTU Panel | RTU Panel | Fabricated Panel |  | F23-SR-601 LV Switchroom |  | EL006 | EL006 | For Motorola RTU | 2000-F00-STS-EL-10008 | 2000-F23-DSH-EL-40003 | 2000-F75-DRG-IC-40002 2000-F75-SCM-IC-40002 | Confirmed | 0 | 4
F23-COM-601 | FIM III Booster Station Switchroom Communications Cabinet | Comms Rack | APC | 42RU 19" Communications Cabinet, PART No. AR3100 (RTX6642G) | F23-SR-601 LV Switchroom |  | EL006 | EL006 | Communications Rack, Free Standing 19" | 2000-F00-STS-EL-10011 | 2000-F23-DSH-EL-40003 | 2000-F23-DRG-IC-40001 2000-F23-SCM-IC-40001 | Confirmed | 0 | 4
F23PP651-VS | FIM III Booster Pump 1 Variable Speed Drive | HV VSD | Siemens | SINAMICS Perfect Harmony GH180 GenVe-11-3.3-200-1250 6SR5502-0NF41-2BH0-Z | F23-SR-601 HV Switchroom | F23-SW-601 | EL006 | EL006 | 11/3.3kV 800kW Heavy Duty MV VSD with 150% overload capacity |  | 2000-F23-DSH-EL-40006 | 2000-F23-SLD-EL-40001 | Confirmed | 0 | 4
F23PP652-VS | FIM III Booster Pump 2 Variable Speed Drive | HV VSD | Siemens | SINAMICS Perfect Harmony GH180 GenVe-11-3.3-200-1250 6SR5502-0NF41-2BH0-Z | F23-SR-601 HV Switchroom | F23-SW-601 | EL006 | EL006 | 11/3.3kV 800kW Heavy Duty MV VSD with 150% overload capacity |  | 2000-F23-DSH-EL-40006 | 2000-F23-SLD-EL-40001 | Confirmed | 0 | 4
F23PW651-VS | FIM III Booster Pump 1 Seal Water Pump 1 Variable Speed Drive | LV VSD | Rockwell / Allen Bradley | Powerflex 753 20F11NC3P5JA0NNNNN | F23-SR-601 LV Switchroom | F23-SW-602 | EL006 | EL006 | 1.5kW Heavy Duty 415V VSD. Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10006 |  | 2000-F23-SCM-EL-40020 | Confirmed | 0 | 4
F23PW652-VS | FIM III Booster Pump 1 Seal Water Pump 2 Variable Speed Drive | LV VSD | Rockwell / Allen Bradley | Powerflex 753 20F11NC3P5JA0NNNNN | F23-SR-601 LV Switchroom | F23-SW-602 | EL006 | EL006 | 1.5kW Heavy Duty 415V VSD. Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10006 |  | 2000-F23-SCM-EL-40021 | Confirmed | 0 | 4
F23PW653-VS | FIM III Booster Pump 2 Seal Water Pump 1 Variable Speed Drive | LV VSD | Rockwell / Allen Bradley | Powerflex 753 20F11NC3P5JA0NNNNN | F23-SR-601 LV Switchroom | F23-SW-602 | EL006 | EL006 | 1.5kW Heavy Duty 415V VSD. Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10006 |  | 2000-F23-SCM-EL-40022 | Confirmed | 0 | 4
F23PW654-VS | FIM III Booster Pump 2 Seal Water Pump 2 Variable Speed Drive | LV VSD | Rockwell / Allen Bradley | Powerflex 753 20F11NC3P5JA0NNNNN | F23-SR-601 LV Switchroom | F23-SW-602 | EL006 | EL006 | 1.5kW Heavy Duty 415V VSD. Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10006 |  | 2000-F23-SCM-EL-40023 | Confirmed | 0 | 4
F75PW606-VS | Decant Dam 4 Return Pump 1 Variable Speed Drive | LV VSD | Rockwell / Allen Bradley | Powerflex 755 20G11JC910JN0NNNNN | F23-SR-601 LV Switchroom | F23-SW-602 | EL006 | EL006 | 450kW Normal Duty 415V VSD. Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10006 |  | 2000-F75-SCM-EL-40001 | Confirmed | 0 | 4
F75PW607-VS | Decant Dam 4 Return Pump 2 Variable Speed Drive | LV VSD | Rockwell / Allen Bradley | Powerflex 755 20G11JC910JN0NNNNN | F23-SR-601 LV Switchroom | F23-SW-602 | EL006 | EL006 | 450kW Normal Duty 415V VSD. Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10006 |  | 2000-F75-SCM-EL-40002 | Confirmed | 0 | 4
F75PW608-VS | Decant Dam 4 Return Pump 3 Variable Speed Drive | LV VSD | Rockwell / Allen Bradley | Powerflex 755 20G11JC910JN0NNNNN | F23-SR-601 LV Switchroom | F23-SW-602 | EL006 | EL006 | 450kW Normal Duty 415V VSD. Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10006 |  | 2000-F75-SCM-EL-40003 | Confirmed | 0 | 4
| FIM III Booster Pump 1 Local Control Station Enclosure | Local Control Station | Fabricated | 3 Station LCS Enclosure PB2SS6 with Sunshade | FIM III Booster Pump 1 | N/A | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 | Confirmed | 1 | 4
F23PP651-LCS | FIM III Booster Pump 1 Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series | FIM III Booster Pump 1 Local Control Station Enclosure | F23-SW-601 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 2000-F23-SLD-EL-40001 | Confirmed | 1 | 4
F23FN651-LCS | FIM III Booster Pump 1 Gearbox Fan Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series | FIM III Booster Pump 1 Local Control Station Enclosure | F23-SW-602 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 2000-F23-SCM-EL-40028 | Confirmed | 1 | 4
F23FN653-LCS | FIM III Booster Pump 1 Motor Fan Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series | FIM III Booster Pump 1 Local Control Station Enclosure | F23-SW-602 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 2000-F23-SCM-EL-40026 | Confirmed | 1 | 4
| FIM III Booster Pump 2 Local Control Station Enclosure | Local Control Station | Fabricated | 3 Station LCS Enclosure PB2SS6 with Sunshade | FIM III Booster Pump 2 | N/A | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 | Confirmed | 1 | 4
F23PP652-LCS | FIM III Booster Pump 2 Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series | FIM III Booster Pump 2 Local Control Station Enclosure | F23-SW-601 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 2000-F23-SLD-EL-40001 | Confirmed | 1 | 4
F23FN652-LCS | FIM III Booster Pump 2 Gearbox Fan Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series | FIM III Booster Pump 2 Local Control Station Enclosure | F23-SW-602 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 2000-F23-SCM-EL-40029 | Confirmed | 1 | 4
F23FN654-LCS | FIM III Booster Pump 2 Motor Fan Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series | FIM III Booster Pump 2 Local Control Station Enclosure | F23-SW-602 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 2000-F23-SCM-EL-40027 | Confirmed | 1 | 4
| FIM III Booster Pump 1 Seal Water Pumps 1 & 2 Local Control Station Enclosure | Local Control Station | Fabricated | 2 Station LCS Enclosure PB2SS6 with Sunshade | FIM III Booster Pump 1 Seal Water Pumps 1 & 2 | N/A | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 | Confirmed | 1 | 4
F23PW651-LCS | FIM III Booster Pump 1 Seal Water Pump 1 Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series | FIM III Booster Pump 1 Seal Water Pumps 1 & 2 Local Control Station Enclosure | F23-SW-602 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 2000-F23-SCM-EL-40020 2000-F23-SCM-EL-40021 | Confirmed | 1 | 4
F23PW652-LCS | FIM III Booster Pump 1 Seal Water Pump 2 Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series | FIM III Booster Pump 1 Seal Water Pumps 1 & 2 Local Control Station Enclosure | F23-SW-602 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 2000-F23-SCM-EL-40020 2000-F23-SCM-EL-40021 | Confirmed | 1 | 4
| FIM III Booster Pump 2 Seal Water Pumps 1 & 2 Local Control Station Enclosure | Local Control Station | Fabricated | 2 Station LCS Enclosure PB2SS6 with Sunshade | FIM III Booster Pump 1 Seal Water Pumps 1 & 2 | N/A | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 | Confirmed | 1 | 4
F23PW653-LCS | FIM III Booster Pump 2 Seal Water Pump 1 Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series | FIM III Booster Pump 2 Seal Water Pumps 1 & 2 Local Control Station Enclosure | F23-SW-602 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 2000-F23-SCM-EL-40022 2000-F23-SCM-EL-40023 | Confirmed | 1 | 4
F23PW654-LCS | FIM III Booster Pump 2 Seal Water Pump 2 Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series | FIM III Booster Pump 2 Seal Water Pumps 1 & 2 Local Control Station Enclosure | F23-SW-602 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 2000-F23-SCM-EL-40022 2000-F23-SCM-EL-40023 | Confirmed | 1 | 4
F75PW606-LCS | Decant Dam 4 Return Pump 1 Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series ¦ Enclosure PB2SS6 ¦ Sunshade | F75-PW-606 | F23-SW-602 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40023 2000-F75-SCM-EL-40001 | Confirmed | 0 | 4
F75PW607-LCS | Decant Dam 4 Return Pump 2 Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series ¦ Enclosure PB2SS6 ¦ Sunshade | F75-PW-607 | F23-SW-602 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40023 2000-F75-SCM-EL-40002 | Confirmed | 0 | 4
F75PW608-LCS | Decant Dam 4 Return Pump 3 Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series ¦ Enclosure PB2SS6 ¦ Sunshade | F75-PW-608 | F23-SW-602 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40023 2000-F75-SCM-EL-40003 | Confirmed | 0 | 4
Client: | NORTHERN STAR RESOURCES | FIM III BOOSTER STATION ELECTRICAL EQUIPMENT LIST | [12 empty] | 5
Project: | KCGM FIM TSF PROJECT | [13 empty] | 5
Document Number: | 2000-F23-LST-EL-40002 | [13 empty] | 5
Revision: | 1 | [13 empty] | 5
F75PV414-LCS | Decant Dam 4 Vacuum Pump Local Control Station | Local Control Station | EATON | 2 button (SRT,ESTOP). Cutler Hammer E34 & T-Series ¦ Enclosure PB2SS6 ¦ Sunshade | F75-PV-414 | F23-SW-602 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40023 2000-F75-SCM-EL-40004 | Confirmed | 0 | 5
F75PW665-LCS | FIM III Booster Station Washdown Pump Local Control Station | Local Control Station | EATON | 2 button (SRT, ESTOP). Cutler Hammer E34 & T-Series ¦ Enclosure PB2SS6 ¦ Sunshade | F75-PW-665 | F23-SW-602 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 2000-F75-SCM-EL-40005 | Confirmed | 0 | 5
F23-IJB-601 | FIM III Booster Station Instrument Junction Box | Instrument Junction Box | Fabricated Panel | Outdoor - Stainless Steel IP65, stainless steel 316 enclosure with sloped roof, complete with terminal blocks and gland plate |  | Seal Water Area | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10008 |  | 2000-F23-DRG-IC-40003 | Confirmed | 0 | 5
F75-IJB-606 | Decant Dam 4 Instrument Junction Box | Instrument Junction Box | Fabricated Panel | Outdoor - Stainless Steel IP65, stainless steel 316 enclosure with sloped roof, complete with terminal blocks and gland plate |  | Decant Dam 4 Area | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10008 |  | 2000-F75-DRG-IC-40001 | Confirmed | 0 | 5
F75-RTU-329 | Decant Dam 4 Telemetry Panel | Remote Telemetry Unit | Fabricated Panel | IP65, 2mm SS316 600Wx800Hx400D stand mounted enclosure with sloped roof mounted on a welded galvanised steel mounting frame. With: MCBs, DINRail, WDU2.5 terminals, DCS & telemetry | Next to Decant Dam 4 | F75-SW-556 | CN037-E&I | CN037-E&I | Includes mains power, Instrumentation & telemetry. Refer to DCS Equipment List 2000-F75-LST-IC-40003 for DCS and telemetry components. | 2000-F00-STS-EL-10008 |  | 2000-F23-DRG-EL-40023 | Preliminary | 0 | 5
| FIM III Booster Station Switchroom lighting | Area Light | Coolon | DLK3-60-NWTAMB-BW3-MP (Normal) DLK3-60-NWTAMB-BW3-MP-MAX (Emergency) | F23-SR-601 - External | F23-DB-601 | EL006 | EL006 | Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  |  | Confirmed | 0 | 5
| FIM III Booster Station Area Floodlighting - 3 x 150W LED floodlighting - cross-arm mounted on 6.0m pole | Floodlight | Coolon | BLF-150-CWT-T2-MP | FIM III Booster Station Pumps Area | F23-DB-601 | CN037-E&I | CN037-E&I | 3 x floodlights - mounted on 6.0m Mid Hinged Heavy Duty Tapered Octagonal Pole with + bracket & Ubolts. Base Plate Mounted to switchboard skid and with spiked lightning terminal. | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 | Confirmed | 1 | 5
| FIM III Booster Station 1-ph 15A switched socket outlet | GPO | Clipsal | 56 series | FIM III Booster Station Switchroom - External | F23-DB-601 | EL006 | EL006 |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 | Confirmed | 1 | 5
| FIM III Booster Station 3-ph 32A switched socket outlet | WO | Clipsal | 56 series | FIM III Booster Station Switchroom - External | F23-DB-601 | EL006 | EL006 |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 | Confirmed | 1 | 5
| FIM III Booster Station Safety Shower Lighting - 11W LED Green Eye Wash Safety Beacon Light with Emergency Pack | Safety Beacon Light | Coolon | EWL-GRN-EM-KIT2 | FIM III Booster Station Safety Shower F23-SE-431 | F23-DB-601 | CN037-E&I | CN037-E&I | Mounted to Safety Shower | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  |  | Deleted | 1 | 5
| Seal Water Tank Area Floodlighting - 3 x 150W LED floodlighting - cross-arm mounted on 6.0m pole | Floodlight | Coolon | BLF-150-CWT-T2-MP | Seal Water Pumps Area | F23-DB-601 | CN037-E&I | CN037-E&I | 3 x floodlights - mounted on 6.0m Mid Hinged Heavy Duty Tapered Octagonal Pole with + bracket & Ubolts. Base Plate Mounted to switchboard skid and with spiked lightning terminal. | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 | Confirmed | 1 | 5
| Seal Water Pumps Area 1-ph 15A switched socket outlet | GPO | Clipsal | 56 series | Seal Water Pumps Area | F23-DB-601 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 | Confirmed | 0 | 5
| Seal Water Pumps Area 3-ph 32A switched socket outlet | WO | Clipsal | 56 series | Seal Water Pumps Area | F23-DB-601 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40022 | Confirmed | 0 | 5
| Decant Dam 4 Area Floodlighting - 2 x 150W LED floodlighting - cross-arm mounted on 6.0m pole | Floodlight | Coolon | BLF-150-CWT-T2-MP | Decant Dam 4 | F23-DB-601 | CN037-E&I | CN037-E&I | 2 x floodlights - mounted on 6.0m Mid Hinged Heavy Duty Tapered Octagonal Pole with + bracket & Ubolts. Base Plate Mounted to switchboard skid and with spiked lightning terminal. | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40023 | Confirmed | 1 | 5
| Decant Dam 4 Area 1-ph 15A switched socket outlet | GPO | Clipsal | 56 series | Decant Dam 4 | F23-DB-601 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40023 | Confirmed | 0 | 5
| Decant Dam 4 Area 3-ph 32A switched socket outlet | WO | Clipsal | 56 series | Decant Dam 4 | F23-DB-601 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40023 | Confirmed | 0 | 5
F75PP482-GPO | Decant Dam 4 Antiscalant Dosing Pump 1 1-ph 10A switched socket outlet | GPO | Clipsal | 56 series | Decant Dam 4 | F23-DB-601 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40023 | Confirmed | 1 | 5
F75PP483-GPO | Decant Dam 4 Antiscalant Dosing Pump 2 1-ph 10A switched socket outlet | GPO | Clipsal | 56 series | Decant Dam 4 | F23-DB-601 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40023 | Confirmed | 1 | 5
F75PP484-GPO | Decant Dam 4 Antiscalant Dosing Pump 3 1-ph 10A switched socket outlet | GPO | Clipsal | 56 series | Decant Dam 4 | F23-DB-601 | CN037-E&I | CN037-E&I |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  | 2000-F23-DRG-EL-40023 | Confirmed | 1 | 5
| Hydrogen Peroxide Dosing Plant 1-ph 15A switched socket outlet | GPO | Clipsal | 56 series | Hydrogen Peroxide Dosing Plant | F23-DB-601 | Future | Future |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  |  | Deleted | 1 | 5
| Hydrogen Peroxide Dosing Plant 3-ph 32A switched socket outlet | WO | Clipsal | 56 series | Hydrogen Peroxide Dosing Plant | F23-DB-601 | Future | Future |  | 2000-F00-STS-EL-10012 2000-F00-STS-EL-10014 |  |  | Deleted | 1 | 5
F75-CAM-601 | Decant Dam 4 PTZ CCTV Camera | PTZ CCTV CAMERA | HikVision | DS-2DE5425IW-AE(T5) 4 MP 25X IR Network Speed Dome with DS-1604ZJ-Pole Vertical Pole Mounting Bracket | Decant Dam 4 | F23-COM-601 | CN037-E&I | CN037-E&I | With 3.0m free-standing pole and mounting accessories: Swivelpole Australia Type F7 M2 HG swivelpole with pole cap. Mounted on dam wall with concrete footing. | 2000-F00-STS-EL-10010 2000-F00-STS-EL-10012 |  | 2000-F23-DRG-EL-40023 | Confirmed | 1 | 5
F23-FOB-601 | FIM III Booster Station Switchroom Communications Rack FOBOT 1 | FOBOT | AFL | FRE-1RU-MOD-S 1RU static sliding enclosure, fully loaded for 24C SMOF (SM OS2), with LC duplex/UPC connectors | F23-COM-601 | N/A | EL006 | EL006 | Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10014 |  | 2000-F23-BLK-IC-40001 2000-F23-DRG-IC-40001 | Confirmed | 0 | 5
F23-FOB-602 | FIM III Booster Station Switchroom Communications Rack FOBOT 2 | FOBOT | AFL | FRE-1RU-MOD-S 1RU static sliding enclosure, fully loaded for 24C SMOF (SM OS2), with LC duplex/UPC connectors | F23-COM-601 | N/A | EL006 | EL006 | Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10014 |  | 2000-F23-BLK-IC-40001 2000-F23-DRG-IC-40001 | Confirmed | 0 | 5
F23-ETH-601 | Ethernet Switch 1 (PCN Switch 1) | Ethernet Switch | CISCO | C9200L-24T-4X 24 Cu PORTS / 4 Fixed SFP 19" Rack Mounted Network Switch + SFP-10G-LR-S SFP+ Transceiver Modules Single Mode (LC) + C9200L-Stack-Kit C/W Stackpower & Stackwise Leads | F23-COM-601 | N/A | EL006 | EL006 | Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10014 |  | 2000-F23-BLK-IC-40001 2000-F23-DRG-IC-40001 | Confirmed | 0 | 5
F23-ETH-602 | Ethernet Switch 2 (PCN Switch 2) | Ethernet Switch | CISCO | C9200L-24T-4X 24 Cu PORTS / 4 Fixed SFP 19" Rack Mounted Network Switch + SFP-10G-LR-S SFP+ Transceiver Modules Single Mode (LC) + C9200L-Stack-Kit C/W Stackpower & Stackwise Leads | F23-COM-601 | N/A | EL006 | EL006 | Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10014 |  | 2000-F23-BLK-IC-40001 2000-F23-DRG-IC-40001 | Confirmed | 0 | 5
F23-ETH-603 | Ethernet Switch 3 (VNET IP1LAN DCS Switch) | Ethernet Switch | HIRSCHMANN | GRVSW-652FE + GRVSFP-675FA (Yokogawa) | F23-COM-601 | N/A | EL006 | EL006 | Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10014 |  | 2000-F23-BLK-IC-40001 2000-F23-DRG-IC-40001 | Confirmed | 0 | 5
F23-ETH-604 | Ethernet Switch 4 (PCN Switch 3) | Ethernet Switch | CISCO | C9200L-24T-4X 24 Cu PORTS / 4 Fixed SFP 19" Rack Mounted Network Switch + SFP-10G-LR-S SFP+ Transceiver Modules Single Mode (LC) + C9200L-Stack-Kit C/W Stackpower & Stackwise Leads | F23-COM-601 | N/A | EL006 | EL006 | Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10014 |  | 2000-F23-BLK-IC-40001 2000-F23-DRG-IC-40001 | Confirmed | 0 | 5
F23-ETH-605 | Ethernet Switch 5 (CCTV Switch) | Ethernet Switch | CISCO | IE-3300-8P2S: 8xCu + 2xSFP DIN rail mounted network switch with PoE budget | F23-COM-601 | N/A | EL006 | EL006 | Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10014 |  | 2000-F23-BLK-IC-40001 2000-F23-DRG-IC-40001 | Confirmed | 0 | 5
F23-ETH-606 | Ethernet Switch 6 (VNET IP2LAN DCS Switch) | Ethernet Switch | HIRSCHMANN | GRVSW-652FE + GRVSFP-675FA (Yokogawa) | F23-COM-601 | N/A | EL006 | EL006 | Supplied as part of the Switchroom package. | 2000-F00-STS-EL-10014 |  | 2000-F23-BLK-IC-40001 2000-F23-DRG-IC-40001 | Confirmed | 0 | 5