## Cable schedule
Cable Number | Cable Origin Equip. Number | Equipment Name | Cable Destination Equip. Number | Length (m) | Insulation (kV) | Conductor | No. of Cores / Pairs | Conductor Size (mm2) | Construction | Cable Type / Size / Construction | Installation method | Cable Supplier | Cable Installer | Cable Terminator | Drawing Reference | Status | Revision | Comments | Schematic / Termination Drawing | Cable Origin | Cable Destination | Installation method Switchroom | Cable Supplier EL006 | Cable Installer EL006 | Cable Terminator EL006 | Standard Installation Drawing Reference | Cable Supplier CN037-E&I | Cable Installer CN037-E&I | Cable Terminator CN037-E&I | Page
F23TR601-P1 | TSF3-2 | 33kV Overhead Line Power Pole Recloser | F23-TR-601 | 180 | 19/33kV | Cu | 3C | 70 | XLPE/CWS/PVC | 3C 70mm² Cu 19/33kV kV XLPE/CWS/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-SLD-EL-40001 | Confirmed | G | [12 empty] | 5
F23TR601-E1 | TSF3-2-EB | 33kV Overhead Line Power Pole Earth Bar | F23TR601-EB | 180 | 0.6/1 | Cu | 1C | 120 | GnYe PVC | 1C 120mm² Cu 0.6/1kV GnYe PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-SLD-EL-40001 | Confirmed | G | [12 empty] | 5
F23NR601-N1 | F23-TR-601 | FIM III Booster Station 33/11kV Transformer Secondary Side | F23-NR-601 | 20 | 6.35/11 | Cu | 1C | 50 | XLPE/CWS/PVC | 1C 50mm² Cu 6.35/11kV XLPE/CWS/PVC | Cable Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-SLD-EL-40001 | Confirmed | G | [12 empty] | 5
F23NR601-E1 | F23-TR-601 | FIM III Booster Station 33/11kV Transformer Earth Bar | F23-NR-601 | 20 | 0.6/1 | Cu | 1C | 120 | GnYe PVC | 1C 120mm² Cu 0.6/1kV GnYe PVC | Cable Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-SLD-EL-40001 | Confirmed | G | [12 empty] | 5
F23SW601-C1 | TSF3-2 | 33kV Overhead Line Power Pole Recloser | F23-SW-601 | 180 | 0.6/1 | Cu | 6C+E | 1.5 | PVC/PVC | 6C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-SLD-EL-40001 | Confirmed | E | Upstream trips | [11 empty] | 5
F23NR601-C1 | F23-SW-601 | FIM III Booster Station HV Switchboard Incomer | F23-NR-601 | 30 | 0.6/1 | Cu | 6C+E | 2.5 | PVC/PVC | 6C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Cable Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-SLD-EL-40001 | Confirmed | 0 | SE330-AU protection CT2 and sensing resistor ER-15kV | [11 empty] | 5
F23SW601-P1 | F23-TR-601 | FIM III Booster Station 33/11kV Transformer | F23-SW-601 | 30 | 6.35/11 | Cu | 3C | 120 | XLPE/CWS/PVC | 3C 120mm² Cu 6.35/11kV XLPE/CWS/PVC | Cable Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-SLD-EL-40001 | Confirmed | G | [12 empty] | 5
F23SW601-C8 | F23-TR-601 | FIM III Booster Station 33/11kV Transformer | F23-SW-601 | 30 | 0.6/1 | Cu | 12C+E | 1.5 | PVC/PVC | 12C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Cable Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-SLD-EL-40001 | Confirmed | E | Transformer instrumentation, alarm and trips | [11 empty] | 5
F23SW601EB-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23-SW-601 | Note 8 | 0.6/1 | Cu | 1C | 120 | GnYe PVC | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | G | Refer Note 8 | [11 empty] | 5
F23SW601EB-E2 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23-SW-601 | Note 8 | 0.6/1 | Cu | 1C | 120 | GnYe PVC | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | G | Refer Note 8 | [11 empty] | 5
F23TR602-R1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23-TR-602 | Note 8 | 6.35/11 | Cu | 1C | 50 | ATC/EPR/WBT/CWB/XHD-90-PCP | 1C 50mm² Cu 6.35/11kV ATC/EPR/WBT/CWB/XHD-90-PCP | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23TR602-W1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23-TR-602 | Note 8 | 6.35/11 | Cu | 1C | 50 | ATC/EPR/WBT/CWB/XHD-90-PCP | 1C 50mm² Cu 6.35/11kV ATC/EPR/WBT/CWB/XHD-90-PCP | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23TR602-B1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23-TR-602 | Note 8 | 6.35/11 | Cu | 1C | 50 | ATC/EPR/WBT/CWB/XHD-90-PCP | 1C 50mm² Cu 6.35/11kV ATC/EPR/WBT/CWB/XHD-90-PCP | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23TR602-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23TR602-EB | Note 8 | 0.6/1 | Cu | 1C | 120 | GnYe PVC | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | G | Refer Note 8 | [11 empty] | 5
F23TR602-E2 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23TR602-EB | Note 8 | 0.6/1 | Cu | 1C | 120 | GnYe PVC | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | G | Refer Note 8 | [11 empty] | 5
F23SW601-C2 | F23SR601-LCS | FIM III Booster Station HV Switchboard Remote Switching Panel | F23-SW-601 | Note 8 | 0.6/1 | Cu | 15C+E | 1.5 | PVC/PVC | 15C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-TER-EL-40001 | Confirmed | G | Refer Note 8 | [11 empty] | 5
F23SW601-C3 | F23SR601-LCS | FIM III Booster Station HV Switchboard Remote Switching Panel | F23-SW-601 | Note 8 | 0.6/1 | Cu | 30C+E | 1.5 | PVC/PVC | 30C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-TER-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23SW601-C4 | F23SR601-LCS | FIM III Booster Station HV Switchboard Remote Switching Panel | F23-SW-601 | Note 8 | 0.6/1 | Cu | 30C+E | 1.5 | PVC/PVC | 30C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-TER-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23SW601-C5 | F23SR601-LCS | FIM III Booster Station HV Switchboard Remote Switching Panel | F23-SW-601 | Note 8 | 0.6/1 | Cu | 30C+E | 1.5 | PVC/PVC | 30C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-TER-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23SW601-C6 | F23SR601-LCS | FIM III Booster Station HV Switchboard Remote Switching Panel | F23-SW-601 | Note 8 | 0.6/1 | Cu | 30C+E | 1.5 | PVC/PVC | 30C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-TER-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23SW601-C7 | F23SR601-LCS | FIM III Booster Station HV Switchboard Remote Switching Panel | F23-SW-601 | Note 8 | 0.6/1 | Cu | 30C+E | 1.5 | PVC/PVC | 30C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-TER-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23SW601LCS-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23SW601-LCS | Note 8 | 0.6/1 | Cu | 1C | 16 | GnYe PVC | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | G | Refer Note 8 | [11 empty] | 5
F23PP651VS-R1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP651-VS | Note 8 | 6.35/11 | Cu | 1C | 50 | ATC/EPR/WBT/CWB/XHD-90-PCP | 1C 50mm² Cu 6.35/11kV ATC/EPR/WBT/CWB/XHD-90-PCP | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23PP651VS-W1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP651-VS | Note 8 | 6.35/11 | Cu | 1C | 50 | ATC/EPR/WBT/CWB/XHD-90-PCP | 1C 50mm² Cu 6.35/11kV ATC/EPR/WBT/CWB/XHD-90-PCP | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23PP651VS-B1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP651-VS | Note 8 | 6.35/11 | Cu | 1C | 50 | ATC/EPR/WBT/CWB/XHD-90-PCP | 1C 50mm² Cu 6.35/11kV ATC/EPR/WBT/CWB/XHD-90-PCP | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23PP651VS-E1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP651-VS | Note 8 | 0.6/1 | Cu | 1C | 120 | GnYe PVC | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23PP651VS-C1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP651-VS | Note 8 | 0.6/1 | Cu | 10C+E | 1.5 | PVC/PVC | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-TER-EL-40002 | Confirmed | 0 | [12 empty] | 5
F23PP651-P1 | F23PP651-VS | FIM III Booster Pump 1 Variable Speed Drive | F23-PP-651 | 40 | 3.8/6.6 | Cu | 3C | 120 | XLPE/CWS/PVC | 3C 120mm² Cu 3.8/6.6kV XLPE/CWS/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-EL006-B02-40023 2000-EL006-D02-40013 | Confirmed | 0 | [12 empty] | 5
F23PP651-E1 | F23PP651-VS | FIM III Booster Pump 1 Variable Speed Drive | F23-PP-651 | 40 | 0.6/1 | Cu | 1C | 120 | GnYe PVC | 1C 120mm² Cu 0.6/1kV GnYe PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-SLD-EL-40001 | Confirmed | 0 | [12 empty] | 5
F23PP651-P2 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP651-HTR | 40 | 0.6/1 | Cu | 2C+E | 2.5 | PVC/PVC | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-TER-EL-40003 | Confirmed | 0 | [12 empty] | 5
F23PP651-C1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP651-LCS | 40 | 0.6/1 | Cu | 6C+E | 1.5 | PVC/PVC | 6C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-TER-EL-40003 | Confirmed | 0 | [12 empty] | 5
F23PP651-I1 | F23-DCS-601 | FIM III Booster Station HV/LV Switchroom DCS Panel | F23PP651-RTD | 40 | 0.11 | Cu | 12TR | 1.5 | PVC/IOSCN/PVC | 12TR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-TER-IC-40002 | Confirmed | 0 | [12 empty] | 5
F23PP652VS-R1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP652-VS | Note 8 | 6.35/11 | Cu | 1C | 50 | ATC/EPR/WBT/CWB/XHD-90-PCP | 1C 50mm² Cu 6.35/11kV ATC/EPR/WBT/CWB/XHD-90-PCP | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23PP652VS-W1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP652-VS | Note 8 | 6.35/11 | Cu | 1C | 50 | ATC/EPR/WBT/CWB/XHD-90-PCP | 1C 50mm² Cu 6.35/11kV ATC/EPR/WBT/CWB/XHD-90-PCP | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23PP652VS-B1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP652-VS | Note 8 | 6.35/11 | Cu | 1C | 50 | ATC/EPR/WBT/CWB/XHD-90-PCP | 1C 50mm² Cu 6.35/11kV ATC/EPR/WBT/CWB/XHD-90-PCP | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23PP652VS-E1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP652-VS | Note 8 | 0.6/1 | Cu | 1C | 120 | GnYe PVC | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-SLD-EL-40001 | Confirmed | E | Refer Note 8 | [11 empty] | 5
F23PP652VS-C1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP652-VS | Note 8 | 0.6/1 | Cu | 10C+E | 1.5 | PVC/PVC | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 | 2000-F23-TER-EL-40002 | Confirmed | 0 | [12 empty] | 5
F23PP652-P1 | F23PP652-VS | FIM III Booster Pump 2 Variable Speed Drive | F23-PP-652 | 50 | 3.8/6.6 | Cu | 3C | 120 | XLPE/CWS/PVC | 3C 120mm² Cu 3.8/6.6kV XLPE/CWS/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-EL006-B02-40023 2000-EL006-D02-40013 | Confirmed | 0 | [12 empty] | 5
F23PP652-E1 | F23PP652-VS | FIM III Booster Pump 2 Variable Speed Drive | F23-PP-652 | 50 | 0.6/1 | Cu | 1C | 120 | GnYe PVC | 1C 120mm² Cu 0.6/1kV GnYe PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-SLD-EL-40001 | Confirmed | 0 | [12 empty] | 5
F23PP652-P2 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP652-HTR | 50 | 0.6/1 | Cu | 2C+E | 2.5 | PVC/PVC | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-TER-EL-40003 | Confirmed | 0 | [12 empty] | 5
F23PP652-C1 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23PP652-LCS | 50 | 0.6/1 | Cu | 6C+E | 1.5 | PVC/PVC | 6C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-TER-EL-40003 | Confirmed | 0 | [12 empty] | 5
F23PP652-I1 | F23-DCS-601 | FIM III Booster Station HV/LV Switchroom DCS Panel | F23PP652-RTD | 50 | 0.11 | Cu | 12TR | 1.5 | PVC/IOSCN/PVC | 12TR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-TER-IC-40002 | Confirmed | 0 | [12 empty] | 5
Client: | NORTHERN STAR RESOURCES |  | FIM III BOOSTER STATION CABLE SCHEDULE - LV CABLES | [26 empty] | 6
Project: Document No.: | KCGM FIM TSF PROJECT 2000-F23-LST-EL-40003 | [28 empty] | 6
Revision: | 0 | [28 empty] | 6
F23SW602-R1 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-W1 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-B1 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-N1 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-R2 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-W2 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-B2 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-N2 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-R3 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-W3 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-B3 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-N3 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-R4 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-W4 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-B4 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602-N4 | F23-TR-602 | FIM III Booster Station 11/0.433kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 1C 500mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23TR602-C2 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-TR-602 | Note 8 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TER-EL-40011 | [10 empty] | 6
F23TR602-I1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | F23-TR-602 | Note 8 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TER-EL-40011 2000-F23-TER-IC-40009 | [10 empty] | 6
F23SW602EB-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23SW602-EB | Note 8 | [5 empty] | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23SW602EB-E2 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23SW602-EB | Note 8 | [5 empty] | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 6
F23EB601-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23-EB-601 | 90 | [5 empty] | 1C 120mm² Cu 0.6/1kV GnYe PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G | [12 empty] | 6
F75EB606-E1 |  | Decant Dam 4 Area Electrode | F75-EB-606 | 5 | [5 empty] | 1C 120mm² Cu 0.6/1kV GnYe PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E | [12 empty] | 6
F23SW602-C1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | F23-SW-602 | Note 8 | [5 empty] | 15C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TER-EL-40011 2000-F23-TER-IC-40001 | [10 empty] | 6
F23SW602-C2 | F23-SW-601 | FIM III Booster Station HV Switchboard | F23-SW-602 | Note 8 | [5 empty] | 6C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TER-EL-40011 | [10 empty] | 6
F23SW602-C3 | F23SR601-LCS01/02 | FIM III Booster Station Switchroom Emergency Shutdown | F23-SW-602 | Note 8 | [5 empty] | 6C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TER-EL-40012 | [10 empty] | 6
F23SR601LCS-C1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | F23SR601-LCS01/02 | Note 8 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TER-EL-40012 2000-F23-TER-IC-40001 | [10 empty] | 6
F23SW602-C5 | F23-TR-602 | FIM III Booster Station 33kV/11kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8. Formerly F23AFD602-C1-R | 2000-F23-TER-EL-40011 | [10 empty] | 6
F23SW602-C6 | F23-TR-602 | FIM III Booster Station 33kV/11kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8. Formerly F23AFD602-C1-W | 2000-F23-TER-EL-40011 | [10 empty] | 6
F23SW602-C7 | F23-TR-602 | FIM III Booster Station 33kV/11kV Transformer | F23-SW-602 | Note 8 | [5 empty] | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8. Formerly F23AFD602-C1-B | 2000-F23-TER-EL-40011 | [10 empty] | 6
F23SW602LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23SW602-LCS | Note 8 | [5 empty] | 20C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TER-EL-40011 | [10 empty] | 6
F23SW602LCS-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23SW602-LCS | Note 8 | [5 empty] | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | [11 empty] | 6
F23DCS601-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23-DCS-601 | Note 8 | [5 empty] | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | [11 empty] | 6
F23RTU606-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23-RTU-606 | Note 8 | [5 empty] | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | [11 empty] | 6
F23HF601-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-HF-601 | Note 8 | [5 empty] | 4C+E 95mm² Cu 0.6/1kV XLPE/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-SCM-EL-40031 | [10 empty] | 6
F23HF601-P2 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-HF-601 | Note 8 | [5 empty] | 4C+E 95mm² Cu 0.6/1kV XLPE/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-SCM-EL-40031 | [10 empty] | 6
F23HF601-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23-HF-601 | Note 8 | [5 empty] | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SCM-EL-40031 | [10 empty] | 6
F23HF601-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-HF-601 | Note 8 | [5 empty] | 2C+E 6mm² Cu 0.6/1kV R-EP-90 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8. Formerly F23HF602-C1-R | 2000-F23-SCM-EL-40031 2000-F23-TER-EL-40011 | [10 empty] | 6
F23HF601-C2 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-HF-601 | Note 8 | [5 empty] | 2C+E 6mm² Cu 0.6/1kV R-EP-90 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8. Formerly F23HF602-C1-W | 2000-F23-SCM-EL-40031 2000-F23-TER-EL-40011 | [10 empty] | 6
F23HF601-C3 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-HF-601 | Note 8 | [5 empty] | 2C+E 6mm² Cu 0.6/1kV R-EP-90 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8. Formerly F23HF602-C1-B | 2000-F23-SCM-EL-40031 2000-F23-TER-EL-40011 | [10 empty] | 6
F23PW651VS-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PW651-VS | Note 8 | [5 empty] | 3C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-SCM-EL-40020 | [10 empty] | 6
F23PW651-P1 | F23PW651-VS | FIM III Booster Pump 1 Seal Water Pump 1 Variable Speed Drive | F23-PW-651 | 70 | [5 empty] | 3C+3E 4mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC FLEXIBLE X90 | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-SCM-EL-40020 | [10 empty] | 6
F23PW651VS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PW651-VS | Note 8 | [5 empty] | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-SCM-EL-40020 | [10 empty] | 6
F23PW651LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PW651-LCS | 70 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-EL-40020 | [10 empty] | 6
F23PW651VS-E1 | F23SR601-EB | FIM III Booster Station Earth Bar | F23PW651-VS | Note 8 | [5 empty] | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SCM-EL-40020 | [10 empty] | 6
F23PW652VS-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PW652-VS | Note 8 | [5 empty] | 3C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-SCM-EL-40021 | [10 empty] | 6
F23PW652-P1 | F23PW652-VS | FIM III Booster Pump 1 Seal Water Pump 2 Variable Speed Drive | F23-PW-652 | 70 | [5 empty] | 3C+3E 4mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC FLEXIBLE X90 | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-SCM-EL-40021 | [10 empty] | 6
F23PW652VS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PW652-VS | Note 8 | [5 empty] | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-SCM-EL-40021 | [10 empty] | 6
F23PW652LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PW652-LCS | 70 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-EL-40021 | [10 empty] | 6
F23PW652VS-E1 | F23SR601-EB | FIM III Booster Station Earth Bar | F23PW652-VS | Note 8 | [5 empty] | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SCM-EL-40021 | [10 empty] | 6
F23PW653VS-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PW653-VS | Note 8 | [5 empty] | 3C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-SCM-EL-40022 | [10 empty] | 6
F23PW653-P1 | F23PW653-VS | FIM III Booster Pump 2 Seal Water Pump 1 Variable Speed Drive | F23-PW-653 | 70 | [5 empty] | 3C+3E 4mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC FLEXIBLE X90 | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-SCM-EL-40022 | [10 empty] | 6
F23PW653VS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PW653-VS | Note 8 | [5 empty] | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-SCM-EL-40022 | [10 empty] | 6
F23PW653LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PW653-LCS | 70 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-EL-40022 | [10 empty] | 6
F23PW653VS-E1 | F23SR601-EB | FIM III Booster Station Earth Bar | F23PW653-VS | Note 8 | [5 empty] | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SCM-EL-40022 | [10 empty] | 6
F23PW654VS-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PW654-VS | Note 8 | [5 empty] | 3C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-SCM-EL-40023 | [10 empty] | 7
F23PW654-P1 | F23PW654-VS | FIM III Booster Pump 2 Seal Water Pump 2 Variable Speed Drive | F23-PW-654 | 70 | [5 empty] | 3C+3E 4mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC FLEXIBLE X90 | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-SCM-EL-40023 | [10 empty] | 7
F23PW654VS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PW654-VS | Note 8 | [5 empty] | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-SCM-EL-40023 | [10 empty] | 7
F23PW654LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PW654-LCS | 70 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-EL-40023 | [10 empty] | 7
F23PW654VS-E1 | F23SR601-EB | FIM III Booster Station Earth Bar | F23PW654-VS | Note 8 | [5 empty] | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SCM-EL-40023 | [10 empty] | 7
F75FL600-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75-FL-600 | 70 | [5 empty] | 4C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-SCM-EL-40024 | [10 empty] | 7
F23HY420-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-HY-420 | 50 | [5 empty] | 3C+E 16mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-F23-SCM-EL-40025 | [10 empty] | 7
F23HY420-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-HY-420 | 50 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-SCM-EL-40025 | [10 empty] | 7
F23SE431-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-SE-431 | 30 | [5 empty] | 4C+E 4mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-F23-SCM-EL-40030 | [10 empty] | 7
F75PW665-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75-PW-665 | 70 | [5 empty] | 3C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F75-SCM-EL-40005 | [10 empty] | 7
F75PW665LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW665-LCS | 70 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F75-SCM-EL-40005 | [10 empty] | 7
F23FN653-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-FN-653 | 40 | [5 empty] | 3C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-EL-40026 | [10 empty] | 7
F23FN653LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23FN653-LCS | 40 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-EL-40026 | [10 empty] | 7
F23FN654-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-FN-654 | 40 | [5 empty] | 3C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-EL-40027 | [10 empty] | 7
F23FN654LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23FN654-LCS | 40 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-EL-40027 | [10 empty] | 7
F23FN651-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-FN-651 | 40 | [5 empty] | 3C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-EL-40028 | [10 empty] | 7
F23FN651LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23FN651-LCS | 40 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-EL-40028 | [10 empty] | 7
F23FN652-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-FN-652 | 40 | [5 empty] | 3C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-EL-40029 | [10 empty] | 7
F23FN652LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23FN652-LCS | 40 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-EL-40029 | [10 empty] | 7
F75SW557-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75-SW-557 | 170 | [5 empty] | 4C+E 150mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F75-SCM-40006 | [10 empty] | 7
F75PW606VS-R1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW606-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40001 | [10 empty] | 7
F75PW606VS-W1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW606-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40001 | [10 empty] | 7
F75PW606VS-B1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW606-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40001 | [10 empty] | 7
F75PW606VS-R2 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW606-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40001 | [10 empty] | 7
F75PW606VS-W2 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW606-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40001 | [10 empty] | 7
F75PW606VS-B2 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW606-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40001 | [10 empty] | 7
F75PW606VS-E1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW606-VS | Note 8 | [5 empty] | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F75-SCM-EL-40001 | [10 empty] | 7
F75PW606-P1 | F75PW606-VS | Decant Dam 4 Return Pump 1 Variable Speed Drive | F75-PW-606 | 100 | [5 empty] | 3C+3E 300mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC FLEXIBLE X90 | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-F75-SCM-EL-40001 | [10 empty] | 7
F75PW606-P2 | F75PW606-VS | Decant Dam 4 Return Pump 1 Variable Speed Drive | F75-PW-606 | 100 | [5 empty] | 3C+3E 300mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC FLEXIBLE X90 | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-F75-SCM-EL-40001 | [10 empty] | 7
F75PW606-P3 | F75PW606-VS | Decant Dam 4 Return Pump 1 Variable Speed Drive | F75-PW-606 | 100 | [5 empty] | 3C+3E 300mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC FLEXIBLE X90 | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Deleted | 0 |  | 2000-F75-SCM-EL-40001 | [10 empty] | 7
F75PW606-P7 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75-PW-606 | 100 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F75-SCM-EL-40001 | [10 empty] | 7
F75PW606-I1 | F75-RTU-606 | FIM III Booster Station Switchroom RTU Panel | F75-PW-606 | 100 | [5 empty] | 12TR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F75-SCM-EL-40001 2000-F75-TER-IC-40003/4 | [10 empty] | 7
F75PW606VS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW606-VS | Note 8 | [5 empty] | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F75-SCM-EL-40001 | [10 empty] | 7
F75PW606LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW606-LCS | 100 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F75-SCM-EL-40001 | [10 empty] | 7
F75PW607VS-R1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW607-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40002 | [10 empty] | 7
F75PW607VS-W1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW607-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40002 | [10 empty] | 7
F75PW607VS-B1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW607-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40002 | [10 empty] | 7
F75PW607VS-R2 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW607-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40002 | [10 empty] | 7
F75PW607VS-W2 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW607-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40002 | [10 empty] | 7
F75PW607VS-B2 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW607-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40002 | [10 empty] | 7
F75PW607VS-E1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW607-VS | Note 8 | [5 empty] | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F75-SCM-EL-40002 | [10 empty] | 7
F75PW607-P1 | F75PW607-VS | Decant Dam 4 Return Pump 2 Variable Speed Drive | F75-PW-607 | 100 | [5 empty] | 3C+3E 300mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC FLEXIBLE X90 | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-F75-SCM-EL-40002 | [10 empty] | 7
F75PW607-P2 | F75PW607-VS | Decant Dam 4 Return Pump 2 Variable Speed Drive | F75-PW-607 | 100 | [5 empty] | 3C+3E 300mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC FLEXIBLE X90 | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-F75-SCM-EL-40002 | [10 empty] | 7
F75PW607-P3 | F75PW607-VS | Decant Dam 4 Return Pump 2 Variable Speed Drive | F75-PW-607 | 100 | [5 empty] | 3C+3E 300mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC FLEXIBLE X90 | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Deleted | 0 |  | 2000-F75-SCM-EL-40002 | [10 empty] | 7
F75PW607-P7 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75-PW-607 | 100 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F75-SCM-EL-40002 | [10 empty] | 7
F75PW607-I1 | F75-RTU-606 | FIM III Booster Station Switchroom RTU Panel | F75-PW-607 | 100 | [5 empty] | 12TR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F75-SCM-EL-40002 2000-F75-TER-IC-40004 | [10 empty] | 7
F75PW607VS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW607-VS | Note 8 | [5 empty] | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F75-SCM-EL-40002 | [10 empty] | 7
F75PW607LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW607-LCS | 100 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F75-SCM-EL-40002 | [10 empty] | 7
F75PW608VS-R1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW608-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40003 | [10 empty] | 7
F75PW608VS-W1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW608-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40003 | [10 empty] | 7
F75PW608VS-B1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW608-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40003 | [10 empty] | 8
F75PW608VS-R2 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW608-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40003 | [10 empty] | 8
F75PW608VS-W2 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW608-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40003 | [10 empty] | 8
F75PW608VS-B2 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW608-VS | Note 8 | [5 empty] | 1C 185mm² Cu 0.6/1kV XLPE/PVC FLEXIBLE X110 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F75-SCM-EL-40003 | [10 empty] | 8
F75PW608VS-E1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW608-VS | Note 8 | [5 empty] | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F75-SCM-EL-40003 | [10 empty] | 8
F75PW608-P1 | F75PW608-VS | Decant Dam 4 Return Pump 3 Variable Speed Drive | F75-PW-608 | 100 | [5 empty] | 3C+3E 300mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC FLEXIBLE X90 | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-F75-SCM-EL-40003 | [10 empty] | 8
F75PW608-P2 | F75PW608-VS | Decant Dam 4 Return Pump 3 Variable Speed Drive | F75-PW-608 | 100 | [5 empty] | 3C+3E 300mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC FLEXIBLE X90 | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-F75-SCM-EL-40003 | [10 empty] | 8
F75PW608-P3 | F75PW608-VS | Decant Dam 4 Return Pump 3 Variable Speed Drive | F75-PW-608 | 100 | [5 empty] | 3C+3E 300mm² Cu 0.6/1kV XLPE/PVC/CuSCN/PVC FLEXIBLE X90 | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Deleted | 0 |  | 2000-F75-SCM-EL-40003 | [10 empty] | 8
F75PW608-P7 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75-PW-608 | 100 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F75-SCM-EL-40003 | [10 empty] | 8
F75PW608-I1 | F75-RTU-606 | FIM III Booster Station Switchroom RTU Panel | F75-PW-608 | 100 | [5 empty] | 12TR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F75-SCM-EL-40003 2000-F75-TER-IC-40006 | [10 empty] | 8
F75PW608VS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW608-VS | Note 8 | [5 empty] | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F75-SCM-EL-40003 | [10 empty] | 8
F75PW608LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PW608-LCS | 100 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F75-SCM-EL-40003 | [10 empty] | 8
F75PV414-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75-PV-414 | 60 | [5 empty] | 3C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-F75-SCM-EL-40003 | [10 empty] | 8
F75PV414LCS-C1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75PV414-LCS | 60 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F75-SCM-EL-40003 | [10 empty] | 8
F23PP651VS-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PP651-VS | Note 8 | [5 empty] | 4C+E 6mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 8
F23PP652VS-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23PP652-VS | Note 8 | [5 empty] | 4C+E 6mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-SLD-EL-40011 | [10 empty] | 8
F23DB601-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-DB-601 | Note 8 | [5 empty] | 4C+E 150mm² Cu 0.6/1kV XLPE/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F23DB601-W3 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board | F23-PE-601 | Note 8 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F23DB601-E1 | F23SR601-EB | FIM III Booster Station Earth Bar | F23-DB-601 | Note 8 | [5 empty] | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F23DB602-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23-DB-602 | Note 8 | [5 empty] | 4C+E 150mm² Cu 0.6/1kV XLPE/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 8
F23DB602-C1 | F23-FIP-601 | FIM III Booster Station Switchroom Fire Indicator Panel | F23-DB-602 | Note 8 | [5 empty] | 2C 1.5mm² Cu 0.6/1kV R-EP-110°C | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 8
F23DB602-E1 | F23SR601-EB | FIM III Booster Station Earth Bar | F23-DB-602 | Note 8 | [5 empty] | 1C 120mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 8
F23UPS601ISL-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F23UPS601-ISL | Note 8 | [5 empty] | 4C+E 16mm² Cu 0.6/1kV XLPE/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23UPS601-P1 | F23UPS601-ISL | FIM III Booster Station Switchroom 240V AC UPS Bypass Switch | F23-UPS-601 | Note 8 | [5 empty] | 4C+E 10mm² Cu 0.6/1kV R-EP-90 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23UPS601ISL-P2 | F23-UPS-601 | FIM III Booster Station Switchroom 240V AC UPS | F23UPS601-ISL | Note 8 | [5 empty] | 2C+E 10mm² Cu 0.6/1kV R-EP-90 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23UPS601-C1 | F23UPS601-ISL | FIM III Booster Station Switchroom 240V AC UPS Bypass Switch | F23-UPS-601 | Note 8 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23DB603-P1 | F23UPS601-ISL | FIM III Booster Station Switchroom 240V AC UPS Bypass Switch | F23-DB-603 | Note 8 | [5 empty] | 2C+E 16mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23UPS601ISL-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23UPS601-ISL | Note 8 | [5 empty] | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23UPS601-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23-UPS-601 | Note 8 | [5 empty] | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23DB603-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23-DB-603 | Note 8 | [5 empty] | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23DCS601-P1 | F23-DB-603 | FIM III Booster Station Switchroom 240V AC UPS DB | F23-DCS-601 | Note 8 | [5 empty] | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23SW602-P1 | F23-DB-603 | FIM III Booster Station Switchroom 240V AC UPS DB | F23-SW-602 | Note 8 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23SW602-P2 | F23-DB-603 | FIM III Booster Station Switchroom 240V AC UPS DB | F23-SW-602 | Note 8 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23RTU606-P1 | F23-DB-603 | FIM III Booster Station Switchroom 240V AC UPS DB | F23-RTU-606 | Note 8 | [5 empty] | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23COM601-P1 | F23-DB-603 | FIM III Booster Station Switchroom 240V AC UPS DB | F23-COM-601 | Note 8 | [5 empty] | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23COM601-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23-COM-601 | Note 8 | [5 empty] | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | [11 empty] | 8
F23PP651VS-P2 | F23-DB-603 | FIM III Booster Station Switchroom 240V AC UPS DB | F23PP651-VS | Note 8 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23PP652VS-P2 | F23-DB-603 | FIM III Booster Station Switchroom 240V AC UPS DB | F23PP652-VS | Note 8 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23FIP601-P1 | F23-DB-603 | FIM III Booster Station Switchroom 240V AC UPS DB | F23-FIP-601 | Note 8 | [5 empty] | 2C 1.5mm² Cu 0.45/0.75kV R-EP-110°C | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TLD-EL-40013 | [10 empty] | 8
F23FIP601-C1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | F23-FIP-601 | Note 8 | [5 empty] | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TER-IC-40009 | [10 empty] | 8
F23FIP601XE-P1 | F23-FIP-601 | FIM III Booster Station Switchroom Fire Indicator Panel | F23FIP601-XE | Note 8 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | [11 empty] | 8
F23FIP601-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23-FIP-601 | Note 8 | [5 empty] | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | [11 empty] | 8
F23BC601-P1 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board | F23-BC-601 | Note 8 | [5 empty] | 4C+E 6mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40001 | [10 empty] | 8
F23BC601-E1 | F23SR601-EB | FIM III Booster Station Switchroom Earth Bar | F23-BC-601 | Note 8 | [5 empty] | 1C 16mm² Cu 0.6/1kV GnYe PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | [11 empty] | 8
F23DB601-R4 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board | F23-SW-601 | Note 8 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F23DB601-W4 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board | F23-TR-602 | Note 8 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F23DB601-B4 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | Note 8 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F23DB601-R5 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | Note 8 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F23DB601-W5 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | Note 8 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F23DB601-B5 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | Note 8 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F23DB601-R6 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | 50 | [5 empty] | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F23DB601-W6 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | 80 | [5 empty] | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F23DB601-RWB7 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | Note 8 | [5 empty] | 4C+E 16mm² Cu 0.6/1kV XLPE/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F23DB601-RWB8 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | 80 | [5 empty] | 4C+E 16mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F23DB601-RWB9 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | 50 | [5 empty] | 4C+E 16mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-TLD-EL-40011 | [10 empty] | 8
F75PP482-P1 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board | F75-PP-482 | 90 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TLD-EL-40011 | [10 empty] | 9
F75PP483-P1 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board | F75-PP-483 | 90 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-TLD-EL-40011 | [10 empty] | 9
F75PP484-P1 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board | F75-PP-484 | 90 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-TLD-EL-40011 | [10 empty] | 9
F23DB601-R13 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | 40 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-TLD-EL-40011 | [10 empty] | 9
F23DB601-W13 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | 80 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-TLD-EL-40011 | [10 empty] | 9
F23DB601-B13 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | 50 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit/Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-TLD-EL-40011 | [10 empty] | 9
F23DB601-R14 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | Note 8 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 9
F23DB601-W14 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board | F23-SE-431 | 20 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Cable ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TLD-EL-40011 | [10 empty] | 9
F23DB601-R15 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | 90 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | G |  | 2000-F23-TLD-EL-40011 | [10 empty] | 9
F23DB601-B15 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | Note 8 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 9
F23DB601-R16 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board | F23-SW-601 | 30 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Cable ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-F23-TLD-EL-40011 | [10 empty] | 9
F23DB601-R17 | F23-DB-601 | FIM III Booster Station Switchroom and Area L&SP Distribution Board |  | Note 8 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40011 | [10 empty] | 9
F23BC601-C1 | F23-BC-601 | FIM III Booster Station Switchroom 48V DC Battery Charger | F23-DCS-601 | Note 8 | [5 empty] | 4C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TLD-EL-40001 2000-F23-TER-IC-40001 | [10 empty] | 9
F23SW601-P3 | F23-BC-601 | FIM III Booster Station Switchroom 48V DC Battery Charger | F23-SW-601 | Note 8 | [5 empty] | 2C+E 6mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40001 | [10 empty] | 9
F23SW601LCS-P1 | F23-BC-601 | FIM III Booster Station Switchroom 48V DC Battery Charger | F23SW601-LCS | Note 8 | [5 empty] | 2C+E 4mm² Cu 0.6/1kV PVC/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TLD-EL-40001 | [10 empty] | 9
F23DB602-R2 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-W2 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-B2 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB | F23-CP-601 | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-R3 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-W3 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-B3 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-R4 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-W4 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-B4 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-R5 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-W5 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-B5 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-R6 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-W6 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-B6 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-R7 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-W7 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-B7 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-R8 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-W8 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-B8 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-R10 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-W10 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-B10 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-R12 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-W12 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
F23DB602-B12 | F23-DB-602 | FIM III Booster Station Switchroom 415V HVAC DB |  | Note 8 | [5 empty] | Note 8 | Switchroom | EL006 | EL006 | EL006 |  | Preliminary | E | Refer Note 8 | 2000-F23-TLD-EL-40012 | [10 empty] | 9
Client: | NORTHERN STAR RESOURCES |  | FIM III BOOSTER STATION CABLE SCHEDULE - COMMS CABLES | [26 empty] | 10
Project: Document No.: | KCGM FIM TSF PROJECT 2000-F23-LST-EL-40003 | [28 empty] | 10
Revision: | 0 | [28 empty] | 10
F23FOB601-FO1 | F75-FOB-403 | Saline Dam #3 LV Switchroom Communications Rack FOBOT 3 | F23-FOB-601 | N/A | [5 empty] | 24C SMOF OS2 Loose Tube Cores with Water Blocking, Gel Fill and PE/Ny/PE UV Stabilised Sheath | Underground Conduit | By Others | By Others | CN037-E&I |  | Confirmed | 0 |  | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23FOB602-FO1 | F23-FOB-601 | FIM III Booster Station Switchroom Communications Rack FOBOT 1 | F23-FOB-602 | Note 8 | [5 empty] | 24C SMOF OS2 Loose Tube Cores with Water Blocking, Gel Fill and PE/Ny/PE UV Stabilised Sheath | Switchroom | EL006 | EL006 | EL006 |  | Deleted | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F75FOB557-FO1 | F23-FOB-601 | FIM III Booster Station Switchroom Communications Rack FOBOT 1 | F75-FOB-557 | 140 | [5 empty] | 24C SMOF OS2 Loose Tube Cores with Water Blocking, Gel Fill and PE/Ny/PE UV Stabilised Sheath | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23ETH601-FO1 | F23-FOB-601 | FIM III Booster Station Switchroom Communications Rack FOBOT 1 | F23-ETH-601 | Note 8 | [5 empty] | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23ETH602-FO1 | F23-FOB-601 | FIM III Booster Station Switchroom Communications Cabinet FOBOT 2 | F23-ETH-602 | Note 8 | [5 empty] | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 |  | Deleted | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23ETH603-FO1 | F23-FOB-601 | FIM III Booster Station Switchroom Communications Rack FOBOT 1 | F23-ETH-603 | Note 8 | [5 empty] | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23ETH604-FO1 | F23-FOB-601 | FIM III Booster Station Switchroom Communications Rack FOBOT 1 | F23-ETH-604 | Note 8 | [5 empty] | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23ETH605-FO1 | F23-FOB-601 | FIM III Booster Station Switchroom Communications Rack FOBOT 1 | F23-ETH-605 | Note 8 | [5 empty] | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23ETH606-FO1 | F23-FOB-601 | FIM III Booster Station Switchroom Communications Rack FOBOT 1 | F23-ETH-606 | Note 8 | [5 empty] | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23FIP601-FO1 | F23-FOB-601 | FIM III Booster Station Switchroom Communications Rack FOBOT 1 | F23-FIP-601 | Note 8 | [5 empty] | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23ETH606-FO1 | F23-FOB-602 | FIM III Booster Station Switchroom Communications Rack FOBOT 2 | F23-ETH-606 | Note 8 | [5 empty] | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 |  | Deleted | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23ETH604-FO2 | F23-FOB-602 | FIM III Booster Station Switchroom Communications Rack FOBOT 2 | F23-ETH-604 | Note 8 | [5 empty] | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23ETH604-FO3 | F23-FOB-602 | FIM III Booster Station Switchroom Communications Rack FOBOT 2 | F23-ETH-604 | Note 8 | [5 empty] | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23ETH607-FO1 | F23-FOB-602 | FIM III Booster Station Switchroom Communications Rack FOBOT 1 | F23-ETH-607 | Note 8 | [5 empty] | 2C SMOF OS2 Ruggedised Patch Lead | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23PP651VS-D1 | F23-ETH-602 | FIM III Booster Station Ethernet Switch 2 (PCN Switch 2) - Port 1 | F23PP651-VS | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23PP652VS-D1 | F23-ETH-602 | FIM III Booster Station Ethernet Switch 2 (PCN Switch 2) - Port 2 | F23PP652-VS | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23PW651VS-D1 | F23-ETH-602 | FIM III Booster Station Ethernet Switch 2 (PCN Switch 2) - Port 3 | F23PW651-VS | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23PW652VS-D1 | F23-ETH-602 | FIM III Booster Station Ethernet Switch 2 (PCN Switch 2) - Port 4 | F23PW652-VS | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23PW653VS-D1 | F23-ETH-602 | FIM III Booster Station Ethernet Switch 2 (PCN Switch 2) - Port 5 | F23PW653-VS | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23PW654VS-D1 | F23-ETH-602 | FIM III Booster Station Ethernet Switch 2 (PCN Switch 2) - Port 6 | F23PW654-VS | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F75PW606VS-D1 | F23-ETH-604 | FIM III Booster Station Ethernet Switch 4 (Water Services Switch) - Port 2 | F75PW606-VS | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F75PW607VS-D1 | F23-ETH-604 | FIM III Booster Station Ethernet Switch 4 (Water Services Switch) - Port 3 | F75PW607-VS | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F75PW608VS-D1 | F23-ETH-604 | FIM III Booster Station Ethernet Switch 4 (Water Services Switch) - Port 4 | F75PW608-VS | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F75RTU606-D1 | F23-ETH-604 | FIM III Booster Station Ethernet Switch 4 (Water Services Switch) - Port 5 | F75-RTU-606 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F75RTU606-D2 | F23-ETH-604 | FIM III Booster Station Ethernet Switch 4 (Water Services Switch) - Port 6 | F75-RTU-606 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23HF601-D1 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 7 | F23-HF-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23UPS601-D1 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 8 | F23-UPS-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23SW602-D1 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 1 | F23-SW-602 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8. | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23SW602-D2 | F23-GWY-602 | FIM III Booster Station LV Motor Control Centre Anybus Comms Module | F23-SW-602 | Note 8 | [5 empty] | RS485 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23FN651-D1 | F23-ETH-602 | FIM III Booster Station Ethernet Switch 2 (PCN Switch 2) - Port 13 | F23-FN-651 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23FN652-D1 | F23-ETH-602 | FIM III Booster Station Ethernet Switch 2 (PCN Switch 2) - Port 14 | F23-FN-652 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23FN653-D1 | F23-ETH-602 | FIM III Booster Station Ethernet Switch 2 (PCN Switch 2) - Port 15 | F23-FN-653 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23FN654-D1 | F23-ETH-602 | FIM III Booster Station Ethernet Switch 2 (PCN Switch 2) - Port 16 | F23-FN-654 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F75PW665-D1 | F23-ETH-602 | FIM III Booster Station Ethernet Switch 2 (PCN Switch 2) - Port 17 | F75-PW-665 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23HY420-D1 | F23-ETH-602 | FIM III Booster Station Ethernet Switch 2 (PCN Switch 2) - Port 18 | F23-HY-420 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F75PV414-D1 | F23-ETH-604 | FIM III Booster Station Ethernet Switch 4 (PCN Switch 3) - Port 5 | F75-PV-414 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23PM602-D1 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 2 | F23-PM-602 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23AFD602-D1 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 3 | F23-AFD-602 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23SW601-D1 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 4 | F23-SW-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23SW601-D2 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 6 | F23-SW-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23SW601-D3 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 9 | F23-SW-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23SW601-D4 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 10 | F23-SW-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23SW601-D5 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 11 | F23-SW-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23SW601-D6 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 12 | F23-SW-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23DCS601-D1 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 13 | F23-DCS-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23DCS601-D2 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 14 | F23-DCS-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23DCS601-D3 | F23-ETH-603 | FIM III Booster Station Ethernet Switch 3 (VNET IP1LAN DCS Switch) - Port 7 | F23-DCS-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23DCS601-D4 | F23-ETH-603 | FIM III Booster Station Ethernet Switch 3 (VNET IP1LAN DCS Switch) - Port 8 | F23-DCS-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23BC601-D1 | F23-ETH-601 | FIM III Booster Station Ethernet Switch 1 (PCN Switch 1) - Port 5 | F23-BC-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F75SD601-D1 | F23-ETH-605 | FIM III Booster Station Ethernet Switch 5 (CCTV Switch) - Port 1 | F75-SD-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F75CAM601-D1 | F75-SD-601 | FIM III Decant Dam 4 PTZ CCTV Camera Surge Diverter | F75-CAM-601 | 100 | [5 empty] | 4Pr Cu Cat6 SF/UTP Outdoor Cable | Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | F |  | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23DCS601-D5 | F23-ETH-606 | FIM III Booster Station Ethernet Switch 6 (VNET IP2LAN DCS Switch) - Port 7 | F23-DCS-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23DCS601-D6 | F23-ETH-606 | FIM III Booster Station Ethernet Switch 6 (VNET IP2LAN DCS Switch) - Port 8 | F23-DCS-601 | Note 8 | [5 empty] | 4Pr Cu Cat6 SF/UTP | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | F | Refer Note 8 | 2000-F23-BLK-IC-40001 | [10 empty] | 10
F23RTU606-N1 | F23-RTU-606 | FIM III Booster Station Switchroom RTU Panel ACE 3600 Serial Port 1 | F23-RTU-606_Radio | Note 8 | [5 empty] | RS232 c/w 9 pin male plug and RJ45 Plug | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Cable on DCS Equipment List, 2000- F23-LST-IC-40003 | [11 empty] | 10
F23RTU606A-C1 | F23-RTU-606_Radio | FIM III Booster Station Switchroom RTU Panel Data Radio | F23-SS-606A | Note 8 | [5 empty] | CNT-400 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Low Loss 5ohm Cable | [11 empty] | 10
F23RTU606A-C2 |  |  |  | Note 8 | [5 empty] | CNT-400 | [5 empty] | Confirmed | E | Low Loss 5ohm Cable |  | F23-SS-606A | F23-ANT-606A | [8 empty] | 11
F23RTU606-N2 |  |  |  | Note 8 | [5 empty] | RS232 c/w 9 pin male plug and RJ45 Plug | [5 empty] | Confirmed | E | Cable on DCS Equipment List, 2000- F23-LST-IC-40003 |  | F23-RTU-606 | F23-RTU-606_Modem | Switchroom | EL006 | EL006 | EL006 |  |  |  |  | 11
F23RTU606B-C1 |  |  |  | Note 8 | [5 empty] | CNT-400 | [5 empty] | Confirmed | E | Low Loss 5ohm Cable |  | F23-RTU-606_Modem | F23-SS-606B | Switchroom | EL006 | EL006 | EL006 |  |  |  |  | 11
F23RTU606B-C2 |  |  |  | Note 8 | [5 empty] | CNT-400 | [5 empty] | Confirmed | E | Low Loss 5ohm Cable |  | F23-SS-606B | F23-ANT-606B | Switchroom | EL006 | EL006 | EL006 |  |  |  |  | 11
Client: | [19 empty] | NORTHERN STAR RESOURCES | FIM III BOOSTER STATION CABLE SCHEDULE - INSTRUMENT CABLES | [8 empty] | 12
Project: Document No.: | [19 empty] | KCGM 2000-F23-LST-EL-40003 | [9 empty] | 12
Revision: | [19 empty] | 0 | [9 empty] | 12
F23COM601-I1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | F23-COM-601 | Note 8 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TER-IC-40001 | [10 empty] | 12
F23SW602PS-I1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | F23-SW-602 | Note 8 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TER-IC-40001 | [10 empty] | 12
UT23575-I1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | UT23575 | Note 8 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-TER-IC-40008 | [10 empty] | 12
UT23576-I1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | UT23576 | Note 8 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-TER-IC-40008 | [10 empty] | 12
UT23577-I1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | UT23577 | Note 8 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Refer Note 8 | 2000-F23-TER-IC-40008 | [10 empty] | 12
F23TR602-I1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | F23-TR-602 | Note 8 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | E | Refer Note 8 | 2000-F23-TER-IC-40009 | [10 empty] | 12
ZS23550-I1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | ZS23550 | Note 8 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TER-IC-40009 | [10 empty] | 12
ZS23551-I1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | ZS23551 | Note 8 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | G | Refer Note 8 | 2000-F23-TER-IC-40009 | [10 empty] | 12
US23519-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | US23519 | 30 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40021 | [10 empty] | 12
US23539-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | US23539 | 20 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40021 | [10 empty] | 12
ZSO23527-I1 | ZS23527-JB | FIM III Booster Pump 1 Suction Drain Valve Position Switch Junction Box | ZSO23527 | 2 | [5 empty] | Vendor Cable PVC /M12 Straight Plug 4 Pin, 2m | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40021 | [10 empty] | 12
ZSC23527-I1 | ZS23527-JB | FIM III Booster Pump 1 Suction Drain Valve Position Switch Junction Box | ZSC23527 | 2 | [5 empty] | Vendor Cable PVC /M12 Straight Plug 4 Pin, 2m | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40021 | [10 empty] | 12
ZS23527-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | ZS23527-JB | 55 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40021 | [10 empty] | 12
ZSO23545-I1 | ZS23545-JB | FIM III Booster Pump 2 Suction Drain Valve Position Switch Junction Box | ZSO23545 | 2 | [5 empty] | Vendor Cable PVC /M12 Straight Plug 4 Pin, 2m | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40021 | [10 empty] | 12
ZSC23545-I1 | ZS23545-JB | FIM III Booster Pump 2 Suction Drain Valve Position Switch Junction Box | ZSC23545 | 2 | [5 empty] | Vendor Cable PVC /M12 Straight Plug 4 Pin, 2m | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40021 | [10 empty] | 12
ZS23545-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | ZS23545-JB | 35 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40021 | [10 empty] | 12
HS75316-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | HS75316 | 20 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40021 | [10 empty] | 12
HS75317-I1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | HS75317 | 45 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder/Underground | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40003 | [10 empty] | 12
ZSO23512-I1 | ZS23512-JB | Final Tails Line D to FIM III Booster Pump 1 Supply Valve Position Switch Junction Box | ZSO23512 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSC23512-I1 | ZS23512-JB | Final Tails Line D to FIM III Booster Pump 1 Supply Valve Position Switch Junction Box | ZSC23512 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZS23512-I1 | F23-HY-420 | FIM III Booster Station Hydraulic Power Pack Control Panel | ZS23512-JB | 10 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSO23514-I1 | ZS23514-JB | Flushing Water from Decant Dam 4 Bypass to FIM III Booster Pump 1 Supply Valve Position Switch Junction Box | ZSO23514 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSC23514-I1 | ZS23514-JB | Flushing Water from Decant Dam 4 Bypass to FIM III Booster Pump 1 Supply Valve Position Switch Junction Box | ZSC23514 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZS23514-I1 | F23-HY-420 | FIM III Booster Station Hydraulic Power Pack Control Panel | ZS23514-JB | 10 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSO23517-I1 | ZS23517-JB | FIM III Booster Pump 1 to Valve Station Final Tails Discharge Valve Position Switch Junction Box | ZSO23517 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSC23517-I1 | ZS23517-JB | FIM III Booster Pump 1 to Valve Station Final Tails Discharge Valve Position Switch Junction Box | ZSC23517 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZS23517-I1 | F23-HY-420 | FIM III Booster Station Hydraulic Power Pack Control Panel | ZS23517-JB | 40 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSO23518-I1 | ZS23518-JB | FIM III Booster Pump 1 to FIM III Scour Pit Discharge Valve Position Switch Junction Box | ZSO23518 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSC23518-I1 | ZS23518-JB | FIM III Booster Pump 1 to FIM III Scour Pit Discharge Valve Position Switch Junction Box | ZSC23518 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZS23518-I1 | F23-HY-420 | FIM III Booster Station Hydraulic Power Pack Control Panel | ZS23518-JB | 40 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSO23532-I1 | ZS23532-JB | Final Tails Line B to FIM III Booster Pump 2 Supply Valve Position Switch Junction Box | ZSO-23532 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSC23532-I1 | ZS23532-JB | Final Tails Line B to FIM III Booster Pump 2 Supply Valve Position Switch Junction Box | ZSC-23532 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZS23532-I1 | F23-HY-420 | FIM III Booster Station Hydraulic Power Pack Control Panel | ZS23532-JB | 30 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSO23534-I1 | ZS23534-JB | Flushing Water from Decant Dam 4 Bypass to FIM III Booster Pump 2 Supply Valve Position Switch Junction Box | ZSO23534 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSC23534-I1 | ZS23534-JB | Flushing Water from Decant Dam 4 Bypass to FIM III Booster Pump 2 Supply Valve Position Switch Junction Box | ZSC23534 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZS23534-I1 | F23-HY-420 | FIM III Booster Station Hydraulic Power Pack Control Panel | ZS23534-JB | 30 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSO23537-I1 | ZS23537-JB | FIM III Booster Pump 2 to Valve Station Final Tails Discharge Valve Position Switch Junction Box | ZSO23537 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSC23537-I1 | ZS23537-JB | FIM III Booster Pump 2 to Valve Station Final Tails Discharge Valve Position Switch Junction Box | ZSC23537 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZS23537-I1 | F23-HY-420 | FIM III Booster Station Hydraulic Power Pack Control Panel | ZS23537-JB | 50 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSO23538-I1 | ZS23538-JB | FIM III Booster Pump 2 to FIM III Scour Pit Discharge Valve Position Switch Junction Box | ZSO23538 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZSC23538-I1 | ZS23538-JB | FIM III Booster Pump 2 to FIM III Scour Pit Discharge Valve Position Switch Junction Box | ZSC23538 | 2 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
ZS23538-I1 | F23-HY-420 | FIM III Booster Station Hydraulic Power Pack Control Panel | ZS23538-JB | 50 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-PP009-D02-40001 | [10 empty] | 12
XV75301-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | XV75301 | 15 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40022 | [10 empty] | 12
XV75301-P1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | XV75301 | 90 | [5 empty] | 2C+E 10mm² Cu 0.6/1kV PVC/PVC | Ladder/Underground | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-IC-40002 2000-F23-TER-IC-40022 | [10 empty] | 12
XV75302-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | XV75302 | 15 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 2000-F23-TER-IC-40022 | [10 empty] | 12
XV75302-P1 | F23-DCS-601 | FIM III Booster Station Switchroom DCS Panel | XV75302 | 90 | [5 empty] | 2C+E 10mm² Cu 0.6/1kV PVC/PVC | Ladder/Underground | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-SCM-IC-40002 2000-F23-TER-IC-40022 | [10 empty] | 12
FIT23541-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | FIT23541 | 20 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40023 | [6 empty] | 2000-F00-STD-EL-10015 |  |  |  | 12
FIT75321-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | FIT75321 | 15 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40023 | [6 empty] | 2000-F00-STD-EL-10015 |  |  |  | 12
PIT23511-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | PIT23511 | 55 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40023 | [10 empty] | 12
PIT23520-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | PIT23520 | 40 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40023 | [10 empty] | 12
FIT23523-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | FIT23523 | 70 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40023 | [6 empty] | 2000-F00-STD-EL-10015 |  |  |  | 12
PIT75303-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | PIT75303 | 65 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40023 | [10 empty] | 12
PIT23531-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | PIT23531 | 35 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40023 | [10 empty] | 12
PIT23540-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | PIT23540 | 15 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40023 | [10 empty] | 12
FIT23543-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | FIT23543 | 25 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40023 | [6 empty] | 2000-F00-STD-EL-10015 |  |  |  | 12
FIT23521-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | FIT23521 | 35 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40023 | [6 empty] | 2000-F00-STD-EL-10015 |  |  |  | 12
PIT75306-I1 | F23-IJB-601 | FIM III Booster Station Instrument Junction Box | PIT75306 | 25 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | E |  | 2000-F23-TER-IC-40023 | [10 empty] | 12
LIT75300-I1 |  |  |  | 15 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Ladder |  |  |  |  | Confirmed | E |  | 2000-F23-TER-IC-40023 | F23-IJB-601 | LIT75300-JB | [8 empty] | 13
LIT75300-I2 |  |  |  | 15 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run |  |  |  |  | Confirmed | E |  | 2000-F23-TER-IC-40023 | LIT75300-JB | LIT75300 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
LCV75300-I1 |  |  |  | 15 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Ladder |  |  |  |  | Confirmed | 0 |  | 2000-F23-TER-IC-40023 | F23-IJB-601 | LCV75300 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
LCV75300-P1 |  |  |  | 90 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder |  |  |  |  | Confirmed | 0 |  | 2000-F23-SCM-IC-40002 2000-F23-TER-IC-40023 | F23-DCS-601 | LCV75300 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
F23IJB601-I1 |  |  |  | 90 | [5 empty] | 16PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder |  |  |  |  | Confirmed | G |  | 2000-F23-TER-IC-40003 2000-F23-TER-IC-40021 | F23-DCS-601 | F23-IJB-601 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
F23IJB601-I2 |  |  |  | 90 | [5 empty] | 24PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder |  |  |  |  | Confirmed | 0 |  | 2000-F23-TER-IC-40004 2000-F23-TER-IC-40008 2000-F23-TER-IC-40022 | F23-DCS-601 | F23-IJB-601 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
F23IJB601-I3 |  |  |  | 90 | [5 empty] | 20PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Ladder |  |  |  |  | Confirmed | G |  | 2000-F23-TER-IC-40007 2000-F23-TER-IC-40023 | F23-DCS-601 | F23-IJB-601 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FIT23541-P1 |  |  |  | 90 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder |  |  |  |  | Confirmed | E |  | 2000-F23-SCM-IC-40002 2000-F23-TER-IC-40023 | F23-DCS-601 | FIT23541 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FIT75321-P1 |  |  |  | 100 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder |  |  |  |  | Confirmed | E |  | 2000-F23-SCM-IC-40002 2000-F23-TER-IC-40023 | F23-DCS-601 | FIT75321 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FIT23521-P1 |  |  |  | 90 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder |  |  |  |  | Confirmed | E |  | 2000-F23-SCM-IC-40002 2000-F23-TER-IC-40023 | F23-DCS-601 | FIT23521 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FIT23523-P1 |  |  |  | 60 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder |  |  |  |  | Confirmed | E |  | 2000-F23-SCM-IC-40002 2000-F23-TER-IC-40023 | F23-DCS-601 | FIT23523 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FIT23543-P1 |  |  |  | 60 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder |  |  |  |  | Confirmed | E |  | 2000-F23-SCM-IC-40002 2000-F23-TER-IC-40023 | F23-DCS-601 | FIT23543 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
F23HY420-I1 |  |  |  | 45 | [5 empty] | 24PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder |  |  |  |  | Confirmed | 0 |  | 2000-F23-TER-IC-40003 2000-F23-TER-IC-40021 | F23-DCS-601 | F23-HY-420 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
F23HY420-I2 |  |  |  | 45 | [5 empty] | 24PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder |  |  |  |  | Confirmed | 0 |  | 2000-F23-TER-IC-40004 2000-F23-TER-IC-40008 2000-F23-TER-IC-40022 | F23-DCS-601 | F23-HY-420 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
F23HY420-I3 |  |  |  | 45 | [5 empty] | 8PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Ladder |  |  |  |  | Confirmed | 0 |  | 2000-F23-TER-IC-40007 2000-F23-TER-IC-40023 | F23-DCS-601 | F23-HY-420 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FIT75333-I1 |  |  |  | 15 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Final Run |  |  |  |  | Confirmed | G |  | 2000-F75-TER-IC-40011 2000-F75-TER-IC-40012 | F75-IJB-606 | FIT75333 |  |  |  |  | 2000-F00-STD-EL-10015 | CN037-E&I | CN037-E&I | CN037-E&I | 13
LIT75332-I1 |  |  |  | 35 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run |  |  |  |  | Confirmed | 0 |  | 2000-F75-TER-IC-40012 | F75-IJB-606 | LIT75332 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
LIT75362-I1 |  |  |  | 65 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run |  |  |  |  | Confirmed | 0 |  | 2000-F75-TER-IC-40012 | F75-IJB-606 | LIT75362 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
PIT75338-I1 |  |  |  | 10 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run |  |  |  |  | Confirmed | E |  | 2000-F75-TER-IC-40012 | F75-IJB-606 | PIT75338 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FSL75335-I1 |  |  |  | 15 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run |  |  |  |  | Confirmed | E |  | 2000-F75-TER-IC-40011 | F75-IJB-606 | FSL75335-JB | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FSL75335-I2 |  |  |  | 5 | [5 empty] | Vendor Cable PVC /M12 Straight Plug 4 Pin, 5m | Final Run |  |  |  |  | Confirmed | E |  | 2000-F75-TER-IC-40011 | FSL75335-JB | FSL-75335 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FSL75336-I1 |  |  |  | 15 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run |  |  |  |  | Confirmed | E |  | 2000-F75-TER-IC-40011 | F75-IJB-606 | FSL75336-JB | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FSL75336-I2 |  |  |  | 5 | [5 empty] | Vendor Cable PVC /M12 Straight Plug 4 Pin, 5m | Final Run |  |  |  |  | Confirmed | 0 |  | 2000-F75-TER-IC-40011 | FSL75336-JB | FSL75336 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FSL75337-I1 |  |  |  | 10 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run |  |  |  |  | Confirmed | E |  | 2000-F75-TER-IC-40011 | F75-IJB-606 | FSL75337-JB | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FSL75337-I2 |  |  |  | 5 | [5 empty] | Vendor Cable PVC /M12 Straight Plug 4 Pin, 5m | Final Run |  |  |  |  | Confirmed | 0 |  | 2000-F75-TER-IC-40011 | FSL75337-JB | FSL75337 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
ZS75330-I1 |  |  |  | 30 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run |  |  |  |  | Confirmed | E |  | 2000-F75-TER-IC-40011 | F75-IJB-606 | ZS75330 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
ZS75331-I1 |  |  |  | 15 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run |  |  |  |  | Confirmed | E |  | 2000-F75-TER-IC-40011 | F75-IJB-606 | ZS75331 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
ZS75341-I1 |  |  |  | 20 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run |  |  |  |  | Confirmed | E |  | 2000-F75-TER-IC-40011 | F75-IJB-606 | ZS75341 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
LSH75363-I1 |  |  |  | 25 | [5 empty] | Vendor Cable PVC /M12 Plug 4 Pin, 25m | Final Run |  |  |  |  | Confirmed | E |  | 2000-F75-TER-IC-40011 | F75-IJB-606 | LSH75363 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FIT75333-P1 |  |  |  | 110 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit |  |  |  |  | Confirmed | E |  | 2000-F75-SCM-IC-40002 2000-F75-TER-IC-40012 | F75-RTU-606 | FIT75333 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FIT75793-P1 |  |  |  | 25 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit |  |  |  |  | Confirmed | 0 |  | 2000-F75-SCM-IC-40002 2000-F75-TER-IC-40012 | F75-RTU-606 | FIT75793 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
F75IJB606-I1 |  |  |  | 90 | [5 empty] | 20PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground Conduit |  |  |  |  | Confirmed | 0 |  | 2000-F75-TER-IC-40001 2000-F75-TER-IC-40011 | F75-RTU-606 | F75-IJB-606 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
F75IJB606-I2 |  |  |  | 90 | [5 empty] | 8PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Underground Conduit |  |  |  |  | Confirmed | 0 |  | 2000-F75-TER-IC-40003 2000-F75-TER-IC-40006 2000-F75-TER-IC-40012 | F75-RTU-606 | F75-IJB-606 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
PIT75339-I1 |  |  |  | 45 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder |  |  |  |  | Confirmed | E |  | 2000-F75-TER-IC-40003 | F75-RTU-606 | PIT75339 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
XV75340-P1 |  |  |  | 45 | [5 empty] | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder |  |  |  |  | Confirmed | 0 |  | 2000-F75-SCM-IC-40002 2000-F75-TER-IC-40005 | F75-RTU-606 | XV75340 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
XV75340-I1 |  |  |  | 45 | [5 empty] | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder |  |  |  |  | Confirmed | 0 |  | 2000-F75-TER-IC-40002 | F75-RTU-606 | XV75340 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
LIT75364-I1 |  |  |  | 20 | [5 empty] | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run |  |  |  |  | Confirmed | E |  | 2000-F75-TER-IC-40012 | F75-IJB-606 | LIT75364 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13
FIT75793-I1 |  |  |  | 25 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Underground Conduit |  |  |  |  | Confirmed | 0 |  | 2000-F75-TER-IC-40011 2000-F75-TER-IC-40012 | F75-IJB-606 | FIT75793 |  |  |  |  | 2000-F00-STD-EL-10015 | CN037-E&I | CN037-E&I | CN037-E&I | 13
F75FI600-I1 |  |  |  | 20 | [5 empty] | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Ladder |  |  |  |  | Preliminary | E | Awaiting Vendor Information | 2000-F75-TER-IC-40006 | F23-DCS-601 | F75-FI-600 | [5 empty] | CN037-E&I | CN037-E&I | CN037-E&I | 13