## MCC schedule
Sort | Equipment Number | Module No. | Schematic Drawing No. | Name Plate kW | Full Load Current (A) | MCC No. | Circuit Breaker Model - Verify Against Nameplate (NHP) | Rated Current (In, A) | Long Time Trip (lr, xln) | Instantaneous Trip (Ii, xln) | ELR Make/Model | ELR Threshold IΔn (A) | ELR Delay (s) | Frequency Response | Electronic Overload Model - Verify Against Nameplate | Full Load Current (171-FLA) (A) | Trip Class (172-Class) | Current-Based Trips (183-TripEnable) | Control-Based Trips (186-TripEnableC) | Operating Mode (195- SetOperatingMode) | CT Ratio (263-CT Primary) | CT Ratio (264-CT Secondary) | Ground Fault Trip (183-Trip Enable) | Approx. Full Load Current (A) | MCC No | Make / Model | Rating (A) | Circuit Breaker Model - Verify Against Nameplate (Terasaki) | Long Time Trip 1 (Ir, A) | Long Time Trip 2 (Ir, A) | Long Time Delay (tr, s) | Short Time Trip (Isd, A) | Short Time Delay (tsd, s) | Short Time Delay (I²t) | Instantaneous Setting (Ii, A) | Long Time Trip (Ir, A) | Characteristic Curve No. | Internal Ground Fault (Ig, A) | Internal Ground Fault Delay (tg,s) | Page
1 | F23-HY-420 | 3F-13 | 2000-F23-SCM-EL-40025 | 7.5 | 13.4 | F23-SW-602 | P160-H-2-3-32-TM | 32 A | 0.63 (20 A) | 12 (384 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | 193-ESM-IG-30A-C55 | 13.4 | 10 | 91 | 1 | 2=NetOverload | 5 | 5 | NO | [16 empty] | 16
2 | F23-FN-653 | 3F-05 | 2000-F23-SCM-EL-40026 | 5.5 | 9.8 | F23-SW-602 | P160-H-2-3-20-TM | 20 A | 0.63 (12.5 A) | 12 (240 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | 193-ESM-IG-60A-C55 | 9.8 | 10 | 91 | 1 | 2=NetOverload | 5 | 5 | NO | [16 empty] | 16
3 | F23-FN-654 | 3F-09 | 2000-F23-SCM-EL-40027 | 5.5 | 9.8 | F23-SW-602 | P160-H-2-3-20-TM | 20 A | 0.63 (12.5 A) | 12 (240 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | 193-ESM-IG-60A-C55 | 9.8 | 10 | 91 | 1 | 2=NetOverload | 5 | 5 | NO | [16 empty] | 16
4 | F23-FN-651 | 4R-13 | 2000-F23-SCM-EL-40028 | 0.18 | 0.6 | F23-SW-602 | P160-H-2-3-20-TM | 20 A | 0.63 (12.5 A) | 12 (240 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | 193-ESM-IG-30A-C55 | 0.6 | 10 | 91 | 1 | 2=NetOverload | 5 | 5 | NO | [16 empty] | 16
5 | F23-FN-652 | 4R-17 | 2000-F23-SCM-EL-40029 | 0.18 | 0.6 | F23-SW-602 | P160-H-2-3-20-TM | 20 A | 0.63 (12.5 A) | 12 (240 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | 193-ESM-IG-30A-C55 | 0.6 | 10 | 91 | 1 | 2=NetOverload | 5 | 5 | NO | [16 empty] | 16
6 | F75-PV-414 | 4F-10 | 2000-F75-SCM-EL-40004 | 2.2 | 4.3 | F23-SW-602 | P160-H-2-3-20-TM | 20 A | 0.63 (12.5 A) | 12 (240 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | 193-ESM-IG-30A-C55 | 4.3 | 10 | 91 | 1 | 2=NetOverload | 5 | 5 | NO | [16 empty] | 16
7 | F75-PW-665 | 3R-13 | 2000-F75-SCM-EL-40005 | 1.5 | 3.2 | F23-SW-602 | P160-H-2-3-20-TM | 20 A | 0.63 (12.5 A) | 12 (240 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | 193-ESM-IG-30A-C55 | 3.2 | 10 | 91 | 1 | 2=NetOverload | 5 | 5 | NO | [16 empty] | 16
| Param No. | Param Name | Device Profile Tag Name | Description | Type | Data Size | Scale Factor | Min | Max | Default | Modified Setting | Units | [27 empty] | 17
Overload Setup | 171 | FLASetting | C.FLA1 | Overload Full Load Current Setting | UDINT | 4 | 100 | 50 | 6553500 | 50 | Refer "Sheet 9 LV DOL Settings". | Amps | [27 empty] | 17
| 172 | TripClass | C.TripClass | Trip Class Setting | USINT | 1 | 1 | 5 | 30 | 10 | 10 | [28 empty] | 17
| 173 | OLPTCResetMode | C.OverloadResetMode | Overload and PTC Trip Reset Mode | BOOL | 1 | 1 | 0=Manual 1=Automatic |  | 0 | [29 empty] | 17
| 174 | OLResetLevel | C.OverloadResetLevel | Overload Trip Reset Level | USINT | 1 | 1 | 0 | 100 | 75 |  | %TCU | [27 empty] | 17
| 175 | OLWarningLevel | C.OverloadWarningLimit | Overload Warning Reset Level | USINT | 1 | 1 | 0 | 100 | 85 |  | %TCU | [27 empty] | 17
| 176 | SingleOrThree Ph | C.ThreePhase | Single Phase = L1 and L2 | BOOL | 1 | 1 | 0=SinglePhase 1=ThreePhase |  | 1 | [29 empty] | 17
| 177 | FLA2Setting | C.FLA2 | Overload Full Load Current Setting 2 | UDINT | 4 | 100 | 50 | 6553500 | 50 |  | Amps | [27 empty] | 17
| 178 | Reserved | [37 empty] | 17
| 179 | Reserved | [37 empty] | 17
| 180 | Reserved | [37 empty] | 17
| 181 | Reserved | [37 empty] | 17
| 182 | Reserved | [37 empty] | 17
Device Setup | 183 | TripEnable | C.Protection.OverloadTripEnEn C.Protection.PhaseLossTripEn C.Protection.GroundFaultCurrentTripEn C.Protection.StallTripEn C.Protection.JamTripEn C.Protection.UnderloadTripEn C.Protection.CurrentImbalanceTripEn C.Protection.L1UnderCurrentTripEn C.Protection.L2UnderCurrentTripEn C.Protection.L3UnderCurrentTripEn C.Protection.L1OverCurrentTripEn C.Protection.L2OverCurrentTripEn C.Protection.L3OverCurrentTripEn C.Protection.L1LineLossTripEn C.Protection.L2LineLossTripEn C.Protection.L3LineLossTripEn | Bitmask used to enable/disable current-based trips | UINT | 2 | 1 | Decimal Number Bit0= OverloadTrip Bit1= PhaseLossTrip Bit2= GroundFaultTrip Bit3= StallTrip Bit4= JamTrip Bit5= UnderloadTrip Bit6= CurrentImbalTrip Bit7= L1UnderCurrTrip Bit8= L2UnderCurrTrip Bit9= L3UnderCurrTrip Bit10= L1OverCurrenTrip Bit11= L2OverCurrenTrip Bit12= L3OverCurrenTrip Bit13= L1LineLossTrip Bit14= L2LineLossTrip Bit15= L3LineLossTrip |  | 15 1 1 1 1 | 91 1 1 1 1 1 | [28 empty] | 17
| 184 | TripEnableV | C.Protection.UnderVoltageTripEn C.Protection.OverVoltageTripEn C.Protection.VoltageImbalanceTripEn C.Protection.PhaseRotationMismatchTripEn C.Protection.UnderFrequencyTripEn C.Protection.OverFrequencyTripEn | Bitmask used to enable/disable current-based trips | UINT | 2 | 1 | Decimal Number Bit0= UnderVoltageTrip Bit1= OvervoltageTrip Bit2= VoltageUnbalTrip Bit3= PhaseRotationTrp Bit4= UnderFreqTrip Bit5= OverFreqTrip |  | 0 | [29 empty] | 17
| 186 | TripEnableC | C.Protection.TestTripEn C.Protection.PTCTripEn C.Protection.OperatorStationTripEn C.Protection.RemoteTripEn C.Protection.BlockedStartTripEn C.Protection.HardwareFaultTripEn C.Protection.ConfigurationTripEn C.Protection.ModuleMismatchTripEn C.Protection.ExpansionBusTripEn C.Protection.NVMErrorTripEn C.Protection.MCCTestPositionTripEn | Bitmask used to enable/ disable control-based trips | UINT | 2 | 1 | Decimal Number Bit0= TestTrip Bit1= PTCTrip Bit2= DLXTrip Bit3= OperStationTrip Bit4= RemoteTrip Bit5= BlockedStartTrip Bit6= HardwareFltTrip Bit7= ConfigTrip Bit8= OptionMatchTrip Bit9= DLXFBTimeoutTrip Bit10= ExpansionBusTrip Bit11= Reserved Bit12= Reserved Bit13= NVSTrip Bit14=TestModeTrip |  | 1 1 | 1 1 | [28 empty] | 17
| 195 | SetOperatingMode | [5 empty] | 2 | 54 | Net Overload | Refer "Sheet 9 LV DOL Settings". | [28 empty] | 17
| 202 | OutPt0Assignment | [5 empty] | 0=Normal 1=TripRelay 2=ControlRelay 3=TripAlarm 4=WarningAlarm 5=MonL1TripRelay 6= MonL2TripRelay 7= MonL3TripRelay |  | Trip Relay | ControlRelay | [28 empty] | 17
| Param No. | Param Name | Device Profile Tag Name | Description | Type | Data Size | Scale Factor | Min | Max | Default | Modified Setting | Units | [27 empty] | 18
Current Setup | 203 | OutPt1Assignment | [5 empty] | 0=Normal 1=TripRelay 2=ControlRelay 3=TripAlarm 4=WarningAlarm 5=MonL1TripRelay 6= MonL2TripRelay 7= MonL3TripRelay |  | Normal | [29 empty] | 18
| 204 | OutPt2Assignment | [5 empty] | 0=Normal 1=TripRelay 2=ControlRelay 3=TripAlarm 4=WarningAlarm 5=MonL1TripRelay 6= MonL2TripRelay 7= MonL3TripRelay |  | Normal | [29 empty] | 18
| 222 | SensingModuleTyp |  | Select Sensing Module Type | USINT | 1 | 1 | 0= IgnoreType 1= VIGPt5to30Amp 2= VIG6to60Amp 3= VIG10to100Amp 4= VIG20to200Amp 5= IGPt5to30Amp 6= IG6to60Amp 7= IG10to100Amp 8= IG20to200Amp 9= IPt5to30Amp 10= I6to60Amp 11= I10to100Amp 12= I20to200Amp |  | 0 | Refer "Sheet 9 LV DOL Settings". | [28 empty] | 18
| 239 | PLInhibitTime | C.PhaseLossInhibitTime | Phase Loss Inhibit Time | USINT | 1 | 1 | 0 | 250 | 0 | 10 | Seconds | [27 empty] | 18
| 240 | PLTripDelay | C.PhaseLossTripDelay | Phase Loss Trip Delay | USINT | 1 | 10 | 1 | 250 | 10 | 5 | Seconds | [27 empty] | 18
| 241 | GroundFaultType | C.GroundFaultType | Select Ground Fault Type | USINT | 1 | 1 | 0= Disabled 1= Internal1to5Amps 2= ExtPt02toPt1Amps 3= ExtPt1toPt5Amps 4= ExtPt5to1Amps 5= External1to5Amps |  | 0 | [29 empty] | 18
| 242 | GFInhibitTime | C.GroundFaultInhibitTime | Ground Fault Inhibit Time | USINT | 1 | 1 | 0 | 250 | 10 | 10 | Seconds | [27 empty] | 18
| 243 | GFTripDelay | C.GroundFaultTripDelay | Ground Fault Trip Delay | USINT | 1 | 10 | 0 | 250 | 5 | Refer "Sheet 9 LV DOL Settings". | Seconds | [27 empty] | 18
| 244 | GFTripLevel | C.GroundFaultTripLimit | Ground Fault Trip Level | UINT | 2 | 100 | 2 | 500 | 200 | Refer "Sheet 9 LV DOL Settings". | Amps | [27 empty] | 18
| 245 | GFWarningDelay | C.GroundFaultWarnDelay | Ground Fault Warning Delay | USINT | 1 | 10 | 0 | 250 | 0 |  | Seconds | [27 empty] | 18
| 246 | GFWarningLevel | C.GroundFaultWarnLimit | Ground Fault Warning Level | UINT | 2 | 100 | 2 | 500 | 200 |  | Amps | [27 empty] | 18
| 247 | GFFilter | C.GroundFaultFilterEn | Filter GF current from %TCU calculation | BOOL | 1 | 1 | 0=Disable 1=Enable |  | 0 | [29 empty] | 18
| 248 | GFMaxInhibit | C.GroundFaultMaxInhibitEn | Trip is inhibited when GF exceeds max value | BOOL | 1 | 1 | 0=Disable 1=Enable |  | 0 | [29 empty] | 18
| 249 | StallEnabledTime | C.StallEnabledTime | Stall Monitor and Trip Delay | USINT | 1 | 1 | 0 | 250 | 10 |  | Seconds | [27 empty] | 18
| 250 | StallTripLevel | C.StallTripLimit | Stall Trip Level | UINT | 2 | 10 | 100 | 600 | 600 | 300 | %FLA | [27 empty] | 18
| 251 | JamInhibitTime | C.JamInhibitTime | Jam Detect Inhibit Time | USINT | 1 | 1 | 0 | 250 | 10 |  | Seconds | [27 empty] | 18
| 252 | JamTripDelay | C.JamTripDelay | Jam Detect Trip Delay | USINT | 1 | 10 | 1 | 250 | 50 | 2.5 | Seconds | [27 empty] | 18
| 253 | JamTripLevel | C.JamTripLimit | Jam Detect Trip Level | UINT | 2 | 1 | 50 | 600 | 250 | 150 | %FLA | [27 empty] | 18
| 254 | JamWarningLevel | C.JamWarnLimit | Jam Detect Warning Level | UINT | 2 | 1 | 50 | 600 | 150 | 125 | %FLA | [27 empty] | 18
| 255 | ULInhibitTime | C.UnderloadInhibitTime | Underload Inhibit Time | USINT | 1 | 1 | 0 | 250 | 10 |  | Seconds | [27 empty] | 18
| 256 | ULTripDelay | C.UnderloadTripDelay | Underload Trip Delay | USINT | 1 | 10 | 1 | 250 | 50 |  | Seconds | [27 empty] | 18
| 257 | ULTripLevel | C.UnderloadTripLimit | Underload Trip Level | USINT | 1 | 1 | 10 | 100 | 50 |  | %FLA | [27 empty] | 18
| 258 | ULWarningLevel | C.UnderloadWarnLimit | Underload Warning Level | USINT | 1 | 1 | 10 | 100 | 70 |  | %FLA | [27 empty] | 18
| 259 | CIInhibitTime | C.CurrentImbalanceInhibitTime | Current Imbalance Inhibit Time | USINT | 1 | 1 | 0 | 250 | 10 |  | Seconds | [27 empty] | 18
| 260 | CITripDelay | C.CurrentImbalanceTripDelay | Current Imbalance Trip Delay | USINT | 1 | 10 | 1 | 250 | 50 | 5 | Seconds | [27 empty] | 18
| 261 | CITripLevel | C.CurrentImbalanceTripLimit | Current Imbalance Trip Level | USINT | 1 | 1 | 10 | 100 | 35 | 20 | % | [27 empty] | 18
| 262 | CIWarningLevel | C.CurrentImbalanceWarnLimit | Current Imbalance Warning Level | USINT | 1 | 1 | 10 | 100 | 20 | 15 | % | [27 empty] | 18
| 263 | CTPrimary | C.CTPrimary | Current Transformer Primary Ratio | UINT | 2 | 1 | 1 | 65535 | 5 | Refer "Sheet 9 LV DOL Settings". | [28 empty] | 18
| 264 | CTSecondary | C.CTSecondary | Current Transformer Secondary Ratio | UINT | 2 | 1 | 1 | 65535 | 5 | Refer "Sheet 9 LV DOL Settings". | [28 empty] | 18
| 265 | UCInhibit Time | C.UnderCurrentInhibitTime | Inhibit Time | USINT | 1 | 1 | 0 | 250 | 10 |  | Seconds | [27 empty] | 18
| 266 | L1UCTripDelay | C.L1UnderCurrentTripDelay | L1 Under Current Trip Delay | USINT | 1 | 10 | 0 | 250 | 10 |  | Seconds | [27 empty] | 18
| 267 | L1UCTripLevel | C.L1UnderCurrentTripLimit | L1 Under Current Trip Level | USINT | 1 | 1 | 10 | 100 | 35 |  | % | [27 empty] | 18
| Param No. | Param Name | Device Profile Tag Name | Description | Type | Data Size | Scale Factor | Min | Max | Default | Modified Setting | Units | [27 empty] | 19
| 268 | L1UCWarningLevel | C.L1UnderCurrentWarnLimit | L1 Under Current Warning Level | USINT | 1 | 1 | 10 | 100 | 40 |  | % | [27 empty] | 19
| 269 | L2UCTripDelay | C.L2UnderCurrentTripDelay | L2 Under Current Trip Delay | USINT | 1 | 10 | 0 | 250 | 10 |  | Seconds | [27 empty] | 19
| 270 | L2UCTripLevel | C.L2UnderCurrentTripLimit | L2 Under Current Trip Level | USINT | 1 | 1 | 10 | 100 | 35 |  | % | [27 empty] | 19
| 271 | L2UCWarningLevel | C.L2UnderCurrentWarnLimit | L2 Under Current Warning Level | USINT | 1 | 1 | 10 | 100 | 40 |  | % | [27 empty] | 19
| 272 | L3UCTripDelay | C.L3UnderCurrentTripDelay | L3 Under Current Trip Delay | USINT | 1 | 10 | 0 | 250 | 10 |  | Seconds | [27 empty] | 19
| 273 | L3UCTripLevel | C.L3UnderCurrentTripLimit | L3 Under Current Trip Level | USINT | 1 | 1 | 10 | 100 | 35 |  | % | [27 empty] | 19
| 274 | L3UCWarningLevel | C.L3UnderCurrentWarnLimit | L3 Under Current Warning Level | USINT | 1 | 1 | 10 | 100 | 40 |  | % | [27 empty] | 19
| 275 | OCInhibitTime | C.OverCurrentInhibitTime | Over Current Inhibit Time | USINT | 1 | 1 | 0 | 250 | 10 |  | Seconds | [27 empty] | 19
| 276 | L1OCTripDelay | C.L1OverCurrentTripDelay | L1 Over Current Trip Delay | USINT | 1 | 10 | 0 | 250 | 10 |  | Seconds | [27 empty] | 19
| 277 | L1OCTripLevel | C.L1OverCurrentTripLimit | L1 Over Current Trip Level | USINT | 1 | 1 | 10 | 200 | 100 |  | % | [27 empty] | 19
| 278 | L1OCWarningLevel | C.L1OverCurrentWarnLimit | L1 Over Current Warning Level | USINT | 1 | 1 | 10 | 200 | 90 |  | % | [27 empty] | 19
| 279 | L2OCTripDelay | C.L2OverCurrentTripDelay | L2 Over Current Trip Delay | USINT | 1 | 10 | 0 | 250 | 10 |  | Seconds | [27 empty] | 19
| 280 | L2OCTripLevel | C.L2OverCurrentTripDelay | L2 Over Current Trip Level | USINT | 1 | 1 | 10 | 200 | 100 |  | % | [27 empty] | 19
| 281 | L2OCWarningLevel | C.L2OverCurrentTripLimit | L2 Over Current Warning Level | USINT | 1 | 1 | 10 | 200 | 90 |  | % | [27 empty] | 19
| 282 | L3OCTripDelay | C.L2OverCurrentWarnLimit | L3 Over Current Trip Delay | USINT | 1 | 10 | 0 | 250 | 10 |  | Seconds | [27 empty] | 19
| 283 | L3OCTripLevel | C.L3OverCurrentTripDelay | L3 Over Current Trip Level | USINT | 1 | 1 | 10 | 200 | 100 |  | % | [27 empty] | 19
| 284 | L3OCWarningLevel | C.L3OverCurrentTripLimit | L3 Over Current Warning Level | USINT | 1 | 1 | 10 | 200 | 90 |  | % | [27 empty] | 19
| 285 | LineLossInhTime | C.L3OverCurrentWarnLimit | Line Loss Inhibit Time | USINT | 1 | 1 | 0 | 250 | 10 |  | Seconds | [27 empty] | 19
| 286 | L1LossTripDelay | C.LineLossInhibitTime | L1 Line Loss Trip Delay | USINT | 1 | 10 | 0 | 250 | 10 |  | Seconds | [27 empty] | 19
| 287 | L2LossTripDelay | C.L1LineLossTripDelay | L2 Line Loss Trip Delay | USINT | 1 | 10 | 0 | 250 | 10 |  | Seconds | [27 empty] | 19
| 288 | L3LossTripDelay | C.L2LineLossTripDelay | L3 Line Loss Trip Delay | USINT | 1 | 10 | 0 | 250 | 10 |  | Seconds | [27 empty] | 19
Anybus-E300- MBTCP | - | Modbus Config. | Modbus TCP Timeout | [6 empty] | 120 | 5 | Seconds | [27 empty] | 19
| Feeder Load Data | [5 empty] | Fault Current Limiting Fuse |  | Circuit Breaker Settings | [13 empty] | Earth Leakage Relay | [16 empty] | 20
1 | F23-DB-601 | 3F-17 | 2000-F23-SCM-EL-40015 | 30 |  |  |  | 250 A | 0.63 (157.5 A) | 6 (1500 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | [9 empty] | 52.2 | F23-SW-602 | IPD / NHG1-250 (TBC) | 250 (TBC) | P250-H-2-3-250-TM | - | - | - | - | - | - | - | - | - | - | - | 20
2 | F23-DB-602 | 4F-17 | 2000-F23-SCM-EL-40016 | 89.5 (TBC) |  |  |  | 400 A 250 A | 1.0 (400 A) 0.63 (157.5) | 6 (2400 A) 6 (1500 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | [9 empty] | 144.2 (TBC) | F23-SW-602 | IPD / NHG1-250 (TBC) | 250 (TBC) | P400-H-3-400-TM P250-H-2-3-250-TM | - | - | - | - | - | - | - | - | - | - | - | 20
3 | F23-DB-603 | 4F-14 | 2000-F23-SCM-EL-40017 | 10 |  |  |  | 32 A | 0.63 (20 A) | 6 (192 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | [9 empty] | 17.4 | F23-SW-602 | IPD / NHG00-160 (TBC) | 250 (TBC) | P160-H-2-3-32-TM | - | - | - | - | - | - | - | - | - | - | - | 20
4 | F23PP651-VS | 4R-07 | 2000-F23-SCM-EL-40018 | 9 |  |  |  | 32 A | 0.63 (20 A) | 6 (192 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | [9 empty] | 15.7 | F23-SW-602 | - | - | P160-H-2-3-32-TM | - | - | - | - | - | - | - | - | - | - | - | 20
5 | F23PP652-VS | 4R-10 | 2000-F23-SCM-EL-40019 | 9 |  |  |  | 32 A | 0.63 (20 A) | 6 (192 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | [9 empty] | 15.7 | F23-SW-602 | - | - | P160-H-2-3-32-TM | - | - | - | - | - | - | - | - | - | - | - | 20
6 | F23PW651-VS | 3R-01 | 2000-F23-SCM-EL-40020 | 1.5 |  |  |  | 20 A | 0.63 (12.5 A) | 6 (120 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | [9 empty] | 2.6 | F23-SW-602 | - | - | P160-H-2-3-20-TM | - | - | - | - | - | - | - | - | - | - | - | 20
7 | F23PW652-VS | 3R-04 | 2000-F23-SCM-EL-40021 | 1.5 |  |  |  | 20 A | 0.63 (12.5 A) | 6 (120 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | [9 empty] | 2.6 | F23-SW-602 | - | - | P160-H-2-3-20-TM | - | - | - | - | - | - | - | - | - | - | - | 20
8 | F23PW653-VS | 3R-07 | 2000-F23-SCM-EL-40022 | 1.5 |  |  |  | 20 A | 0.63 (12.5 A) | 6 (120 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | [9 empty] | 2.6 | F23-SW-602 | - | - | P160-H-2-3-20-TM | - | - | - | - | - | - | - | - | - | - | - | 20
9 | F23PW654-VS | 3R-10 | 2000-F23-SCM-EL-40023 | 1.5 |  |  |  | 20 A | 0.63 (12.5 A) | 6 (120 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | [9 empty] | 2.6 | F23-SW-602 | - | - | P160-H-2-3-20-TM | - | - | - | - | - | - | - | - | - | - | - | 20
10 | F23-FL-600 | 4R-01 | - | 1.0 |  |  |  | 20 A | 0.63 (12.5 A) | 6 (120 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | [9 empty] | 1.7 | F23-SW-602 | - | - | P160-H-2-3-20-TM | - | - | - | - | - | - | - | - | - | - | - | 20
11 | F23-SE-431 | 4R-04 | - | 2.2 |  |  |  | 20 A | 0.63 (12.5 A) | 6 (120 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | [9 empty] | 3.8 | F23-SW-602 | - | - | P160-H-2-3-20-TM | - | - | - | - | - | - | - | - | - | - | - | 20
12 | F23-HF-601 | 3R-17 | 2000-F23-SCM-EL-40031 | - |  |  |  | 400 A | 0.85 (340 A) | 6 (2400 A) | NHP RD1EP21H (IME Delta 72-S) | 0.2 x 100 = 20A | 0.25 | - | [9 empty] | 300 | F23-SW-602 | - | - | P400-H-3-400-TM P400-H-3-400-BE | 0.64 (350 A) | 0.97 (339.5 A) | 5s | 7 (2376.5 A) | 0.05s | OFF | 6 (2400 A) | - | - | - | - | 20
13 | F75-PW-606 | 01F-01 | 2000-F75-SCM-EL-40001 | 450 |  |  |  | 1250 A | - | - | AmpControl ELV (P/N 170447) | 1.0 (Sw. Posn. 'C') | 0.25 (Sw. Posn. '4') | Weighted Mode (Default) | [9 empty] | 679.4 | F23-SW-602 | - | - | B1250-H-3-1250-BE | - | - | - | - | - | - | - | 0.7 (875 A) | 9 | - | - | 20
14 | F75-PW-607 | 02F-01 | 2000-F75-SCM-EL-40002 | 450 |  |  |  | 1250 A | - | - | AmpControl ELV (P/N 170447) | 1.0 (Sw. Posn. 'C') | 0.25 (Sw. Posn. '4') | Weighted Mode (Default) | [9 empty] | 679.4 | F23-SW-602 | - | - | B1250-H-3-1250-BE | - | - | - | - | - | - | - | 0.7 (875 A) | 9 | - | - | 20
15 | F75-PW-608 | 01R-01 | 2000-F75-SCM-EL-40003 | 450 |  |  |  | 1250 A | - | - | AmpControl ELV (P/N 170447) | 1.0 (Sw. Posn. 'C') | 0.25 (Sw. Posn. '4') | Weighted Mode (Default) | [9 empty] | 679.4 | F23-SW-602 | - | - | B1250-H-3-1250-BE | - | - | - | - | - | - | - | 0.7 (875 A) | 9 | - | - | 20
16 | F75-SW-557 | 4R-21 | 2000-F75-SCM-EL-40006 | 40 |  |  |  | 250 A | 0.63 (157.5 A) | 6 (1500 A) | NHP RD1EP21H (IME Delta 72-S) | 0.1 x 10 = 1.0A | 0.25 | - | [9 empty] | 69.6 | F23-SW-602 | - | - | P250-H-2-3-250-TM P250-H-3-250-BE | 0.64 (160 A) | 0.92 (156.8 A) | 5s | 8 (1254.4 A) | 0.05s | OFF | 6 (1500 A) | - | - | - | - | 20
[8 empty] | F23-PW-653 | F23-PW-654 | [16 empty] | Equipment Number | F23-PW-651 | F23-PW-652 | [11 empty] | 21
[8 empty] | FIM III Booster Pump 2 Seal Water Pump 1 | FIM III Booster Pump 2 Seal Water Pump 2 | [16 empty] | Description | FIM III Booster Pump 1 Seal Water Pump 1 | FIM III Booster Pump 1 Seal Water Pump 2 | [11 empty] | 21
[8 empty] | 20F11NC3P5JA0NNNNN+20- 750-S+20-750-20COMM+20- HIM-A6+20-750-APS | 20F11NC3P5JA0NNNNN+20- 750-S+20-750-20COMM+20- HIM-A6+20-750-APS | [16 empty] | VVVF Model Number | 20F11NC3P5JA0NNNNN+20- 750-S+20-750-20COMM+20- HIM-A6+20-750-APS | 20F11NC3P5JA0NNNNN+20- 750-S+20-750-20COMM+20- HIM-A6+20-750-APS | [11 empty] | 21
[8 empty] | TBA | TBA | [16 empty] | VVVF Input Current (A) | TBA | TBA | [11 empty] | 21
[8 empty] | 1.5 | 1.5 | [16 empty] | Rating (kW) | 1.5 | 1.5 | [11 empty] | 21
[8 empty] | 1 | 1 | [16 empty] | No of Motors | 1 | 1 | [11 empty] | 21
[8 empty] | 3.18 | 3.18 | [16 empty] | FLC (A) | 3.18 | 3.18 | [11 empty] | 21
[8 empty] | 2000-F23-SCM-EL-40022 | 2000-F23-SCM-EL-40023 | [16 empty] | Schematic Drawing | 2000-F23-SCM-EL-40020 | 2000-F23-SCM-EL-40021 | [11 empty] | 21
[8 empty] | N/A | N/A | [16 empty] | VVVF Datasheet | N/A | N/A | [11 empty] | 21
[8 empty] | https://configurator.rockwellaut | https://configurator.rockwellaut | [16 empty] | VVVF Website Cutsheet | https://configurator.rockwellaut | https://configurator.rockwellaut | [11 empty] | 21
[8 empty] | omation.com/api/Product/20F1 | omation.com/api/Product/20F1 | [17 empty] | omation.com/api/Product/20F1 | omation.com/api/Product/20F1 | [11 empty] | 21
[8 empty] | 1NC3P5JA0NNNNN/cutsheet | 1NC3P5JA0NNNNN/cutsheet | [17 empty] | 1NC3P5JA0NNNNN/cutsheet | 1NC3P5JA0NNNNN/cutsheet | [11 empty] | 21
[8 empty] | 2000-ME015-F14- 40001AIFA | 2000-ME015-F14- 40001AIFA | [16 empty] | Motor Datasheet | 2000-ME015-F14- 40001AIFA | 2000-ME015-F14- 40001AIFA | [11 empty] | 21
[8 empty] | __ Note 5 | __ Note 5 | [16 empty] | IP Address | __ Note 5 | __ Note 5 | [11 empty] | 21
[8 empty] | P160-H-2-3-20-TM | P160-H-2-3-20-TM | [16 empty] | Circuit Breaker | P160-H-2-3-20-TM | P160-H-2-3-20-TM | [11 empty] | 21
[8 empty] | 20 | 20 | [16 empty] | Nominal Rating of Trip Unit (A) | 20 | 20 | [11 empty] | 21
[8 empty] | 0.63 (12.5 A) | 0.63 (12.5 A) | [16 empty] | Ir (xIn) | 0.63 (12.5 A) | 0.63 (12.5 A) | [11 empty] | 21
[8 empty] | - | - | [16 empty] | Ii (xIn) | - | - | [11 empty] | 21
[8 empty] | 0.7 (875 A) | 0.7 (875 A) | [16 empty] | Long Time - Ir1 | 0.7 (875 A) | 0.7 (875 A) | [11 empty] | 21
[8 empty] | 6 (120 A) | 6 (120 A) | [16 empty] | Long Time - Ir2 | 6 (120 A) | 6 (120 A) | [11 empty] | 21
[8 empty] | - | - | [16 empty] | Long Time Delay - tr (sec) | - | - | [11 empty] | 21
[8 empty] | - | - | [16 empty] | Short Time - Isd | - | - | [11 empty] | 21
[8 empty] | - | - | [16 empty] | Short Time Delay - tsd (sec) | - | - | [11 empty] | 21
[8 empty] | - | - | [16 empty] | Short Time Delay I²t | - | - | [11 empty] | 21
[8 empty] | - | - | [16 empty] | Instantaneous - Ii | - | - | [11 empty] | 21
[8 empty] | - | - | [16 empty] | Characteristic No. | - | - | [11 empty] | 21
[8 empty] | - | - | [16 empty] | TOL | - | - | [11 empty] | 21
[8 empty] | - | - | [16 empty] | TOL Setting (A) | - | - | [11 empty] | 21
File / Group | Port | No. | Display Name | Data Type | [19 empty] | Setting Notes | [15 empty] | 21
MOTOR CONTROL - Motor Data | 0 | 25 | Motor NP Volts | Real |  |  |  | 415V | 415V | [14 empty] | 415V |  |  | 415V | 415V | [11 empty] | 21
MOTOR CONTROL - Motor Data | 0 | 26 | Motor NP Amps | Real |  |  |  | 3.18 | 3.18 | [14 empty] | Lookup |  |  | 3.18 | 3.18 | [11 empty] | 21
MOTOR CONTROL - Motor Data | 0 | 27 | Motor NP Hertz | Real |  |  |  | 50 | 50 | [14 empty] | 50 |  |  | 50 | 50 | [11 empty] | 21
MOTOR CONTROL - Motor Data | 0 | 28 | Motor NP RPM | Real |  |  |  | 2895 | 2895 | [14 empty] | Datasheet |  |  | 2895 | 2895 | [11 empty] | 21
MOTOR CONTROL - Motor Data | 0 | 29 | Mtr NP Pwr Units | 32-bit Integer |  |  |  | 1 = kW | 1 = kW | [14 empty] | 1 – kW |  |  | 1 = kW | 1 = kW | [11 empty] | 21
MOTOR CONTROL - Motor Data | 0 | 30 | Motor NP Power | Real |  |  |  | 1.5 | 1.5 | [14 empty] | Lookup |  |  | 1.5 | 1.5 | [11 empty] | 21
MOTOR CONTROL - Motor Data | 0 | 31 | Motor Poles | 32-bit Integer |  |  |  | 2 | 2 | [14 empty] | Lookup |  |  | 2 | 2 | [11 empty] | 21
MOTOR CONTROL - Mtr Ctrl Options | 0 | 35 | Motor Ctrl Mode | 32-bit Integer |  |  |  | 1 - Induction SV | 1 - Induction SV | [14 empty] | 1 – Induction SV | Note 1 |  | 1 - Induction SV | 1 - Induction SV | [11 empty] | 21
MOTOR CONTROL - Mtr Ctrl Options | 0 | 36 | Maximum Voltage | Real |  |  |  | 415 | 415 | [14 empty] | 415 |  |  | 415 | 415 | [11 empty] | 21
MOTOR CONTROL - Mtr Ctrl Options | 0 | 37 | Maximum Freq | Real |  |  |  | 50 | 50 | [14 empty] | 50 |  |  | 50 | 50 | [11 empty] | 21
MOTOR CONTROL - Mtr Ctrl Options | 0 | 38 | PWM Frequency | Real |  |  |  | Default, Dependant on Frame size | Default, Dependant on Frame size | [14 empty] | Default, Dependant on Frame size |  |  | Default, Dependant on Frame size | Default, Dependant on Frame size | [11 empty] | 21
MOTOR CONTROL - Mtr Ctrl Options | 0 | 41 | Common Mode Type | 32-bit Integer |  |  |  | 0 – CMV | 0 – CMV | [14 empty] | 0 – CMV |  |  | 0 – CMV | 0 – CMV | [11 empty] | 21
MOTOR CONTROL - Volts per Hertz | 0 | 60 | Start Acc Boost | Real |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
MOTOR CONTROL - Volts per Hertz | 0 | 61 | Run Boost | Real |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
MOTOR CONTROL - Volts per Hertz | 0 | 62 | Break Voltage | Real |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
MOTOR CONTROL - Volts per Hertz | 0 | 63 | Break Frequency | Real |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
MOTOR CONTROL - Volts per Hertz | 0 | 65 | VHz Curve | 32-bit Integer |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
MOTOR CONTROL - Autotune | 0 | 70 | Autotune | 32-bit Integer |  |  |  | 1 – Calculate | 1 – Calculate | [14 empty] | 1 – Calculate |  |  | 1 – Calculate | 1 – Calculate | [11 empty] | 21
MOTOR CONTROL - Autotune | 0 | 71 | Autotune Torque | Real |  |  |  | 50% | 50% | [14 empty] | 50% |  |  | 50% | 50% | [11 empty] | 21
MOTOR CONTROL - Autotune | 0 | 73 | IR Voltage Drop | Real |  |  |  | Set By Autotune | Set By Autotune | [14 empty] | Set By Autotune |  |  | Set By Autotune | Set By Autotune | [11 empty] | 21
MOTOR CONTROL - Autotune | 0 | 74 | Ixo Voltage Drop | Real |  |  |  | Set By Autotune | Set By Autotune | [14 empty] | Set By Autotune |  |  | Set By Autotune | Set By Autotune | [11 empty] | 21
MOTOR CONTROL - Autotune | 0 | 75 | Flux Current Ref | Real |  |  |  | Set By Autotune | Set By Autotune | [14 empty] | Set By Autotune |  |  | Set By Autotune | Set By Autotune | [11 empty] | 21
MOTOR CONTROL - Autotune | 0 | 76 | Total Inertia | Real |  |  |  | Set By Autotune | Set By Autotune | [14 empty] | Set By Autotune |  |  | Set By Autotune | Set By Autotune | [11 empty] | 21
FEEDBACK & I/O - Digin Functions | 0 | 150 | Digital In Cfg | 32-bit Integer |  |  |  | 0 – Run Edge | 0 – Run Edge | [14 empty] | 0 – Run Edge |  |  | 0 – Run Edge | 0 – Run Edge | [11 empty] | 21
FEEDBACK & I/O - Digin Functions | 0 | 155 | DI Enable | 32-bit Integer |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
FEEDBACK & I/O - Digin Functions | 0 | 156 | DI Clear Fault | 32-bit Integer |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
FEEDBACK & I/O - Digin Functions | 0 | 157 | DI Aux Fault | 32-bit Integer |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
FEEDBACK & I/O - Digin Functions | 0 | 158 | DI Stop | 32-bit Integer |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
FEEDBACK & I/O - Digin Functions | 0 | 159 | DI Cur Lmt Stop | 32-bit Integer |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
FEEDBACK & I/O - Digin Functions | 0 | 160 | DI Coast Stop | 32-bit Integer |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
FEEDBACK & I/O - Digin Functions | 0 | 161 | DI Start | 32-bit Integer |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
FEEDBACK & I/O - Digin Functions | 0 | 162 | DI Fwd Reverse | 32-bit Integer |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
FEEDBACK & I/O - Digin Functions | 0 | 163 | DI Run | 32-bit Integer |  |  |  | Port 0: Dig In Sts.Input 1 | Port 0: Dig In Sts.Input 1 | [14 empty] | Default |  |  | Port 0: Dig In Sts.Input 1 | Port 0: Dig In Sts.Input 1 | [11 empty] | 21
FEEDBACK & I/O - Digin Functions | 0 | 164 | DI Run Forward | 32-bit Integer |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
FEEDBACK & I/O - Digin Functions | 0 | 165 | DI Run Reverse | 32-bit Integer |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
FEEDBACK & I/O - Digout Functions | 0 | 230 | RO0 Sel | 32-bit Integer |  |  |  | Default | Default | [14 empty] | 0 |  |  | Default | Default | [11 empty] | 21
DRIVE CFG - Control Cfg | 0 | 306 | Duty Rating | 32-bit Integer |  |  |  | 1 = “Heavy Duty” | 1 = “Heavy Duty” | [14 empty] | 0 normally, 1 for HD |  |  | 1 = “Heavy Duty” | 1 = “Heavy Duty” | [11 empty] | 21
DRIVE CFG - Control Cfg | 0 | 308 | Direction Mode | 32-bit Integer |  |  |  | 0 = “Unipolar” | 0 = “Unipolar” | [14 empty] | 0 = “Unipolar” 1 = “Reversing" |  |  | 0 = “Unipolar” | 0 = “Unipolar” | [11 empty] | 21
Protection - Motor Overload | 0 | 410 | Motor OL Actn | 32-bit Integer |  |  |  | 3 = “FltCoastStop” | 3 = “FltCoastStop” | [14 empty] | 3 = “FltCoastStop” |  |  | 3 = “FltCoastStop” | 3 = “FltCoastStop” | [11 empty] | 21
Protection - Motor Overload | 0 | 411 | Mtr OL at Pwr | 32-bit Integer |  |  |  | 0 = “Assume Cold” | 0 = “Assume Cold” | [14 empty] | 0 = “Assume Cold” |  |  | 0 = “Assume Cold” | 0 = “Assume Cold” | [11 empty] | 21
Protection - Motor Overload | 0 | 412 | Mtr OL Alarm Lvl | Real |  |  |  | N/A | N/A | [14 empty] | N/A |  |  | N/A | N/A | [11 empty] | 21
Protection - Motor Overload | 0 | 413 | Mtr OL Factor | Real |  |  |  | 1 | 1 | [14 empty] | 1 |  |  | 1 | 1 | [11 empty] | 21
Protection - Motor Overload | 0 | 414 | Mtr OL Hertz | Real |  |  |  | 20 | 20 | [14 empty] | 20 |  |  | 20 | 20 | [11 empty] | 21
Protection - Motor Overload | 0 | 415 | Mtr OL Reset Lvl | Real |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
Protection - Load Limits | 0 | 420 | Drive OL Mode | 32-bit Integer |  |  |  | 3 = “Both PWM 1st” | 3 = “Both PWM 1st” | [14 empty] | 3 = “Both PWM 1st” |  |  | 3 = “Both PWM 1st” | 3 = “Both PWM 1st” | [11 empty] | 21
Protection - Load Limits | 0 | 421 | Current Lmt Sel | 32-bit Integer |  |  |  | 422 | 422 | [14 empty] | 422 |  |  | 422 | 422 | [11 empty] | 21
Protection - Load Limits | 0 | 422 423 | Current Limit 1 Current Limit 2 | Real |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
Protection - Load Limits | 0 | 425 | Current Rate Lmt | Real |  |  |  | 400 | 400 | [14 empty] | 400 |  |  | 400 | 400 | [11 empty] | 21
Speed Control - Speed Limits | 0 | 520 | Max Fwd Speed | Real |  |  |  | 50 Hz | 50 Hz | [14 empty] | Default |  |  | 50 Hz | 50 Hz | [11 empty] | 21
Speed Control - Speed Limits | 0 | 521 | Max Rev Speed | Real |  |  |  | 0 Hz | 0 Hz | [14 empty] | Default |  |  | 0 Hz | 0 Hz | [11 empty] | 21
Speed Control - Speed Limits | 0 | 522 | Min Fwd Speed | Real |  |  |  | 10 Hz | 10 Hz | [14 empty] | 0 |  |  | 10 Hz | 10 Hz | [11 empty] | 21
Speed Control - Speed Limits | 0 | 523 | Min Rev Speed | Real |  |  |  | 0 Hz | 0 Hz | [14 empty] | 0 |  |  | 0 Hz | 0 Hz | [11 empty] | 21
Speed Control - Speed Limits | 0 | 524 | Overspeed Limit | Real |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
Speed Control - Speed Limits | 0 | 525 | Zero Speed Limit | Real |  |  |  | Default | Default | [14 empty] | Default |  |  | Default | Default | [11 empty] | 21
Speed Control - Speed Ramp Rates | 0 | 535 536 | Accel Time 1 Accel Time 2 | Real |  |  |  | 20 | 20 | [14 empty] | 10, or 20 for Heavy Duty |  |  | 20 | 20 | [11 empty] | 21
Speed Control - Speed Ramp Rates | 0 | 537 538 | Decel Time 1 Decel Time 2 | Real |  |  |  | 20 | 20 | [14 empty] | 10, or 20 for Heavy Duty |  |  | 20 | 20 | [11 empty] | 21
Speed Control - Speed Reference | 0 | 545 | Spd Ref A Sel Spd Ref B Sel | 32-bit Integer |  |  |  | Port 0: P871 | Port 0: P871 | [14 empty] | Default |  |  | Port 0: P871 | Port 0: P871 | [11 empty] | 21
22-Series I/O Analog Outputs | 4 | 10 | RO0 Sel | 32-bit Integer |  |  |  | N/A | N/A | [17 empty] | N/A | N/A | [11 empty] | 21
22-Series I/O Analog Outputs | 4 | 6 | Dig Out Invert | 32-bit Integer |  |  |  | N/A | N/A | [17 empty] | N/A | N/A | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 3 | BOOTP |  |  |  |  | Disabled | Disabled | [14 empty] | Disabled |  |  | Disabled | Disabled | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 4 | IP Addr Cfg 1 |  |  |  |  | 10 | 10 | [14 empty] | 10 |  |  | 10 | 10 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 5 | IP Addr Cfg 2 |  |  |  |  | 10 | 10 | [14 empty] | 10 |  |  | 10 | 10 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 6 | IP Addr Cfg 3 |  |  |  |  | 145 | 145 | [14 empty] | 145 |  |  | 145 | 145 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 7 | IP Addr Cfg 4 |  |  |  |  | 67 | 68 | [14 empty] | Specific to drive |  |  | 65 | 66 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 8 | Subnet Cfg 1 |  |  |  |  | 255 | 255 | [14 empty] | 255 |  |  | 255 | 255 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 9 | Subnet Cfg 2 |  |  |  |  | 255 | 255 | [14 empty] | 255 |  |  | 255 | 255 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 10 | Subnet Cfg 3 |  |  |  |  | 255 | 255 | [14 empty] | 255 |  |  | 255 | 255 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 11 | Subnet Cfg 4 |  |  |  |  | 0 | 0 | [14 empty] | 0 |  |  | 0 | 0 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 12 | Gateway Cfg 1 |  |  |  |  | 10 | 10 | [14 empty] | 10 |  |  | 10 | 10 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 12 | Gateway Cfg 2 |  |  |  |  | 10 | 10 | [14 empty] | 10 |  |  | 10 | 10 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 13 | Gateway Cfg 3 |  |  |  |  | 142 | 142 | [14 empty] | 142 |  |  | 142 | 142 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 14 | Gateway Cfg 4 |  |  |  |  | 1 | 1 | [14 empty] | 1 |  |  | 1 | 1 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 23 | Comm Flt Action | Real |  |  |  | 1 = Stop | 1 = Stop | [14 empty] | 1 = Stop |  |  | 1 = Stop | 1 = Stop | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 38 | Indirect Par #1 |  |  |  |  | 220 | 220 | [14 empty] | 220 (PF753) or 14001 (PF755) |  |  | 220 | 220 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 39 | Indirect Par #2 |  |  |  |  | 933 | 933 | [14 empty] | 933 |  |  | 933 | 933 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 40 | Indirect Par #3 |  |  |  |  | 724 | 724 | [14 empty] | 724 |  |  | 724 | 724 | [11 empty] | 21
Port 6 (20-750-20COMM) | 6 | 41 | Indirect Par #4 |  |  |  |  | 937 | 937 | [14 empty] | 937 |  |  | 937 | 937 | [11 empty] | 21
[8 empty] | F75-PW-608 | [17 empty] | Equipment Number | F75-PW-606 | F75-PW-607 | [11 empty] | 22
[8 empty] | Decant Dam 4 Return Pump 3 | [17 empty] | Description | Decant Dam 4 Return Pump 1 | Decant Dam 4 Return Pump 2 | [11 empty] | 22
[8 empty] | 20G11JC910JN0NNNNN+ 20- 750-S+20-750-20COMM+20- HIM-C6S+20-750-2262C-2R | [17 empty] | VVVF Model Number | 20G11JC910JN0NNNNN+ 20- 750-S+20-750-20COMM+20- HIM-C6S+20-750-2262C-2R | 20G11JC910JN0NNNNN+ 20- 750-S+20-750-20COMM+20- HIM-C6S+20-750-2262C-2R | [11 empty] | 22
[8 empty] | 770 | [17 empty] | VVVF Input Current (A) | 770 | 770 | [11 empty] | 22
[8 empty] | 450 | [17 empty] | Rating (kW) | 450 | 450 | [11 empty] | 22
[8 empty] | 1 | [17 empty] | No of Motors | 1 | 1 | [11 empty] | 22
[8 empty] | 750.0 | [17 empty] | FLC (A) | 750.0 | 750.0 | [11 empty] | 22
[8 empty] | 2000-F75-SCNM-EL-40001 | [17 empty] | Schematic Drawing | 2000-F75-SCM-EL-40001 | 2000-F75-SCM-EL-40001 | [11 empty] | 22
[8 empty] | N/A | [17 empty] | VVVF Datasheet | N/A | N/A | [11 empty] | 22
[8 empty] | https://configurator.rockwellaut | [17 empty] | VVVF Website Cutsheet | https://configurator.rockwellaut | https://configurator.rockwellaut | [11 empty] | 22
[8 empty] | omation.com/api/Product/20G1 | [18 empty] | omation.com/api/Product/20G1 | omation.com/api/Product/20G1 | [11 empty] | 22
[8 empty] | 1JC910JN0NNNNN/cutsheet | [18 empty] | 1JC910JN0NNNNN/cutsheet | 1JC910JN0NNNNN/cutsheet | [11 empty] | 22
[8 empty] | 2000-ME015-F14- 40001AIFA | [17 empty] | Motor Datasheet | 2000-ME015-F14- 40001AIFA | 2000-ME015-F14- 40001AIFA | [11 empty] | 22
[8 empty] | __ Note 5 | [17 empty] | IP Address | __ Note 5 | __ Note 5 | [11 empty] | 22
[8 empty] | B1250-H-3-1250-BE | [17 empty] | Circuit Breaker | B1250-H-3-1250-BE | B1250-H-3-1250-BE | [11 empty] | 22
[8 empty] | 1250 | [17 empty] | Nominal Rating of Trip Unit (A) | 1250 | 1250 | [11 empty] | 22
[8 empty] | - | [17 empty] | Ir (xIn) | - | - | [11 empty] | 22
[8 empty] | - | [17 empty] | Ii (xIn) | - | - | [11 empty] | 22
[8 empty] | 0.7 (875 A) | [17 empty] | Long Time - Ir1 | 0.7 (875 A) | 0.7 (875 A) | [11 empty] | 22
[8 empty] | - | [17 empty] | Long Time - Ir2 | - | - | [11 empty] | 22
[8 empty] | - | [17 empty] | Long Time Delay - tr (sec) | - | - | [11 empty] | 22
[8 empty] | - | [17 empty] | Short Time - Isd | - | - | [11 empty] | 22
[8 empty] | - | [17 empty] | Short Time Delay - tsd (sec) | - | - | [11 empty] | 22
[8 empty] | - | [17 empty] | Short Time Delay I²t | - | - | [11 empty] | 22
[8 empty] | - | [17 empty] | Instantaneous - Ii | - | - | [11 empty] | 22
[8 empty] | 9 | [17 empty] | Characteristic No. | 9 | 9 | [11 empty] | 22
[8 empty] | - | [17 empty] | TOL | - | - | [11 empty] | 22
[8 empty] | - | [17 empty] | TOL Setting (A) | - | - | [11 empty] | 22
File / Group | Port | No. | Display Name | Data Type | [19 empty] | Setting Notes | [15 empty] | 22
MOTOR CONTROL - Motor Data | 0 | 25 | Motor NP Volts | Real |  |  |  | 415V | [15 empty] | 415V |  |  | 415V | 415V | [11 empty] | 22
MOTOR CONTROL - Motor Data | 0 | 26 | Motor NP Amps | Real |  |  |  | 750 | [15 empty] | Lookup |  |  | 750 | 750 | [11 empty] | 22
MOTOR CONTROL - Motor Data | 0 | 27 | Motor NP Hertz | Real |  |  |  | 50 | [15 empty] | 50 |  |  | 50 | 50 | [11 empty] | 22
MOTOR CONTROL - Motor Data | 0 | 28 | Motor NP RPM | Real |  |  |  | 1490 | [15 empty] | Datasheet |  |  | 1492 | 1490 | [11 empty] | 22
MOTOR CONTROL - Motor Data | 0 | 29 | Mtr NP Pwr Units | 32-bit Integer |  |  |  | 1 = kW | [15 empty] | 1 – kW |  |  | 1 = kW | 1 = kW | [11 empty] | 22
MOTOR CONTROL - Motor Data | 0 | 30 | Motor NP Power | Real |  |  |  | 450 | [15 empty] | Lookup |  |  | 450 | 450 | [11 empty] | 22
MOTOR CONTROL - Motor Data | 0 | 31 | Motor Poles | 32-bit Integer |  |  |  | 4 | [15 empty] | Lookup |  |  | 4 | 4 | [11 empty] | 22
MOTOR CONTROL - Mtr Ctrl Options | 0 | 35 | Motor Ctrl Mode | 32-bit Integer |  |  |  | 1 - Induction SV | [15 empty] | 1 – Induction SV | Note 1 |  | 1 - Induction SV | 1 - Induction SV | [11 empty] | 22
MOTOR CONTROL - Mtr Ctrl Options | 0 | 36 | Maximum Voltage | Real |  |  |  | 415 | [15 empty] | 415 |  |  | 415 | 415 | [11 empty] | 22
MOTOR CONTROL - Mtr Ctrl Options | 0 | 37 | Maximum Freq | Real |  |  |  | 50 | [15 empty] | 50 |  |  | 50 | 50 | [11 empty] | 22
MOTOR CONTROL - Mtr Ctrl Options | 0 | 38 | PWM Frequency | Real |  |  |  | Default, Dependant on Frame size | [15 empty] | Default, Dependant on Frame size |  |  | Default, Dependant on Frame size | Default, Dependant on Frame size | [11 empty] | 22
MOTOR CONTROL - Mtr Ctrl Options | 0 | 41 | Common Mode Type | 32-bit Integer |  |  |  | 0 – CMV | [15 empty] | 0 – CMV |  |  | 0 – CMV | 0 – CMV | [11 empty] | 22
MOTOR CONTROL - Volts per Hertz | 0 | 60 | Start Acc Boost | Real |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
MOTOR CONTROL - Volts per Hertz | 0 | 61 | Run Boost | Real |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
MOTOR CONTROL - Volts per Hertz | 0 | 62 | Break Voltage | Real |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
MOTOR CONTROL - Volts per Hertz | 0 | 63 | Break Frequency | Real |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
MOTOR CONTROL - Volts per Hertz | 0 | 65 | VHz Curve | 32-bit Integer |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
MOTOR CONTROL - Autotune | 0 | 70 | Autotune | 32-bit Integer |  |  |  | 1 – Calculate | [15 empty] | 1 – Calculate |  |  | 1 – Calculate | 1 – Calculate | [11 empty] | 22
MOTOR CONTROL - Autotune | 0 | 71 | Autotune Torque | Real |  |  |  | 50% | [15 empty] | 50% |  |  | 50% | 50% | [11 empty] | 22
MOTOR CONTROL - Autotune | 0 | 73 | IR Voltage Drop | Real |  |  |  | Set By Autotune | [15 empty] | Set By Autotune |  |  | Set By Autotune | Set By Autotune | [11 empty] | 22
MOTOR CONTROL - Autotune | 0 | 74 | Ixo Voltage Drop | Real |  |  |  | Set By Autotune | [15 empty] | Set By Autotune |  |  | Set By Autotune | Set By Autotune | [11 empty] | 22
MOTOR CONTROL - Autotune | 0 | 75 | Flux Current Ref | Real |  |  |  | Set By Autotune | [15 empty] | Set By Autotune |  |  | Set By Autotune | Set By Autotune | [11 empty] | 22
MOTOR CONTROL - Autotune | 0 | 76 | Total Inertia | Real |  |  |  | Set By Autotune | [15 empty] | Set By Autotune |  |  | Set By Autotune | Set By Autotune | [11 empty] | 22
FEEDBACK & I/O - Digin Functions | 0 | 150 | Digital In Cfg | 32-bit Integer |  |  |  | 0 – Run Edge | [15 empty] | 0 – Run Edge |  |  | 0 – Run Edge | 0 – Run Edge | [11 empty] | 22
FEEDBACK & I/O - Digin Functions | 0 | 155 | DI Enable | 32-bit Integer |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
FEEDBACK & I/O - Digin Functions | 0 | 156 | DI Clear Fault | 32-bit Integer |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
FEEDBACK & I/O - Digin Functions | 0 | 157 | DI Aux Fault | 32-bit Integer |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
FEEDBACK & I/O - Digin Functions | 0 | 158 | DI Stop | 32-bit Integer |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
FEEDBACK & I/O - Digin Functions | 0 | 159 | DI Cur Lmt Stop | 32-bit Integer |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
FEEDBACK & I/O - Digin Functions | 0 | 160 | DI Coast Stop | 32-bit Integer |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
FEEDBACK & I/O - Digin Functions | 0 | 161 | DI Start | 32-bit Integer |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
FEEDBACK & I/O - Digin Functions | 0 | 162 | DI Fwd Reverse | 32-bit Integer |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
FEEDBACK & I/O - Digin Functions | 0 | 163 | DI Run | 32-bit Integer |  |  |  | Port 4: Dig In Sts.Input 1 | [15 empty] | Default |  |  | Port 4: Dig In Sts.Input 1 | Port 4: Dig In Sts.Input 1 | [11 empty] | 22
FEEDBACK & I/O - Digin Functions | 0 | 164 | DI Run Forward | 32-bit Integer |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
FEEDBACK & I/O - Digin Functions | 0 | 165 | DI Run Reverse | 32-bit Integer |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
FEEDBACK & I/O - Digout Functions | 0 | 230 | RO0 Sel | 32-bit Integer |  |  |  | N/A | [15 empty] | 0 |  |  | N/A | N/A | [11 empty] | 22
DRIVE CFG - Control Cfg | 0 | 306 | Duty Rating | 32-bit Integer |  |  |  | 1 = “Heavy Duty” | [15 empty] | 0 normally, 1 for HD |  |  | 1 = “Heavy Duty” | 1 = “Heavy Duty” | [11 empty] | 22
DRIVE CFG - Control Cfg | 0 | 308 | Direction Mode | 32-bit Integer |  |  |  | 0 = “Unipolar” | [15 empty] | 0 = “Unipolar” 1 = “Reversing" |  |  | 0 = “Unipolar” | 0 = “Unipolar” | [11 empty] | 22
Protection - Motor Overload | 0 | 410 | Motor OL Actn | 32-bit Integer |  |  |  | 3 = “FltCoastStop” | [15 empty] | 3 = “FltCoastStop” |  |  | 3 = “FltCoastStop” | 3 = “FltCoastStop” | [11 empty] | 22
Protection - Motor Overload | 0 | 411 | Mtr OL at Pwr | 32-bit Integer |  |  |  | 0 = “Assume Cold” | [15 empty] | 0 = “Assume Cold” |  |  | 0 = “Assume Cold” | 0 = “Assume Cold” | [11 empty] | 22
Protection - Motor Overload | 0 | 412 | Mtr OL Alarm Lvl | Real |  |  |  | N/A | [15 empty] | N/A |  |  | N/A | N/A | [11 empty] | 22
Protection - Motor Overload | 0 | 413 | Mtr OL Factor | Real |  |  |  | 1 | [15 empty] | 1 |  |  | 1 | 1 | [11 empty] | 22
Protection - Motor Overload | 0 | 414 | Mtr OL Hertz | Real |  |  |  | 20 | [15 empty] | 20 |  |  | 20 | 20 | [11 empty] | 22
Protection - Motor Overload | 0 | 415 | Mtr OL Reset Lvl | Real |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
Protection - Load Limits | 0 | 420 | Drive OL Mode | 32-bit Integer |  |  |  | 3 = “Both PWM 1st” | [15 empty] | 3 = “Both PWM 1st” |  |  | 3 = “Both PWM 1st” | 3 = “Both PWM 1st” | [11 empty] | 22
Protection - Load Limits | 0 | 421 | Current Lmt Sel | 32-bit Integer |  |  |  | 422 | [15 empty] | 422 |  |  | 422 | 422 | [11 empty] | 22
Protection - Load Limits | 0 | 422 423 | Current Limit 1 Current Limit 2 | Real |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
Protection - Load Limits | 0 | 425 | Current Rate Lmt | Real |  |  |  | 400 | [15 empty] | 400 |  |  | 400 | 400 | [11 empty] | 22
Speed Control - Speed Limits | 0 | 520 | Max Fwd Speed | Real |  |  |  | 50 Hz | [15 empty] | Default |  |  | 50 Hz | 50 Hz | [11 empty] | 22
Speed Control - Speed Limits | 0 | 521 | Max Rev Speed | Real |  |  |  | 0 Hz | [15 empty] | Default |  |  | 0 Hz | 0 Hz | [11 empty] | 22
Speed Control - Speed Limits | 0 | 522 | Min Fwd Speed | Real |  |  |  | 10 Hz | [15 empty] | 0 |  |  | 10 Hz | 10 Hz | [11 empty] | 22
Speed Control - Speed Limits | 0 | 523 | Min Rev Speed | Real |  |  |  | 0 Hz | [15 empty] | 0 |  |  | 0 Hz | 0 Hz | [11 empty] | 22
Speed Control - Speed Limits | 0 | 524 | Overspeed Limit | Real |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
Speed Control - Speed Limits | 0 | 525 | Zero Speed Limit | Real |  |  |  | Default | [15 empty] | Default |  |  | Default | Default | [11 empty] | 22
Speed Control - Speed Ramp Rates | 0 | 535 536 | Accel Time 1 Accel Time 2 | Real |  |  |  | 20 | [15 empty] | 10, or 20 for Heavy Duty |  |  | 20 | 20 | [11 empty] | 22
Speed Control - Speed Ramp Rates | 0 | 537 538 | Decel Time 1 Decel Time 2 | Real |  |  |  | 20 | [15 empty] | 10, or 20 for Heavy Duty |  |  | 20 | 20 | [11 empty] | 22
Speed Control - Speed Reference | 0 | 545 | Spd Ref A Sel Spd Ref B Sel | 32-bit Integer |  |  |  | Port 0: P871 | [15 empty] | Default |  |  | Port 0: P871 | Port 0: P871 | [11 empty] | 22
22-Series I/O Analog Outputs | 4 | 10 | RO0 Sel | 32-bit Integer |  |  |  | Port 0: P935 Bit 16 [Running] | [18 empty] | Port 0: P935 Bit 16 [Running] | Port 0: P935 Bit 16 [Running] | [11 empty] | 22
22-Series I/O Analog Outputs | 4 | 6 | Dig Out Invert | 32-bit Integer |  |  |  | xxxx xxxx xxxx xx00 | [18 empty] | xxxx xxxx xxxx xx00 | xxxx xxxx xxxx xx00 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 3 | BOOTP |  |  |  |  | Disabled | [15 empty] | Disabled |  |  | Disabled | Disabled | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 4 | IP Addr Cfg 1 |  |  |  |  | 10 | [15 empty] | 10 |  |  | 10 | 10 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 5 | IP Addr Cfg 2 |  |  |  |  | 10 | [15 empty] | 10 |  |  | 10 | 10 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 6 | IP Addr Cfg 3 |  |  |  |  | 145 | [15 empty] | 145 |  |  | 145 | 145 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 7 | IP Addr Cfg 4 |  |  |  |  | 71 | [15 empty] | Specific to drive |  |  | 69 | 70 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 8 | Subnet Cfg 1 |  |  |  |  | 255 | [15 empty] | 255 |  |  | 255 | 255 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 9 | Subnet Cfg 2 |  |  |  |  | 255 | [15 empty] | 255 |  |  | 255 | 255 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 10 | Subnet Cfg 3 |  |  |  |  | 255 | [15 empty] | 255 |  |  | 255 | 255 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 11 | Subnet Cfg 4 |  |  |  |  | 0 | [15 empty] | 0 |  |  | 0 | 0 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 12 | Gateway Cfg 1 |  |  |  |  | 10 | [15 empty] | 10 |  |  | 10 | 10 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 12 | Gateway Cfg 2 |  |  |  |  | 10 | [15 empty] | 10 |  |  | 10 | 10 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 13 | Gateway Cfg 3 |  |  |  |  | 142 | [15 empty] | 142 |  |  | 142 | 142 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 14 | Gateway Cfg 4 |  |  |  |  | 1 | [15 empty] | 1 |  |  | 1 | 1 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 23 | Comm Flt Action | Real |  |  |  | 1 = Stop | [15 empty] | 1 = Stop |  |  | 1 = Stop | 1 = Stop | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 38 | Indirect Par #1 |  |  |  |  | 14001 | [15 empty] | 220 (PF753) or 14001 (PF755) |  |  | 14001 | 14001 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 39 | Indirect Par #2 |  |  |  |  | 933 | [15 empty] | 933 |  |  | 933 | 933 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 40 | Indirect Par #3 |  |  |  |  | 724 | [15 empty] | 724 |  |  | 724 | 724 | [11 empty] | 22
Port 6 (20-750-20COMM) | 6 | 41 | Indirect Par #4 |  |  |  |  | 937 | [15 empty] | 937 |  |  | 937 | 937 | [11 empty] | 22

## Equipment list
Equipment Number | Schematic Drawing No. | Instantaneous Trip (Ii, xln) | ELR Make/Model | ELR Threshold IΔn (A) | Sort | Make / Model | Rating (A) | Page
- | Modbus TCP Word Order | Little endian | Little endian | - |  |  |  | 19
[5 empty] | LV VVVF SETTINGS Notes: 1. All Settings to be verified during pre-commissioning. 2. Motor load current values and RPM are to be confirmed against motor nameplate data on site. 3. Parameters given for all protection settings on this list, not all functions enabled. 4. Long Time Setting Check - thermal / long time setting is higher than VVVF input current. 5. Refer to DCS Communications document for IP Address Register for details. 6. Motor RTDs wired to DCS, not VVVF. 7. STO implementation is "out-of-the-box" and "hardwired", refer Rockwell Automation Publication 750-UM002O-EN-P - January 2025. Note, PowerFlex 755 drives (frames 8...10) control boards do not have a SAFETY enable jumper. PowerFlex 753 do have a SAFETY enable jumber that is required to be removed from the Main Control Board to ensure the drive does does not fault. Refer <https://www.rockwellautomation.com/en-us/products/details.20-750-S.html> and extract below. | Allen-Bradley PowerFlex Series | PF 753 Series | 21
[5 empty] | LV VVVF SETTINGS Notes: 1. All Settings to be verified during pre-commissioning. 2. Motor load current values and RPM are to be confirmed against motor nameplate data on site. 3. Parameters given for all protection settings on this list, not all functions enabled. 4. Long Time Setting Check - thermal / long time setting is higher than VVVF input current. 5. Refer to DCS Communications document for IP Address Register for details. 6. Motor RTDs wired to DCS, not VVVF. 7. STO implementation is "out-of-the-box" and "hardwired", refer Rockwell Automation Publication 750-UM002O-EN-P - January 2025. Note, PowerFlex 755 drives (frames 8...10) control boards do not have a SAFETY enable jumper. PowerFlex 753 do have a SAFETY enable jumber that is required to be removed from the Main Control Board to ensure the drive does does not fault. Refer <https://www.rockwellautomation.com/en-us/products/details.20-750-S.html> and extract below. | Allen-Bradley PowerFlex Series | PF 755 Series | 22
F23-HF-601 |  |  |  |  | Equipment Number |  |  | 23
FIM III Booster Station 415V Switchroom Active Harmonic Filter |  |  |  |  | Description |  |  | 23
Schneider AccuSine PCS+ PCSP300D5IP31 |  |  |  |  | Make/Model |  |  | 23
F23-SW-602 |  |  |  |  | Motor Control Centre |  |  | 23
300A |  |  |  |  | System Rating |  |  | 23
415V 50Hz |  |  |  |  | Nominal Voltage ¦ Frequency |  |  | 23
No |  |  |  |  | External Transformer |  |  | 23
3P3W |  |  |  |  | Wiring Type |  |  | 23
3 CTs |  |  |  |  | CT Configuration |  |  | 23
Source |  |  |  |  | CT Position |  |  | 23
300 Amps |  |  |  |  | Total Capacity |  |  | 23
4000:5, Positive |  |  |  |  | CT Setting |  |  | 23
On |  |  |  |  | Harmonic Mode |  |  | 23
On |  |  |  |  | PF Mode |  |  | 23
On |  |  |  |  | Optimised PF Mode |  |  | 23
Off |  |  |  |  | Load Balancing |  |  | 23
Manual (Pre-comissioning) Autostart Enable (Post-commissioning) |  |  |  |  | Power On Mode |  |  | 23
On |  |  |  |  | Output Enabled |  |  | 23
On |  |  |  |  | 5th |  |  | 23
On |  |  |  |  | 7th |  |  | 23
On |  |  |  |  | 11th |  |  | 23
On |  |  |  |  | 13th |  |  | 23
On |  |  |  |  | 17th |  |  | 23
On |  |  |  |  | 19th |  |  | 23
On |  |  |  |  | 23rd |  |  | 23
On |  |  |  |  | 25th |  |  | 23
Off |  |  |  |  | All other Harmonics |  |  | 23
Inductive |  |  |  |  | Inductive or Capacitive |  |  | 23
0.96 |  |  |  |  | Target PF |  |  | 23
Factory Default |  |  |  |  | OTHER SETTINGS |  |  | 23
Refer harmonics calculation for details of sizing requirement 2000-F23-CAL-EL-40003. |  |  |  |  | General Notes |  |  | 23
P155 F23-SW-601 26 02 12 |  |  |  |  | SEL 735/751 Relays (F23-SW-601) |  |  | 24
P155 F23-SW-602 26 02 12 |  |  |  |  | SEL 735 Relay (F23-SW-602) |  |  | 24
P155 FIM III Proposed LV VSD Settings for FAT 26 02 04 1 |  |  |  |  | Allen-Bradley PowerFlex PF753/755 VSDs |  |  | 24
Anybus Communicator configuration F23SW602-ACB 2026-02-17 11 1 |  |  |  |  | AnyBus ABC3090-A Gateway (F23-SW-602 LV ACB) |  |  | 24