## Cable schedule
Cable Number | Equip. Number - From | Equipment Name - From | Location - From | Equip. Number - To | Equipment Name - To | Location - To | nductor Size (mm | Insulation (kV) | Length | o. of Cores / Pai | Conductor | Construction | eath (Preferred colou | r Installation Method | Supplied By | Installed By | Comments | Rev | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Length (m) | No. of Cores / Pairs | Sheath (Preferred colour) | Installation Method | Page
F28NR013-P1 | F28-DB-001 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM L&SP DISTRIBUTION BOARD | F28 Field | F28-NR-013 | ULTRA FINE GRINDING 33KV/11KV TRANSFORMER NEUTRAL EARTHING RESISTOR | F28 field | 2.5 | 0.6/1 | 30 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Flat, Touching | Primero | Primero | NER Anti-condensation heater | 0 | [11 empty] | 2
F28NR013-C1 | F28-SW-013 | ULTRA FINE GRINDING 11KV SWITCHBOARD | F28-SR-001 | F28-NR-013 | ULTRA FINE GRINDING 33KV/11KV TRANSFORMER NEUTRAL EARTHING RESISTOR | F28 field | 4 | 0.6/1 | 30 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | NER CT to protection relay | 0 | [11 empty] | 2
F28TR013-C1 | F28-SW-013 | ULTRA FINE GRINDING 11KV SWITCHBOARD | F28-SR-001 | F28-TR-013 | ULTRA FINE GRINDING 33KV/11KV TRANSFORMER | F28 Field | 1.5 | 0.6/1 | 30 | 12C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | Transformer trips to protection relay | 0 | [11 empty] | 2
F28SW109-P3 | F28-GE-109 | ULTRA FINE GRINDING ESSENTIAL SUPPLY 415V GENERATOR | Ultrafine Grinding 415V Generator | F28-SW-109 | ULTRA FINE GRINDING ESSENTIAL 415V SWITCHBOARD | Ultrafine Grinding Switchroom | 150 | 0.6/1 | 30 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 0 | [11 empty] | 2
F28SW109-P4 | F28-GE-109 | ULTRA FINE GRINDING ESSENTIAL SUPPLY 415V GENERATOR | Ultrafine Grinding 415V Generator | F28-SW-109 | ULTRA FINE GRINDING ESSENTIAL 415V SWITCHBOARD | Ultrafine Grinding Switchroom | 150 | 0.6/1 | 30 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 0 | [11 empty] | 2
F28GE109CP-P1 | F28-DB-001 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM L&SP DISTRIBUTION BOARD | Ultrafine Grinding Switchroom | F28GE109-CP | ULTRA FINE GRINDING ESSENTIAL SUPPLY 415V GENERATOR CONTROL PANEL | Ultrafine Grinding 415V Generator | 2.5 | 0.6/1 | 30 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | Genset Battery Charger | 0 | [11 empty] | 2
F28GE109CP-C1 | F28-DCS-410 | ULTRA FINE GRINDING 415V SWITCHROOM DCS PANEL | Ultrafine Grinding Switchroom | F28GE109-CP | ULTRA FINE GRINDING ESSENTIAL SUPPLY 415V GENERATOR CONTROL PANEL | Ultrafine Grinding 415V Generator | 1.5 | 0.6/1 | 30 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | Generator Feedback to DCS | 0 | [11 empty] | 2
F28GE109CP-C2 | F28-SW-109 | ULTRA FINE GRINDING ESSENTIAL 415V SWITCHBOARD | Ultrafine Grinding Switchroom | F28GE109-CP | ULTRA FINE GRINDING ESSENTIAL SUPPLY 415V GENERATOR CONTROL PANEL | Ultrafine Grinding 415V Generator | 1.5 | 0.6/1 | 30 | 2C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | Generator Feedback to MCC | 0 | [11 empty] | 2
F28GE109CP-D1 | F28-COM-001 | ULTRA FINE GRINDING 415V SWITCHROOM COMMUNICATIONS RACK | Ultrafine Grinding Switchroom | F28GE109-CP | ULTRA FINE GRINDING ESSENTIAL SUPPLY 415V GENERATOR CONTROL PANEL | Ultrafine Grinding 415V Generator | N/A | N/A | 30 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | Generator to Comms | 0 | [11 empty] | 2
F28RIO001-P1 | F28-DB-201 | ULTRA FINE GRINDING 415V SWITCHROOM 240V UPS DISTRIBUTION BOARD | Ultrafine Grinding Switchroom | F28-RIO-001 | ULTRA FINE GRINDING FIELD N-IO PANEL | Field | 35 | 0.6/1 | 60 | 2C+E | Cu | XLPE/PVC | Orange | Buried in Conduit / Ladder - Single layer touching | Primero | Primero |  | 0 | [11 empty] | 2
F28RIO002-P1 | F28-DB-201 | ULTRA FINE GRINDING 415V SWITCHROOM 240V UPS DISTRIBUTION BOARD | Ultrafine Grinding Switchroom | F28-RIO-002 | ULTRA FINE GRINDING FIELD N-IO PANEL | Field | 35 | 0.6/1 | 60 | 2C+E | Cu | XLPE/PVC | Orange | Buried in Conduit / Ladder - Single layer touching | Primero | Primero |  | 0 | [11 empty] | 2
F28RIO003-P1 | F28-DB-201 | ULTRA FINE GRINDING 415V SWITCHROOM 240V UPS DISTRIBUTION BOARD | Ultrafine Grinding Switchroom | F28-RIO-003 | ULTRA FINE GRINDING FIELD N-IO PANEL | Field | 35 | 0.6/1 | 60 | 2C+E | Cu | XLPE/PVC | Orange | Buried in Conduit / Ladder - Single layer touching | Primero | Primero |  | 0 | [11 empty] | 2
F28RIO004-P1 | F28-DB-201 | ULTRA FINE GRINDING 415V SWITCHROOM 240V UPS DISTRIBUTION BOARD | Ultrafine Grinding Switchroom | F28-RIO-004 | ULTRA FINE GRINDING FIELD N-IO PANEL | Field | 35 | 0.6/1 | 60 | 2C+E | Cu | XLPE/PVC | Orange | Buried in Conduit / Ladder - Single layer touching | Primero | Primero |  | 0 | [11 empty] | 2
F28COM001/F28RIO001-FO1 | F28-COM-001 | ULTRA FINE GRINDING 415V SWITCHROOM COMMUNICATIONS RACK | Ultrafine Grinding Switchroom | F28-RIO-001 | ULTRA FINE GRINDING FIELD N-IO PANEL | Field | 9/125µm | N/A | 60 | 24C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Buried in Conduit / Ladder - Comms | Primero | Primero | Fibre allowance | 0 | [11 empty] | 2
F28RIO001/F28RIO002-FO1 | F28-RIO-001 | ULTRA FINE GRINDING FIELD N-IO PANEL | Field | F28-RIO-002 | ULTRA FINE GRINDING FIELD N-IO PANEL | Field | 9/125µm | N/A | 30 | 24C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | Fibre allowance | 0 | [11 empty] | 2
F28RIO002/F28COM001-FO1 | F28-RIO-002 | ULTRA FINE GRINDING FIELD N-IO PANEL | Field | F28-COM-001 | ULTRA FINE GRINDING 415V SWITCHROOM COMMUNICATIONS RACK | Field | 9/125µm | N/A | 30 | 24C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | Fibre allowance | 0 | [11 empty] | 2
F28COM001/F28RIO003-FO1 | F28-COM-001 | ULTRA FINE GRINDING 415V SWITCHROOM COMMUNICATIONS RACK | Ultrafine Grinding Switchroom | F28-RIO-003 | ULTRA FINE GRINDING FIELD N-IO PANEL | Field | 9/125µm | N/A | 60 | 24C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Buried in Conduit / Ladder - Comms | Primero | Primero | Fibre allowance | 0 | [11 empty] | 2
F28RIO003/F28RIO004-FO1 | F28-RIO-003 | ULTRA FINE GRINDING FIELD N-IO PANEL | Field | F28-RIO-004 | ULTRA FINE GRINDING FIELD N-IO PANEL | Field | 9/125µm | N/A | 30 | 24C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero | Fibre allowance | 0 | [11 empty] | 2
F28RIO004/F28COM001-FO1 | F28-RIO-004 | ULTRA FINE GRINDING FIELD N-IO PANEL | Field | F28-COM-001 | ULTRA FINE GRINDING 415V SWITCHROOM COMMUNICATIONS RACK | Ultrafine Grinding Switchroom | 9/125µm | N/A | 60 | 24C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Buried in Conduit / Ladder - Comms | Primero | Primero | Fibre allowance | 0 | [11 empty] | 2
F28COM001/F72RIO002-FO1 | F28-COM-001 | ULTRA FINE GRINDING 415V SWITCHROOM COMMUNICATIONS RACK | Ultrafine Grinding Switchroom | F72-RIO-002 | REAGENTS FIELD N-IO PANEL | Field | 9/125µm | N/A | 300 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Buried in Conduit / Ladder - Comms | Primero | Primero | Fibre allowance | 0 | [11 empty] | 2
F72RIO002/F28COM001-FO1 | F72-RIO-002 | REAGENTS FIELD N-IO PANEL | Field | F28-COM-001 | ULTRA FINE GRINDING 415V SWITCHROOM COMMUNICATIONS RACK | Ultrafine Grinding Switchroom | 9/125µm | N/A | 300 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Buried in Conduit / Ladder - Comms | Primero | Primero | Fibre allowance | 0 | [11 empty] | 2
F28DB301-P1 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-DB-301 | ULTRA FINE GRINDING AREA L&SP DISTRIBUTION BOARD | Field | 185 | 0.6/1 | 60 | 4C+E | Cu | XLPE/PVC Flexible | Orange | Buried in Conduit / Ladder - Single layer touching | Primero | Primero | Average UFG | 0 | [11 empty] | 2
F28PE301-P1 | F28-DB-301 | ULTRA FINE GRINDING AREA L&SP DISTRIBUTION BOARD | Field | F28-PE-301 | ULTRA FINE GRINDING AREA PHOTO-ELECTRIC CELL | Field | 2.5 | 0.6/1 | 10 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | PE Circuit for L&SP DB | 0 | [11 empty] | 2
F28AN431-P1 | F28-RIO-001 | ULTRA FINE GRINDING FIELD N-IO PANEL | UFG Drive Platform | F28-AN-431 | UFG PARTICLE SIZE ANALYSER | UFG Drive Platform | 4 | 0.6/1 | 15 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | Power to Sampler | 0 | [11 empty] | 2
F28AN431-D1 | F28-RIO-001 | Ultra Fine Grinding Field N-IO Panel | UFG Drive Platform | F28-AN-431 | UFG PARTICLE SIZE ANALYSER | UFG Drive Platform | N/A | N/A | 15 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | Ethernet to Sampler | 0 | [11 empty] | 2
F28AN431JB01-P1 | F28-DB-301 | ULTRA FINE GRINDING AREA L&SP DISTRIBUTION BOARD | UFG Drive Platform | F28AN431-JB01 | UFG PARTICLE SIZE ANALYSER PUMP CONTROL JUNCTION BOX | UFG Drive Platform | 2.5 | 0.6/1 | 15 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | Power to Pump Control Box | 0 | [11 empty] | 2
F28AN431JB01-I1 | F28-AN-431 | UFG PARTICLE SIZE ANALYSER | UFG Drive Platform | F28AN431-JB01 | UFG PARTICLE SIZE ANALYSER PUMP CONTROL JUNCTION BOX | UFG Drive Platform | VENDOR | VENDOR | 10 | VENDOR | Cu | VENDOR | VENDOR | Above Ground Conduit V | endor - ME068 Mets | Primero | Signal Cable from Sampler to Pump Control Box | 0 | [11 empty] | 2
F28AN431-I1 | F28AN431-JB01 | UFG PARTICLE SIZE ANALYSER Pump Control Junction Box | UFG Drive Platform | F28-AN-431 | UFG PARTICLE SIZE ANALYSER | UFG Drive Platform | VENDOR | VENDOR | 10 | VENDOR | Cu | VENDOR | VENDOR | Above Ground Conduit V | endor - ME068 Mets | Primero | Signal Cable to Tank Level | 0 | [11 empty] | 2
F28AN431-P2 | F28AN431-JB01 | UFG PARTICLE SIZE ANALYSER Pump Control Junction Box | UFG Drive Platform | F28-AN-431 | UFG PARTICLE SIZE ANALYSER | UFG Drive Platform | VENDOR | VENDOR | 10 | VENDOR | Cu | VENDOR | VENDOR | Above Ground Conduit V | endor - ME068 Mets | Primero | Power Cable to Pump | 0 | [11 empty] | 2
F28CR430ISL-P1 | F28-SW-109 | ULTRA FINE GRINDING ESSENTIAL 415V SWITCHBOARD | Ultrafine Grinding Switchroom | F28CR430-ISL | UFG AREA CRANE FIELD ISOLATOR | UFG Crane Platform | 25 | 0.6/1 | 80 | 3C+E | Cu | XLPE/PVC | Orange | Buried in Conduit / Ladder - Single layer touching | Primero | Primero |  | 0 | [11 empty] | 2
F28CR430-P1 | F28CR430-ISL | UFG AREA CRANE FIELD ISOLATOR | UFG Crane Platform | F28-CR-430 | UFG AREA CRANE | UFG Crane Platform | 25 | 0.6/1 | 10 | 3C+E | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 0 | [11 empty] | 2
F28FN481-P1 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-FN-481 | UFG MILL 2 BEARING OIL COOLER FAN 1 | UFG Ground Floor | 4 | 0.6/1 | 60 | 3C+E | Cu | PVC/PVC | Orange | Buried in Conduit | Primero | Primero |  | 0 | [11 empty] | 2
F28FN481LCS-C1 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28FN481-LCS | UFG MILL 2 BEARING OIL COOLER FAN 1 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 0.6/1 | 60 | 4C+E | Cu | PVC/PVC | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | Primero | Primero | LCS | 0 | [11 empty] | 2
F28FN482-P1 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-FN-482 | UFG MILL 2 GEARBOX OIL COOLER FAN 1 | UFG Ground Floor | 4 | 0.6/1 | 60 | 3C+E | Cu | PVC/PVC | Orange | Buried in Conduit | Primero | Primero |  | 0 | [11 empty] | 2
F28FN482LCS-C1 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28FN482-LCS | UFG MILL 2 GEARBOX OIL COOLER FAN 1 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 0.6/1 | 60 | 4C+E | Cu | PVC/PVC | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | Primero | Primero | LCS | 0 | [11 empty] | 2
F28FN483-P1 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-FN-483 | UFG MILL 2 GEARBOX OIL COOLER FAN 2 | UFG Ground Floor | 4 | 0.6/1 | 60 | 3C+E | Cu | PVC/PVC | Orange | Buried in Conduit | Primero | Primero |  | 0 | [11 empty] | 2
F28FN483LCS-C1 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28FN483-LCS | UFG MILL 2 GEARBOX OIL COOLER FAN 2 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 0.6/1 | 60 | 4C+E | Cu | PVC/PVC | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | Primero | Primero | LCS | 0 | [11 empty] | 2
F28HT481-P1 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-HT-481 | UFG MILL 2 BEARING OLS HEATERS | UFG Ground Floor | 4 | 0.6/1 | 60 | 2C+E | Cu | PVC/PVC | Orange | Buried in Conduit | Primero | Primero | TB2 | 0 | [11 empty] | 2
F28HT482-P1 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-HT-482 | UFG MILL 2 GEARBOX OLS HEATERS | UFG Ground Floor | 4 | 0.6/1 | 60 | 2C+E | Cu | PVC/PVC | Orange | Buried in Conduit | Primero | Primero | TB2 | 0 | [11 empty] | 2
F28HT483-P1 | F28-SW-013 | ULTRA FINE GRINDING 11KV SWITCHBOARD | Ultrafine Grinding Switchroom | F28-HT-483 | UFG MILL 2 MOTOR SPACE HEATERS | UFG Drive Platform | 4 | 0.6/1 | 60 | 2C+E | Cu | PVC/PVC | Orange | Buried in Conduit / Ladder - Single layer touching | Primero | Primero |  | 0 | [11 empty] | 2
F28PO465-P1 | F28-GPO-00X | ULTRA FINE GRINDING AREA 3 PHASE GPO ULTRA FINE GRINDING AREA 3 PHASE GPO | UFG Drive Platform | F28-PO-465 | UFG MILL 2 HYDRAULIC POWER PACK PUMP | UFG Drive Platform | N/A | 0.6/1 | 10 | 3C+E | Cu | N/A | Orange | Loose | Primero | Primero | Heavy Duty 3 Phase 32A extension cord | 0 | [11 empty] | 2
F28LR402-P1 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-LR-402 | UFG MILL 2 MOTOR LRS | UFG Ground Floor | 25 | 0.6/1 | 60 | 4C+E | Cu | XLPE/PVC | Orange | Buried in Conduit | Primero | Primero |  | 0 | [11 empty] | 2
F28LR402-D1 | F28-RIO-001 | ULTRA FINE GRINDING FIELD N-IO PANEL | UFG Drive Platform | F28-LR-402 | UFG MILL 2 MOTOR LRS | UFG Ground Floor | N/A | N/A | 30 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Buried in Conduit / Ladder - Comms | Primero | Primero |  | 0 | [11 empty] | 2
F28LR402-C1 | F28-SW-013 | ULTRA FINE GRINDING 11KV SWITCHBOARD | Ultrafine Grinding Switchroom | F28-LR-402 | UFG MILL 2 MOTOR LRS | UFG Ground Floor | 1.5 | 0.6/1 | 60 | 8C+E | Cu | PVC/PVC | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | Primero | Primero | Hardwired fault/start/ready to start | 0 | [11 empty] | 2
F28MUF402JB14-FO1 | F28-SW-013 | ULTRA FINE GRINDING 11KV SWITCHBOARD | Ultrafine Grinding Switchroom | F28MUF402-JB14 | ULTRA FINE GRINDING MILL 2 MOTOR RTD RELAY JUNCTION BOX | UFG Motor Platform | 62.5/200 µm | N/A | 60 | 2C | MMOF | Simplex ST/ST | Orange | Buried in Conduit / Ladder - Comms | Switchgear Vendor | Primero | Fibre to RTD Module Junction Box | 0 | [11 empty] | 2
F28MUF402JB14-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | Power to RTD Module Junction Box. | 0 | F28-RIO-001 | ULTRA FINE GRINDING FIELD N-IO PANEL | Ultrafine Grinding Switchroom | F28MUF402-JB14 | ULTRA FINE GRINDING MILL 2 MOTOR RTD RELAY JUNCTION BOX | UFG Motor Platform | 2.5 | 60 | 2C+E | Orange | Buried in Conduit / Ladder - Single layer touching | 3
F28PO461-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PO-461 | UFG MILL 2 BEARING OIL COOLER PUMP 1 | UFG Ground Floor | 4 | 60 | 3C+E | Orange | Buried in Conduit | 3
F28PO461LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PO461-LCS | UFG MILL 2 BEARING OIL COOLER PUMP 1 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 60 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28PO462-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PO-462 | UFG MILL 2 BEARING OIL COOLER PUMP 2 | UFG Ground Floor | 4 | 60 | 3C+E | Orange | Buried in Conduit | 3
F28PO462LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PO462-LCS | UFG MILL 2 BEARING OIL COOLER PUMP 2 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 60 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28PO463-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PO-463 | UFG MILL 2 GEARBOX OIL COOLER PUMP 1 | UFG Ground Floor | 6 | 60 | 3C+E | Orange | Buried in Conduit | 3
F28PO463LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PO463-LCS | UFG MILL 2 GEARBOX OIL COOLER PUMP 1 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 60 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28PO464-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PO-464 | UFG MILL 2 GEARBOX OIL COOLER PUMP 2 | UFG Ground Floor | 6 | 60 | 3C+E | Orange | Buried in Conduit | 3
F28PO464LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PO464-LCS | UFG MILL 2 GEARBOX OIL COOLER PUMP 2 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 60 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28PP409-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC/CTS/PVC Flexible |  |  | Primero | Primero |  | 0 | F28PP409-VS | UFG Product Pump 1 LV VSD | Ultrafine Grinding Switchroom | F28-PP-409 | UFG PRODUCT PUMP 1 | UFG Ground Floor | 120 | 60 | 3C+3E | Black | Buried in Conduit | 3
F28PP409-P2 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | Space Heater | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PP-409 | UFG PRODUCT PUMP 1 SPACE HEATER | UFG Ground Floor | 2.5 | 60 | 2C+E | Orange | Buried in Conduit | 3
F28PP409-I1 | [7 empty] | 0.11 |  |  | Cu | PVC/OSCN/PVC |  |  | Primero | Primero | Thermistor | 0 | F28PP409-VS | UFG Product Pump 1 LV VSD | Ultrafine Grinding Switchroom | F28-PP-409 | UFG PRODUCT PUMP 1 THERMISTOR | UFG Ground Floor | 1.5 | 60 | 1PR | Black | Buried in Conduit | 3
F28PP409LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PP409-LCS | UFG PRODUCT PUMP 1 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 60 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28PP410-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC/CTS/PVC Flexible |  |  | Primero | Primero |  | 0 | F28PP410-VS | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PP-410 | UFG PRODUCT PUMP 2 | UFG Ground Floor | 120 | 60 | 3C+3E | Black | Buried in Conduit | 3
F28PP410-P2 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | Space Heater | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PP-410 | UFG PRODUCT PUMP 2 SPACE HEATER | UFG Ground Floor | 2.5 | 60 | 2C+E | Orange | Buried in Conduit | 3
F28PP410-I1 | [7 empty] | 0.11 |  |  | Cu | PVC/OSCN/PVC |  |  | Primero | Primero | Thermistor | 0 | F28PP410-VS | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PP-410 | UFG PRODUCT PUMP 2 THERMISTOR | UFG Ground Floor | 1.5 | 60 | 1PR | Black | Buried in Conduit | 3
F28PP410LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PP410-LCS | UFG PRODUCT PUMP 2 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 60 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28PP451-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC/CTS/PVC Flexible |  |  | Primero | Primero |  | 0 | F28PP451-VS | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PP-451 | UFG MILL 2 FEED PUMP | UFG Ground Floor | 35 | 80 | 3C+3E | Black | Buried in Conduit | 3
F28PP451-I1 | [7 empty] | 0.11 |  |  | Cu | PVC/OSCN/PVC |  |  | Primero | Primero | Thermistor | 0 | F28PP451-VS | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PP-451 | UFG MILL 2 FEED PUMP THERMISTOR | UFG Ground Floor | 1.5 | 80 | 1PR | Black | Buried in Conduit | 3
F28PP451LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PP451-LCS | UFG MILL 2 FEED PUMP LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 80 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28PP453-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC/CTS/PVC Flexible |  |  | Primero | Primero |  | 0 | F28PP453-VS | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PP-453 | UFG MILL 2 DISCHARGE PUMP | UFG Ground Floor | 150 | 80 | 3C+3E | Black | Buried in Conduit | 3
F28PP453-P2 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | Space Heater | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PP-453 | UFG MILL 2 DISCHARGE PUMP SPACE HEATER | UFG Ground Floor | 2.5 | 80 | 2C+E | Orange | Buried in Conduit | 3
F28PP453-I1 | [7 empty] | 0.11 |  |  | Cu | PVC/OSCN/PVC |  |  | Primero | Primero | Thermistor | 0 | F28PP453-VS | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PP-453 | UFG MILL 2 DISCHARGE PUMP THERMISTOR | UFG Ground Floor | 1.5 | 80 | 1PR | Black | Buried in Conduit | 3
F28PP453LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PP453-LCS | UFG MILL 2 DISCHARGE PUMP LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 80 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28PP494-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC/CTS/PVC Flexible |  |  | Primero | Primero |  | 0 | F28PP494-VS | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PP-494 | UFG MILL 2 PRODUCT SAMPLE PUMP | UFG Ground Floor | 4 | 60 | 3C+3E | Black | Buried in Conduit | 3
F28PP494LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PP494-LCS | UFG MILL 2 PRODUCT SAMPLE PUMP LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 60 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28PS421LCS-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PS421-LCS | UFG MILL AREA SUMP PUMP 1 LOCAL CONTROL STATION | UFG Ground Floor | 25 | 70 | 3C+E | Orange | Buried in Conduit | 3
F28PS421-P1 | [7 empty] | 0.6/1 |  |  | Cu | EPR/CSP |  |  | Primero | Primero | Flexible for decontactor to motor | 0 | F28PS421-LCS | UFG MILL AREA SUMP PUMP 1 LOCAL CONTROL STATION | UFG Ground Floor | F28-PS-421 | UFG MILL AREA SUMP PUMP 1 | UFG Ground Floor | 25 | 10 | 3C+E | Black | Ladder - Single Layer Touching | 3
F28PS421LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultrafine Grinding Switchroom | F28PS421-LCS | UFG Mill Area Sump Pump 1 Local Control Station | UFG Ground Floor | 1.5 | 70 | 6C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28PS422LCS-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PS422-LCS | UFG MILL AREA SUMP PUMP 2 LOCAL CONTROL STATION | UFG Ground Floor | 25 | 70 | 3C+E | Orange | Buried in Conduit | 3
F28PS422-P1 | [7 empty] | 0.6/1 |  |  | Cu | EPR/CSP |  |  | Primero | Primero | Flexible for decontactor to motor | 0 | F28PS422-LCS | UFG MILL AREA SUMP PUMP 2 LOCAL CONTROL STATION | UFG Ground Floor | F28-PS-422 | UFG MILL AREA SUMP PUMP 2 | UFG Ground Floor | 25 | 10 | 3C+E | Black | Ladder - Single Layer Touching | 3
F28PS422LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultrafine Grinding Switchroom | F28PS422-LCS | UFG MILL AREA SUMP PUMP 2 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 70 | 6C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28PW411-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PW-411 | UFG GSW PUMP 1 | UFG Ground Floor | 10 | 90 | 3C+E | Orange | Buried in Conduit / Ladder - Single layer touching | 3
F28PW411LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PW411-LCS | UFG GSW PUMP 1 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 90 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28PW412-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PW-412 | UFG GSW PUMP 2 | UFG Ground Floor | 10 | 90 | 3C+E | Orange | Buried in Conduit / Ladder - Single layer touching | 3
F28PW412LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PW412-LCS | UFG GSW PUMP 2 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 90 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28PW421-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28-PW-421 | UFG MILL 2 ISACHARGER PUMP | UFG Ground Floor | 25 | 70 | 3C+E | Orange | Buried in Conduit | 3
F28PW421LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding Switchroom | F28PW421-LCS | UFG MILL 2 ISACHARGER PUMP LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 70 | 4C+E | Black | Buried in Conduit | 3
F28MUF402JB01-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | Intertrip relay board Power | 0 | F28-DB-301 | ULTRA FINE GRINDING AREA L&SP DISTRIBUTION BOARD | UFG Drive Platform | F28MUF402-JB01 | ULTRA FINE GRINDING MILL 2 HEADFRAME JUNCTION BOX | UFG Drive Platform | 4 | 45 | 2C+E | Orange | Ladder - Single Layer Touching | 3
F28MUF402LCS01-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | E-stop circuit | 0 | F28-SW-013 | ULTRA FINE GRINDING 11KV SWITCHBOARD | Ultrafine Grinding Switchroom | F28MUF402-LCS01 | UFG MILL 2 LOCAL CONTROL STATION | UFG Drive Platform | 1.5 | 60 | 4C+E | Black | Ladder - Bunched Ctrl/Inst | 3
F28MUF402LCS02-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | E-stop circuit | 0 | F28MUF402-LCS01 | UFG MILL 2 LOCAL CONTROL STATION | UFG Drive Platform | F28MUF402-LCS02 | UFG MILL 2 LOCAL CONTROL STATION | UFG Drive Platform | 1.5 | 45 | 4C+E | Black | Ladder - Bunched Ctrl/Inst | 3
F28MUF402LCS03-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | E-stop circuit | 0 | F28MUF402-LCS02 | UFG MILL 2 LOCAL CONTROL STATION | UFG Drive Platform | F28MUF402-LCS03 | UFG MILL 2 LOCAL CONTROL STATION | UFG Drive Platform | 1.5 | 45 | 4C+E | Black | Ladder - Bunched Ctrl/Inst | 3
F28MUF402LCS04-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | E-stop circuit | 0 | F28MUF402-LCS03 | UFG MILL 2 LOCAL CONTROL STATION | UFG Drive Platform | F28MUF402-LCS04 | UFG MILL 2 LOCAL CONTROL STATION | UFG Drive Platform | 1.5 | 45 | 4C+E | Black | Ladder - Bunched Ctrl/Inst | 3
F28CAM001-D1 | [7 empty] | N/A |  |  | Cu | CAT6 SF/UTP Outdoor Cable |  |  | Primero | Primero | CCTV | 0 | F28-RIO-001 | ULTRA FINE GRINDING FIELD N-IO PANEL | Ultra Fine Grinding Platform | F28-CAM-001 | ULTRA FINE GRINDING MILLS CCTV CAMERA | Ultra Fine Grinding Platform | N/A | 40 | 4PR | Black | Ladder - Bunched Ctrl/Inst | 3
F28FN484-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-FN-484 | UFG MILL 3 BEARING OIL COOLER FAN 1 | UFG Ground Floor | 4 | 50 | 3C+E | Orange | Buried in Conduit | 3
F28FN484LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28FN484-LCS | UFG MILL 3 BEARING OIL COOLER FAN 1 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 50 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 3
F28FN485-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-FN-485 | UFG MILL 3 GEARBOX OIL COOLER FAN 1 | UFG Ground Floor | 4 | 50 | 3C+E | Orange | Buried in Conduit | 4
F28FN485LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28FN485-LCS | UFG MILL 3 GEARBOX OIL COOLER FAN 1 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 50 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 4
F28FN486-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-FN-486 | UFG MILL 3 GEARBOX OIL COOLER FAN 2 | UFG Ground Floor | 4 | 50 | 3C+E | Orange | Buried in Conduit | 4
F28FN486LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28FN486-LCS | UFG MILL 3 GEARBOX OIL COOLER FAN 2 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 50 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 4
F28HT484-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | TB2 | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-HT-484 | UFG MILL 3 BEARING OLS HEATER | UFG Ground Floor | 4 | 50 | 2C+E | Orange | Buried in Conduit | 4
F28HT485-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | TB2 | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-HT-485 | UFG MILL 3 GEARBOX OLS HEATER | UFG Ground Floor | 4 | 50 | 2C+E | Orange | Buried in Conduit | 4
F28HT486-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-013 | ULTRA FINE GRINDING 11KV SWITCHBOARD | Ultrafine Grinding 415V Switchroom | F28-HT-486 | UFG MILL 3 MOTOR SPACE HEATERS | UFG Drive Platform | 4 | 50 | 2C+E | Orange | Buried in Conduit / Ladder - Single layer touching | 4
F28PO565-P1 | [7 empty] | 0.6/1 |  |  | Cu | N/A |  |  | Primero | Primero | Heavy Duty 3 Phase 32A extension cord | 0 | F28-GPO-00X | ULTRA FINE GRINDING AREA 3 PHASE GPO | Ultrafine Grinding 415V Switchroom | F28-PO-565 | UFG MILL 3 HYDRAULIC POWER PACK PUMP | UFG Ground Floor | N/A | 10 | 3C+E | Orange | Loose | 4
F28LR403-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-LR-403 | UFG MILL 3 MOTOR LRS | UFG Ground Floor | 25 | 50 | 4C+E | Orange | Buried in Conduit | 4
F28LR403-D1 | [7 empty] | N/A |  |  | Cu | CAT6 SF/UTP Outdoor Cable |  |  | Primero | Primero |  | 0 | F28-RIO-001 | ULTRA FINE GRINDING FIELD N-IO PANEL | Ultrafine Grinding 415V Switchroom | F28-LR-403 | UFG MILL 3 MOTOR LRS | UFG Ground Floor | N/A | 50 | 4PR | Black | Buried in Conduit / Ladder - Comms | 4
F28LR403-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | Hardwired fault/start/ready to start | 0 | F28-SW-013 | ULTRA FINE GRINDING 11KV SWITCHBOARD | Ultrafine Grinding 415V Switchroom | F28-LR-403 | UFG MILL 3 MOTOR LRS | UFG Ground Floor | 1.5 | 50 | 8C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 4
F28MUF403JB14-FO1 | [7 empty] | N/A |  |  | MMOF | Simplex ST/ST |  |  | Switchgear Vendor | Primero | Fibre to RTD Module Junction Box | 0 | F28-SW-013 | ULTRA FINE GRINDING 11KV SWITCHBOARD | Ultrafine Grinding 415V Switchroom | F28MUF403-JB14 | ULTRA FINE GRINDING MILL 3 MOTOR RTD RELAY JUNCTION BOX | UFG Motor Platform | 62.5/200 µm | 70 | 2C | Orange | Buried in Conduit / Ladder - Comms | 4
F28MUF403JB14-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | Power to RTD Module Junction Box. | 0 | F28-RIO-003 | ULTRA FINE GRINDING FIELD N-IO PANEL | Ultrafine Grinding 415V Switchroom | F28MUF403-JB14 | ULTRA FINE GRINDING MILL 3 MOTOR RTD RELAY JUNCTION BOX | UFG Motor Platform | 2.5 | 70 | 3C+E | Orange | Buried in Conduit / Ladder - Single layer touching | 4
F28PO561-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-PO-561 | UFG MILL 3 BEARING OIL COOLER PUMP 1 | UFG Ground Floor | 4 | 50 | 3C+E | Orange | Buried in Conduit | 4
F28PO561LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28PO561-LCS | UFG MILL 3 BEARING OIL COOLER PUMP 1 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 50 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 4
F28PO562-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-PO-562 | UFG MILL 3 BEARING OIL COOLER PUMP 2 | UFG Ground Floor | 4 | 50 | 3C+E | Orange | Buried in Conduit | 4
F28PO562LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28PO562-LCS | UFG MILL 3 BEARING OIL COOLER PUMP 2 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 50 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 4
F28PO563-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-PO-563 | UFG MILL 3 GEARBOX OIL COOLER PUMP 1 | UFG Ground Floor | 6 | 50 | 3C+E | Orange | Buried in Conduit | 4
F28PO563LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28PO563-LCS | UFG MILL 3 GEARBOX OIL COOLER PUMP 1 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 50 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 4
F28PO564-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-PO-564 | UFG MILL 3 GEARBOX OIL COOLER PUMP 2 | UFG Ground Floor | 6 | 50 | 3C+E | Orange | Buried in Conduit | 4
F28PO564LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28PO564-LCS | UFG MILL 3 GEARBOX OIL COOLER PUMP 2 LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 50 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 4
F28PP461-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC/CTS/PVC Flexible |  |  | Primero | Primero |  | 0 | F28PP461-VS | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-PP-461 | UFG MILL 3 FEED PUMP | UFG Ground Floor | 35 | 50 | 3C+3E | Black | Buried in Conduit | 4
F28PP461-I1 | [7 empty] | 0.11 |  |  | Cu | PVC/OSCN/PVC |  |  | Primero | Primero | Thermistor | 0 | F28PP461-VS | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-PP-461 | UFG MILL 3 FEED PUMP THERMISTOR | UFG Ground Floor | 1.5 | 50 | 1PR | Black | Buried in Conduit | 4
F28PP461LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28PP461-LCS | UFG MILL 3 FEED PUMP LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 50 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 4
F28PP463-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC/CTS/PVC Flexible |  |  | Primero | Primero |  | 0 | F28PP463-VS | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-PP-463 | UFG MILL 3 DISCHARGE PUMP | UFG Ground Floor | 150 | 70 | 3C+3E | Black | Buried in Conduit | 4
F28PP463-P2 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | Space Heater | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-PP-463 | UFG MILL 3 DISCHARGE PUMP SPACE HEATER | UFG Ground Floor | 2.5 | 70 | 2C+E | Orange | Buried in Conduit | 4
F28PP463-I1 | [7 empty] | 0.11 |  |  | Cu | PVC/OSCN/PVC |  |  | Primero | Primero | Thermistor | 0 | F28PP463-VS | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-PP-463 | UFG MILL 3 DISCHARGE PUMP THERMISTOR | UFG Ground Floor | 1.5 | 70 | 1PR | Black | Buried in Conduit | 4
F28PP463LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28PP463-LCS | UFG MILL 3 DISCHARGE PUMP LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 70 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 4
F28PP495-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC/CTS/PVC Flexible |  |  | Primero | Primero |  | 0 | F28PP495-VS | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-PP-495 | UFG MILL 3 PRODUCT SAMPLE PUMP | UFG Ground Floor | 4 | 50 | 3C+3E | Black | Buried in Conduit | 4
F28PP495LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28PP495-LCS | UFG MILL 3 PRODUCT SAMPLE PUMP LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 50 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 4
F28PW431-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28-PW-431 | UFG MILL 3 ISACHARGER PUMP | UFG Ground Floor | 25 | 70 | 3C+E | Orange | Buried in Conduit | 4
F28PW431LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultrafine Grinding 415V Switchroom | F28PW431-LCS | UFG MILL 3 ISACHARGER PUMP LOCAL CONTROL STATION | UFG Ground Floor | 1.5 | 70 | 4C+E | Black | Buried in Conduit / Ladder - Bunched Ctrl/Inst | 4
F28MUF403LCS01-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | E-stop circuit | 0 | F28-SW-013 | ULTRA FINE GRINDING 11KV SWITCHBOARD | Ultrafine Grinding 415V Switchroom | F28MUF403-LCS01 | UFG MILL 3 LOCAL CONTROL STATION | UFG Drive Platform | 1.5 | 45 | 4C+E | Black | Ladder - Bunched Ctrl/Inst | 4
F28MUF403LCS02-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | E-stop circuit | 0 | F28MUF403-LCS01 | UFG MILL 3 LOCAL CONTROL STATION | UFG Drive Platform | F28MUF403-LCS02 | UFG MILL 3 LOCAL CONTROL STATION | UFG Drive Platform | 1.5 | 45 | 4C+E | Black | Ladder - Bunched Ctrl/Inst | 4
F28MUF403LCS03-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | E-stop circuit | 0 | F28MUF403-LCS02 | UFG MILL 3 LOCAL CONTROL STATION | UFG Drive Platform | F28MUF403-LCS03 | UFG MILL 3 LOCAL CONTROL STATION | UFG Drive Platform | 1.5 | 45 | 4C+E | Black | Ladder - Bunched Ctrl/Inst | 4
F28MUF403LCS04-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | E-stop circuit | 0 | F28MUF403-LCS03 | UFG MILL 3 LOCAL CONTROL STATION | UFG Drive Platform | F28MUF403-LCS04 | UFG MILL 3 LOCAL CONTROL STATION | UFG Drive Platform | 1.5 | 45 | 4C+E | Black | Ladder - Bunched Ctrl/Inst | 4
F72DB302-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC Flexible |  |  | Primero | Primero |  | 0 | F28-SW-109 | ULTRA FINE GRINDING ESSENTIAL 415V SWITCHBOARD | UtraFine Grinding 415V Switchroom | F72-DB-302 | REAGENTS MIXING AND STORAGE AREA L&SP DISTRIBUTION BOARD | Reagents Stage 2 Area Piperack | 120 | 300 | 4C+E | Orange | Ladder - Single Layer Touching | 4
F72DB302-P2 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC Flexible |  |  | Primero | Primero |  | 0 | F28-SW-109 | ULTRA FINE GRINDING ESSENTIAL 415V SWITCHBOARD | UtraFine Grinding 415V Switchroom | F72-DB-302 | REAGENTS MIXING AND STORAGE AREA L&SP DISTRIBUTION BOARD | Reagents Stage 2 Area Piperack | 120 | 300 | 4C+E | Orange | Ladder - Single Layer Touching | 4
F72PE302-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | PE Circuit for L&SP DB | 0 | F72-DB-302 | REAGENTS MIXING AND STORAGE AREA L&SP DISTRIBUTION BOARD | Reagents Stage 2 Area Piperack | F72-PE-302 | REAGENTS MIXING AND STORAGE AREA PHOTO-ELECTRIC CELL | Reagents Stage 2 Area Piperack | 2.5 | 10 | 3C+E | Orange | Ladder - Single Layer Touching | 4
F72DB303-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 | F72-DB-302 | REAGENTS MIXING AND STORAGE AREA L&SP DISTRIBUTION BOARD | Reagents Stage 2 Area Piperack | F72-DB-303 | HYDROGEN PEROXIDE AREA L&SP DISTRIBUTION BOARD | Hydrogen Peroxide Area | 25 | 40 | 4C+E | Orange | Buried in Conduit | 4
F72PE303-P1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | PE Circuit for L&SP DB | 0 | F72-DB-302 | REAGENTS MIXING AND STORAGE AREA L&SP DISTRIBUTION BOARD | Reagents Stage 2 Area Piperack | F72-PE-303 | HYDROGEN PEROXIDE AREA PHOTO-ELECTRIC CELL | Reagents Stage 2 Area Piperack | 2.5 | 10 | 3C+E | Orange | Ladder - Single Layer Touching | 4
F72RIO002-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC |  |  | Primero | Primero |  | 0 | F28-DB-201 | ULTRA FINE GRINDING 415V SWITCHROOM 240V UPS DISTRIBUTION BOARD | UtraFine Grinding 415V Switchroom | F72-RIO-002 | REAGENTS FIELD N-IO PANEL | Reagents Stage 2 Area Piperack | 35 | 300 | 2C+E | Orange | Ladder - Single Layer Touching | 4
F72PP521-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC/CTS/PVC Flexible |  |  | Primero | Primero |  | 0 | F72PP521-VS | HYDROGEN PEROXIDE DOSING PUMP 1 LV VSD | UtraFine Grinding 415V Switchroom | F72-PP-521 | HYDROGEN PEROXIDE DOSING PUMP 1 | Hydrogen Peroxide Area | 4 | 335 | 3C+3E | Black | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | 4
F72PP521LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | UtraFine Grinding 415V Switchroom | F72PP521-LCS | HYDROGEN PEROXIDE DOSING PUMP 1 LOCAL CONTROL STATION | Hydrogen Peroxide Area | 1.5 | 335 | 4C+E | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | 4
F72PP522-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC/CTS/PVC Flexible |  |  | Primero | Primero |  | 0 | F72PP522-VS | HYDROGEN PEROXIDE DOSING PUMP 2 LV VSD | UtraFine Grinding 415V Switchroom | F72-PP-522 | HYDROGEN PEROXIDE DOSING PUMP 2 | Hydrogen Peroxide Area | 4 | 335 | 3C+3E | Black | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | 4
F72PP522LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | UtraFine Grinding 415V Switchroom | F72PP522-LCS | HYDROGEN PEROXIDE DOSING PUMP 2 LOCAL CONTROL STATION | Hydrogen Peroxide Area | 1.5 | 335 | 4C+E | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | 4
F72PP523-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC/CTS/PVC Flexible |  |  | Primero | Primero |  | 0 | F72PP523-VS | HYDROGEN PEROXIDE DOSING PUMP 3 LV VSD | UtraFine Grinding 415V Switchroom | F72-PP-523 | HYDROGEN PEROXIDE DOSING PUMP 3 | Hydrogen Peroxide Area | 4 | 335 | 3C+3E | Black | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | 4
F72PP523LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | UtraFine Grinding 415V Switchroom | F72PP523-LCS | HYDROGEN PEROXIDE DOSING PUMP 3 LOCAL CONTROL STATION | Hydrogen Peroxide Area | 1.5 | 335 | 4C+E | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | 5
F72PP524-P1 | [7 empty] | 0.6/1 |  |  | Cu | XLPE/PVC/CTS/PVC Flexible |  |  | Primero | Primero |  | 0 | F72PP524-VS | HYDROGEN PEROXIDE DOSING PUMP 4 LV VSD | UtraFine Grinding 415V Switchroom | F72-PP-524 | HYDROGEN PEROXIDE DOSING PUMP 4 | Hydrogen Peroxide Area | 4 | 335 | 3C+3E | Black | Ladder - Bunched in Groups up to 9 (2 Layers) / Buried in Conduit | 5
F72PP524LCS-C1 | [7 empty] | 0.6/1 |  |  | Cu | PVC/PVC |  |  | Primero | Primero | LCS | 0 | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | UtraFine Grinding 415V Switchroom | F72PP524-LCS | HYDROGEN PEROXIDE DOSING PUMP 4 LOCAL CONTROL STATION | Hydrogen Peroxide Area | 1.5 | 335 | 4C+E | Black | Ladder - Bunched Ctrl/Inst / Buried in Conduit | 5