## Equipment list
Rev | Equip. Number | Equipment Name | Qty | Description | Make | Model | Supplied By | Installed By | Comments | Page
0 | F28-SR-002 | Ultra Fine Grinding 415V Switchroom | 1 | Transportable switchroom complete with 1.8m legs and landings, transported to site 600kms on sealed roads. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero | F28-SR-001, F28-SR-002, Transformer room(s) and Air Lock are all part of the same building Refer 2000-F00-DSH-EL-11001 | 2
0 | - | Ultra Fine Grinding 415V Switchroom Landings and stairs | 1 | Equipment Landing to be structural steel baseframe complete with 1.8m legs and landings, designed to support heaviest piece of equipment to be installed in room. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero |  | 2
0 | - | Ultra Fine Grinding 415V Switchroom Transformer cubicle | 1 | Separate dry transformer enclosure with removable wall panel and personnel access door. Fortress key locked (Keyed alike) with 33kV feeder earth switch on F00-SW-010 33kV switchgear. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Access to transformer cubicle is only possible with 33kV Feeder isolated and earthed. Switchroom manufacturer to coordinate Fortress keys with TEKSAL. | 2
0 | - | Ultra Fine Grinding 415V Switchroom Transformer cubicle Signage | 1 | TRANSFORMER ENCLOSURE F28-TR-009 33,000/433 VOLTS (Modify to suit) DANGER – HIGH VOLTAGE (with the lightning bolt sign) NO UNAUTHORISED ACCESS – ENSURE SUPPLY IS ISOLATED AND EARTHED PRIOR TO ENTRY ISOLATE AT F00-SW-010, PANEL BXX (BXX being the 33kV panel/tier number) | Switchroom Vendor |  | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Signage to be placed on outside of transformer enclosure | 2
0 | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | 1 | 33/0.433kV, 1000kVA, ANAF | Siemens | 33/0.433kV 1000kVA | Primero | Switchroom/MCC Vendor | Vendor to remove wheels and secure transformer once installed. Wheels to be stored securely within the transformer room. Vendor to bolt down/brace for transport. Refer transformer GAs. | 2
0 | F28-SW-009 | Ultra Fine Grinding 415V MCC | 1 | Demountable Form 4a double sided 415V Switchboard, 1600A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Vendor to install free issued network switches in MCC Refer datasheet 2000-F00-DSH-EL-11008 | 2
0 | F28-SW-109 | Ultra Fine Grinding Essential 415V Switchboard | 1 | Demountable Form 4a single sided 415V Essential Switchboard, 400A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Refer datasheet 2000-F00-DSH-EL-11012 | 2
0 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | 1 | 415V 3Ø 250A DB. Fitted with incoming isolator, PE Cell circuit (night/day), Auto / Manual selector, Emergency light test controller, Rapidtest RCD test units, Lighting Contactors, air conditioner Contactors and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-EL-10025 & 2000-F00-STD-EL-10022; Switchroom Vendor to calculate number of required poles including the number of circuits for Air conditioners, 20% loaded Spare circuit breakers and 20% spare space. | 2
0 | F28-DB-201 | Ultra Fine Grinding 415V Switchroom 240V UPS Distribution Board | 1 | 240VAC 250A UPS DB. Fitted with incoming isolator and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-EL-10027. Switchroom Vendor to calculate number of required poles including 20% loaded Spare circuit breakers and 20% spare space. | 2
0 | F28-UPS-002 | Ultra Fine Grinding 415V Switchroom 240VAC UPS | 1 | LV Switchroom 240V AC, 10kVA UPS, free-standing. 8 hours autonomy time. 3-Phase in / 1-Phase Out. | Riello | S3M 10 XTD T5 LL | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 10kVA/10kW Sentryum Xtend UPS - 3 Phase in- 1 out. With 9Ah Long Life Batteries. Vendor to secure wheels once installed. Vendor to bolt down/brace for transport. W: 440mm, D: 840mm, H: 1320mm, Weight: 415Kg | 2
0 | F28-BA-002 | Ultra Fine Grinding 415V Switchroom 240VAC UPS Battery Bank | 1 | UPS Battery Cabinet w/ 120 x 9Ah batteries. | Riello | BB 1320 480-T5 LL | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 480V Extension Battery Cabinet with 120 x 9Ah Long life batteries W: 400mm, D: 815mm, H: 1320mm, Weight: 402Kg | 2
0 | - | Ultra Fine Grinding 415V Switchroom 240VAC UPS Ethernet Card | 1 | Netman UPS Ethernet Card | Riello | Netman 208 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Supplied and installed into UPS by Switchroom Vendor | 2
0 | - | Ultra Fine Grinding 415V Switchroom 240VAC UPS Dry Contact Relay Card | 1 | Multicom Configurable Slot In Relay Card, 3 Inputs & 8 Outputs | Riello | Mulitcom 392 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Supplied and installed into UPS by Switchroom Vendor | 2
0 | F28UPS002-ISL | Ultra Fine Grinding 415V Switchroom 240VAC UPS Maintenance Bypass Switch | 1 | External Wall-mount UPS bypass switch. | Riello | WABS 0063A-31H | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Wall mounted rotary style bypass switch. 3Ph in/1Ph out, 10kVA. Dimensions: 400 x 300 x 210mm | 2
0 | F28PP409-VS | UFG PRODUCT PUMP 1 LV VSD | 1 | Allen-Bradley 90 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750- APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC205JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F28PP410-VS | UFG PRODUCT PUMP 2 LV VSD | 1 | Allen-Bradley 90 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750- APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC205JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F28PP451-VS | UFG MILL 2 FEED PUMP LV VSD | 1 | Allen-Bradley 45 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F5, 20-HIM-A6, 20-750- APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC104JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F28PP453-VS | UFG MILL 2 DISCHARGE PUMP LV VSD | 1 | Allen-Bradley 110 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F7, 20-HIM-A6, 20- 750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC302JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F28PP461-VS | UFG MILL 3 FEED PUMP LV VSD | 1 | Allen-Bradley 45 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F5, 20-HIM-A6, 20-750- APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC104JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F28PP463-VS | UFG MILL 3 DISCHARGE PUMP LV VSD | 1 | Allen-Bradley 110 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F7, 20-HIM-A6, 20- 750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC302JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F28PP494-VS | UFG MILL 2 PRODUCT SAMPLE PUMP LV VSD | 1 | Allen-Bradley 5.5 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM-A6, 20- 750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC015JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 2
0 | F28PP495-VS | UFG MILL 3 PRODUCT SAMPLE PUMP LV VSD | 1 | Allen-Bradley 5.5 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM-A6, 20- 750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC015JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F72PP521-VS | HYDROGEN PEROXIDE DOSING PUMP 1 LV VSD | 1 | Allen-Bradley 0.37 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM-A6, 20- 750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC8P7JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F72PP522-VS | HYDROGEN PEROXIDE DOSING PUMP 2 LV VSD | 1 | Allen-Bradley 0.37 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM-A6, 20- 750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC8P7JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F72PP523-VS | HYDROGEN PEROXIDE DOSING PUMP 3 LV VSD | 1 | Allen-Bradley 0.37 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM-A6, 20- 750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC8P7JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
2 | F72PP524-VS | HYDROGEN PEROXIDE DOSING PUMP 4 LV VSD | 1 | Allen-Bradley 0.37 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM-A6, 20- 750-APS, 20-750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC8P7JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | 3
0 | F72PP521-XE | HYDROGEN PEROXIDE DOSING PUMP 1 LV VSD Output Filter | 1 | Output dv/dt filter, 12A, Floor mounted | Allen-Bradley | TBC | Primero | Switchroom/MCC Vendor | Refer drawing 2000-EL006-B02-10001 | 3
0 | F72PP522-XE | HYDROGEN PEROXIDE DOSING PUMP 2 LV VSD Output Filter | 1 | Output dv/dt filter, 12A, Floor mounted | Allen-Bradley | TBC | Primero | Switchroom/MCC Vendor | Refer drawing 2000-EL006-B02-10001 | 3
0 | F72PP523-XE | HYDROGEN PEROXIDE DOSING PUMP 3 LV VSD Output Filter | 1 | Output dv/dt filter, 12A, Floor mounted | Allen-Bradley | TBC | Primero | Switchroom/MCC Vendor | Refer drawing 2000-EL006-B02-10001 | 3
2 | F72PP524-XE | HYDROGEN PEROXIDE DOSING PUMP 4 LV VSD Output Filter | 1 | Output dv/dt filter, 12A, Floor mounted | Allen-Bradley | TBC | Primero | Switchroom/MCC Vendor | Refer drawing 2000-EL006-B02-10001 | 3
0 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | 1 | Communications Rack, Free Standing 19", 42U, 1000mm deep, Mesh door, Lift Off Side Panels. Fitted with 10 way 240VAC plug power distribution panel, wire management covers, shelves and cage nuts. Fitted out with FOBOTs (vendor supplied), DIN rail adapter (vendor supplied), and network switches (free issued). | Rittal | TS IT Enclosure (P/N 5514.110) + Accessories | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-IC-10101 | 3
1 | F28COM001-JB | Ultra Fine Grinding 415V Switchroom Communications Rack 240VAC UPS Junction Box | 1 | Junction box mounted on the rear of the communications rack. All 240VAC UPS powered non-RCD Protected outlets shall be red with a "Warning. Socket not RCD Protected" Warning label. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Junction box for PDU Rail | 3
0 | F28-FOB-001 | Ultra Fine Grinding 415 Switchroom Fibre Optic Breakout Tray (SP 1) | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | 3
0 | F28-FOB-002 | Ultra Fine Grinding 415 Switchroom Fibre Optic Breakout Tray (SP 1) | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | 3
0 | F28-FOB-003 | Ultra Fine Grinding 415 Switchroom Fibre Optic Breakout Tray (SP 2) | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | 3
0 | F28-FOB-004A/B | Ultra Fine Grinding 415V Switchroom RIO Circuit Fibre Optic Breakout Ring 1 Tray #1 (SP 1) | 1 | 2 X 12C SMOF Capacity FOBOT C/W Splice hardware & 1-6 LC Duplex Faceplate (LHS) + 1-6 LC Duplex Faceplate (RHS) | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. One FOBOT with two 12C faceplates. Vendor to label each side as per equipment number and name. | 3
0 | F28-FOB-005A/B | Ultra Fine Grinding 415V Switchroom RIO Circuit Fibre Optic Breakout Ring 1 Tray #2 (SP 1) | 1 | 2 X 12C SMOF Capacity FOBOT C/W Splice hardware & 1-6 LC Duplex Faceplate (LHS) + 1-6 LC Duplex Faceplate (RHS) | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. One FOBOT with two 12C faceplates. Vendor to label each side as per equipment number and name. | 3
0 | F28-FOB-006A/B | Ultra Fine Grinding 415V Switchroom RIO Circuit Fibre Optic Breakout Ring 1 Tray #3 (SP 2) | 1 | 2 X 12C SMOF Capacity FOBOT C/W Splice hardware & 1-6 LC Duplex Faceplate (LHS) + 1-6 LC Duplex Faceplate (RHS) | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. One FOBOT with two 12C faceplates. Vendor to label each side as per equipment number and name. | 3
0 | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | 1 | Custom Built Panel. Contains DCS hardware, power supply, MCBs and marshalling terminals. | Fabricated Panel | Custom | Primero | Switchroom/MCC Vendor |  | 3
0 | F28SR001-LCS | Ultra Fine Grinding 11kV / 415V Switchroom Emergency Shutdown | 1 | Switchroom Emergency Shutdown C/w shroud or lift-up flap and labelling | Fabricated Panel | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | With E34 Red 40mm Mushroom pushbutton (P/N E34LB2), and 4 off 2 N/O Contact Blocks (10250T2). Refer 2000-F00-STS-EL-10011 Section 4.19. | 3
0 | F28-FIP-001 | Ultra Fine Grinding 11kV / 415V Switchroom Fire Indicator Panel | 1 | Fire Indicator Panel c/w full installation, wiring, certification, testing and commissioning. HVAC trip upon alarm. FIP shall include SMOF modem(s) for connection to site-wide fire system network. | Wormald | Vigilant 8 Zone F3200 Conventional SHCIE FIP | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Rated to operate in 50C ambience temperature | 3
0 | F28FIP001-XE1 | Ultra Fine Grinding 415V Switchroom VESDA Panel | 1 | VESDA Panel c/w full installation, wiring, certification, testing and commissioning.Alarm and fault signals to fire panel. | Xtralis | VESDA LaserPlus Scanner 12 relay VLS300 ASD system | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Rated to operate in 50C ambience temperature | 3
0 | F28FIP001-XE2 | Ultra Fine Grinding 415V Switchroom Manual Call Points | VTA | Fire system Manual Call points (internal and external) as required by Australian Standards | Wormald | Manual Call Points | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Manual call points shall be tagged in sequential order | 3
0 | F28FIP001-XE3 | Ultra Fine Grinding 415V Switchroom Smoke Detector | VTA | Fire system smoke detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order | 3
0 | F28FIP001-XE4 | Ultra Fine Grinding 415V Switchroom Heat Detector | VTA | Fire system heat detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order | 3
0 | F28FIP001-UA | Ultra Fine Grinding 415V Switchroom External Alarm Bells | VTA | Fire system alarm bells as required by Australian Standards | Wormald | External Sounder / Red Strobe | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Alarm sirens shall be tagged in sequential order | 3
0 | F28FIP001-XE5 | Ultra Fine Grinding 415V Switchroom Gas Suppression System (Inergen) | 1 | Inergen gas suppression system incl. all valves and pipework, gas cylinders placed inside switchroom, refer to Switchroom General Arrangement | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Ultra Fine Grinding 415V Switchroom Fire Extinguishers | VTA | 5kg dry powder fire extinguishers complete with wall mount and signage. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Ultra Fine Grinding 415V Switchroom Automatic External Defibrillator | 1 | Automatic external defibrillator complete with wall-mounted cabinet. | Physio Control | Lifepak Defibrillator CR2 Fully Automatic | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Ultra Fine Grinding 415V Switchroom 415V Rescue Kit | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Ultra Fine Grinding 415V Switchroom CPR Signage | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 3
0 | - | Ultra Fine Grinding 11kV / 415V Switchroom HVAC Controller | VTA | Wall mounted Air Conditioner Controller, with relay contacts for Faulty & Healthy | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | One wall mounted controller to control all A/C's per room (One per transformer room, LV room, HV room). | 4
0 | F28-AC-0XX | Ultra Fine Grinding 415V Switchroom Air Conditioners | VTA | High Wall split system, single phase, MULTIPLE (N+1 reqd) with drip trays if necessary | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. AC units shall be tagged in numercial order (e.g. F28-AC-001, F28-AC-002 etc. ) | 4
0 | F28AC0XX-ISL | Ultra Fine Grinding 415V Switchroom Air Conditioner Isolators | VTA | Field isolator, one per split system AC | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Isolators shall be tagged with the respective AC equipment number (e.g. F28AC0XX-ISL etc) | 4
0 | - | Ultra Fine Grinding 415V Switchroom Normal Light Fittings | 1 lot | Lighting to meet National Construction Code | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | 4
0 | - | Ultra Fine Grinding 415V Switchroom Emergency Light Fittings | 1 lot | Lighting to meet National Construction Code; C/w built in battery pack. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | 4
0 | UT28006 | F28-SR-002 Ultra Fine Grinding 415V Switchroom Temperature/Humidity Transmitter | 1 | 415V Switchroom Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | 4
0 | UT28007 | F28-SR-002 Ultra Fine Grinding 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | 1 | Transformer Room Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | 4
0 | F28-PE-001 | Ultra Fine Grinding 11kV / 415V Switchroom Photo-electric cell | 1 | Switchroom Photo-electric cell | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | PE Cell - 1 per building. Vendor to position | 4
0 | F28SW009-LCS | Ultra Fine Grinding 415V MCC Remote Switching Panel | 1 | LV MCC Incomer Remote Switching Panel | NHP | TemRack LCS | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | 1 | External to Room: 50 x 6.3mm Tinned Flat Copper Bus bar mounted on insulated standoffs under switchroom floor. Drilled/punch 12mm diameter holes suitable for connection of all internal equipment earth cables to meet requirements of cable schedule. To have spare capacity for connection of an additional 4 x 120mm2 conductors and 4 x 70mm2 conductors, as a minimum. | GVK or similar | - | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | F28TR009-EB01 | Ultra Fine Grinding 415V Switchroom Transformer Earth bar | 1 | 50 x 6.3mm Tinned Flat Copper Bus bar mounted on insulated standoffs on Transformer. | Generic |  | Transformer Vendor | Transformer Vendor |  | 4
0 | F28SW009-EB01 | Ultra Fine Grinding 415V MCC Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on insulated standoffs inside MCC | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4
0 | F28SW109-EB01 | Ultra Fine Grinding Essential 415V MCC Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on insulated standoffs inside MCC | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor |  | 4

## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred Colour) | Installation | Supplied By | Installed By | Revision | Comments | Page
F28SW009-P1-R | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28SW009-P1-W | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28SW009-P1-B | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28SW009-P2-R | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28SW009-P2-W | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28SW009-P2-B | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28SW009-P3-R | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28SW009-P3-W | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28SW009-P3-B | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28SW009-N-1 | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28SW009-N-2 | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28SW009-N-3 | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 240 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28SW109-P1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28-SW-109 | Ultra Fine Grinding Essential 415V Switchboard | Ultra Fine Grinding 415V Switchroom | 120 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 5
F28SW109-P2 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28-SW-109 | Ultra Fine Grinding Essential 415V Switchboard | Ultra Fine Grinding 415V Switchroom | 120 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 5
F28PP409VS-P1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP409-VS | UFG PRODUCT PUMP 1 LV VSD | Ultra Fine Grinding 415V Switchroom | 95 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28PP410VS-P1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP410-VS | UFG PRODUCT PUMP 2 LV VSD | Ultra Fine Grinding 415V Switchroom | 95 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28PP451VS-P1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP451-VS | UFG MILL 2 FEED PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 35 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28PP453VS-P1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP453-VS | UFG MILL 2 DISCHARGE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 120 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28PP461VS-P1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP461-VS | UFG MILL 3 FEED PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 35 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28PP463VS-P1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP463-VS | UFG MILL 3 DISCHARGE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 120 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28PP494VS-P1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP494-VS | UFG MILL 2 PRODUCT SAMPLE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F28PP495VS-P1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP495-VS | UFG MILL 3 PRODUCT SAMPLE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72PP521VS-P1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F72PP521-VS | HYDROGEN PEROXIDE DOSING PUMP 1 LV VSD | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72PP522VS-P1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F72PP522-VS | HYDROGEN PEROXIDE DOSING PUMP 2 LV VSD | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72PP523VS-P1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F72PP523-VS | HYDROGEN PEROXIDE DOSING PUMP 3 LV VSD | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72PP524VS-P1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F72PP524-VS | HYDROGEN PEROXIDE DOSING PUMP 4 LV VSD | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | 5
F72PP521XE-P1 | F72PP523-VS | HYDROGEN PEROXIDE DOSING PUMP 3 LV VSD | Ultra Fine Grinding 415V Switchroom | F72PP521-XE | HYDROGEN PEROXIDE DOSING PUMP 1 LV VSD Output Filter | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 3C+3E | Cu | PVC/PVC/CTS/PVC Flexible | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | VSD To Output filter | 5
F72PP522XE-P1 | F72PP523-VS | HYDROGEN PEROXIDE DOSING PUMP 3 LV VSD | Ultra Fine Grinding 415V Switchroom | F72PP522-XE | HYDROGEN PEROXIDE DOSING PUMP 2 LV VSD Output Filter | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 3C+3E | Cu | PVC/PVC/CTS/PVC Flexible | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | VSD To Output filter | 5
F72PP523XE-P1 | F72PP523-VS | HYDROGEN PEROXIDE DOSING PUMP 3 LV VSD | Ultra Fine Grinding 415V Switchroom | F72PP523-XE | HYDROGEN PEROXIDE DOSING PUMP 3 LV VSD Output Filter | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 3C+3E | Cu | PVC/PVC/CTS/PVC Flexible | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | VSD To Output filter | 5
F72PP524XE-P1 | F72PP524-VS | HYDROGEN PEROXIDE DOSING PUMP 4 LV VSD | Ultra Fine Grinding 415V Switchroom | F72PP524-XE | HYDROGEN PEROXIDE DOSING PUMP 4 LV VSD Output Filter | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 3C+3E | Cu | PVC/PVC/CTS/PVC Flexible | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | VSD To Output filter | 5
F28DB001-P1 | F28-SW-109 | Ultra Fine Grinding Essential 415V Switchboard | Ultra Fine Grinding 415V Switchroom | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | 150 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Flexible cable. Previously 95 | 5
F28UPS002ISL-P1 | F28-SW-109 | Ultra Fine Grinding Essential 415V Switchboard | Ultra Fine Grinding 415V Switchroom | F28UPS002-ISL | Ultra Fine Grinding 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | MCC to Bypass Switch. | 5
F28UPS002-P1 | F28UPS002-ISL | Ultra Fine Grinding 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Ultra Fine Grinding 415V Switchroom | F28-UPS-002 | Ultra Fine Grinding 415V Switchroom 240VAC UPS | Ultra Fine Grinding 415V Switchroom | 10 | 0.6/1 | 4C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | Bypass Switch to UPS. | 5
F28UPS002ISL-P2 | F28-UPS-002 | Ultra Fine Grinding 415V Switchroom 240VAC UPS | Ultra Fine Grinding 415V Switchroom | F28UPS002-ISL | Ultra Fine Grinding 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Ultra Fine Grinding 415V Switchroom | 10 | 0.6/1 | 2C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | UPS to Bypass Switch | 5
F28BA002-P1 | F28-UPS-002 | Ultra Fine Grinding 415V Switchroom 240VAC UPS | Ultra Fine Grinding 415V Switchroom | F28-BA-002 | Ultra Fine Grinding 415V Switchroom 240VAC UPS Battery Bank | Ultra Fine Grinding 415V Switchroom | 6 | 0.6/1 | 3C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F28DB201-P1 | F28UPS002-ISL | Ultra Fine Grinding 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Ultra Fine Grinding 415V Switchroom | F28-DB-201 | Ultra Fine Grinding 415V Switchroom 240V UPS Distribution Board | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Bypass Switch to UPS DB | 5
F28DCS410-P1 | F28-DB-201 | Ultra Fine Grinding 415V Switchroom 240V UPS Distribution Board | Ultra Fine Grinding 415V Switchroom | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F28COM001-P1 | F28-DB-201 | Ultra Fine Grinding 415V Switchroom 240V UPS Distribution Board | Ultra Fine Grinding 415V Switchroom | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | PDU | 5
F28SW009-P4 | F28-DB-201 | Ultra Fine Grinding 415V Switchroom 240V UPS Distribution Board | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | MCC PSU 1 | 6
F28SW009-P5 | F28-DB-201 | Ultra Fine Grinding 415V Switchroom 240V UPS Distribution Board | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | MCC PSU 2 | 6
F28SW109-P3 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28-SW-109 | Ultra Fine Grinding Essential 415V Switchboard | Ultra Fine Grinding 415V Switchroom | 10 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 24VDC Supply to Essential Board | 6
F28TR009-P2 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | 240V for transformer cooling fans | 6
F28FIP001-P1 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | F28-FIP-001 | Ultra Fine Grinding 11kV / 415V Switchroom Fire Indicator Panel | Ultra Fine Grinding 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28FIP001XE1-P1 | F28-FIP-001 | Ultra Fine Grinding 11kV / 415V Switchroom Fire Indicator Panel | Ultra Fine Grinding 415V Switchroom | F28FIP001-XE1 | Ultra Fine Grinding 415V Switchroom VESDA Panel | Ultra Fine Grinding 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-B10 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom |  | Lighting - Switchroom External Lighting Junction Box (for site use) | Ultra Fine Grinding 415V Switchroom | 4 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-R13 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | F28AC001-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 1 Isolator | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28AC001-P1 | F28AC001-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 1 Isolator | Ultra Fine Grinding 415V Switchroom | F28-AC-001 | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 1 | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-W13 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | F28AC002-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 2 Isolator | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28AC002-P1 | F28AC002-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 2 Isolator | Ultra Fine Grinding 415V Switchroom | F28-AC-002 | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 2 | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-B13 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | F28AC003-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 3 Isolator | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28AC003-P1 | F28AC003-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 3 Isolator | Ultra Fine Grinding 415V Switchroom | F28-AC-003 | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 3 | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-R15 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | F28AC004-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 4 Isolator | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28AC004-P1 | F28AC004-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 4 Isolator | Ultra Fine Grinding 415V Switchroom | F28-AC-004 | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 4 | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-R14 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | F28AC005-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 5 Isolator | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28AC005-P1 | F28AC005-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 5 Isolator | Ultra Fine Grinding 415V Switchroom | F28-AC-005 | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 5 | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-W14 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | F28AC006-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 6 Isolator | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28AC006-P1 | F28AC006-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 6 Isolator | Ultra Fine Grinding 415V Switchroom | F28-AC-006 | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 6 | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-B14 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | F28AC007-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 7 Isolator | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28AC007-P1 | F28AC007-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 7 Isolator | Ultra Fine Grinding 415V Switchroom | F28-AC-007 | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 7 | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-R16 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | F28AC008-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 8 Isolator | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28AC008-P1 | F28AC008-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 8 Isolator | Ultra Fine Grinding 415V Switchroom | F28-AC-008 | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 8 | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-W16 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | F28AC009-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 9 Isolator | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28AC009-P1 | F28AC009-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 9 Isolator | Ultra Fine Grinding 415V Switchroom | F28-AC-009 | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 9 | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-B16 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | F28AC010-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 10 Isolator | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28AC010-P1 | F28AC010-ISL | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 10 Isolator | Ultra Fine Grinding 415V Switchroom | F28-AC-010 | Ultra Fine Grinding 11kV / 415V Switchroom Air Conditioner No. 10 | Ultra Fine Grinding 415V Switchroom | 10 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-R11 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom |  | Lighting - Switchroom Internal 1 (Low Side of Roof) | Ultra Fine Grinding 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-R11_ | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom |  | Lighting - Switchroom Internal 1 (Emergency) | Ultra Fine Grinding 415V Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-W11 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom |  | Lighting - Switchroom Internal 2 (High Side of Roof) | Ultra Fine Grinding 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-W11_ | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom |  | Lighting - Switchroom Internal 2 (Emergency) | Ultra Fine Grinding 415V Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-W12 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom |  | Lighting - Switchroom External 1 | Ultra Fine Grinding 415V Switchroom | 2.5 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-W12_ | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom |  | Lighting - Switchroom External 1 (Emergency) | Ultra Fine Grinding 415V Switchroom | 2.5 | 0.45/0.75 | 1C | Cu | PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28DB001-R03 | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom |  | General Power - Switchroom GPO's | Ultra Fine Grinding 415V Switchroom | 4 | 0.45/0.75 | 2C+E | Cu | Flat - PVC/PVC | White | Walls | Switchroom Vendor | Switchroom Vendor | 3 |  | 6
F28SW009-C1 | F28SR001-LCS | Ultra Fine Grinding 11kV / 415V Switchroom Emergency Shutdown | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Emerg/ Shutdown Circuit. E-stop to trip incomer | 6
F28TR009-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28-TR-009 | Ultra Fine Grinding 415V MCC Transformer | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F28SW109-C2 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28-SW-109 | Ultra Fine Grinding Essential 415V Switchboard | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | ELR Shunt Trip | 7
F28PP409VS-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP409-VS | UFG PRODUCT PUMP 1 LV VSD | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F28PP410VS-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP410-VS | UFG PRODUCT PUMP 2 LV VSD | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F28PP451VS-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP451-VS | UFG MILL 2 FEED PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F28PP453VS-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP453-VS | UFG MILL 2 DISCHARGE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F28PP461VS-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP461-VS | UFG MILL 3 FEED PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F28PP463VS-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP463-VS | UFG MILL 3 DISCHARGE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F28PP494VS-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP494-VS | UFG MILL 2 PRODUCT SAMPLE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F28PP495VS-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28PP495-VS | UFG MILL 3 PRODUCT SAMPLE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72PP521VS-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F72PP521-VS | HYDROGEN PEROXIDE DOSING PUMP 1 LV VSD | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72PP522VS-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F72PP522-VS | HYDROGEN PEROXIDE DOSING PUMP 2 LV VSD | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72PP523VS-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F72PP523-VS | HYDROGEN PEROXIDE DOSING PUMP 3 LV VSD | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72PP524VS-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F72PP524-VS | HYDROGEN PEROXIDE DOSING PUMP 4 LV VSD | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | 7
F28DB001-C1 | F28-FIP-001 | Ultra Fine Grinding 11kV / 415V Switchroom Fire Indicator Panel | Ultra Fine Grinding 415V Switchroom | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 2C | Cu | R-EP-110 | Red | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | HVAC trip. | 7
F28SW009-C2 | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | MCC Incomer Signals to DCS. | 7
F28SW109-C1 | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | F28-SW-109 | Ultra Fine Grinding Essential 415V Switchboard | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Incomer Signals to DCS. | 7
F28FIP001-C1 | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | F28-FIP-001 | Ultra Fine Grinding 11kV / 415V Switchroom Fire Indicator Panel | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F28DB001-C2 | F28-PE-001 | Ultra Fine Grinding 11kV / 415V Switchroom Photo-electric cell | Ultra Fine Grinding 415V Switchroom | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | 2.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | Lighting control | 7
UT28006-I1 | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | UT28006 | F28-SR-002 Ultra Fine Grinding 415V Switchroom Temperature/Humidity Transmitter | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
UT28007-I1 | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | UT28007 | F28-SR-002 Ultra Fine Grinding 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F28SR001LCS-C1 | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | F28SR001-LCS | Ultra Fine Grinding 11kV / 415V Switchroom Emergency Shutdown | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | 24VDC Supply to PILZ Relay in Switchroom E-Shut, plus feedback | 7
ZSC28009-I1 | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | ZSC28009 | F28-SR-002 Ultra Fine Grinding 415V MCC Transformer Enclosure Door Position Switch Closed | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.15 | 2 PR | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Transformer Enclosure Door feedback | 7
F28SW009LCS-C1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28SW009-LCS | Ultra Fine Grinding 415V MCC Remote Switching Panel | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 20C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F28UPS002-C1 | F28UPS002-ISL | Ultra Fine Grinding 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Ultra Fine Grinding 415V Switchroom | F28-UPS-002 | Ultra Fine Grinding 415V Switchroom 240VAC UPS | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | Bypass | 7
F28SW009-C51 | F28-TR-009 | ULTRA FINE GRINDING 415V MCC TRANSFORMER | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultra Fine Grinding 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 7
F28SW009-C52 | F28-TR-009 | ULTRA FINE GRINDING 415V MCC TRANSFORMER | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultra Fine Grinding 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 7
F28SW009-C53 | F28-TR-009 | ULTRA FINE GRINDING 415V MCC TRANSFORMER | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultra Fine Grinding 415V Switchroom | 6 | 0.6/1 | 2C+E | Cu | R-EP-90 | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 | AFD CT Cable | 7
F28SW009-C3 | F28-DCS-410 | ULTRA FINE GRINDING 415V SWITCHROOM DCS PANEL | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | 24VDC PSU monitoring | 7
F28SW009-C4 | F28-DCS-410 | ULTRA FINE GRINDING 415V SWITCHROOM DCS PANEL | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | ULTRA FINE GRINDING 415V MCC | Ultra Fine Grinding 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | 24VDC PSU monitoring | 7
F28FIP001-FO1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-FIP-001 | Ultra Fine Grinding 11kV / 415V Switchroom Fire Indicator Panel | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Site-Wide Fire network - patch to FIP. | 7
F28FIP001-FO2 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-FIP-001 | Ultra Fine Grinding 11kV / 415V Switchroom Fire Indicator Panel | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Site-Wide Fire network - patch to FIP. | 7
F28UPS002-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-UPS-002 | Ultra Fine Grinding 415V Switchroom 240VAC UPS | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F28SW109-D1 | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | F28-SW-109 | Ultra Fine Grinding Essential 415V Switchboard | Ultra Fine Grinding 415V Switchroom | N/A | N/A | N/A | Cu | VAMP CAN Bus | Grey | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 3 | VAMP CAN Bus Cable. | 7
F28SW109-D2 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-SW-109 | Ultra Fine Grinding Essential 415V Switchboard | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Ethernet allowance | 7
F28PP409VS-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28PP409-VS | UFG PRODUCT PUMP 1 LV VSD | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP410VS-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28PP410-VS | UFG PRODUCT PUMP 2 LV VSD | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP451VS-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28PP451-VS | UFG MILL 2 FEED PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP453VS-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28PP453-VS | UFG MILL 2 DISCHARGE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP461VS-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28PP461-VS | UFG MILL 3 FEED PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP463VS-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28PP463-VS | UFG MILL 3 DISCHARGE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP494VS-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28PP494-VS | UFG MILL 2 PRODUCT SAMPLE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP495VS-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28PP495-VS | UFG MILL 3 PRODUCT SAMPLE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72PP521VS-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F72PP521-VS | HYDROGEN PEROXIDE DOSING PUMP 1 LV VSD | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72PP522VS-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F72PP522-VS | HYDROGEN PEROXIDE DOSING PUMP 2 LV VSD | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72PP523VS-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F72PP523-VS | HYDROGEN PEROXIDE DOSING PUMP 3 LV VSD | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72PP524VS-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F72PP524-VS | HYDROGEN PEROXIDE DOSING PUMP 4 LV VSD | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 2 |  | 8
F28SW009-D11 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches | 8
F28SW009-D12 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches | 8
F28SW009-D13 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches | 8
F28SW009-D14 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches | 8
F28SW009-D15 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-SW-009 | Ultra Fine Grinding 415V MCC | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 2 | Connected to local MCC ethernet switches | 8
F28DCS410-D1 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Orange | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 1 PRIMARY | 8
F28DCS410-D2 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Orange | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 1 SECONDARY | 8
F28DCS410-D3 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Purple | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 2 PRIMARY | 8
F28DCS410-D4 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Purple | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 2 SECONDARY | 8
F28DCS410-D5 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | DCS Comms Allowance - ALE CARD (AS REQUIRED) | 8
F28DCS410-D6 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | DCS Comms Allowance - ALE CARD (AS REQUIRED) | 8
F28DCS410-F01 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-DCS-410 | ULTRA FINE GRINDING 415V SWITCHROOM DCS PANEL | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED). | 8
F28DCS410-F02 | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | F28-DCS-410 | ULTRA FINE GRINDING 415V SWITCHROOM DCS PANEL | Ultra Fine Grinding 415V Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED). | 8
F28TR009EB01-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28TR009-EB01 | Ultra Fine Grinding 415V Switchroom Transformer Earth bar | Ultra Fine Grinding 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28TR009EB01-E2 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28TR009-EB01 | Ultra Fine Grinding 415V Switchroom Transformer Earth bar | Ultra Fine Grinding 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28SW009EB01-E2 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28SW009-EB01 | Ultra Fine Grinding 415V MCC Earth Bar | Ultra Fine Grinding 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28SW009EB01-E3 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28SW009-EB01 | Ultra Fine Grinding 415V MCC Earth Bar | Ultra Fine Grinding 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28SW109EB01-E2 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28SW109-EB01 | Ultra Fine Grinding Essential 415V MCC Earth Bar | Ultra Fine Grinding 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28SW109EB01-E3 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28SW109-EB01 | Ultra Fine Grinding Essential 415V MCC Earth Bar | Ultra Fine Grinding 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP409VS-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28PP409-VS | UFG PRODUCT PUMP 1 LV VSD | Ultra Fine Grinding 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP410VS-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28PP410-VS | UFG PRODUCT PUMP 2 LV VSD | Ultra Fine Grinding 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP451VS-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28PP451-VS | UFG MILL 2 FEED PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP453VS-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28PP453-VS | UFG MILL 2 DISCHARGE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP461VS-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28PP461-VS | UFG MILL 3 FEED PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP463VS-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28PP463-VS | UFG MILL 3 DISCHARGE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP494VS-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28PP494-VS | UFG MILL 2 PRODUCT SAMPLE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F28PP495VS-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28PP495-VS | UFG MILL 3 PRODUCT SAMPLE PUMP LV VSD | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72PP521VS-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F72PP521-VS | HYDROGEN PEROXIDE DOSING PUMP 1 LV VSD | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F72PP522VS-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F72PP522-VS | HYDROGEN PEROXIDE DOSING PUMP 2 LV VSD | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F72PP523VS-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F72PP523-VS | HYDROGEN PEROXIDE DOSING PUMP 3 LV VSD | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F72PP524VS-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F72PP524-VS | HYDROGEN PEROXIDE DOSING PUMP 4 LV VSD | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 2 |  | 9
F28COM001-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28-COM-001 | Ultra Fine Grinding 415V Switchroom Communications Rack | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F28DCS410-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28-DCS-410 | Ultra Fine Grinding 415V Switchroom DCS Panel | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F28UPS002-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28-UPS-002 | Ultra Fine Grinding 415V Switchroom 240VAC UPS | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F28UPS002ISL-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28UPS002-ISL | Ultra Fine Grinding 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F28BA002-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28-BA-002 | Ultra Fine Grinding 415V Switchroom 240VAC UPS Battery Bank | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F28DB201-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28-DB-201 | Ultra Fine Grinding 415V Switchroom 240V UPS Distribution Board | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F28SW009LCS-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28SW009-LCS | Ultra Fine Grinding 415V MCC Remote Switching Panel | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F28FIP001-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28-FIP-001 | Ultra Fine Grinding 11kV / 415V Switchroom Fire Indicator Panel | Ultra Fine Grinding 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 3 |  | 9
F28DB001-E1 | F28SR001-EB01 | Ultra Fine Grinding 11kV / 415V Switchroom Earth Bar | Ultra Fine Grinding 415V Switchroom | F28-DB-001 | Ultra Fine Grinding 11kV / 415V Switchroom L&SP Distribution Board | Ultra Fine Grinding 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 3 |  | 9