## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | Length (m) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred colour) | Installation Method | Supplied By | Installed By | Rev | Comments | Page
F28SW013-P1-R | F28-TR-013 | Ultra Fine Grinding 33kV/11kV Transformer | F28 Field | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard | F28-SR-001 | 240 | 6.35/11 | 25 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D, grouped up to 6 | Primero | Primero | 0 |  | 2
F28SW013-P2-R | F28-TR-013 | Ultra Fine Grinding 33kV/11kV Transformer | F28 Field | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard | F28-SR-001 | 240 | 6.35/11 | 25 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D, grouped up to 6 | Primero | Primero | 0 |  | 2
F28SW013-P1-W | F28-TR-013 | Ultra Fine Grinding 33kV/11kV Transformer | F28 Field | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard | F28-SR-001 | 240 | 6.35/11 | 25 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D, grouped up to 6 | Primero | Primero | 0 |  | 2
F28SW013-P2-W | F28-TR-013 | Ultra Fine Grinding 33kV/11kV Transformer | F28 Field | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard | F28-SR-001 | 240 | 6.35/11 | 25 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D, grouped up to 6 | Primero | Primero | 0 |  | 2
F28SW013-P1-B | F28-TR-013 | Ultra Fine Grinding 33kV/11kV Transformer | F28 Field | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard | F28-SR-001 | 240 | 6.35/11 | 25 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D, grouped up to 6 | Primero | Primero | 0 |  | 2
F28SW013-P2-B | F28-TR-013 | Ultra Fine Grinding 33kV/11kV Transformer | F28 Field | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard | F28-SR-001 | 240 | 6.35/11 | 25 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, spaced 2D, grouped up to 6 | Primero | Primero | 0 |  | 2
F28NR013-N1 | F28-TR-013 | Ultra Fine Grinding 33kV/11kV Transformer | F28 Field | F28-NR-013 | Ultra Fine Grinding 33kV/11kV Transformer Neutral Earthing Resistor | F28 field | 50 | 6.35/11 | 20 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Flat, Touching | Primero | Primero | 0 | NER cable. | 2
F28MUF402-P1 | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard | F28-SR-001 | F28-MUF-402 | Ultra Fine Grinding Mill 2 | F28 Field | 150 | 6.35/11 | 50 | 3C | Cu | XLPE/CWS/PVC | Black | Buried in Conduit | Primero | Primero | 0 |  | 2
F28LR402-P1-R | F28-MUF-402 | Ultra Fine Grinding Mill 2 Rotor Term. Box | F28 Field | F28-LR-402 | UFG MILL 2 MOTOR LRS | F28 Field | 240 | 6.35/11 | 30 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR402-P1-W | F28-MUF-402 | Ultra Fine Grinding Mill 2 Rotor Term. Box | F28 Field | F28-LR-402 | UFG MILL 2 MOTOR LRS | F28 Field | 240 | 6.35/11 | 30 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR402-P1-B | F28-MUF-402 | Ultra Fine Grinding Mill 2 Rotor Term. Box | F28 Field | F28-LR-402 | UFG MILL 2 MOTOR LRS | F28 Field | 240 | 6.35/11 | 30 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR402-P2-R | F28-MUF-402 | Ultra Fine Grinding Mill 2 Rotor Term. Box | F28 Field | F28-LR-402 | UFG MILL 2 MOTOR LRS | F28 Field | 240 | 6.35/11 | 30 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR402-P2-W | F28-MUF-402 | Ultra Fine Grinding Mill 2 Rotor Term. Box | F28 Field | F28-LR-402 | UFG MILL 2 MOTOR LRS | F28 Field | 240 | 6.35/11 | 30 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR402-P2-B | F28-MUF-402 | Ultra Fine Grinding Mill 2 Rotor Term. Box | F28 Field | F28-LR-402 | UFG MILL 2 MOTOR LRS | F28 Field | 240 | 6.35/11 | 30 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR402-P3-R | F28-MUF-402 | Ultra Fine Grinding Mill 2 Rotor Term. Box | F28 Field | F28-LR-402 | UFG MILL 2 MOTOR LRS | F28 Field | 240 | 6.35/11 | 30 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR402-P3-W | F28-MUF-402 | Ultra Fine Grinding Mill 2 Rotor Term. Box | F28 Field | F28-LR-402 | UFG MILL 2 MOTOR LRS | F28 Field | 240 | 6.35/11 | 30 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR402-P3-B | F28-MUF-402 | Ultra Fine Grinding Mill 2 Rotor Term. Box | F28 Field | F28-LR-402 | UFG MILL 2 MOTOR LRS | F28 Field | 240 | 6.35/11 | 30 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR402-P4-R | F28-MUF-402 | Ultra Fine Grinding Mill 2 Rotor Term. Box | F28 Field | F28-LR-402 | UFG MILL 2 MOTOR LRS | F28 Field | 240 | 6.35/11 | 30 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR402-P4-W | F28-MUF-402 | Ultra Fine Grinding Mill 2 Rotor Term. Box | F28 Field | F28-LR-402 | UFG MILL 2 MOTOR LRS | F28 Field | 240 | 6.35/11 | 30 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR402-P4-B | F28-MUF-402 | Ultra Fine Grinding Mill 2 Rotor Term. Box | F28 Field | F28-LR-402 | UFG MILL 2 MOTOR LRS | F28 Field | 240 | 6.35/11 | 30 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28MUF403-P1 | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard | F28-SR-001 | F28-MUF-403 | Ultra Fine Grinding Mill 3 | F28 Field | 150 | 6.35/11 | 45 | 3C | Cu | XLPE/CWS/PVC | Black | Buried in Conduit | Primero | Primero | 0 |  | 2
F28LR403-P1-R | F28-MUF-403 | Ultra Fine Grinding Mill 3 Rotor Term. Box | F28 Field | F28-LR-403 | UFG MILL 3 MOTOR LRS | F28 Field | 240 | 6.35/11 | 20 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR403-P1-W | F28-MUF-403 | Ultra Fine Grinding Mill 3 Rotor Term. Box | F28 Field | F28-LR-403 | UFG MILL 3 MOTOR LRS | F28 Field | 240 | 6.35/11 | 20 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR403-P1-B | F28-MUF-403 | Ultra Fine Grinding Mill 3 Rotor Term. Box | F28 Field | F28-LR-403 | UFG MILL 3 MOTOR LRS | F28 Field | 240 | 6.35/11 | 20 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR403-P2-R | F28-MUF-403 | Ultra Fine Grinding Mill 3 Rotor Term. Box | F28 Field | F28-LR-403 | UFG MILL 3 MOTOR LRS | F28 Field | 240 | 6.35/11 | 20 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR403-P2-W | F28-MUF-403 | Ultra Fine Grinding Mill 3 Rotor Term. Box | F28 Field | F28-LR-403 | UFG MILL 3 MOTOR LRS | F28 Field | 240 | 6.35/11 | 20 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR403-P2-B | F28-MUF-403 | Ultra Fine Grinding Mill 3 Rotor Term. Box | F28 Field | F28-LR-403 | UFG MILL 3 MOTOR LRS | F28 Field | 240 | 6.35/11 | 20 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR403-P3-R | F28-MUF-403 | Ultra Fine Grinding Mill 3 Rotor Term. Box | F28 Field | F28-LR-403 | UFG MILL 3 MOTOR LRS | F28 Field | 240 | 6.35/11 | 20 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR403-P3-W | F28-MUF-403 | Ultra Fine Grinding Mill 3 Rotor Term. Box | F28 Field | F28-LR-403 | UFG MILL 3 MOTOR LRS | F28 Field | 240 | 6.35/11 | 20 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR403-P3-B | F28-MUF-403 | Ultra Fine Grinding Mill 3 Rotor Term. Box | F28 Field | F28-LR-403 | UFG MILL 3 MOTOR LRS | F28 Field | 240 | 6.35/11 | 20 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR403-P4-R | F28-MUF-403 | Ultra Fine Grinding Mill 3 Rotor Term. Box | F28 Field | F28-LR-403 | UFG MILL 3 MOTOR LRS | F28 Field | 240 | 6.35/11 | 20 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR403-P4-W | F28-MUF-403 | Ultra Fine Grinding Mill 3 Rotor Term. Box | F28 Field | F28-LR-403 | UFG MILL 3 MOTOR LRS | F28 Field | 240 | 6.35/11 | 20 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2
F28LR403-P4-B | F28-MUF-403 | Ultra Fine Grinding Mill 3 Rotor Term. Box | F28 Field | F28-LR-403 | UFG MILL 3 MOTOR LRS | F28 Field | 240 | 6.35/11 | 20 | 1C | Cu | XLPE/CWS/PVC | Black | Ladder - Trefoil, Touching | Primero | Primero | 0 |  | 2