## Equipment list
Rev | Equip. Number | Equipment Name | Qty | Description | Make | Model | Supplied By | Installed By | Comments | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred colour) | Installation | Revision | Page
0 | F28-SR-001 | Ultra Fine Grinding 11kV Switchroom | 1 | Transportable switchroom on structural steel baseframe complete with 1.8m legs and landings, transported to site 600kms on sealed roads. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero | F28-SR-001, F28-SR-002, Transformer room(s) and Air Lock are all part of the same building | [14 empty] | 2
0 | - | Ultra Fine Grinding 11kV Switchroom Landings and stairs | 1 | Equipment Landing to be structural steel baseframe complete with 1.8m legs and landings, designed to support heaviest piece of equipment to be installed in room. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero | [15 empty] | 2
0 | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard | 1 | Metal clad, partition metal, 11kV switchboard. 1250A bus, 25kA/3s fault rating. Internally arc fault contained AFLR. With top mount arc absorbing duct on top - no arc vent to outdoors. 1 x VT/Earth Switch panel, 1 x Incomer panel, 2 x Motor feeder panels, 1 x Spare Feeder panel | ABB | UniGear ZS1 | Primero | Switchroom/MCC Vendor | Refer 2000-EL003-B02-10012 (Panel Arrangement), 2000-EL003-B03-10004 (Section View), 2000-EL003-C01-10011 (Foundation Frame Detail), 2000-EL003-C03-10010 (Foundation Layout), 2000-EL003-D01-10004 (SLD) 2000-F00-DSH-EL-11003 11kV Datasheet Switchboard Dimensions (W = 3310mm, H = 2533mm, D = 1340mm) approx. weight 4,250kg | [14 empty] | 2
0 | F28-BA-001 | Ultra Fine Grinding 11kV Switchroom 48VDC Battery | 1 | 48V DC Tripping and Closing Supply, 200Ah battery bank. Free-standing industrial cabinet. | Magellan | 1 string of 4 x 12V, 200Ah VRLA batteries | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 1 x U220 Battery enclosure (W:800mm, D: 800mm, H: 2200mm). IP-42, Bottom cable entry, 5mm Aluminium gland plate complete with 1 string of 4 X 12V 200Ah VRLA Batteries. And all associated accessories. | [14 empty] | 2
0 | F28-BC-001 | Ultra Fine Grinding 11kV Switchroom 48VDC Charger | 1 | 48V DC Tripping and Closing Supply, with 100A charger complete with integral DB. Free-standing industrial cabinet. | Magellan | 48MCRII3P100 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 1 x U220 Battery enclosure (W:800mm, D: 800mm, H: 2200mm). 100A MCRII 3 Phase input charger. Compete with: Alarm relay board (voltage free alarm relays, including Floating Earth Fault). Blocking Diode Communications Board (For Modbus TCP) Including Lifting lugs, battery test facility, 1 hour battery discharge test, and integrated DC DB with 8 off 2P, 20A MCBs and 1 spare MCB with shunt trip. | [14 empty] | 2
0 | F28FIP001-XE2 | Ultra Fine Grinding 11kV Switchroom Manual Call Points | VTA | Fire system Manual Call points (internal and external) as required by Australian Standards | Wormald | Manual Call Points | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Manual call points shall be tagged in sequential order | [14 empty] | 2
0 | F28FIP001-XE3 | Ultra Fine Grinding 11kV Switchroom Smoke Detector | VTA | Fire system smoke detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order | [14 empty] | 2
0 | F28FIP001-XE4 | Ultra Fine Grinding 11kV Switchroom Fire Detector | VTA | Fire system fire detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order | [14 empty] | 2
0 | F28FIP001-UA | Ultra Fine Grinding 11kV Switchroom External Alarm Bells | VTA | Fire system alarm sirens as required by Australian Standards | Wormald | External Sounder / Red Strobe | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Alarm sirens shall be tagged in sequential order | [14 empty] | 2
0 | - | Ultra Fine Grinding 11kV Switchroom Fire Extinguishers | VTA | 5kg dry powder fire extinguishers complete with wall mount and signage. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [15 empty] | 2
0 | - | Ultra Fine Grinding 11kV Switchroom Automatic External Defibrillator | 1 | Automatic external defibrillator complete with wall-mounted cabinet. | Physio Control | Lifepak Defibrillator CR2 Fully Automatic | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [15 empty] | 2
0 | - | Ultra Fine Grinding 11kV Switchroom HV Rescue Kit | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [15 empty] | 2
0 | - | Ultra Fine Grinding 11kV Switchroom CPR signage | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [15 empty] | 2
0 | - | Ultra Fine Grinding 11kV / 415V Switchroom HVAC Controller | VTA | Wall mounted Air Conditioner Controller, with relay contacts for Faulty & Healthy | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | One wall mounted controller to control all A/C's per room (One per transformer room, LV room, HV room). | [14 empty] | 2
0 | F28-AC-0XX | Ultra Fine Grinding 11kV Switchroom Air Conditioners | VTA | High Wall split system, single phase, MULTIPLE (N+1 reqd) with drip trays if necessary | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. AC units shall be tagged in numercial order (e.g. F28-AC-001, F28-AC-002 etc. ) | [14 empty] | 2
0 | F28AC0XX-ISL | Ultra Fine Grinding 11kV Switchroom Air Conditioner Isolators | 1 lot | Field isolator, one per split system AC | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Isolators shall be tagged with the respective AC equipment number (e.g. F28AC0XX-ISL etc) | [14 empty] | 2
0 | - | Ultra Fine Grinding 11kV Switchroom Normal Light Fittings | 1 lot | Lighting to meet National Construction Code | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | [14 empty] | 2
0 | - | Ultra Fine Grinding 11kV Switchroom Emergency Light Fittings | 1 lot | Lighting to meet National Construction Code; C/w built in battery pack. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | [14 empty] | 2
0 | UT28005 | F28-SR-001 Ultra Fine Grinding 11kV Switchroom Temperature/Humidity Transmitter | 1 | Switchroom Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | [14 empty] | 2
1 | F28SW013-LCS | Ultra Fine Grinding 11kV Switchboard Remote Switching Panel | 1 | IP65 Enclosure, hinged, lockable, clear perspex escutcheon cover over operator interfaces to prevent inadvertent/unauthorised operation. Remote Switching Local control station (visual mimic and control of CBs, VSD Contactors, earth switches) with door mounted selector switches providing open/close functionality for CBs, Contactors and earth switches, rack in/rack out functionality of circuit breakers and contactors and indication lights for status. Provided with the following for each panel type: Bus VT & Earth Switch Panels (1 off) • 1 off Earth Switch Indicator (RD/GN) • 1 off VT Rack Indicator (RD/GN) • 1 off 3-position Selector Switches • 1 off 2-position Selector Switches Fused Contactor Feeder Panels (0 off) • 3 off Contactor/Earth Switch Indicators (RD/GN) • 1 off Fused Contactor Racked In/Racked Out Indicators (RD/GN) • 3 off 3-position Selector Switches • 1 off 2-position Selector Switches Incomer & CB Feeder Panels (4 off) • 3 off Circuit Breaker/Earth Switch Indicators (RD/GN) • 1 off CB Racked In/Racked Out Indicators (RD/GN) • 3 off 3-position Selector Switches • 1 off 2-position Selector Switches | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Typical Schematics & GA to be provided to Switchroom Vendor to design and fabricate panel. | [14 empty] | 3
0 | --000 |  | 1 | Tinned Flat Copper Bus bar mounted on insulated standoffs inside Switchboard. | TBC | TBC | Primero | Switchroom/MCC Vendor | [15 empty] | 3
[7 empty] | Switchroom Vendor | Switchroom Vendor | Earth bonding conductors shall be equal to the larger of 16mm2 or equipment phase conductor size, but no greater than 120mm2. | F28SR001-EB01 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EARTH BAR | Ultra Fine Grinding 11kV Switchroom | Multiple | Each Battery charger, UPS, DB, Remote switching panel, HVAC control panel, FIP or other electrical panels. | Ultra Fine Grinding 11kV Switchroom | Note 6. | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | 0 | 4
[7 empty] | Switchroom Vendor | Switchroom Vendor | Ladder to be bonded to earth bar in two places . | F28SR001-EB01 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EARTH BAR | Ultra Fine Grinding 11kV Switchroom |  | Subfloor cable ladder. | Ultra Fine Grinding 11kV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | 0 | 4
[7 empty] | Switchroom Vendor | Switchroom Vendor | Switchroom subframe to be bonded to switchroom earth bar. Earth bonds to be at two opposing corners. | F28SR001-EB01 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EARTH BAR | Ultra Fine Grinding 11kV Switchroom |  | Switchroom subframe. | Ultra Fine Grinding 11kV Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | 0 | 4

## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred colour) | Installation | Supplied By | Installed By | Revision | Comments | Page
F28BC001-P1 | F28-DB-001 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM L&SP DISTRIBUTION BOARD | Ultra Fine Grinding Switchroom | F28-BC-001 | Ultra Fine Grinding 11kV Switchroom 48VDC Charger | Ultra Fine Grinding 11kV Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F28BA001-P1-R | F28-BC-001 | Ultra Fine Grinding 11kV Switchroom 48VDC Charger | Ultra Fine Grinding 11kV Switchroom | F28-BA-001 | Ultra Fine Grinding 11kV Switchroom 48VDC Battery | Ultra Fine Grinding 11kV Switchroom | 35 | 0.6/1 | 1C | Cu | XLPE/PVC Flexible | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F28BA001-P1-B | F28-BC-001 | Ultra Fine Grinding 11kV Switchroom 48VDC Charger | Ultra Fine Grinding 11kV Switchroom | F28-BA-001 | Ultra Fine Grinding 11kV Switchroom 48VDC Battery | Ultra Fine Grinding 11kV Switchroom | 35 | 0.6/1 | 1C | Cu | XLPE/PVC Flexible | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F28SW013-P3 | F28-BC-001 | Ultra Fine Grinding 11kV Switchroom 48VDC Charger | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard | Ultra Fine Grinding 11kV Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | Charger - 48VDC to switchboard | 4
F28SW013LCS-P1 | F28-BC-001 | Ultra Fine Grinding 11kV Switchroom 48VDC Charger | Ultra Fine Grinding 11kV Switchroom | F28SW013-LCS | Ultra Fine Grinding 11kV Switchboard Remote Switching Panel | Ultra Fine Grinding 11kV Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Charger - 48VDC to ROP | 4
F28SW013-P4 | F28-DB-001 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM L&SP DISTRIBUTION BOARD | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard | Ultra Fine Grinding 11kV Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | 240V for panel anticondensation heaters. | 4
F28SW013-C1 | F28SR001-LCS | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EMERGENCY SHUTDOWN | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard | Ultra Fine Grinding 11kV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Emerg/ Shutdown Circuit. E-stop to trip incomer | 4
F28SW013-C2 | F28SW013-LCS | Ultra Fine Grinding 11kV Switchboard Remote Switching Panel | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard Panel 01 | Ultra Fine Grinding 11kV Switchroom | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 4
F28SW013-C8 | F28-DCS-410 | ULTRA FINE GRINDING 415V SWITCHROOM DCS PANEL | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard Panel 01 | Ultra Fine Grinding 11kV Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 | Panel A01 Feedback | 4
F28SW013-C3 | F28SW013-LCS | Ultra Fine Grinding 11kV Switchboard Remote Switching Panel | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard Panel 02 | Ultra Fine Grinding 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 4
F28SW013-C5 | F28SW013-LCS | Ultra Fine Grinding 11kV Switchboard Remote Switching Panel | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard Panel 03 | Ultra Fine Grinding 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 |  | 4
F28SW013-C4 | F28-DCS-410 | ULTRA FINE GRINDING 415V SWITCHROOM DCS PANEL | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard Panel 03 | Ultra Fine Grinding 11kV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 2 | DCS incomer Open/Close | 4
F28SW013-C6 | F28SW013-LCS | Ultra Fine Grinding 11kV Switchboard Remote Switching Panel | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard Panel 04 | Ultra Fine Grinding 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 4
F28SW013-C7 | F28SW013-LCS | Ultra Fine Grinding 11kV Switchboard Remote Switching Panel | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard Panel 05 | Ultra Fine Grinding 11kV Switchroom | 1.5 | 0.6/1 | 30C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 4
F28BC001-C1 | F28-DCS-410 | ULTRA FINE GRINDING 415V SWITCHROOM DCS PANEL | Ultra Fine Grinding 11kV Switchroom | F28-BC-001 | Ultra Fine Grinding 11kV Switchroom 48VDC Charger | Ultra Fine Grinding 11kV Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
UT28005-I1 | F28-DCS-410 | ULTRA FINE GRINDING 415V SWITCHROOM DCS PANEL | Ultra Fine Grinding 11kV Switchroom | UT28005 | F28-SR-001 Ultra Fine Grinding 11kV Switchroom Temperature/Humidity Transmitter | Ultra Fine Grinding 11kV Switchroom | 1.5 | 0.15 | 2pr | Cu | PVC/IOSCN/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F28SW013-D1 | F28-COM-001 | ULTRA FINE GRINDING 415V SWITCHROOM COMMUNICATIONS RACK | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard INC Panel 3 - SEL 787 | Ultra Fine Grinding 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F28SW013-D2 | F28-COM-001 | ULTRA FINE GRINDING 415V SWITCHROOM COMMUNICATIONS RACK | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard INC Panel 3 - SEL 751 | Ultra Fine Grinding 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F28SW013-D3 | F28-COM-001 | ULTRA FINE GRINDING 415V SWITCHROOM COMMUNICATIONS RACK | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard INC Panel 3 - SEL 753 | Ultra Fine Grinding 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F28SW013-D4 | F28-COM-001 | ULTRA FINE GRINDING 415V SWITCHROOM COMMUNICATIONS RACK | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard Panel 02 - SEL 710 | Ultra Fine Grinding 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F28SW013-D5 | F28-COM-001 | ULTRA FINE GRINDING 415V SWITCHROOM COMMUNICATIONS RACK | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard Panel 04 - SEL 710 | Ultra Fine Grinding 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 4
F28SW013-D6 | F28-COM-013 | Ultra Fine Grinding 11kV Switchroom Communications Rack | Ultra Fine Grinding 11kV Switchroom | F28-SW-013 | Ultra Fine Grinding 11kV Switchboard Panel 05 - SEL 751 | Ultra Fine Grinding 11kV Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F28SW013EB01-E1 | F28SR001-EB01 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EARTH BAR | Ultra Fine Grinding 11kV Switchroom | F28SW013-EB01 | #N/A | Ultra Fine Grinding 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Each end of HV switchboard earth bar to be bonded to switchroom earth bar. | 4
F28SW013EB01-E2 | F28SR001-EB01 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EARTH BAR | Ultra Fine Grinding 11kV Switchroom | F28SW013-EB01 | #N/A | Ultra Fine Grinding 11kV Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Each end of HV switchboard earth bar to be bonded to switchroom earth bar. | 4
F28BA001-E1 | F28SR001-EB01 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EARTH BAR | Ultra Fine Grinding 11kV Switchroom | F28-BA-001 | Ultra Fine Grinding 11kV Switchroom 48VDC Battery | Ultra Fine Grinding 11kV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F28BC001-E1 | F28SR001-EB01 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EARTH BAR | Ultra Fine Grinding 11kV Switchroom | F28-BC-001 | Ultra Fine Grinding 11kV Switchroom 48VDC Charger | Ultra Fine Grinding 11kV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F28SW013LCS-E1 | F28SR001-EB01 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EARTH BAR | Ultra Fine Grinding 11kV Switchroom | F28SW013-LCS | Ultra Fine Grinding 11kV Switchboard Remote Switching Panel | Ultra Fine Grinding 11kV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F28SR001LCS-E1 | F28SR001-EB01 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EARTH BAR | Ultra Fine Grinding 11kV Switchroom | F28SR001-LCS | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EMERGENCY SHUTDOWN | Ultra Fine Grinding 11kV Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F28SR001-E3 | F28SR001-EB01 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EARTH BAR | Ultra Fine Grinding 11kV Switchroom | F28-SR-001 | Subfloor Cable Ladder | Ultra Fine Grinding 11kV Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
F28SR001-E4 | F28SR001-EB01 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EARTH BAR | Ultra Fine Grinding 11kV Switchroom | F28-SR-001 | Subfloor Cable Ladder | Ultra Fine Grinding 11kV Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 4
Ladder Joint Bonds | F28-SR-001 | Subfloor Cable Ladder | Ultra Fine Grinding 11kV Switchroom | F28-SR-001 | Subfloor Cable Ladder | Ultra Fine Grinding 11kV Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F28SR001-E1 | F28SR001-EB01 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EARTH BAR | Ultra Fine Grinding 11kV Switchroom | F28-SR-001 | Switchroom Subframe | Ultra Fine Grinding 11kV Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 5
F28SR001-E2 | F28SR001-EB01 | ULTRA FINE GRINDING 11KV / 415V SWITCHROOM EARTH BAR | Ultra Fine Grinding 11kV Switchroom | F28-SR-001 | Switchroom Subframe | Ultra Fine Grinding 11kV Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 3 |  | 5