## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | Length (m) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred colour) | Installation Method | Supplied By | Installed By | Comments | Reference Drawing (SLD/SCM/TER) | Area | Rev | Page
30PC61A-FO1 | 30-COM-02 | SUBSTATION 38 COMMUNICATIONS RACK - SMOF SUB68 FOBOT | SUBSTATION 38 | 30-PC-61A | SUBSTATION 38 PROCESS CONTROL CABINET A - FCS0205/N1S3 ANT401 CARD | SUBSTATION 38 | 9/125µm | N/A | 20 | 2C | OS2 SMOF | Single Mode Fibre Patch Lead (SC-LC) | Yellow | Ladder - Comms | Primero | Primero | Optical ESB Bus A - for F30-RIO-401/402/403. LENGTH TO BE CONFIRMED ON SITE | N/A | 300 | 0 | 2
30PC61A-FO2 | 30-COM-02 | SUBSTATION 38 COMMUNICATIONS RACK - SMOF SUB68 FOBOT | SUBSTATION 38 | 30-PC-61A | SUBSTATION 38 PROCESS CONTROL CABINET A - FCS0205/N1S4 ANT401 CARD | SUBSTATION 38 | 9/125µm | N/A | 20 | 2C | OS2 SMOF | Single Mode Fibre Patch Lead (SC-LC) | Yellow | Ladder - Comms | Primero | Primero | Optical ESB Bus B - for F30-RIO-401/402/403. LENGTH TO BE CONFIRMED ON SITE | N/A | 300 | 0 | 2
F30SW401-P1-R | 30-SW-62A | CIL 3 415V MCC - TIER 5F | SUBSTATION 68 | F30-SW-401 | CIL 3 415V MCC - INCOMING MODULE | SUBSTATION 68 | 500 | 0.6/1 | 15 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Single Layer in Trefoil | Primero | Primero |  | 2000-F30-SLD-EL-10301 | 300 | 0 | 2
F30SW401-P1-W | 30-SW-62A | CIL 3 415V MCC - TIER 5F | SUBSTATION 68 | F30-SW-401 | CIL 3 415V MCC - INCOMING MODULE | SUBSTATION 68 | 500 | 0.6/1 | 15 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Single Layer in Trefoil | Primero | Primero |  | 2000-F30-SLD-EL-10301 | 300 | 0 | 2
F30SW401-P1-B | 30-SW-62A | CIL 3 415V MCC - TIER 5F | SUBSTATION 68 | F30-SW-401 | CIL 3 415V MCC - INCOMING MODULE | SUBSTATION 68 | 500 | 0.6/1 | 15 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Single Layer in Trefoil | Primero | Primero |  | 2000-F30-SLD-EL-10301 | 300 | 0 | 2
F30SW401-N1 | 30-SW-62A | CIL 3 415V MCC - TIER 5F | SUBSTATION 68 | F30-SW-401 | CIL 3 415V MCC - INCOMING MODULE | SUBSTATION 68 | 500 | 0.6/1 | 15 | 1C | Cu | X-HF-110/HFS-110-TP Flexible | Black | Ladder - Single Layer in Trefoil | Primero | Primero |  | 2000-F30-SLD-EL-10301 | 300 | 0 | 2
F30SW401-E1 | 30-SW-62A | CIL 3 415V MCC - TIER 5F | SUBSTATION 68 | F30-SW-401 | CIL 3 415V MCC - MAIN EARTH BAR | SUBSTATION 68 | 120 | 0.6/1 | 15 | 1C | Cu | PVC | Green/Yellow | Ladder - Single Layer | Primero | Primero |  | 2000-F30-SLD-EL-10301 | 300 | 0 | 2
F30SW401-E2 | -- | SUBSTATION NO.68 EARTH BAR | SUBSTATION 68 | F30-SW-401 | CIL 3 415V MCC - MAIN EARTH BAR | SUBSTATION 68 | 120 | 0.6/1 | 15 | 1C | Cu | PVC | Green/Yellow | Ladder - Single Layer | Primero | Primero |  | 2000-F30-SLD-EL-10301 | 300 | 0 | 2
F30SW401-D1 | 30-SW-62A | CIL 3 415V MCC - TIER 4F VAMP10LD IO UNIT | SUBSTATION 68 | F30-SW-401 | CIL 3 415V MCC - VAMP10LD IO UNIT | SUBSTATION 68 | Vendor | Vendor | 15 | Vendor | Vendor | VX001 ARC FLASH COMM CABLE | Vendor | Ladder - Bunched Ctrl/Inst | EL001 | Primero |  | TBA | 300 | 0 | 2
F30SW401-P2 | 30-DB-62 | SUBSTATION 68 240V INSTRUMENT DISTRIBUTION BOARD | SUBSTATION 68 | F30-SW-401 | CIL 3 415V MCC - 24VDC DISTRIBUTION MODULE | SUBSTATION 68 | 2.5 | 0.6/1 | 25 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-SCM-EL-10034 | 300 | 0 | 2
FCS0205-FO1 | 65-COM-01 | SUBSTATION 68 COMMUNICATIONS RACK - SMOF SUB38 FOBOT | SUBSTATION 68 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK - F30-FOB-401B | SUBSTATION 68 | 9/125µm | N/A | 5 | 2C | OS2 SMOF | Single Mode Fibre Patch Lead (SC-LC) | Yellow | Ladder - Comms | Primero | Primero | FCS0205 Optical ESB Bus A - for F30-RIO-401/402/403 | 2000-F30-TER-IC-10001 | 300 | 0 | 2
FCS0205-FO2 | 65-COM-01 | SUBSTATION 68 COMMUNICATIONS RACK - SMOF SUB38 FOBOT | SUBSTATION 68 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK - F30-FOB-401A | SUBSTATION 68 | 9/125µm | N/A | 5 | 2C | OS2 SMOF | Single Mode Fibre Patch Lead (SC-LC) | Yellow | Ladder - Comms | Primero | Primero | FCS0205 Optical ESB Bus B - for F30-RIO-401/402/403 | 2000-F30-TER-IC-10001 | 300 | 0 | 2
F30ETH401-FO1 | 65-COM-01 | SUBSTATION 68 COMMUNICATIONS RACK - SMOF SUB35 FOBOT | SUBSTATION 68 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK - F30-ETH-401 | SUBSTATION 68 | 9/125µm | N/A | 5 | 2C | OS2 SMOF | Single Mode Fibre Patch Lead (SC-LC) | Yellow | Ladder - Comms | Primero | Primero | Modbus Network - to Sub35 | 2000-F30-TER-IC-10002 | 300 | 0 | 2
FCS0206-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK - F30-ETH-401 | SUBSTATION 68 | 30PC62-L | SUBSTATION 68 DCS CABINET L - FCS0206N1S5 ALE111 CARD | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-TER-IC-10002 | 300 | 0 | 2
F30PP417VS-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP417-VS | CONCENTRATE THICKENER U/F PUMP 1 LV VSD | SUBSTATION 68 | 25 | 0.6/1 | 30 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10017 | 300 | 0 | 2
F30PP417VS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP417-VS | CONCENTRATE THICKENER U/F PUMP 1 LV VSD | SUBSTATION 68 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10017 | 300 | 0 | 2
F30PP417VS-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30PP417-VS | CONCENTRATE THICKENER U/F PUMP 1 LV VSD | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10017 | 300 | 0 | 2
F30PP418VS-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP418-VS | CONCENTRATE THICKENER U/F PUMP 2 LV VSD | SUBSTATION 68 | 25 | 0.6/1 | 30 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10018 | 300 | 0 | 2
F30PP418VS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP418-VS | CONCENTRATE THICKENER U/F PUMP 2 LV VSD | SUBSTATION 68 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10018 | 300 | 0 | 2
F30PP418VS-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30PP418-VS | CONCENTRATE THICKENER U/F PUMP 2 LV VSD | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10018 | 300 | 0 | 2
F30RIO401-P1 | 30-DB-62 | SUBSTATION 68 240V INSTRUMENT DISTRIBUTION BOARD | SUBSTATION 68 | F30-RIO-401 | CONCENTRATE LEACH AND ADSORPTION FIELD N-IO PANEL | CIRCUIT WATER TANK | 10 | 0.6/1 | 115 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-SCM-IC-10401 | 300 | 0 | 2
65COM02/F30RIO401-FO1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30-RIO-401 | CONCENTRATE LEACH AND ADSORPTION FIELD N-IO PANEL | CIRCUIT WATER TANK | 9/125µm | N/A | 115 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero |  | 2000-F30-TER-IC-10400 | 300 | 0 | 2
F30PP417-P1 | F30PP417-VS | CONCENTRATE THICKENER U/F PUMP 1 LV VSD | SUBSTATION 68 | F30-PP-417 | CONCENTRATE THICKENER UNDERFLOW PUMP 1 | CONCENTRATE THICKENER (30- TH-61) | 25 | 0.6/1 | 160 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10017 | 300 | 0 | 2
F30PP417LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP417-LCS | CONCENTRATE THICKENER UNDERFLOW PUMP 1 LOCAL CONTROL STATION | CONCENTRATE THICKENER (30- TH-61) | 1.5 | 0.6/1 | 160 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10017 | 300 | 0 | 2
F30PP418-P1 | F30PP418-VS | CONCENTRATE THICKENER U/F PUMP 2 LV VSD | SUBSTATION 68 | F30-PP-418 | CONCENTRATE THICKENER UNDERFLOW PUMP 2 | CONCENTRATE THICKENER (30- TH-61) | 25 | 0.6/1 | 160 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10018 | 300 | 0 | 2
F30PP418LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP418-LCS | CONCENTRATE THICKENER UNDERFLOW PUMP 2 LOCAL CONTROL STATION | CONCENTRATE THICKENER (30- TH-61) | 1.5 | 0.6/1 | 160 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10018 | 300 | 0 | 2