## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | Length (m) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred colour) | Installation Method | Supplied By | Installed By | Comments | Reference Drawing (SLD/SCM/TER) | Area | Rev | Page
F30ETH403-D1 | 65-COM-01 | SUBSTATION 68 COMMUNICATIONS RACK - SWITCH SUB68CAM | SUBSTATION 68 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK - F30-ETH-403 | SUBSTATION 68 | N/A | N/A | 5 | 4PR | Cu | CAT6 | Yellow | Ladder - Bunched Ctrl/Inst | Primero | Primero | Existing CCTV Network tie-in | 2000-F30-TER-IC-10001 | 300 | 0 | 2
F30PP415VS-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP415-VS | CONCENTRATE PRE-LEACH THICKENER U/F PUMP 1 LV VSD | SUBSTATION 68 | 25 | 0.6/1 | 30 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10001 | 300 | 0 | 2
F30PP415VS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP415-VS | CONCENTRATE PRE-LEACH THICKENER U/F PUMP 1 LV VSD | SUBSTATION 68 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10001 | 300 | 0 | 2
F30PP415VS-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30PP415-VS | CONCENTRATE PRE-LEACH THICKENER U/F PUMP 1 LV VSD | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10001 | 300 | 0 | 2
F30PP416VS-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP416-VS | CONCENTRATE PRE-LEACH THICKENER U/F PUMP 2 LV VSD | SUBSTATION 68 | 25 | 0.6/1 | 30 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10002 | 300 | 0 | 2
F30PP416VS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP416-VS | CONCENTRATE PRE-LEACH THICKENER U/F PUMP 2 LV VSD | SUBSTATION 68 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10002 | 300 | 0 | 2
F30PP416VS-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30PP416-VS | CONCENTRATE PRE-LEACH THICKENER U/F PUMP 2 LV VSD | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10002 | 300 | 0 | 2
F30PP426VS-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP426-VS | CONCENTRATE LEACH TRANSFER PUMP 1 LV VSD | SUBSTATION 68 | 70 | 0.6/1 | 30 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10003 | 300 | 0 | 2
F30PP426VS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP426-VS | CONCENTRATE LEACH TRANSFER PUMP 1 LV VSD | SUBSTATION 68 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10003 | 300 | 0 | 2
F30PP426VS-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30PP426-VS | CONCENTRATE LEACH TRANSFER PUMP 1 LV VSD | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10003 | 300 | 0 | 2
F30PP427VS-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP427-VS | CONCENTRATE LEACH TRANSFER PUMP 2 LV VSD | SUBSTATION 68 | 70 | 0.6/1 | 30 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10004 | 300 | 0 | 2
F30PP427VS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP427-VS | CONCENTRATE LEACH TRANSFER PUMP 2 LV VSD | SUBSTATION 68 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10004 | 300 | 0 | 2
F30PP427VS-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30PP427-VS | CONCENTRATE LEACH TRANSFER PUMP 2 LV VSD | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10004 | 300 | 0 | 2
F30PP428VS-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP428-VS | CIL3 TAILS PUMP 1 LV VSD | SUBSTATION 68 | 50 | 0.6/1 | 30 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10005 | 300 | 0 | 2
F30PP428VS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP428-VS | CIL3 TAILS PUMP 1 LV VSD | SUBSTATION 68 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10005 | 300 | 0 | 2
F30PP428VS-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30PP428-VS | CIL3 TAILS PUMP 1 LV VSD | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10005 | 300 | 0 | 2
F30PP429VS-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP429-VS | CIL3 TAILS PUMP 2 LV VSD | SUBSTATION 68 | 50 | 0.6/1 | 30 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10006 | 300 | 0 | 2
F30PP429VS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP429-VS | CIL3 TAILS PUMP 2 LV VSD | SUBSTATION 68 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10006 | 300 | 0 | 2
F30PP429VS-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30PP429-VS | CIL3 TAILS PUMP 2 LV VSD | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10006 | 300 | 0 | 2
F30PP496VS-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP496-VS | ACID EFFLUENT & FINE CARBON PUMP 1 LV VSD | SUBSTATION 68 | 70 | 0.6/1 | 30 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10020 | 300 | 0 | 2
F30PP496VS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP496-VS | ACID EFFLUENT & FINE CARBON PUMP 1 LV VSD | SUBSTATION 68 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10020 | 300 | 0 | 2
F30PP496VS-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30PP496-VS | ACID EFFLUENT & FINE CARBON PUMP 1 LV VSD | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10020 | 300 | 0 | 2
F30PP497VS-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP497-VS | ACID EFFLUENT & FINE CARBON PUMP 2 LV VSD | SUBSTATION 68 | 70 | 0.6/1 | 30 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10032 | 300 | 0 | 2
F30PP497VS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP497-VS | ACID EFFLUENT & FINE CARBON PUMP 2 LV VSD | SUBSTATION 68 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10032 | 300 | 0 | 2
F30PP497VS-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30PP497-VS | ACID EFFLUENT & FINE CARBON PUMP 2 LV VSD | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10032 | 300 | 0 | 2
F30SA442EOL-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30-SW-401 | CIL 3 415V MCC - F30-SA-442 EOL | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10021 | 300 | 0 | 2
F30SC412EOL-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30-SW-401 | CIL 3 415V MCC - F30-SC-412 EOL | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10015 | 300 | 0 | 2
F30PP476EOL-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30-SW-401 | CIL 3 415V MCC - F30-PP-476 EOL | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10029 | 300 | 0 | 2
F65SC471EOL-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F30-SW-401 | CIL 3 415V MCC - F65-SC-471 EOL | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10030 | 650 | 0 | 2
F65PP481VS-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F65PP481-VS | CIL3 LOADED CARBON PUMP LV VSD | SUBSTATION 68 | 35 | 0.6/1 | 30 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10031 | 650 | 0 | 2
F65PP481VS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F65PP481-VS | CIL3 LOADED CARBON PUMP LV VSD | SUBSTATION 68 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10031 | 650 | 0 | 2
F65PP481VS-D1 | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | F65PP481-VS | CIL3 LOADED CARBON PUMP LV VSD | SUBSTATION 68 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10031 | 650 | 0 | 2
F30RIO402-P1 | 30-DB-62 | SUBSTATION 68 240V INSTRUMENT DISTRIBUTION BOARD | SUBSTATION 68 | F30-RIO-402 | CONCENTRATE LEACH AND ADSORPTION FIELD N-IO PANEL | CIL3 PIPERACK | 10 | 0.6/1 | 90 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-SCM-IC-10421 | 300 | 0 | 2
F30RIO403-P1 | 30-DB-62 | SUBSTATION 68 240V INSTRUMENT DISTRIBUTION BOARD | SUBSTATION 68 | F30-RIO-403 | CONCENTRATE LEACH AND ADSORPTION FIELD N-IO PANEL | ELUTION / CIL2 SOUTH | 10 | 0.6/1 | 80 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-SCM-IC-10441 | 300 | 0 | 2
F30RIO401/F30RIO403-FO1 | F30-RIO-401 | CONCENTRATE LEACH AND ADSORPTION FIELD N-IO PANEL | CIRCUIT WATER TANK | F30-RIO-403 | CONCENTRATE LEACH AND ADSORPTION FIELD N-IO PANEL | ELUTION / CIL2 SOUTH | 9/125µm | N/A | 115 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero |  | 2000-F30-TER-IC-10440 | 300 | 0 | 2
F30RIO403/F30RIO402-FO1 | F30-RIO-403 | CONCENTRATE LEACH AND ADSORPTION FIELD N-IO PANEL | ELUTION / CIL2 SOUTH | F30-RIO-402 | CONCENTRATE LEACH AND ADSORPTION FIELD N-IO PANEL | CIL3 PIPERACK | 9/125µm | N/A | 140 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero |  | 2000-F30-TER-IC-10420 | 300 | 0 | 2
F30RIO402/65COM02-FO1 | F30-RIO-402 | CONCENTRATE LEACH AND ADSORPTION FIELD N-IO PANEL | CIL3 PIPERACK | 65-COM-02 | SUBSTATION 68 COMMUNICATIONS RACK | SUBSTATION 68 | 9/125µm | N/A | 100 | 12C | OS2 SMOF | Gel-filled Loose Tube, FRP center, Water Blocking Tape, PE sheath, Nylon Jacket, UV Stabilised, Sacrificial PE Sheath | Black | Ladder - Comms | Primero | Primero |  | 2000-F30-TER-IC-10001 | 300 | 0 | 2
F30PP415-P1 | F30PP415-VS | CONCENTRATE PRE-LEACH THICKENER U/F PUMP 1 LV VSD | SUBSTATION 68 | F30-PP-415 | CONCENTRATE PRE-LEACH THICKENER U/F PUMP 1 | CONCENTRATE PRE-LEACH THICKENER (30-TH-31) | 25 | 0.6/1 | 165 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-SCM-EL-10001 | 300 | 0 | 2
F30PP415LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP415-LCS | CONCENTRATE PRE-LEACH THICKENER U/F PUMP 1 LOCAL CONTROL STATION | CONCENTRATE PRE-LEACH THICKENER (30-TH-31) | 1.5 | 0.6/1 | 165 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10001 | 300 | 0 | 2
F30PP416-P1 | F30PP416-VS | CONCENTRATE PRE-LEACH THICKENER U/F PUMP 2 LV VSD | SUBSTATION 68 | F30-PP-416 | CONCENTRATE PRE-LEACH THICKENER U/F PUMP 2 | CONCENTRATE PRE-LEACH THICKENER (30-TH-31) | 25 | 0.6/1 | 170 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-SCM-EL-10002 | 300 | 0 | 2
F30PP416LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP416-LCS | CONCENTRATE PRE-LEACH THICKENER U/F PUMP 2 LOCAL CONTROL STATION | CONCENTRATE PRE-LEACH THICKENER (30-TH-31) | 1.5 | 0.6/1 | 170 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10002 | 300 | 0 | 2
F30PP426-P1 | F30PP426-VS | CONCENTRATE LEACH TRANSFER PUMP 1 LV VSD | SUBSTATION 68 | F30-PP-426 | CONCENTRATE LEACH TRANSFER PUMP 1 | CIL2 TANK F (SOUTH) | 70 | 0.6/1 | 120 | 3C+3E | Cu | XLPE/PVC/ATC Braiding/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10003 | 300 | 0 | 2
F30PP426LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP426-LCS | CONCENTRATE LEACH TRANSFER PUMP 1 LOCAL CONTROL STATION | CIL2 TANK F (SOUTH) | 1.5 | 0.6/1 | 120 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10003 | 300 | 0 | 2
F30PP426-I1 | F30PP426-VS | CONCENTRATE LEACH TRANSFER PUMP 1 LV VSD | SUBSTATION 68 | F30-PP-426 | CONCENTRATE LEACH TRANSFER PUMP 1 THERMISTOR | CIL2 TANK F (SOUTH) | 1.5 | 0.11 | 120 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10003 | 300 | 0 | 2
F30PP427-P1 | F30PP427-VS | CONCENTRATE LEACH TRANSFER PUMP 2 LV VSD | SUBSTATION 68 | F30-PP-427 | CONCENTRATE LEACH TRANSFER PUMP 2 | CIL2 TANK F (SOUTH) | 70 | 0.6/1 | 120 | 3C+3E | Cu | XLPE/PVC/ATC Braiding/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10004 | 300 | 0 | 2
F30PP427LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP427-LCS | CONCENTRATE LEACH TRANSFER PUMP 2 LOCAL CONTROL STATION | CIL2 TANK F (SOUTH) | 1.5 | 0.6/1 | 120 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10004 | 300 | 0 | 2
F30PP427-I1 | F30PP427-VS | CONCENTRATE LEACH TRANSFER PUMP 2 LV VSD | SUBSTATION 68 | F30-PP-427 | CONCENTRATE LEACH TRANSFER PUMP 2 THERMISTOR | CIL2 TANK F (SOUTH) | 1.5 | 0.11 | 120 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10004 | 300 | 0 | 2
F30PP428-P1 | F30PP428-VS | CIL3 TAILS PUMP 1 LV VSD | SUBSTATION 68 | F30-PP-428 | CIL3 TAILS PUMP 1 | CIL3 TAILS AREA | 50 | 0.6/1 | 150 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10005 | 300 | 0 | 2
F30PP428LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP428-LCS | CIL3 TAILS PUMP 1 LOCAL CONTROL STATION | CIL3 TAILS AREA | 1.5 | 0.6/1 | 150 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10005 | 300 | 0 | 2
F30PP428-I1 | F30PP428-VS | CIL3 TAILS PUMP 1 LV VSD | SUBSTATION 68 | F30-PP-428 | CIL3 TAILS PUMP 1 THERMISTOR | CIL3 TAILS AREA | 1.5 | 0.11 | 150 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10005 | 300 | 0 | 3
F30PP429-P1 | F30PP429-VS | CIL3 TAILS PUMP 2 LV VSD | SUBSTATION 68 | F30-PP-429 | CIL3 TAILS PUMP 2 | CIL3 TAILS AREA | 50 | 0.6/1 | 150 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10006 | 300 | 0 | 3
F30PP429LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP429-LCS | CIL3 TAILS PUMP 2 LOCAL CONTROL STATION | CIL3 TAILS AREA | 1.5 | 0.6/1 | 150 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10006 | 300 | 0 | 3
F30PP429-I1 | F30PP429-VS | CIL3 TAILS PUMP 2 LV VSD | SUBSTATION 68 | F30-PP-429 | CIL3 TAILS PUMP 2 THERMISTOR | CIL3 TAILS AREA | 1.5 | 0.11 | 150 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10006 | 300 | 0 | 3
F30PP496-P1 | F30PP496-VS | ACID EFFLUENT & FINE CARBON PUMP 1 LV VSD | SUBSTATION 68 | F30-PP-496 | ACID EFFLUENT & FINE CARBON PUMP 1 | CIL3 TAILS AREA | 70 | 0.6/1 | 160 | 3C+3E | Cu | XLPE/PVC/ATC Braiding/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10020 | 300 | 0 | 3
F30PP496LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP496-LCS | ACID EFFLUENT & FINE CARBON PUMP 1 LOCAL CONTROL STATION | CIL3 TAILS AREA | 1.5 | 0.6/1 | 160 | 4C+E | Cu | PVC/PVC | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10020 | 300 | 0 | 3
F30PP496-I1 | F30PP496-VS | ACID EFFLUENT & FINE CARBON PUMP 1 LV VSD | SUBSTATION 68 | F30-PP-496 | ACID EFFLUENT & FINE CARBON PUMP 1 THERMISTOR | CIL3 TAILS AREA | 1.5 | 0.11 | 160 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10020 | 300 | 0 | 3
F30PP497-P1 | F30PP497-VS | ACID EFFLUENT & FINE CARBON PUMP 2 LV VSD | SUBSTATION 68 | F30-PP-497 | ACID EFFLUENT & FINE CARBON PUMP 2 | CIL3 TAILS AREA | 70 | 0.6/1 | 160 | 3C+3E | Cu | XLPE/PVC/ATC Braiding/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10032 | 300 | 0 | 3
F30PP497LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP497-LCS | ACID EFFLUENT & FINE CARBON PUMP 2 LOCAL CONTROL STATION | CIL3 TAILS AREA | 1.5 | 0.6/1 | 160 | 4C+E | Cu | PVC/PVC | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10032 | 300 | 0 | 3
F30PP497-I1 | F30PP497-VS | ACID EFFLUENT & FINE CARBON PUMP 2 LV VSD | SUBSTATION 68 | F30-PP-497 | ACID EFFLUENT & FINE CARBON PUMP 2 THERMISTOR | CIL3 TAILS AREA | 1.5 | 0.11 | 160 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10032 | 300 | 0 | 3
F30SA442-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30-SA-442 | CIL2 FEED SECONDARY SAMPLER | CONCENTRATE PRE-LEACH THICKENER (30-TH-31) | 2.5 | 0.6/1 | 150 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-SCM-EL-10021 | 300 | 0 | 3
F30SA442LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30SA442-LCS | CIL2 FEED SECONDARY SAMPLER LOCAL CONTROL STATION | CONCENTRATE PRE-LEACH THICKENER (30-TH-31) | 1.5 | 0.6/1 | 150 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10021 | 300 | 0 | 3
F30SC412JB-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30SC412-JB | CIL3 BARREN CARBON SIZING SCREEN JUNCTION BOX | CIL3 UPPER PLATFORM / TANKS E & F | 2.5 | 0.6/1 | 155 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-SCM-EL-10015 | 300 | 0 | 3
F30SC412JB-P2 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30SC412-JB | CIL3 BARREN CARBON SIZING SCREEN JUNCTION BOX | CIL3 UPPER PLATFORM / TANKS E & F | 2.5 | 0.6/1 | 155 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-SCM-EL-10015 | 300 | 0 | 3
F30SC412A-P1 | F30SC412-JB | CIL3 BARREN CARBON SIZING SCREEN JUNCTION BOX | CIL3 UPPER PLATFORM / TANKS E & F | F30-SC-412A | CIL3 BARREN CARBON SIZING SCREEN MOTOR 1 | CIL3 UPPER PLATFORM / TANKS E & F | VENDOR | VENDOR | 5 | 3C+E | VENDOR | VENDOR FLEX LEAD | VENDOR | Final Run | Vendor - ME011 | Primero | Flexible cable from JB to motor | 2000-F30-SCM-EL-10015 | 300 | 0 | 3
F30SC412B-P1 | F30SC412-JB | CIL3 BARREN CARBON SIZING SCREEN JUNCTION BOX | CIL3 UPPER PLATFORM / TANKS E & F | F30-SC-412B | CIL3 BARREN CARBON SIZING SCREEN MOTOR 2 | CIL3 UPPER PLATFORM / TANKS E & F | VENDOR | VENDOR | 5 | 3C+E | VENDOR | VENDOR FLEX LEAD | VENDOR | Final Run | Vendor - ME011 | Primero | Flexible cable from JB to motor | 2000-F30-SCM-EL-10015 | 300 | 0 | 3
F30SC412LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30SC412-LCS | CIL3 BARREN CARBON SIZING SCREEN LOCAL CONTROL STATION | CIL3 UPPER PLATFORM / TANKS E & F | 1.5 | 0.6/1 | 155 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10015 | 300 | 0 | 3
F30TK32APP01-P1 | 30-VS-62A | CIL2 OXYGEN INJECTION PUMP 1 LV VSD | SUBSTATION 68 | F30TK32A-PP01 | CIL2 OXYGEN INJECTION PUMP 1 | CIL2 TANK A (NORTH) | 120 | 0.6/1 | 105 | 3C+3E | Cu | XLPE/PVC/ATC Braiding/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10010 | 300 | 0 | 3
F30TK32APP01-P2 | 30-VS-62A | CIL2 OXYGEN INJECTION PUMP 1 LV VSD | SUBSTATION 68 | F30TK32A-PP01 | CIL2 OXYGEN INJECTION PUMP 1 | CIL2 TANK A (NORTH) | 120 | 0.6/1 | 105 | 3C+3E | Cu | XLPE/PVC/ATC Braiding/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10010 | 300 | 0 | 3
F30TK32APP01-P3 | 30-VS-62A | CIL2 OXYGEN INJECTION PUMP 1 LV VSD | SUBSTATION 68 | F30TK32A-PP01 | CIL2 OXYGEN INJECTION PUMP 1 SPACE HEATER | CIL2 TANK A (NORTH) | 2.5 | 0.6/1 | 105 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-SCM-EL-10010 | 300 | 0 | 3
F30TK32APP01JB-C1 | 30PC62-DR | SUBSTATION 68 DCS CABINET DR - TERMINAL STRIP TS-K | SUBSTATION 68 | F30TK32APP01-JB | CIL2 OXYGEN INJECTION PUMP 1 JUNCTION BOX | CIL2 TANK A (NORTH) | 1.5 | 0.6/1 | 110 | 2C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 110VAC | 2000-F30-TER-IC-10475 | 300 | 0 | 3
F30TK32APP01JB-C2 | 30PC62-BR | SUBSTATION 68 DCS CABINET BR - TERMINAL STRIP TS-E | SUBSTATION 68 | F30TK32APP01-JB | CIL2 OXYGEN INJECTION PUMP 1 JUNCTION BOX | CIL2 TANK A (NORTH) | 1.5 | 0.6/1 | 110 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 24VDC | 2000-F30-TER-IC-10475 | 300 | 0 | 3
F30TK32APP01LCS-C1 | F30TK32APP01-JB | CIL2 OXYGEN INJECTION PUMP 1 JUNCTION BOX | CIL2 TANK A (NORTH) | F30TK32APP01-LCS | CIL2 OXYGEN INJECTION PUMP 1 LOCAL CONTROL STATION | CIL2 TANK A (NORTH) | 1.5 | 0.6/1 | 5 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-TER-IC-10475 | 300 | 0 | 3
F30TK32BPP01-P1 | 30-VS-62C | CIL2 OXYGEN INJECTION PUMP 2 LV VSD | SUBSTATION 68 | F30TK32B-PP01 | CIL2 OXYGEN INJECTION PUMP 2 | CIL2 TANK B (SOUTH) | 120 | 0.6/1 | 75 | 3C+3E | Cu | XLPE/PVC/ATC Braiding/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10009 | 300 | 0 | 3
F30TK32BPP01-P2 | 30-VS-62C | CIL2 OXYGEN INJECTION PUMP 2 LV VSD | SUBSTATION 68 | F30TK32B-PP01 | CIL2 OXYGEN INJECTION PUMP 2 | CIL2 TANK B (SOUTH) | 120 | 0.6/1 | 75 | 3C+3E | Cu | XLPE/PVC/ATC Braiding/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10009 | 300 | 0 | 3
F30TK32BPP01-P3 | 30-VS-62C | CIL2 OXYGEN INJECTION PUMP 2 LV VSD | SUBSTATION 68 | F30TK32B-PP01 | CIL2 OXYGEN INJECTION PUMP 2 SPACE HEATER | CIL2 TANK B (SOUTH) | 2.5 | 0.6/1 | 75 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-SCM-EL-10009 | 300 | 0 | 3
F30TK32BPP01JB-C1 | 30PC62-DR | SUBSTATION 68 DCS CABINET DR - TERMINAL STRIP TS-K | SUBSTATION 68 | F30TK32BPP01-JB | CIL2 OXYGEN INJECTION PUMP 2 JUNCTION BOX | CIL2 TANK B (SOUTH) | 1.5 | 0.6/1 | 80 | 2C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 110VAC | 2000-F30-TER-IC-10475 | 300 | 0 | 3
F30TK32BPP01JB-C2 | 30PC62-BR | SUBSTATION 68 DCS CABINET BR - TERMINAL STRIP TS-E | SUBSTATION 68 | F30TK32BPP01-JB | CIL2 OXYGEN INJECTION PUMP 2 JUNCTION BOX | CIL2 TANK B (SOUTH) | 1.5 | 0.6/1 | 80 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 24VDC | 2000-F30-TER-IC-10475 | 300 | 0 | 3
F30TK32BPP01LCS-C1 | F30TK32BPP01-JB | CIL2 OXYGEN INJECTION PUMP 2 JUNCTION BOX | CIL2 TANK B (SOUTH) | F30TK32BPP01-LCS | CIL2 OXYGEN INJECTION PUMP 2 LOCAL CONTROL STATION | CIL2 TANK B (SOUTH) | 1.5 | 0.6/1 | 5 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-TER-IC-10475 | 300 | 0 | 3
F30PP476LCS01-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP476-LCS01 | CIL3 TANK A LOADED CARBON RECOVERY PUMP LOCAL CONTROL STATION 1 | CIL3 UPPER PLATFORM / TANK A | 50 | 0.6/1 | 70 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero |  | 2000-F30-SCM-EL-10029 | 300 | 0 | 3
F30PP476LCS01-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP476-LCS01 | CIL3 TANK A LOADED CARBON RECOVERY PUMP LOCAL CONTROL STATION 1 | CIL3 UPPER PLATFORM / TANK A | 1.5 | 0.6/1 | 70 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10029 | 300 | 0 | 3
F30PP476LCS01-I1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F30PP476-LCS01 | CIL3 TANK A LOADED CARBON RECOVERY PUMP LOCAL CONTROL STATION 1 | CIL3 UPPER PLATFORM / TANK A | 1.5 | 0.11 | 70 | 1PR | Cu | PVC/OSCN/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | Thermistor cable | 2000-F30-SCM-EL-10029 | 300 | 0 | 3
F30PP476LCS02-P1 | F30PP476-LCS01 | CIL3 TANK A LOADED CARBON RECOVERY PUMP LOCAL CONTROL STATION 1 | CIL3 UPPER PLATFORM / TANK A | F30PP476-LCS02 | CIL3 TANK A LOADED CARBON RECOVERY PUMP LOCAL CONTROL STATION 2 | CIL3 UPPER PLATFORM / TANK B | 70 | 0.6/1 | 30 | 3C+E | Cu | EPR/CSP | Black | Ladder - Single Layer Touching | Primero | Primero | Terminated within New Macey Plug. | 2000-F30-SCM-EL-10029 | 300 | 0 | 3
F30PP476LCS02-C1 | F30PP476-LCS01 | CIL3 TANK A LOADED CARBON RECOVERY PUMP LOCAL CONTROL STATION 1 | CIL3 UPPER PLATFORM / TANK A | F30PP476-LCS02 | CIL3 TANK A LOADED CARBON RECOVERY PUMP LOCAL CONTROL STATION 2 | CIL3 UPPER PLATFORM / TANK B | 1.5 | 0.6/1 | 30 | 6C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10029 | 300 | 0 | 3
F30PP476LCS02-I1 | F30PP476-LCS01 | CIL3 TANK A LOADED CARBON RECOVERY PUMP LOCAL CONTROL STATION 1 | CIL3 UPPER PLATFORM / TANK A | F30PP476-LCS02 | CIL3 TANK A LOADED CARBON RECOVERY PUMP LOCAL CONTROL STATION 2 | CIL3 UPPER PLATFORM / TANK B | 1.5 | 0.3/0.5 | 30 | 4C+E | Cu | PVC/CWS/PVC Flexible Control | Clear | Ladder - Bunched Ctrl/Inst | Primero | Primero | Thermistor + Decontactor status. Terminated within New Macey plug (same as power cable) | 2000-F30-SCM-EL-10029 | 300 | 0 | 3
F30PP476-P1 | F30PP476-LCS01 | CIL3 TANK A LOADED CARBON RECOVERY PUMP LOCAL CONTROL STATION 1 | CIL3 UPPER PLATFORM / TANK A | F30-PP-476 | CIL3 TANK A LOADED CARBON RECOVERY PUMP | CIL3 UPPER PLATFORM / TANK A | 70 | 0.6/1 | 15 | 3C+E | Cu | EPR/CSP | Black | Final Run | Vendor - EL014 | Primero | Terminated in new macey plug | 2000-F30-SCM-EL-10029 | 300 | 0 | 3
F30PP476-I1 | F30PP476-LCS01 | CIL3 TANK A LOADED CARBON RECOVERY PUMP LOCAL CONTROL STATION 1 | CIL3 UPPER PLATFORM / TANK A | F30-PP-476 | CIL3 TANK A LOADED CARBON RECOVERY PUMP THERMISTOR | CIL3 UPPER PLATFORM / TANK A | 1.5 | 0.11 | 15 | 1PR | Cu | PVC/OSCN/PVC | Black | Final Run | Vendor - EL014 | Primero | Terminated in new macey plug | 2000-F30-SCM-EL-10029 | 300 | 0 | 3
F65PP481-P1 | F65PP481-VS | CIL3 LOADED CARBON PUMP LV VSD | SUBSTATION 68 | F65-PP-481 | CIL3 LOADED CARBON PUMP | CIL3 LOADED CARBON SCREEN | 25 | 0.6/1 | 95 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching / Buried in Conduit | Primero | Primero |  | 2000-F30-SCM-EL-10031 | 650 | 0 | 3
F65PP481LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F65PP481-LCS | CIL3 LOADED CARBON PUMP LOCAL CONTROL STATION | CIL3 LOADED CARBON SCREEN | 1.5 | 0.6/1 | 95 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10031 | 650 | 0 | 3
F65SC471JB-P1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F65SC471-JB | CIL3 LOADED CARBON SCREEN JUNCTION BOX | CIL3 LOADED CARBON SCREEN | 2.5 | 0.6/1 | 80 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-SCM-EL-10030 | 650 | 0 | 3
F65SC471JB-P2 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F65SC471-JB | CIL3 LOADED CARBON SCREEN JUNCTION BOX | CIL3 LOADED CARBON SCREEN | 2.5 | 0.6/1 | 80 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-SCM-EL-10030 | 650 | 0 | 3
F65SC471A-P1 | F65SC471-JB | CIL3 LOADED CARBON SCREEN JUNCTION BOX | CIL3 LOADED CARBON SCREEN | F65-SC-471A | CIL3 LOADED CARBON SCREEN MOTOR 1 | CIL3 LOADED CARBON SCREEN | VENDOR | VENDOR | 5 | 3C+E | VENDOR | VENDOR FLEX LEAD | VENDOR | Final Run | Vendor - ME108 | Vendor - ME108 | Flexible cable from JB to motor, pre-terminated at both ends by vendor. | 2000-F30-SCM-EL-10030 | 650 | 0 | 3
F65SC471B-P1 | F65SC471-JB | CIL3 LOADED CARBON SCREEN JUNCTION BOX | CIL3 LOADED CARBON SCREEN | F65-SC-471B | CIL3 LOADED CARBON SCREEN MOTOR 2 | CIL3 LOADED CARBON SCREEN | VENDOR | VENDOR | 5 | 3C+E | VENDOR | VENDOR FLEX LEAD | VENDOR | Final Run | Vendor - ME108 | Vendor - ME108 | Flexible cable from JB to motor, pre-terminated at both ends by vendor. | 2000-F30-SCM-EL-10030 | 650 | 0 | 3
F65SC471LCS-C1 | F30-SW-401 | CIL 3 415V MCC | SUBSTATION 68 | F65SC471-LCS | CIL3 LOADED CARBON SCREEN LOCAL CONTROL STATION | CIL3 LOADED CARBON SCREEN | 1.5 | 0.6/1 | 80 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero |  | 2000-F30-SCM-EL-10030 | 650 | 0 | 3
F72PK407-P1 | 30-DB-68A | SUBSTATION 68 DISTRIBUTION BOARD 68A | SUBSTATION 68 | F72-PK-407 | ANTISCALANT DOSING SKID 2 | EXISTING ELUTION | 10 | 0.6/1 | 90 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-TLD-EL-10003 | 720 | 0 | 3
F72PK408-P1 | 30-DB-68A | SUBSTATION 68 DISTRIBUTION BOARD 68A | SUBSTATION 68 | F72-PK-408 | ANTISCALANT DOSING SKID 3 | EXISTING ELUTION | 16 | 0.6/1 | 115 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-TLD-EL-10003 | 720 | 0 | 3
F72PK409-P1 | 30-DB-68A | SUBSTATION 68 DISTRIBUTION BOARD 68A | SUBSTATION 68 | F72-PK-409 | ANTISCALANT DOSING SKID 4 | EXISTING ELUTION | 16 | 0.6/1 | 115 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-TLD-EL-10003 | 720 | 0 | 3
F30CA422-P1 | 30-DB-68A | SUBSTATION 68 DISTRIBUTION BOARD 68A | SUBSTATION 68 | F30-CA-422 | CIL2 CYANIDE ANALYSER 2 | CIL2 UPPER PLATFORM / TANK D | 25 | 0.6/1 | 115 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-TLD-EL-10003 | 300 | 0 | 3
F30CA423-P1 | 30-DB-68A | SUBSTATION 68 DISTRIBUTION BOARD 68A | SUBSTATION 68 | F30-CA-423 | CIL2 CYANIDE ANALYSER 3 | CIL2 UPPER PLATFORM / TANK F | 25 | 0.6/1 | 135 | 2C+E | Cu | XLPE/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero |  | 2000-F30-TLD-EL-10003 | 300 | 0 | 3