## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | Length (m) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred colour) | Installation Method | Supplied By | Installed By | Reference Drawing (SLD/SCM/TER) | Area | Rev | Comments | Page
34PC01ER-P1 | 34PC01-BF | SUBSTATION 10 PROCESS CONTROL CABINET BF - 24VDC-2 CIRCUIT BREAKER | SUBSTATION 10 | 34PC01-ER | SUBSTATION 10 PROCESS CONTROL CABINET ER | SUBSTATION 10 | 10 | 0.6/1 | 10 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F34-TER-IC-10004 | 340 | 0 |  | 2
F34PP443-C1 | 34PC01-ER | SUBSTATION 10 PROCESS CONTROL CABINET ER | SUBSTATION 10 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC - F34-PP-443 MODULE 24VDC MCB | SUBSTATION 10 | 1.5 | 0.6/1 | 15 | 2C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10001 | 340 | 0 |  | 2
F35PP435-C1 | 34PC01-ER | SUBSTATION 10 PROCESS CONTROL CABINET ER | SUBSTATION 10 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC - F35-PP-435 MODULE 24VDC MCB | SUBSTATION 10 | 1.5 | 0.6/1 | 15 | 2C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10002 | 340 | 0 |  | 2
F35PP448-C1 | 34PC01-ER | SUBSTATION 10 PROCESS CONTROL CABINET ER | SUBSTATION 10 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC - F35-PP-448 MODULE 24VDC MCB | SUBSTATION 10 | 1.5 | 0.6/1 | 15 | 2C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10003 | 340 | 0 |  | 2
F35PP449-C1 | 34PC01-ER | SUBSTATION 10 PROCESS CONTROL CABINET ER | SUBSTATION 10 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC - F35-PP-449 MODULE 24VDC MCB | SUBSTATION 10 | 1.5 | 0.6/1 | 15 | 2C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10004 | 340 | 0 |  | 2
F34ETH401-FO1 | 34PC01-AF | SUBSTATION 10 PROCESS CONTROL CABINET AF - SUB60 FOBOT | SUBSTATION 10 | 34PC01-AF | SUBSTATION 10 PROCESS CONTROL CABINET AF - F34-ETH-401 | SUBSTATION 10 | 9/125µm | N/A | 2 | 2C | OS2 SMOF | Single Mode Fibre Patch Lead (SC-LC) | Yellow | Within Cabinet | Primero | Primero | 2000-F34-TER-IC-10001 | 340 | 0 | Modbus Network - to Sub60. | 2
FCS0213-D1 | 34PC01-AF | SUBSTATION 10 PROCESS CONTROL CABINET AF - F34-ETH-401 | SUBSTATION 10 | 34PC01-BF | SUBSTATION 10 PROCESS CONTROL CABINET BF - FCS0213N1S6 ALE111 CARD | SUBSTATION 10 | N/A | N/A | 5 | 4PR | Cu | CAT6 | Green | Within Cabinet | Primero | Primero | 2000-F34-TER-IC-10001 | 340 | 0 |  | 2
F34PP443VS-P1 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC | SUBSTATION 10 | F34PP443-VS | UFG MILL 1 PRODUCT PUMP LV VSD | SUBSTATION 10 | 16 | 0.6/1 | 30 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Single Layer Touching | Primero | Primero | 2000-F34-SCM-EL-10001 | 340 | 0 |  | 2
F34PP443VS-C1 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC | SUBSTATION 10 | F34PP443-VS | UFG MILL 1 PRODUCT PUMP LV VSD | SUBSTATION 10 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10001 | 340 | 0 |  | 2
F34PP443VS-D1 | 34PC01-AF | SUBSTATION 10 PROCESS CONTROL CABINET AF | SUBSTATION 10 | F34PP443-VS | UFG MILL 1 PRODUCT PUMP LV VSD | SUBSTATION 10 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10001 | 340 | 0 |  | 2
F35PP448VS-P1 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC | SUBSTATION 10 | F35PP448-VS | UFG CIRCUIT 2 FEED PUMP LV VSD | SUBSTATION 10 | 10 | 0.6/1 | 30 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 2000-F34-SCM-EL-10003 | 350 | 0 |  | 2
F35PP448VS-C1 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC | SUBSTATION 10 | F35PP448-VS | UFG CIRCUIT 2 FEED PUMP LV VSD | SUBSTATION 10 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10003 | 350 | 0 |  | 2
F35PP448VS-D1 | 34PC01-AF | SUBSTATION 10 PROCESS CONTROL CABINET AF | SUBSTATION 10 | F35PP448-VS | UFG CIRCUIT 2 FEED PUMP LV VSD | SUBSTATION 10 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10003 | 350 | 0 |  | 2
F35PP435VS-P1 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC | SUBSTATION 10 | F35PP435-VS | UFG CIRCUIT 1 FEED PUMP LV VSD | SUBSTATION 10 | 4 | 0.6/1 | 30 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 2000-F34-SCM-EL-10002 | 350 | 0 |  | 2
F35PP435VS-C1 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC | SUBSTATION 10 | F35PP435-VS | UFG CIRCUIT 1 FEED PUMP LV VSD | SUBSTATION 10 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10002 | 350 | 0 |  | 2
F35PP435VS-D1 | 34PC01-AF | SUBSTATION 10 PROCESS CONTROL CABINET AF | SUBSTATION 10 | F35PP435-VS | UFG CIRCUIT 1 FEED PUMP LV VSD | SUBSTATION 10 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10002 | 350 | 0 |  | 2
F35PP449VS-P1 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC | SUBSTATION 10 | F35PP449-VS | UFG CIRCUIT 3 FEED PUMP LV VSD | SUBSTATION 10 | 10 | 0.6/1 | 30 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 2000-F34-SCM-EL-10004 | 350 | 0 |  | 2
F35PP449VS-C1 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC | SUBSTATION 10 | F35PP449-VS | UFG CIRCUIT 3 FEED PUMP LV VSD | SUBSTATION 10 | 1.5 | 0.6/1 | 30 | 10C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10004 | 350 | 0 |  | 2
F35PP449VS-D1 | 34PC01-AF | SUBSTATION 10 PROCESS CONTROL CABINET AF | SUBSTATION 10 | F35PP449-VS | UFG CIRCUIT 3 FEED PUMP LV VSD | SUBSTATION 10 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10004 | 350 | 0 |  | 2
F34PP443-P1 | F34PP443-VS | UFG MILL 1 PRODUCT PUMP LV VSD | SUBSTATION 10 | F34-PP-443 | UFG MILL 1 PRODUCT PUMP | UFG1 CLASSIFICATION BUILDING | 16 | 0.6/1 | 75 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Single Layer Touching | Primero | Primero | 2000-F34-SCM-EL-10001 | 340 | 0 |  | 2
F34PP443LCS-C1 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC | SUBSTATION 10 | F34PP443-LCS | UFG MILL 1 PRODUCT PUMP LOCAL CONTROL STATION | UFG1 CLASSIFICATION BUILDING | 1.5 | 0.6/1 | 75 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10001 | 340 | 0 |  | 2
F35PP448-P1 (Stage 1) | F35PP448-VS | UFG CIRCUIT 2 FEED PUMP LV VSD | SUBSTATION 10 | F35-PP-448 | UFG CIRCUIT 2 FEED PUMP (STAGE 1) | FILTER FEED TANK A (F35-TK-01A) | 16 | 0.6/1 | 180 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 2000-F34-SCM-EL-10003 | 350 | 0 | Becomes F35PP435-P1 in STAGE 2. Leave adequate spare length at both ends to allow re-use. | 2
F35PP448LCS-C1 (Stage 1) | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC | SUBSTATION 10 | F35PP448-LCS | UFG CIRCUIT 2 FEED PUMP LOCAL CONTROL STATION (STAGE 1) | FILTER FEED TANK A (F35-TK-01A) | 1.5 | 0.6/1 | 180 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10003 | 350 | 0 | Becomes F35PP435LCS-C1 in Stage 2. Leave adequate spare length at both ends to allow re-use. | 2
F35PP435-P1 (Stage 2) | F35PP435-VS | UFG CIRCUIT 1 FEED PUMP LV VSD | SUBSTATION 10 | F35-PP-435 | UFG CIRCUIT 1 FEED PUMP | FILTER FEED TANK A (F35-TK-01A) | 16 | 0.6/1 | 0 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 2000-F34-SCM-EL-10002 | 350 | 0 | RE-PURPOSE EXISTING F35PP448-P1 STAGE 1 CABLE. | 2
F35PP435LCS-C1 (Stage 2) | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC | SUBSTATION 10 | F35PP435-LCS | UFG CIRCUIT 1 FEED PUMP LOCAL CONTROL STATION | FILTER FEED TANK A (F35-TK-01A) | 1.5 | 0.6/1 | 0 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10002 | 350 | 0 | RE-PURPOSE EXISTING F35PP448LCS-C1 STAGE 1 CABLE. | 2
F35PP448-P1 (Stage 2) | F35PP448-VS | UFG CIRCUIT 2 FEED PUMP LV VSD | SUBSTATION 10 | F35-PP-448 | UFG CIRCUIT 2 FEED PUMP (STAGE 2) | FILTER FEED TANK A & B (F35-TK- 01A & B) | 16 | 0.6/1 | 145 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 2000-F34-SCM-EL-10003 | 350 | 0 | INSTALL FOR STAGE 2 LOCATION OF F35-PP-448. | 2
F35PP448LCS-C1 (Stage 2) | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC | SUBSTATION 10 | F35PP448-LCS | UFG CIRCUIT 2 FEED PUMP LOCAL CONTROL STATION (STAGE 2) | FILTER FEED TANK A & B (F35-TK- 01A & B) | 1.5 | 0.6/1 | 145 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10003 | 350 | 0 | INSTALL FOR STAGE 2 LOCATION OF F35-PP-448. | 2
F35PP449-P1 | F35PP449-VS | UFG CIRCUIT 3 FEED PUMP LV VSD | SUBSTATION 10 | F35-PP-449 | UFG CIRCUIT 3 FEED PUMP | FILTER FEED TANK A & B (F35-TK- 01A & B) | 16 | 0.6/1 | 145 | 3C+3E | Cu | XLPE/PVC/CTS/PVC Flexible | Black | Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 2000-F34-SCM-EL-10004 | 350 | 0 |  | 2
F35PP449LCS-C1 | 34-SW-02 | ULTRA FINE GRINDING PLANT 415V MCC | SUBSTATION 10 | F35PP449-LCS | UFG CIRCUIT 3 FEED PUMP LOCAL CONTROL STATION | FILTER FEED TANK A & B (F35-TK- 01A & B) | 1.5 | 0.6/1 | 145 | 4C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F34-SCM-EL-10004 | 350 | 0 |  | 2