## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | Length (m) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred colour) | Installation Method | Supplied By | Installed By | Reference Drawing (SLD/SCM/TER) | Area | Rev | Comments | Page
F66SW402-P1-R | 20-SW-62 | GRINDING 415V MCC - TIER 1F FEEDER | SUBSTATION 35 | F66-SW-402 | GOLDROOM 415V MCC - INCOMING MODULE | SUBSTATION 35 | 240 | 0.6/1 | 15 | 1C | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer in Trefoil | Primero | Primero | 2000-F66-SLD-EL-10101 | 660 | 0 |  | 2
F66SW402-P1-W | 20-SW-62 | GRINDING 415V MCC - TIER 1F FEEDER | SUBSTATION 35 | F66-SW-402 | GOLDROOM 415V MCC - INCOMING MODULE | SUBSTATION 35 | 240 | 0.6/1 | 15 | 1C | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer in Trefoil | Primero | Primero | 2000-F66-SLD-EL-10101 | 660 | 0 |  | 2
F66SW402-P1-B | 20-SW-62 | GRINDING 415V MCC - TIER 1F FEEDER | SUBSTATION 35 | F66-SW-402 | GOLDROOM 415V MCC - INCOMING MODULE | SUBSTATION 35 | 240 | 0.6/1 | 15 | 1C | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer in Trefoil | Primero | Primero | 2000-F66-SLD-EL-10101 | 660 | 0 |  | 2
F66SW402-N1 | 20-SW-62 | GRINDING 415V MCC - TIER 1F FEEDER | SUBSTATION 35 | F66-SW-402 | GOLDROOM 415V MCC - INCOMING MODULE | SUBSTATION 35 | 240 | 0.6/1 | 15 | 1C | Cu | XLPE/PVC Flexible | Orange | Ladder - Single Layer in Trefoil | Primero | Primero | 2000-F66-SLD-EL-10101 | 660 | 0 |  | 2
F66SW402-E1 | 20-SW-62 | GRINDING 415V MCC - TIER 1F FEEDER | SUBSTATION 35 | F66-SW-402 | GOLDROOM 415V MCC - MAIN EARTH BAR | SUBSTATION 35 | 120 | 0.6/1 | 20 | 1C | Cu | PVC | Green/Yellow | Ladder - Single Layer | Primero | Primero | 2000-F66-SLD-EL-10101 | 660 | 0 |  | 2
F66SW402-E2 | -- | SUBSTATION NO.35B EARTH BAR | SUBSTATION 35 | F66-SW-402 | GOLDROOM 415V MCC - MAIN EARTH BAR | SUBSTATION 35 | 120 | 0.6/1 | 20 | 1C | Cu | PVC | Green/Yellow | Ladder - Single Layer | Primero | Primero | 2000-F66-SLD-EL-10101 | 660 | 0 |  | 2
F66SW402-P2 | 20PC61-BR | SUBSTATION 35B DCS (MILLING) CABINET BR | SUBSTATION 35 | F66-SW-402 | GOLDROOM 415V MCC FRONT TIER | SUBSTATION 35 | 4 | 0.6/1 | 15 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F20-TER-IC-10001 | 660 | 0 |  | 2
F66SW402-P3 | 20PC61-BR | SUBSTATION 35B DCS (MILLING) CABINET BR | SUBSTATION 35 | F66-SW-402 | GOLDROOM 415V MCC REAR TIER | SUBSTATION 35 | 4 | 0.6/1 | 15 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F20-TER-IC-10001 | 660 | 0 |  | 2
F66SW402-P4 | 20-SW-62 | GRINDING 415V MCC - TIER 00F | SUBSTATION 68 | F66-SW-402 | GOLDROOM 415V MCC - TIER 1F VAMP10LD IO UNIT | SUBSTATION 68 | 1.5 | 0.6/1 | 15 | 2C+E | Cu | PVC/PVC | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | TBA | 660 | 0 | 24VDC supply to VAMP10LD arc flash units | 2
F66SW402-D1 | 20-SW-62 | GRINDING 415V MCC - TIER 00F | SUBSTATION 68 | F66-SW-402 | GOLDROOM 415V MCC - TIER 1F VAMP10LD IO UNIT | SUBSTATION 68 | Vendor | Vendor | 15 | Vendor | Vendor | VX001 ARC FLASH COMM CABLE | Vendor | Ladder - Bunched Ctrl/Inst | EL001 | Primero | TBA | 660 | 0 | Comms to VAMP10LD arc flash units | 2
F66PW460EOL-D1 | 20PC63-AR | SUBSTATION 35A DCS CABINET AR - F20-ETH-401 | SUBSTATION 35 | F66-SW-402 | GOLDROOM 415V MCC - F66-PW-460 EOL | SUBSTATION 35 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-TER-IC-10021 | 660 | 0 |  | 2
F66PS481EOL-D1 | 20PC63-AR | SUBSTATION 35A DCS CABINET AR - F20-ETH-401 | SUBSTATION 35 | F66-SW-402 | GOLDROOM 415V MCC - F66-PS-481 EOL | SUBSTATION 35 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-TER-IC-10021 | 660 | 0 |  | 2
F66PW461EOL-D1 | 20PC63-AR | SUBSTATION 35A DCS CABINET AR - F20-ETH-401 | SUBSTATION 35 | F66-SW-402 | GOLDROOM 415V MCC - F66-PW-461 EOL | SUBSTATION 35 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-TER-IC-10021 | 660 | 0 |  | 2
F66PW462EOL-D1 | 20PC63-AR | SUBSTATION 35A DCS CABINET AR - F20-ETH-401 | SUBSTATION 35 | F66-SW-402 | GOLDROOM 415V MCC - F66-PW-462 EOL | SUBSTATION 35 | N/A | N/A | 30 | 4PR | Cu | CAT6 | Green | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-TER-IC-10021 | 660 | 0 |  | 2
F66 RUNNING EARTH | -- | SUBSTATION NO.35B EARTH BAR | SUBSTATION 35 |  | GOLDROOM TANKS AREA CABLE LADDER (RUNNING EARTH) | GOLDROOM TANKS AREA | 120 | 0.6/1 | 70 | 1C | Cu | PVC | Green/Yellow | Buried in Conduit | Primero | Primero | N/A | 660 | 0 | Running Earth from Sub35, connect to new cable ladder at goldroom end conduit stub-up. | 2
F66ER401A-D1 | F66-COM-01 | GOLDROOM BUILDING COMMUNICATIONS PANEL | GOLDROOM BUILDING | F66-ER-401A | GRAVITY ELECTROWINNING CELL RECTIFIER 1 | GOLDROOM BUILDING | N/A | N/A | 60 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-SCM-EL-10201 | 660 | 0 |  | 2
F66ER401B-D1 | F66-COM-01 | GOLDROOM BUILDING COMMUNICATIONS PANEL | GOLDROOM BUILDING | F66-ER-401B | GRAVITY ELECTROWINNING CELL RECTIFIER 2 | GOLDROOM BUILDING | N/A | N/A | 60 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-SCM-EL-10202 | 660 | 0 |  | 2
F66ER401A-P1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66-ER-401A | GRAVITY ELECTROWINNING CELL RECTIFIER 1 | GOLDROOM BUILDING | 50 | 0.6/1 | 110 | 3C+E | Cu | XLPE/PVC | Orange | Buried in Conduit (Bunched) / Ladder - Single Layer Touching | Primero | Primero | 2000-F66-SCM-EL-10201 | 660 | 0 |  | 2
F66EC401-P1 | F66-ER-401A | GRAVITY ELECTROWINNING CELL RECTIFIER 1 - POSITIVE (+) BUSBAR | GOLDROOM BUILDING | F66-EC-401 | GRAVITY ELECTROWINNING CELL - RIGHT SIDE ANODE (+) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 3.95 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10201 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC401-P2 | F66-ER-401A | GRAVITY ELECTROWINNING CELL RECTIFIER 1 - POSITIVE (+) BUSBAR | GOLDROOM BUILDING | F66-EC-401 | GRAVITY ELECTROWINNING CELL - RIGHT SIDE ANODE (+) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 4.06 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10201 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC401-N1 | F66-ER-401A | GRAVITY ELECTROWINNING CELL RECTIFIER 1 - NEGATIVE (-) BUSBAR | GOLDROOM BUILDING | F66-EC-401 | GRAVITY ELECTROWINNING CELL - RIGHT SIDE CATHODE (-) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 4.33 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10201 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC401-N2 | F66-ER-401A | GRAVITY ELECTROWINNING CELL RECTIFIER 1 - NEGATIVE (-) BUSBAR | GOLDROOM BUILDING | F66-EC-401 | GRAVITY ELECTROWINNING CELL - RIGHT SIDE CATHODE (-) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 4.22 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10201 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66ER401B-P1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66-ER-401B | GRAVITY ELECTROWINNING CELL RECTIFIER 2 | GOLDROOM BUILDING | 50 | 0.6/1 | 110 | 3C+E | Cu | XLPE/PVC | Orange | Buried in Conduit (Bunched) / Ladder - Single Layer Touching | Primero | Primero | 2000-F66-SCM-EL-10202 | 660 | 0 |  | 2
F66EC401-P3 | F66-ER-401B | GRAVITY ELECTROWINNING CELL RECTIFIER 2 - POSITIVE (+) BUSBAR | GOLDROOM BUILDING | F66-EC-401 | GRAVITY ELECTROWINNING CELL - LEFT SIDE ANODE (+) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 5.5 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10202 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC401-P4 | F66-ER-401B | GRAVITY ELECTROWINNING CELL RECTIFIER 2 - POSITIVE (+) BUSBAR | GOLDROOM BUILDING | F66-EC-401 | GRAVITY ELECTROWINNING CELL - LEFT SIDE ANODE (+) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 5.39 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10202 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC401-N3 | F66-ER-401B | GRAVITY ELECTROWINNING CELL RECTIFIER 2 - NEGATIVE (-) BUSBAR | GOLDROOM BUILDING | F66-EC-401 | GRAVITY ELECTROWINNING CELL - LEFT SIDE CATHODE (-) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 5.16 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10202 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC401-N4 | F66-ER-401B | GRAVITY ELECTROWINNING CELL RECTIFIER 2 - NEGATIVE (-) BUSBAR | GOLDROOM BUILDING | F66-EC-401 | GRAVITY ELECTROWINNING CELL - LEFT SIDE CATHODE (-) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 5.24 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10202 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66PW460-P1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66-PW-460 | GRAVITY ELECTROWINNING PUMP | GOLDROOM TANKS AREA | 4 | 0.6/1 | 80 | 3C+E | Cu | PVC/PVC | Orange | Buried in Conduit (Bunched) / Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 2000-F66-SCM-EL-10208 | 660 | 0 |  | 2
F66PW460-C1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66PW460-LCS | GRAVITY ELECTROWINNING PUMP LOCAL CONTROL STATION | GOLDROOM TANKS AREA | 1.5 | 0.6/1 | 80 | 4C+E | Cu | PVC/PVC | Black | Buried in Conduit (Bunched) / Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-SCM-EL-10208 | 660 | 0 |  | 2
F66PS481LCS-P1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66PS481-LCS | GRAVITY ELECTROWINNING TANK AREA SUMP PUMP LOCAL CONTROL STATION | GOLDROOM TANKS AREA | 35 | 0.6/1 | 80 | 3C+E | Cu | XLPE/PVC | Orange | Buried in Conduit (Bunched) / Ladder - Single Layer Touching | Primero | Primero | 2000-F66-SCM-EL-10209 | 660 | 0 |  | 2
F66PS481-P1 | F66PS481-LCS | GRAVITY ELECTROWINNING TANK AREA SUMP PUMP LOCAL CONTROL STATION | GOLDROOM TANKS AREA | F66-PS-481 | ELECTROWINNING TANK AREA SUMP PUMP | GOLDROOM TANKS AREA | 25 | 0.6/1 | 10 | 3C+E | Cu | EPR/CSP | Black | Final Run | Primero | Primero | 2000-F66-SCM-EL-10209 | 660 | 0 |  | 2
F66PS481LCS-C1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66PS481-LCS | GRAVITY ELECTROWINNING TANK AREA SUMP PUMP LOCAL CONTROL STATION | GOLDROOM TANKS AREA | 1.5 | 0.6/1 | 80 | 6C+E | Cu | PVC/PVC | Black | Buried in Conduit (Bunched) / Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-SCM-EL-10209 | 660 | 0 |  | 2
LSH66424-C1 | F66PS481-LCS | GRAVITY ELECTROWINNING TANK AREA SUMP PUMP LOCAL CONTROL STATION | GOLDROOM TANKS AREA | LSH66424 | F66-PS-481 GRAVITY ELECTROWINNING TANK AREA SUMP PUMP LEVEL SWITCH HIGH | GOLDROOM TANKS AREA | Vendor | Vendor | 5 | 3C | Cu | Vendor | Black | Final Run | Primero | Primero | 2000-F66-SCM-EL-10209 | 660 | 0 | Sump Level Float | 2
F66ER411A-D1 | F66-COM-01 | GOLDROOM BUILDING COMMUNICATIONS PANEL | GOLDROOM BUILDING | F66-ER-411A | CIL4 ELECTROWINNING CELL 1 RECTIFIER 1 | GOLDROOM BUILDING | N/A | N/A | 60 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-SCM-EL-10206 | 660 | 0 |  | 2
F66ER411B-D1 | F66-COM-01 | GOLDROOM BUILDING COMMUNICATIONS PANEL | GOLDROOM BUILDING | F66-ER-411B | CIL4 ELECTROWINNING CELL 1 RECTIFIER 2 | GOLDROOM BUILDING | N/A | N/A | 60 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-SCM-EL-10207 | 660 | 0 |  | 2
F66ER412A-D1 | F66-COM-01 | GOLDROOM BUILDING COMMUNICATIONS PANEL | GOLDROOM BUILDING | F66-ER-412A | CIL4 ELECTROWINNING CELL 2 RECTIFIER 1 | GOLDROOM BUILDING | N/A | N/A | 60 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-SCM-EL-10210 | 660 | 0 |  | 2
F66ER412B-D1 | F66-COM-01 | GOLDROOM BUILDING COMMUNICATIONS PANEL | GOLDROOM BUILDING | F66-ER-412B | CIL4 ELECTROWINNING CELL 2 RECTIFIER 2 | GOLDROOM BUILDING | N/A | N/A | 60 | 4PR | Cu | CAT6 SF/UTP Outdoor Cable | Black | Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-SCM-EL-10211 | 660 | 0 |  | 2
F66ER411A-P1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66-ER-411A | CIL4 ELECTROWINNING CELL 1 RECTIFIER 1 | GOLDROOM BUILDING | 50 | 0.6/1 | 105 | 3C+E | Cu | XLPE/PVC | Orange | Buried in Conduit (Bunched) / Ladder - Single Layer Touching | Primero | Primero | 2000-F66-SCM-EL-10206 | 660 | 0 |  | 2
F66EC411-P1 | F66-ER-411A | CIL4 ELECTROWINNING CELL 1 RECTIFIER 1 - POSITIVE (+) BUSBAR | GOLDROOM BUILDING | F66-EC-411 | CIL4 ELECTROWINNING CELL 1 - LEFT SIDE ANODE (+) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 6.86 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10206 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC411-P2 | F66-ER-411A | CIL4 ELECTROWINNING CELL 1 RECTIFIER 1 - POSITIVE (+) BUSBAR | GOLDROOM BUILDING | F66-EC-411 | CIL4 ELECTROWINNING CELL 1 - LEFT SIDE ANODE (+) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 6.75 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10206 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC411-N1 | F66-ER-411A | CIL4 ELECTROWINNING CELL 1 RECTIFIER 1 - NEGATIVE (-) BUSBAR | GOLDROOM BUILDING | F66-EC-411 | CIL4 ELECTROWINNING CELL 1 - LEFT SIDE CATHODE (-) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 6.31 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10206 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC411-N2 | F66-ER-411A | CIL4 ELECTROWINNING CELL 1 RECTIFIER 1 - NEGATIVE (-) BUSBAR | GOLDROOM BUILDING | F66-EC-411 | CIL4 ELECTROWINNING CELL 1 - LEFT SIDE CATHODE (-) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 6.42 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10206 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66ER411B-P1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66-ER-411B | CIL4 ELECTROWINNING CELL 1 RECTIFIER 2 | GOLDROOM BUILDING | 50 | 0.6/1 | 105 | 3C+E | Cu | XLPE/PVC | Orange | Buried in Conduit (Bunched) / Ladder - Single Layer Touching | Primero | Primero | 2000-F66-SCM-EL-10207 | 660 | 0 |  | 2
F66EC411-P3 | F66-ER-411B | CIL4 ELECTROWINNING CELL 1 RECTIFIER 2 - POSITIVE (+) BUSBAR | GOLDROOM BUILDING | F66-EC-411 | CIL4 ELECTROWINNING CELL 1 - RIGHT SIDE ANODE (+) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 7.23 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10207 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC411-P4 | F66-ER-411B | CIL4 ELECTROWINNING CELL 1 RECTIFIER 2 - POSITIVE (+) BUSBAR | GOLDROOM BUILDING | F66-EC-411 | CIL4 ELECTROWINNING CELL 1 - RIGHT SIDE ANODE (+) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 7.12 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10207 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC411-N3 | F66-ER-411B | CIL4 ELECTROWINNING CELL 1 RECTIFIER 2 - NEGATIVE (-) BUSBAR | GOLDROOM BUILDING | F66-EC-411 | CIL4 ELECTROWINNING CELL 1 - RIGHT SIDE CATHODE (-) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 6.9 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10207 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC411-N4 | F66-ER-411B | CIL4 ELECTROWINNING CELL 1 RECTIFIER 2 - NEGATIVE (-) BUSBAR | GOLDROOM BUILDING | F66-EC-411 | CIL4 ELECTROWINNING CELL 1 - RIGHT SIDE CATHODE (-) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 7.02 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10207 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66ER412A-P1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66-ER-412A | CIL4 ELECTROWINNING CELL 2 RECTIFIER 1 | GOLDROOM BUILDING | 50 | 0.6/1 | 110 | 3C+E | Cu | XLPE/PVC | Orange | Buried in Conduit (Bunched) / Ladder - Single Layer Touching | Primero | Primero | 2000-F66-SCM-EL-10210 | 660 | 0 |  | 2
F66EC412-P1 | F66-ER-412A | CIL4 ELECTROWINNING CELL 2 RECTIFIER 1 - POSITIVE (+) BUSBAR | GOLDROOM BUILDING | F66-EC-412 | CIL4 ELECTROWINNING CELL 2 - LEFT SIDE ANODE (+) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 7.33 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10210 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC412-P2 | F66-ER-412A | CIL4 ELECTROWINNING CELL 2 RECTIFIER 1 - POSITIVE (+) BUSBAR | GOLDROOM BUILDING | F66-EC-412 | CIL4 ELECTROWINNING CELL 2 - LEFT SIDE ANODE (+) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 7.44 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10210 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC412-N1 | F66-ER-412A | CIL4 ELECTROWINNING CELL 2 RECTIFIER 1 - NEGATIVE (-) BUSBAR | GOLDROOM BUILDING | F66-EC-412 | CIL4 ELECTROWINNING CELL 2 - LEFT SIDE CATHODE (-) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 7.87 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10210 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 2
F66EC412-N2 | F66-ER-412A | CIL4 ELECTROWINNING CELL 2 RECTIFIER 1 - NEGATIVE (-) BUSBAR | GOLDROOM BUILDING | F66-EC-412 | CIL4 ELECTROWINNING CELL 2 - LEFT SIDE CATHODE (-) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 7.76 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10210 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 3
F66ER412B-P1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66-ER-412B | CIL4 ELECTROWINNING CELL 2 RECTIFIER 2 | GOLDROOM BUILDING | 50 | 0.6/1 | 110 | 3C+E | Cu | XLPE/PVC | Orange | Buried in Conduit (Bunched) / Ladder - Single Layer Touching | Primero | Primero | 2000-F66-SCM-EL-10211 | 660 | 0 |  | 3
F66EC412-P3 | F66-ER-412B | CIL4 ELECTROWINNING CELL 2 RECTIFIER 2 - POSITIVE (+) BUSBAR | GOLDROOM BUILDING | F66-EC-412 | CIL4 ELECTROWINNING CELL 2 - RIGHT SIDE ANODE (+) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 6.8 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10211 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 3
F66EC412-P4 | F66-ER-412B | CIL4 ELECTROWINNING CELL 2 RECTIFIER 2 - POSITIVE (+) BUSBAR | GOLDROOM BUILDING | F66-EC-412 | CIL4 ELECTROWINNING CELL 2 - RIGHT SIDE ANODE (+) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 6.69 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10211 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 3
F66EC412-N3 | F66-ER-412B | CIL4 ELECTROWINNING CELL 2 RECTIFIER 2 - NEGATIVE (-) BUSBAR | GOLDROOM BUILDING | F66-EC-412 | CIL4 ELECTROWINNING CELL 2 - RIGHT SIDE CATHODE (-) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 6.21 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10211 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 3
F66EC412-N4 | F66-ER-412B | CIL4 ELECTROWINNING CELL 2 RECTIFIER 2 - NEGATIVE (-) BUSBAR | GOLDROOM BUILDING | F66-EC-412 | CIL4 ELECTROWINNING CELL 2 - RIGHT SIDE CATHODE (-) FLEXIBLE BUSBAR | GOLDROOM BUILDING | 1810 | 1 | 6.32 | 1C | CCA | Flexbus - TPE Insulation | Black | Ladder - Single Layer, 20mm Spacing | Vendor - ME053 | Primero | 2000-F66-SCM-EL-10211 | 660 | 0 | Solid copper busbar required at rectifier. Flexible busbar required at electrowinning cell. | 3
F66PW461-P1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66-PW-461 | CIL4 ELECTROWINNING PUMP 1 | GOLDROOM TANKS AREA | 16 | 0.6/1 | 110 | 3C+E | Cu | PVC/PVC | Orange | Buried in Conduit (Bunched) / Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 2000-F66-SCM-EL-10203 | 660 | 0 |  | 3
F66PW461-C1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66PW461-LCS | CIL4 ELECTROWINNING PUMP 1 LOCAL CONTROL STATION | GOLDROOM TANKS AREA | 1.5 | 0.6/1 | 110 | 4C+E | Cu | PVC/PVC | Black | Buried in Conduit (Bunched) / Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-SCM-EL-10203 | 660 | 0 |  | 3
F66PW462-P1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66-PW-462 | CIL4 ELECTROWINNING PUMP 2 | GOLDROOM TANKS AREA | 16 | 0.6/1 | 110 | 3C+E | Cu | PVC/PVC | Orange | Buried in Conduit (Bunched) / Ladder - Bunched in Groups up to 9 (2 Layers) | Primero | Primero | 2000-F66-SCM-EL-10204 | 660 | 0 |  | 3
F66PW462-C1 | F66-SW-402 | GOLDROOM 415V MCC | SUBSTATION 35 | F66PW462-LCS | CIL4 ELECTROWINNING PUMP 2 LOCAL CONTROL STATION | GOLDROOM TANKS AREA | 1.5 | 0.6/1 | 110 | 4C+E | Cu | PVC/PVC | Black | Buried in Conduit (Bunched) / Ladder - Bunched Ctrl/Inst | Primero | Primero | 2000-F66-SCM-EL-10204 | 660 | 0 |  | 3