## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | Length (m) | No. of Cores / Pairs | Conductor | Sheath (Preferred colour) | Supplied By | Installed By | Reference Drawing (SLD/SCM/TER) | Area | Rev | Construction | Page
F72SW172-P4 | F72-GE-172 | REAGENTS EMERGENCY SUPPLY 415V GENERATOR | REAGENTS SWITCHROOM AREA | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS SWITCHROOM | 185 | 0.6/1 | 35 | 4C+E | Cu | Orange | Primero | Primero | 2000-F72-SLD-EL-10211 | 720 | 0 |  | 2
F72SW172-P5 | F72-GE-172 | REAGENTS EMERGENCY SUPPLY 415V GENERATOR | REAGENTS SWITCHROOM AREA | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS SWITCHROOM | 185 | 0.6/1 | 35 | 4C+E | Cu | Orange | Primero | Primero | 2000-F72-SLD-EL-10211 | 720 | 0 |  | 2
F72SW172-P6 | F72-GE-172 | REAGENTS EMERGENCY SUPPLY 415V GENERATOR | REAGENTS SWITCHROOM AREA | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS SWITCHROOM | 185 | 0.6/1 | 35 | 4C+E | Cu | Orange | Primero | Primero | 2000-F72-SLD-EL-10211 | 720 | 0 |  | 2
F72GE172CP-P1 | F72-DB-001 | REAGENTS 415V SWITCHROOM L&SP DISTRIBUTION BOARD | REAGENTS SWITCHROOM | F72GE172-CP | REAGENTS EMERGENCY SUPPLY 415V GENERATOR CONTROL PANEL | REAGENTS SWITCHROOM AREA | 2.5 | 0.6/1 | 35 | 2C+E | Cu | Orange | Primero | Primero | 2000-F72-TLD-EL-10104 | 720 | 0 |  | 2
F72GE172CP-C1 | F72-DCS-413 | REAGENTS 415V SWITCHROOM DCS PANEL | REAGENTS SWITCHROOM | F72GE172-CP | REAGENTS EMERGENCY SUPPLY 415V GENERATOR CONTROL PANEL | REAGENTS SWITCHROOM AREA | 1.5 | 0.6/1 | 35 | 6C+E | Cu | Black | Primero | Primero | 2000-F72-TER-EL-10222 | 720 | 0 |  | 2
F72GE172CP-C2 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS SWITCHROOM | F72GE172-CP | REAGENTS EMERGENCY SUPPLY 415V GENERATOR CONTROL PANEL | REAGENTS SWITCHROOM AREA | 1.5 | 0.6/1 | 35 | 10C+E | Cu | Black | Primero | Primero | 2000-F72-TER-EL-10222 | 720 | 0 |  | 2
F72GE172CP-D1 | F72-COM-001 | REAGENTS 415V SWITCHROOM COMMUNICATIONS RACK | REAGENTS SWITCHROOM | F72GE172-CP | REAGENTS EMERGENCY SUPPLY 415V GENERATOR CONTROL PANEL | REAGENTS SWITCHROOM AREA | N/A | N/A | 35 | 4PR | Cu | Black | Primero | Primero | 2000-F72-TER-EL-10222 | 720 | 0 |  | 2
F72RIO003-P1 | F72-DB-201 | REAGENTS 415V SWITCHROOM 240V UPS DISTRIBUTION BOARD | REAGENTS 415V SWITCHROOM | F72-RIO-003 | REAGENTS FIELD N-IO PANEL | LIME AREA | 25 | 0.6/1 | 125 | 2C+E | Cu | Orange | Primero | Primero | 2000-F72-TLD-EL-10105 | 720 | 0 |  | 2
F72COM001/F72RIO003-FO1 | F72-COM-001 | REAGENTS 415V SWITCHROOM COMMUNICATIONS RACK | REAGENTS 415V SWITCHROOM | F72-RIO-003 | REAGENTS FIELD N-IO PANEL | LIME AREA | 9/125µm | N/A | 125 | 12C | OS2 SMOF | Black | Primero | Primero | 2000-F72-TER-IC-10001 | 720 | 0 |  | 2
F72RIO003/F72COM001-FO1 | F72-RIO-003 | REAGENTS FIELD N-IO PANEL | REAGENTS 415V SWITCHROOM | F72-COM-001 | REAGENTS 415V SWITCHROOM COMMUNICATIONS RACK | LIME AREA | 9/125µm | N/A | 125 | 12C | OS2 SMOF | Black | Primero | Primero | 2000-F72-TER-IC-10001 | 720 | 0 |  | 2
F72BW412-P1 | F72BW412-VS | LIME DELIVERY BLOWER LV VSD | REAGENTS 415V SWITCHROOM | F72-BW-412 | LIME DELIVERY BLOWER | LIME UNLOADING AREA | 95 | 0.6/1 | 145 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10665 | 720 | 0 |  | 2
F72BW412LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72BW412-LCS | LIME DELIVERY BLOWER LOCAL CONTROL STATION | LIME UNLOADING AREA | 1.5 | 0.6/1 | 145 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10665 | 720 | 0 |  | 2
F72BW412-I1 | F72BW412-VS | LIME DELIVERY BLOWER LV VSD | REAGENTS 415V SWITCHROOM | F72-BW-412 | LIME DELIVERY BLOWER THERMISTOR | LIME UNLOADING AREA | 1.5 | 0.11 | 145 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10665 | 720 | 0 |  | 2
F72AG467-P1 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72-AG-467 | MILK OF LIME TANK AGITATOR | LIME AREA | 25 | 0.6/1 | 110 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10211 | 720 | 0 |  | 2
F72AG467LCS-C1 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72AG467-LCS | MILK OF LIME TANK AGITATOR LOCAL CONTROL STATION | LIME AREA | 1.5 | 0.6/1 | 110 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10211 | 720 | 0 |  | 2
F72AT411JB-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72AT411-JB | LIME SILO 1 ACTIVATOR JUNCTION BOX | LIME SILO 1 | 2.5 | 0.6/1 | 160 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10651 | 720 | 0 |  | 2
F72AT411-P1 | F72AT411-JB | LIME SILO 1 ACTIVATOR JUNCTION BOX | LIME SILO 1 | F72-AT-411 | LIME SILO 1 ACTIVATOR | LIME SILO 1 | Vendor | 0.6/1 | 2 | Vendor | Cu | Orange | Vendor | Primero | 2000-F72-SCM-EL-10651 | 720 | 0 |  | 2
F72AT411LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72AT411-LCS | LIME SILO 1 ACTIVATOR LOCAL CONTROL STATION | LIME SILO 1 | 1.5 | 0.6/1 | 160 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10651 | 720 | 0 |  | 2
F72AT412JB-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72AT412-JB | LIME SILO 2 ACTIVATOR JUNCTION BOX | LIME SILO 2 | 2.5 | 0.6/1 | 175 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10652 | 720 | 0 |  | 2
F72AT412-P1 | F72AT412-JB | LIME SILO 2 ACTIVATOR JUNCTION BOX | LIME SILO 2 | F72-AT-412 | LIME SILO 2 ACTIVATOR | LIME SILO 2 | Vendor | 0.6/1 | 2 | Vendor | Cu | Orange | Vendor | Primero | 2000-F72-SCM-EL-10652 | 720 | 0 |  | 2
F72AT412LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72AT412-LCS | LIME SILO 2 ACTIVATOR LOCAL CONTROL STATION | LIME SILO 2 | 1.5 | 0.6/1 | 175 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10652 | 720 | 0 |  | 2
F72AG658-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72-AG-658 | SLAKED LIME DISCHARGE HOPPER 1 AGITATOR | LIME SLAKING MILL 1 | 2.5 | 0.6/1 | 150 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10668 | 720 | 0 |  | 2
F72AG658LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72AG658-LCS | SLAKED LIME DISCHARGE HOPPER 1 AGITATOR LOCAL CONTROL STATION | LIME SLAKING MILL 1 | 1.5 | 0.6/1 | 150 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10668 | 720 | 0 |  | 2
F72AG659-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72-AG-659 | SLAKED LIME DISCHARGE HOPPER 2 AGITATOR | LIME SLAKING MILL 2 | 2.5 | 0.6/1 | 160 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10669 | 720 | 0 |  | 2
F72AG659LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72AG659-LCS | SLAKED LIME DISCHARGE HOPPER 2 AGITATOR LOCAL CONTROL STATION | LIME SLAKING MILL 2 | 1.5 | 0.6/1 | 160 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10669 | 720 | 0 |  | 2
F72FS411-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72-FS-411 | LIME SILO 1 SCREW FEEDER | LIME SILO 1 | 4 | 0.6/1 | 160 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10654 | 720 | 0 |  | 2
F72FS411LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72FS411-LCS | LIME SILO 1 SCREW FEEDER LOCAL CONTROL STATION | LIME SILO 1 | 1.5 | 0.6/1 | 160 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10654 | 720 | 0 |  | 2
F72FS412-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72-FS-412 | LIME SILO 2 SCREW FEEDER | LIME SILO 2 | 4 | 0.6/1 | 175 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10656 | 720 | 0 |  | 2
F72FS412LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72FS412-LCS | LIME SILO 2 SCREW FEEDER LOCAL CONTROL STATION | LIME SILO 2 | 1.5 | 0.6/1 | 175 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10656 | 720 | 0 |  | 2
F72FV411JB-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72FV411-JB | LIME SILO 1 VIBRATING CONVEYOR JUNCTION BOX | LIME SILO 1 | 2.5 | 0.6/1 | 150 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10655 | 720 | 0 |  | 2
F72FV411A-P1 | F72FV411-JB | LIME SILO 1 VIBRATING CONVEYOR JUNCTION BOX | LIME SILO 1 | F72-FV-411A | LIME SILO 1 VIBRATING CONVEYOR MOTOR A | LIME SILO 1 | Vendor | 0.6/1 | 2 | Vendor | Cu | Orange | Vendor | Primero | 2000-F72-SCM-EL-10655 | 720 | 0 |  | 2
F72FV411JB-P2 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72FV411-JB | LIME SILO 1 VIBRATING CONVEYOR JUNCTION BOX | LIME SILO 1 | 2.5 | 0.6/1 | 150 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10655 | 720 | 0 |  | 2
F72FV411B-P1 | F72FV411-JB | LIME SILO 1 VIBRATING CONVEYOR JUNCTION BOX | LIME SILO 1 | F72-FV-411B | LIME SILO 1 VIBRATING CONVEYOR MOTOR B | LIME SILO 1 | Vendor | 0.6/1 | 2 | Vendor | Cu | Orange | Vendor | Primero | 2000-F72-SCM-EL-10655 | 720 | 0 |  | 2
F72FV411LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72FV411-LCS | LIME SILO 1 VIBRATING CONVEYOR LOCAL CONTROL STATION | LIME SILO 1 | 1.5 | 0.6/1 | 150 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10655 | 720 | 0 |  | 2
F72FV412JB-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72FV412-JB | LIME SILO 2 VIBRATING CONVEYOR JUNCTION BOX | LIME SILO 2 | 2.5 | 0.6/1 | 160 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10663 | 720 | 0 |  | 2
F72FV412A-P1 | F72FV412-JB | LIME SILO 2 VIBRATING CONVEYOR JUNCTION BOX | LIME SILO 2 | F72-FV-412A | LIME SILO 2 VIBRATING CONVEYOR MOTOR A | LIME SILO 2 | Vendor | 0.6/1 | 2 | Vendor | Cu | Orange | Vendor | Primero | 2000-F72-SCM-EL-10663 | 720 | 0 |  | 2
F72FV412JB-P2 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72FV412-JB | LIME SILO 2 VIBRATING CONVEYOR JUNCTION BOX | LIME SILO 2 | 2.5 | 0.6/1 | 160 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10663 | 720 | 0 |  | 2
F72FV412B-P1 | F72FV412-JB | LIME SILO 2 VIBRATING CONVEYOR JUNCTION BOX | LIME SILO 2 | F72-FV-412B | LIME SILO 2 VIBRATING CONVEYOR MOTOR B | LIME SILO 2 | Vendor | 0.6/1 | 2 | Vendor | Cu | Orange | Vendor | Primero | 2000-F72-SCM-EL-10663 | 720 | 0 |  | 2
F72FV412LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72FV412-LCS | LIME SILO 2 VIBRATING CONVEYOR LOCAL CONTROL STATION | LIME SILO 2 | 1.5 | 0.6/1 | 160 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10663 | 720 | 0 |  | 2
F72CR660-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS SWITCHROOM | F72-CR-660 | LIME SLAKING MILL BALL KIBBLE HOIST | LIME AREA | 4 | 0.6/1 | 150 | 4C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10664 | 720 | 0 |  | 2
F72CR661-P1 | F72-DB-302 | SOUTH REAGENTS MIXING AND STORAGE AREA L&SP DISTRIBUTION BOARD | SOUTH REAGENTS PIPERACK | F72-CR-661 | SLAKED LIME HYDRO-CYCLONE JIB CRANE | LIME AREA | 4 | 0.6/1 | 80 | 4C+E | Cu | Orange | Primero | Primero | 2000-F72-TLD-EL-10102 | 720 | 0 |  | 2
F72CR662-P1 | F72-DB-302 | SOUTH REAGENTS MIXING AND STORAGE AREA L&SP DISTRIBUTION BOARD | SOUTH REAGENTS PIPERACK | F72-CR-662 | CYANIDE AREA SUMP PUMP JIB CRANE | CYANIDE SUMP PUMP AREA | 4 | 0.6/1 | 120 | 4C+E | Cu | Orange | Primero | Primero | 2000-F72-TLD-EL-10102 | 720 | 0 |  | 2
F72PP658-P1 | F72PP658-VS | SLAKED LIME TRANSFER PUMP 1 LV VSD | REAGENTS 415V SWITCHROOM | F72-PP-658 | SLAKED LIME TRANSFER PUMP 1 | LIME AREA | 35 | 0.6/1 | 150 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10661 | 720 | 0 |  | 2
F72PP658LCS-C1 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72PP658-LCS | SLAKED LIME TRANSFER PUMP 1 LOCAL CONTROL STATION | LIME AREA | 1.5 | 0.6/1 | 150 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10661 | 720 | 0 |  | 2
F72PP659-P1 | F72PP659-VS | SLAKED LIME TRANSFER PUMP 2 LV VSD | REAGENTS 415V SWITCHROOM | F72-PP-659 | SLAKED LIME TRANSFER PUMP 2 | LIME AREA | 35 | 0.6/1 | 150 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10662 | 720 | 0 |  | 2
F72PP659LCS-C1 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72PP659-LCS | SLAKED LIME TRANSFER PUMP 2 LOCAL CONTROL STATION | LIME AREA | 1.5 | 0.6/1 | 150 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10662 | 720 | 0 |  | 2
F72PP656-P1 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-656 | LIME RINGMAIN PUMP 1 | LIME RINGMAIN AREA | 70 | 0.6/1 | 130 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10657 | 720 | 0 |  | 2
F72PP656-P2 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-656 | LIME RINGMAIN PUMP 1 | LIME RINGMAIN AREA | 70 | 0.6/1 | 130 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10657 | 720 | 0 |  | 2
F72PP656-P3 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-656 | LIME RINGMAIN PUMP 1 SPACE HEATER | LIME RINGMAIN AREA | 2.5 | 0.6/1 | 130 | 2C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10657 | 720 | 0 |  | 2
F72PP656-I1 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-656 | LIME RINGMAIN PUMP 1 THERMISTOR | LIME RINGMAIN AREA | 1.5 | 0.11 | 130 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10657 | 720 | 0 | PVC/OSCN/PVC | 3
F72PP656LCS-C1 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72PP656-LCS | LIME RINGMAIN PUMP 1 LOCAL CONTROL STATION | LIME RINGMAIN AREA | 1.5 | 0.6/1 | 130 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10657 | 720 | 0 | PVC/PVC | 3
F72PP657-P1 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-657 | LIME RINGMAIN PUMP 2 | LIME RINGMAIN AREA | 70 | 0.6/1 | 130 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10658 | 720 | 0 | XLPE/PVC Flexible | 3
F72PP657-P2 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-657 | LIME RINGMAIN PUMP 2 | LIME RINGMAIN AREA | 70 | 0.6/1 | 130 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10658 | 720 | 0 | XLPE/PVC Flexible | 3
F72PP657-P3 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-657 | LIME RINGMAIN PUMP 2 SPACE HEATER | LIME RINGMAIN AREA | 2.5 | 0.6/1 | 130 | 2C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10658 | 720 | 0 | PVC/PVC | 3
F72PP657-I1 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-657 | LIME RINGMAIN PUMP 2 THERMISTOR | LIME RINGMAIN AREA | 1.5 | 0.11 | 130 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10658 | 720 | 0 | PVC/OSCN/PVC | 3
F72PP657LCS-C1 | F72-SW-172 | REAGENTS EMERGENCY 415V MCC | REAGENTS 415V SWITCHROOM | F72PP657-LCS | LIME RINGMAIN PUMP 2 LOCAL CONTROL STATION | LIME RINGMAIN AREA | 1.5 | 0.6/1 | 130 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10658 | 720 | 0 | PVC/PVC | 3
F72PP673-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-673 | CAUSTIC RINGMAIN PUMP 1 | CAUSTIC AREA | 10 | 0.6/1 | 100 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10401 | 720 | 0 | PVC/PVC | 3
F72PP673LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PP673-LCS | CAUSTIC RINGMAIN PUMP 1 LOCAL CONTROL STATION | CAUSTIC AREA | 1.5 | 0.6/1 | 100 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10401 | 720 | 0 | PVC/PVC | 3
F72PP674-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-674 | CAUSTIC RINGMAIN PUMP 2 | CAUSTIC AREA | 10 | 0.6/1 | 100 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10402 | 720 | 0 | PVC/PVC | 3
F72PP674LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PP674-LCS | CAUSTIC RINGMAIN PUMP 2 LOCAL CONTROL STATION | CAUSTIC AREA | 1.5 | 0.6/1 | 100 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10402 | 720 | 0 | PVC/PVC | 3
F72HT491-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS SWITCHROOM | F72-HT-491 | CAUSTIC STORAGE TANK IMMERSION HEATER | CAUSTIC AREA | 120 | 0.6/1 | 100 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10405 | 720 | 0 | XLPE/PVC Flexible | 3
F72PP675-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-675 | CYANIDE RINGMAIN PUMP 1 | CYANIDE AREA | 16 | 0.6/1 | 100 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10501 | 720 | 0 | PVC/PVC | 3
F72PP675LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PP675-LCS | CYANIDE RINGMAIN PUMP 1 LOCAL CONTROL STATION | CYANIDE AREA | 1.5 | 0.6/1 | 100 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10501 | 720 | 0 | PVC/PVC | 3
F72PP676-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-676 | CYANIDE RINGMAIN PUMP 2 | CYANIDE AREA | 16 | 0.6/1 | 100 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10502 | 720 | 0 | PVC/PVC | 3
F72PP676LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PP676-LCS | CYANIDE RINGMAIN PUMP 2 LOCAL CONTROL STATION | CYANIDE AREA | 1.5 | 0.6/1 | 100 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10502 | 720 | 0 | PVC/PVC | 3
F72PP681-P1 | F72PP681-VS | LEAD NITRATE DOSING PUMP 1 LV VSD | REAGENTS 415V SWITCHROOM | F72-PP-681 | LEAD NITRATE DOSING PUMP 1 | LEAD NITRATE AREA | 2.5 | 0.6/1 | 115 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10551 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 3
F72PP681LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PP681-LCS | LEAD NITRATE DOSING PUMP 1 LOCAL CONTROL STATION | LEAD NITRATE AREA | 1.5 | 0.6/1 | 115 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10551 | 720 | 0 | PVC/PVC | 3
F72PP682-P1 | F72PP682-VS | LEAD NITRATE DOSING PUMP 2 LV VSD | REAGENTS 415V SWITCHROOM | F72-PP-682 | LEAD NITRATE DOSING PUMP 2 | LEAD NITRATE AREA | 2.5 | 0.6/1 | 115 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10552 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 3
F72PP682LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PP682-LCS | LEAD NITRATE DOSING PUMP 2 LOCAL CONTROL STATION | LEAD NITRATE AREA | 1.5 | 0.6/1 | 115 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10552 | 720 | 0 | PVC/PVC | 3
F72PP683-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-683 | ACID DOSING PUMP 1 | HCL AREA | 6 | 0.6/1 | 100 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10451 | 720 | 0 | PVC/PVC | 3
F72PP683LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PP683-LCS | ACID DOSING PUMP 1 LOCAL CONTROL STATION | HCL AREA | 1.5 | 0.6/1 | 100 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10451 | 720 | 0 | PVC/PVC | 3
F72PP684-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-684 | ACID DOSING PUMP 2 | HCL AREA | 6 | 0.6/1 | 100 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10452 | 720 | 0 | PVC/PVC | 3
F72PP684LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PP684-LCS | ACID DOSING PUMP 2 LOCAL CONTROL STATION | HCL AREA | 1.5 | 0.6/1 | 100 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10452 | 720 | 0 | PVC/PVC | 3
F72PP424-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72-PP-424 | CIL4 DILUTED ACID DOSING PUMP | HCL AREA | 10 | 0.6/1 | 95 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10450 | 720 | 0 | PVC/PVC | 3
F72PP424LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PP424-LCS | CIL4 DILUTED ACID DOSING PUMP LCS | HCL AREA | 1.5 | 0.6/1 | 95 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10450 | 720 | 0 | PVC/PVC | 3
F72PS419LCS-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PS419-LCS | MILK OF LIME AREA SUMP PUMP 1 LOCAL CONTROL STATION | LIME AREA | 35 | 0.6/1 | 130 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10659 | 720 | 0 | XLPE/PVC | 3
F72PS419-P1 | F72PS419-LCS | MILK OF LIME AREA SUMP PUMP 1 LOCAL CONTROL STATION | LIME AREA | F72-PS-419 | MILK OF LIME AREA SUMP PUMP 1 | LIME AREA | 35 | 0.6/1 | 10 | 3C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10659 | 720 | 0 | EPR/CSP | 3
F72PS419LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PS419-LCS | MILK OF LIME AREA SUMP PUMP 1 LOCAL CONTROL STATION | LIME AREA | 1.5 | 0.6/1 | 130 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10659 | 720 | 0 | PVC/PVC | 3
F72PS466LCS-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PS466-LCS | MILK OF LIME AREA SUMP PUMP 1 LOCAL CONTROL STATION | LIME AREA | 35 | 0.6/1 | 150 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10666 | 720 | 0 | XLPE/PVC | 3
F72PS466-P1 | F72PS466-LCS | MILK OF LIME AREA SUMP PUMP 2 LOCAL CONTROL STATION | LIME AREA | F72-PS-466 | MILK OF LIME AREA SUMP PUMP 1 | LIME AREA | 35 | 0.6/1 | 10 | 3C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10666 | 720 | 0 | EPR/CSP | 3
F72PS466LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PS466-LCS | MILK OF LIME AREA SUMP PUMP 1 LOCAL CONTROL STATION | LIME AREA | 1.5 | 0.6/1 | 150 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10666 | 720 | 0 | PVC/PVC | 3
F72PS467LCS-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PS467-LCS | MILK OF LIME AREA SUMP PUMP 1 LOCAL CONTROL STATION | LIME AREA | 35 | 0.6/1 | 145 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10667 | 720 | 0 | XLPE/PVC | 3
F72PS467-P1 | F72PS467-LCS | MILK OF LIME AREA SUMP PUMP 3 LOCAL CONTROL STATION | LIME AREA | F72-PS-467 | MILK OF LIME AREA SUMP PUMP 1 | LIME AREA | 35 | 0.6/1 | 10 | 3C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10667 | 720 | 0 | EPR/CSP | 3
F72PS467LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PS467-LCS | MILK OF LIME AREA SUMP PUMP 1 LOCAL CONTROL STATION | LIME AREA | 1.5 | 0.6/1 | 145 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10667 | 720 | 0 | PVC/PVC | 3
F72PS423LCS-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PS423-LCS | CYANIDE AREA SUMP PUMP LOCAL CONTROL STATION | CYANIDE AREA | 25 | 0.6/1 | 90 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10503 | 720 | 0 | XLPE/PVC | 3
F72PS423-P1 | F72PS423-LCS | CYANIDE AREA SUMP PUMP LOCAL CONTROL STATION | CYANIDE AREA | F72-PS-423 | CYANIDE AREA SUMP PUMP | CYANIDE AREA | 25 | 0.6/1 | 20 | 3C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10503 | 720 | 0 | EPR/CSP | 3
F72PS423LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PS423-LCS | CYANIDE AREA SUMP PUMP LOCAL CONTROL STATION | CYANIDE AREA | 1.5 | 0.6/1 | 90 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10503 | 720 | 0 | PVC/PVC | 3
F72PS424LCS-P1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PS424-LCS | CAUSTIC AREA SUMP PUMP LOCAL CONTROL STATION | CAUSTIC AREA | 25 | 0.6/1 | 105 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10403 | 720 | 0 | XLPE/PVC | 3
F72PS424-P1 | F72PS424-LCS | CAUSTIC AREA SUMP PUMP LOCAL CONTROL STATION | CAUSTIC AREA | F72-PS-424 | CAUSTIC AREA SUMP PUMP | CAUSTIC AREA | 25 | 0.6/1 | 10 | 3C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10403 | 720 | 0 | EPR/CSP | 3
F72PS424LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72PS424-LCS | CAUSTIC AREA SUMP PUMP LOCAL CONTROL STATION | CAUSTIC AREA | 1.5 | 0.6/1 | 105 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10403 | 720 | 0 | PVC/PVC | 3
F72MB411A-P1 | F72MB411A-VS | LIME SLAKING MILL 1 MOTOR 1 LV VSD | REAGENTS 415V SWITCHROOM | F72-MB-411A | LIME SLAKING MILL 1 MOTOR 1 | LIME SLAKING MILL 1 | 95 | 0.6/1 | 145 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10670 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 3
F72MB411LCS-C1 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72MB411-LCS | LIME SLAKING MILL 1 LOCAL CONTROL STATION | LIME SLAKING MILL 1 | 1.5 | 0.6/1 | 145 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10670 | 720 | 0 | PVC/PVC | 3
F72MB411A-I1 | F72MB411A-VS | LIME SLAKING MILL 1 MOTOR 1 LV VSD | REAGENTS 415V SWITCHROOM | F72-MB-411A | LIME SLAKING MILL 1 MOTOR 1 THERMISTOR | LIME SLAKING MILL 1 | 1.5 | 0.11 | 145 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10670 | 720 | 0 | PVC/OSCN/PVC | 3
F72MB411B-P1 | F72MB411B-VS | LIME SLAKING MILL 1 MOTOR 2 LV VSD | REAGENTS 415V SWITCHROOM | F72-MB-411B | LIME SLAKING MILL 1 MOTOR 2 | LIME SLAKING MILL 1 | 95 | 0.6/1 | 150 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10671 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 3
F72MB411LCS-C2 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72MB411-LCS | LIME SLAKING MILL 1 LOCAL CONTROL STATION | LIME SLAKING MILL 1 | 1.5 | 0.6/1 | 150 | 2C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10671 | 720 | 0 | PVC/PVC | 3
F72MB411B-I1 | F72MB411B-VS | LIME SLAKING MILL 1 MOTOR 2 LV VSD | REAGENTS 415V SWITCHROOM | F72-MB-411B | LIME SLAKING MILL 1 MOTOR 2 THERMISTOR | LIME SLAKING MILL 1 | 1.5 | 0.11 | 150 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10671 | 720 | 0 | PVC/OSCN/PVC | 3
F72MB411C-P1 | F72MB411C-VS | LIME SLAKING MILL 1 MOTOR 3 LV VSD | REAGENTS 415V SWITCHROOM | F72-MB-411C | LIME SLAKING MILL 1 MOTOR 3 | LIME SLAKING MILL 1 | 95 | 0.6/1 | 145 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10672 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 3
F72MB411LCS-C3 | F72-SW-072 | REAGENTS 415V MCC | REAGENTS 415V SWITCHROOM | F72MB411-LCS | LIME SLAKING MILL 1 LOCAL CONTROL STATION | LIME SLAKING MILL 1 | 1.5 | 0.6/1 | 145 | 2C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10672 | 720 | 0 | PVC/PVC | 3
F72MB411C-I1 | F72MB411C-VS | LIME SLAKING MILL 1 MOTOR 3 LV VSD |  | F72-MB-411C | LIME SLAKING MILL 1 MOTOR 3 THERMISTOR | LIME SLAKING MILL 1 | 1.5 | 0.11 | 145 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10672 | 720 | 0 | PVC/OSCN/PVC | 4
F72MB411D-P1 | F72MB411D-VS | LIME SLAKING MILL 1 MOTOR 4 LV VSD |  | F72-MB-411D | LIME SLAKING MILL 1 MOTOR 4 | LIME SLAKING MILL 1 | 95 | 0.6/1 | 150 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10673 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 4
F72MB411LCS-C4 | F72-SW-072 | REAGENTS 415V MCC |  | F72MB411-LCS | LIME SLAKING MILL 1 LOCAL CONTROL STATION | LIME SLAKING MILL 1 | 1.5 | 0.6/1 | 150 | 2C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10673 | 720 | 0 | PVC/PVC | 4
F72MB411D-I1 | F72MB411D-VS | LIME SLAKING MILL 1 MOTOR 4 LV VSD |  | F72-MB-411D | LIME SLAKING MILL 1 MOTOR 4 THERMISTOR | LIME SLAKING MILL 1 | 1.5 | 0.11 | 150 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10673 | 720 | 0 | PVC/OSCN/PVC | 4
F72MB411E-P1 | F72MB411E-VS | LIME SLAKING MILL 1 MOTOR 5 LV VSD |  | F72-MB-411E | LIME SLAKING MILL 1 MOTOR 5 | LIME SLAKING MILL 1 | 95 | 0.6/1 | 145 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10674 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 4
F72MB411LCS-C5 | F72-SW-072 | REAGENTS 415V MCC |  | F72MB411-LCS | LIME SLAKING MILL 1 LOCAL CONTROL STATION | LIME SLAKING MILL 1 | 1.5 | 0.6/1 | 145 | 2C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10674 | 720 | 0 | PVC/PVC | 4
F72MB411E-I1 | F72MB411E-VS | LIME SLAKING MILL 1 MOTOR 5 LV VSD |  | F72-MB-411E | LIME SLAKING MILL 1 MOTOR 5 THERMISTOR | LIME SLAKING MILL 1 | 1.5 | 0.11 | 145 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10674 | 720 | 0 | PVC/OSCN/PVC | 4
F72MB411F-P1 | F72MB411F-VS | LIME SLAKING MILL 1 MOTOR 6 LV VSD |  | F72-MB-411F | LIME SLAKING MILL 1 MOTOR 6 | LIME SLAKING MILL 1 | 95 | 0.6/1 | 150 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10675 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 4
F72MB411LCS-C6 | F72-SW-072 | REAGENTS 415V MCC |  | F72MB411-LCS | LIME SLAKING MILL 1 LOCAL CONTROL STATION | LIME SLAKING MILL 1 | 1.5 | 0.6/1 | 150 | 2C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10675 | 720 | 0 | PVC/PVC | 4
F72MB411F-I1 | F72MB411F-VS | LIME SLAKING MILL 1 MOTOR 6 LV VSD |  | F72-MB-411F | LIME SLAKING MILL 1 MOTOR 6 THERMISTOR | LIME SLAKING MILL 1 | 1.5 | 0.11 | 150 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10675 | 720 | 0 | PVC/OSCN/PVC | 4
F72MB412A-P1 | F72MB412A-VS | LIME SLAKING MILL 2 MOTOR 1 LV VSD |  | F72-MB-412A | LIME SLAKING MILL 2 MOTOR 1 | LIME SLAKING MILL 2 | 95 | 0.6/1 | 160 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10676 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 4
F72MB412LCS-C1 | F72-SW-072 | REAGENTS 415V MCC |  | F72MB412-LCS | LIME SLAKING MILL 2 LOCAL CONTROL STATION | LIME SLAKING MILL 2 | 1.5 | 0.6/1 | 160 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10676 | 720 | 0 | PVC/PVC | 4
F72MB412A-I1 | F72MB412A-VS | LIME SLAKING MILL 2 MOTOR 1 LV VSD |  | F72-MB-412A | LIME SLAKING MILL 2 MOTOR 1 THERMISTOR | LIME SLAKING MILL 2 | 1.5 | 0.11 | 160 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10676 | 720 | 0 | PVC/OSCN/PVC | 4
F72MB412B-P1 | F72MB412B-VS | LIME SLAKING MILL 2 MOTOR 2 LV VSD |  | F72-MB-412B | LIME SLAKING MILL 2 MOTOR 2 | LIME SLAKING MILL 2 | 95 | 0.6/1 | 165 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10677 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 4
F72MB412LCS-C2 | F72-SW-072 | REAGENTS 415V MCC |  | F72MB412-LCS | LIME SLAKING MILL 2 LOCAL CONTROL STATION | LIME SLAKING MILL 2 | 1.5 | 0.6/1 | 165 | 2C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10677 | 720 | 0 | PVC/PVC | 4
F72MB412B-I1 | F72MB412B-VS | LIME SLAKING MILL 2 MOTOR 2 LV VSD |  | F72-MB-412B | LIME SLAKING MILL 2 MOTOR 2 THERMISTOR | LIME SLAKING MILL 2 | 1.5 | 0.11 | 165 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10677 | 720 | 0 | PVC/OSCN/PVC | 4
F72MB412C-P1 | F72MB412C-VS | LIME SLAKING MILL 2 MOTOR 3 LV VSD |  | F72-MB-412C | LIME SLAKING MILL 2 MOTOR 3 | LIME SLAKING MILL 2 | 95 | 0.6/1 | 160 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10678 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 4
F72MB412LCS-C3 | F72-SW-072 | REAGENTS 415V MCC |  | F72MB412-LCS | LIME SLAKING MILL 2 LOCAL CONTROL STATION | LIME SLAKING MILL 2 | 1.5 | 0.6/1 | 160 | 2C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10678 | 720 | 0 | PVC/PVC | 4
F72MB412C-I1 | F72MB412C-VS | LIME SLAKING MILL 2 MOTOR 3 LV VSD |  | F72-MB-412C | LIME SLAKING MILL 2 MOTOR 3 THERMISTOR | LIME SLAKING MILL 2 | 1.5 | 0.11 | 160 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10678 | 720 | 0 | PVC/OSCN/PVC | 4
F72MB412D-P1 | F72MB412D-VS | LIME SLAKING MILL 2 MOTOR 4 LV VSD |  | F72-MB-412D | LIME SLAKING MILL 2 MOTOR 4 | LIME SLAKING MILL 2 | 95 | 0.6/1 | 165 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10679 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 4
F72MB412LCS-C4 | F72-SW-072 | REAGENTS 415V MCC |  | F72MB412-LCS | LIME SLAKING MILL 2 LOCAL CONTROL STATION | LIME SLAKING MILL 2 | 1.5 | 0.6/1 | 165 | 2C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10679 | 720 | 0 | PVC/PVC | 4
F72MB412D-I1 | F72MB412D-VS | LIME SLAKING MILL 2 MOTOR 4 LV VSD |  | F72-MB-412D | LIME SLAKING MILL 2 MOTOR 4 THERMISTOR | LIME SLAKING MILL 2 | 1.5 | 0.11 | 165 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10679 | 720 | 0 | PVC/OSCN/PVC | 4
F72MB412E-P1 | F72MB412E-VS | LIME SLAKING MILL 2 MOTOR 5 LV VSD |  | F72-MB-412E | LIME SLAKING MILL 2 MOTOR 5 | LIME SLAKING MILL 2 | 95 | 0.6/1 | 160 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10680 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 4
F72MB412LCS-C5 | F72-SW-072 | REAGENTS 415V MCC |  | F72MB412-LCS | LIME SLAKING MILL 2 LOCAL CONTROL STATION | LIME SLAKING MILL 2 | 1.5 | 0.6/1 | 160 | 2C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10680 | 720 | 0 | PVC/PVC | 4
F72MB412E-I1 | F72MB412E-VS | LIME SLAKING MILL 2 MOTOR 5 LV VSD |  | F72-MB-412E | LIME SLAKING MILL 2 MOTOR 5 THERMISTOR | LIME SLAKING MILL 2 | 1.5 | 0.11 | 160 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10680 | 720 | 0 | PVC/OSCN/PVC | 4
F72MB412F-P1 | F72MB412F-VS | LIME SLAKING MILL 2 MOTOR 6 LV VSD |  | F72-MB-412F | LIME SLAKING MILL 2 MOTOR 6 | LIME SLAKING MILL 2 | 95 | 0.6/1 | 165 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10681 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 4
F72MB412LCS-C6 | F72-SW-072 | REAGENTS 415V MCC |  | F72MB412-LCS | LIME SLAKING MILL 2 LOCAL CONTROL STATION | LIME SLAKING MILL 2 | 1.5 | 0.6/1 | 165 | 2C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10681 | 720 | 0 | PVC/PVC | 4
F72MB412F-I1 | F72MB412F-VS | LIME SLAKING MILL 2 MOTOR 6 LV VSD |  | F72-MB-412F | LIME SLAKING MILL 2 MOTOR 6 THERMISTOR | LIME SLAKING MILL 2 | 1.5 | 0.11 | 165 | 1PR | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10681 | 720 | 0 | PVC/OSCN/PVC | 4
F72VR411-P1 | F72VR411-VS | LIME SILO 1 ROTARY VALVE LV VSD |  | F72-VR-411 | LIME SILO 1 ROTARY VALVE | LIME SILO 1 | 2.5 | 0.6/1 | 150 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10682 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 4
F72VR411LCS-C1 | F72-SW-072 | REAGENTS 415V MCC |  | F72VR411-LCS | LIME SILO 1 ROTARY VALVE LOCAL CONTROL STATION | LIME SILO 1 | 1.5 | 0.6/1 | 150 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10682 | 720 | 0 | PVC/PVC | 4
F72VR412-P1 | F72VR412-VS | LIME SILO 2 ROTARY VALVE LV VSD |  | F72-VR-412 | LIME SILO 2 ROTARY VALVE | LIME SILO 2 | 2.5 | 0.6/1 | 165 | 3C+3E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10683 | 720 | 0 | XLPE/PVC/CTS/PVC Flexible | 4
F72VR412LCS-C1 | F72-SW-072 | REAGENTS 415V MCC |  | F72VR412-LCS | LIME SILO 2 ROTARY VALVE LOCAL CONTROL STATION | LIME SILO 2 | 1.5 | 0.6/1 | 165 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10683 | 720 | 0 | PVC/PVC | 4
F72FN411-P1 | F72-SW-072 | REAGENTS 415V MCC |  | F72-FN-411 | SLAKED LIME WET SCRUBBER 1 FAN | LIME AREA | 2.5 | 0.6/1 | 145 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10660 | 720 | 0 | PVC/PVC | 4
F72FN411LCS-C1 | F72-SW-072 | REAGENTS 415V MCC |  | F72FN411-LCS | SLAKED LIME WET SCRUBBER 1 FAN LOCAL CONTROL STATION | LIME AREA | 1.5 | 0.6/1 | 145 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10660 | 720 | 0 | PVC/PVC | 4
F72FN412-P1 | F72-SW-072 | REAGENTS 415V MCC |  | F72-FN-412 | SLAKED LIME WET SCRUBBER 2 FAN | LIME AREA | 2.5 | 0.6/1 | 145 | 3C+E | Cu | Orange | Primero | Primero | 2000-F72-SCM-EL-10684 | 720 | 0 | PVC/PVC | 4
F72FN412LCS-C1 | F72-SW-072 | REAGENTS 415V MCC |  | F72FN412-LCS | SLAKED LIME WET SCRUBBER 2 FAN LOCAL CONTROL STATION | LIME AREA | 1.5 | 0.6/1 | 145 | 4C+E | Cu | Black | Primero | Primero | 2000-F72-SCM-EL-10684 | 720 | 0 | PVC/PVC | 4
F72CA401-P1 | F72-DB-303 | HYDROGEN PEROXIDE AREA L&SP DISTRIBUTION BOARD |  | F72-CA-401 | HYDROGEN PEROXIDE AREA CYANIDE ANALYSER | HYDROGEN PEROXIDE AREA | 4 | 0.6/1 | 20 | 2C+E | Cu | Orange | Primero | Primero | 2000-F72-TLD-EL-10103 | 720 | 0 | PVC/PVC | 4
F72CA401CP02-D1 | F72-RIO-002 | REAGENTS FIELD N-IO PANEL 2 |  | F72CA401-CP02 | HYDROGEN PEROXIDE AREA CYANIDE ANALYSER CONTROL PANEL | HYDROGEN PEROXIDE AREA | N/A | N/A | 60 | 4PR | Cu | Black | Primero | Primero | 2000-F72-TER-IC-10700 | 720 | 0 | CAT6 SF/UTP Outdoor Cable | 4