## Equipment list
Rev | Equip. Number | Equipment Name | Qty | Description | Make | Model | Supplied By | Installed By | Comments | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred Colour) | Installation | Revision | Equipment Type | Applicable Switchroom(s) | Dimensions Height x Width x Depth (mm) | Weight (kg) | Mounting | Cable Entry | Page
0 | F72-SR-001 | Reagents 415V Switchroom | 1 | Transportable switchroom complete with 1.8m legs and landings, transported to site 600kms on sealed roads. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero | Refer 2000-F00-DSH-EL-11001. | [20 empty] | 2
0 | - | Reagents 415V Switchroom Landings and Stairs | 1 | Equipment Landing to be structural steel baseframe complete with 1.8m legs, designed to support heaviest piece of equipment to be installed in room. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Primero | [21 empty] | 2
0 | - | Reagents 415V Switchroom Transformer cubicle | 1 | Separate dry transformer enclosure with removable wall panel and personnel access door Fortress key locked (Keyed alike) with 11kV feeder earth switch on F23-SW-016 11kV switchgear | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Access to transformer cubicle is only possible with 11kV Feeder isolated and earthed. Switchroom manufacturer to coordinate Fortress keys with TEKSAL. INCLUDE ANY PRESSURE RELIEF VENTS IF DEEMED NECESSARY BY THE VENDORS DESIGN | [20 empty] | 2
0 | - | Reagents 415V Switchroom Transformer cubicle Signage | 1 | TRANSFORMER ENCLOSURE FXX-TR-XXX 11,000/433 VOLTS (Modify to suit) DANGER – HIGH VOLTAGE (with the lightning bolt sign) NO UNAUTHORISED ACCESS – ENSURE SUPPLY IS ISOLATED AND EARTHED PRIOR TO ENTRY ISOLATE AT F23-SW-016, PANEL AXX (AXX being the 11kV panel/tier number) | Switchroom Vendor |  | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Signage to be placed on outside of transformer enclosure | [20 empty] | 2
0 | F72-TR-072 | Reagents 415V MCC Transformer | 1 | 11/0.433kV, 1600kVA, ANAF | Siemens | 11/0.433kV 1600kVA | Primero | Switchroom/MCC Vendor | Vendor to remove wheels and secure transformer once installed. Wheels to be stored securely within the transformer room. Vendor to bolt down/brace for transport. Refer transformer GAs. | [20 empty] | 2
0 | F72-SW-072 | Reagents 415V MCC | 1 | Demountable Form 4a double sided 415V Switchboard, 2500A bus, 65kA/1s fault rating, internal arc fault containment. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Vendor to install free issued network switches in MCC Refer datasheet 2000-F00-DSH-EL-11008 | [20 empty] | 2
0 | F72-SW-172 | Reagents Emergency 415V MCC | 1 | Demountable Form 4a single sided 415V Emergency Switchboard, 630A bus, 65kA/1s fault rating, internal arc fault containment. Automatic changeover switch on the incomer. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Refer datasheet 2000-F00-DSH-EL-11012 | [20 empty] | 2
0 | F72-DB-001 | Reagents 415V Switchroom L&SP Distribution Board | 1 | 415V 3Ø 250A DB. Fitted with incoming isolator, PE Cell circuit (night/day), Auto / Manual selector, Emergency light test controller, Rapidtest RCD test units, Lighting Contactors, air conditioner Contactors and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-EL-10025 & 2000-F00-STD-EL-10022; Switchroom Vendor to calculate number of required poles including the number of circuits for Air conditioners, 20% loaded Spare circuit breakers and 20% spare space. | [20 empty] | 2
0 | F72-DB-201 | Reagents 415V Switchroom 240V UPS Distribution Board | 1 | 240VAC 250A UPS DB. Fitted with incoming isolator and DB Legend. Incomer and circuit breakers to be padlockable in the off position. | Switchroom Vendor | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-EL-10027. Switchroom Vendor to calculate number of required poles including 20% loaded Spare circuit breakers and 20% spare space. | [20 empty] | 2
0 | F72-UPS-001 | Reagents 415V Switchroom 240VAC UPS | 1 | LV Switchroom 240V AC, 10kVA UPS, free-standing. 8 hours autonomy time. 3-Phase in / 1-Phase Out. | Riello | S3M 10 XTD T5 LL | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 10kVA/10kW Sentryum Xtend UPS - 3 Phase in- 1 out. With 9Ah Long Life Batteries. Vendor to secure wheels once installed. Vendor to bolt down/brace for transport. W: 440mm, D: 840mm, H: 1320mm, Weight: 415Kg. Tag updated. | [20 empty] | 2
0 | F72-BA-001 | Reagents 415V Switchroom 240VAC UPS Battery Bank | 1 | UPS Battery Cabinet w/ 120 x 9Ah batteries. | Riello | BB 1320 480-T5 LL | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 480V Extension Battery Cabinet with 120 x 9Ah Long life batteries W: 400mm, D: 815mm, H: 1320mm, Weight: 402Kg. Tag updated. | [20 empty] | 2
0 | - | Reagents 415V Switchroom 240VAC UPS Ethernet Card | 1 | Netman UPS Ethernet Card | Riello | Netman 208 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Supplied and installed into UPS by Switchroom Vendor | [20 empty] | 2
0 | - | Reagents 415V Switchroom 240VAC UPS Dry Contact Relay Card | 1 | Multicom Configurable Slot In Relay Card, 3 Inputs & 8 Outputs | Riello | Mulitcom 392 | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Supplied and installed into UPS by Switchroom Vendor | [20 empty] | 2
0 | F72UPS001-ISL | Reagents 415V Switchroom 240VAC UPS Maintenance Bypass Switch | 1 | External Wall-mount UPS bypass switch. | Riello | WABS 0063A-31H | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Wall mounted rotary style bypass switch. 3Ph in/1Ph out, 10kVA. Dimensions: 400 x 300 x 210mm. Tag updated. | [20 empty] | 2
0 | F72MB411A-VS | Lime Mill 1 Motor 1 LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 2
0 | F72MB411B-VS | Lime Mill 1 Motor 2 LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 2
0 | F72MB411C-VS | Lime Mill 1 Motor 3 LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 2
0 | F72MB411D-VS | Lime Mill 1 Motor 4 LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 2
0 | F72MB411E-VS | Lime Mill 1 Motor 5 LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 2
0 | F72MB411F-VS | Lime Mill 1 Motor 6 LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 2
0 | F72MB412A-VS | Lime Mill 2 Motor 1 LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 2
0 | F72MB412B-VS | Lime Mill 2 Motor 2 LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 2
0 | F72MB412C-VS | Lime Mill 2 Motor 3 LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 2
0 | F72MB412D-VS | Lime Mill 2 Motor 4 LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
0 | F72MB412E-VS | Lime Mill 2 Motor 5 LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
0 | F72MB412F-VS | Lime Mill 2 Motor 6 LV VSD | 1 | Allen-Bradley 55 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
0 | F72PP658-VS | Slaked Lime Transfer Pump 1 LV VSD | 1 | Allen-Bradley 30 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F5, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC085JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
0 | F72PP659-VS | Slaked Lime Transfer Pump 2 LV VSD | 1 | Allen-Bradley 30 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F5, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC085JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
0 | F72PP681-VS | Lead Nitrate Dosing Pump 1 LV VSD | 1 | Allen-Bradley 1.5 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC3P5JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
0 | F72PP682-VS | Lead Nitrate Dosing Pump 2 LV VSD | 1 | Allen-Bradley 1.5 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC3P5JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
0 | F72VR411-VS | Lime Silo 1 Rotary Valve LV VSD | 1 | Allen-Bradley 1.1 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC8P7JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
0 | F72VR412-VS | Lime Silo 2 Rotary Valve LV VSD | 1 | Allen-Bradley 1.1 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F2, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, 0, 0 | Allen-Bradley | 20F11NC8P7JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
1 | F72BW412-VS | Lime Delivery Blower LV VSD | 1 | Allen-Bradley 75 kW Heavy Duty, 415VAC, IP20 Wall mount. Accessories supplied loose: 20-750-NEMA1-F6, 20-HIM-A6, 20-750-APS, 20- 750-S, 20-750-20COMM + 20-COMM-M, , | Allen-Bradley | 20F1ANC170JA0NNNNN | Primero | Switchroom/MCC Vendor | Note 5 | [20 empty] | 3
0 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | 1 | Communications Rack, Free Standing 19", 42U, 1000mm deep, Mesh door, Lift Off Side Panels. Fitted with 10 way 240VAC plug power distribution panel, wire management covers, shelves and cage nuts. Fitted out with FOBOTs (vendor supplied), DIN rail adapter (vendor supplied), and network switches (free issued). | Rittal | TS IT Enclosure (P/N 5514.110) + Accessories | Switchroom/MCC Vendor | Switchroom/MCC Vendor | In accordance to Drawing 2000-F00-STD-IC-10101 | [20 empty] | 3
0 | F72COM001-JB | Reagents 415V Switchroom Communications Rack 240VAC UPS Junction Box | 1 | Communications Rack, Free Standing 19", 42U, 1000mm deep, Mesh door, Lift Off Side Panels. Fitted with 10 way 240VAC plug power distribution panel, wire management covers, shelves and cage nuts. Fitted out with FOBOTs (vendor supplied), DIN rail adapter (vendor supplied), and network switches (free issued). | Rittal | TS IT Enclosure (P/N 5514.110) + Accessories | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Junction box for PDU Rail | [20 empty] | 3
0 | F72-FOB-001 | Reagents 415V Switchroom Fibre Optic Breakout Tray | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | [20 empty] | 3
0 | F72-FOB-002 | Reagents 415V Switchroom Fibre Optic Breakout Tray | 1 | 48C SMOF Capacity FOBOT C/W Splice hardware & 1-12 LC Duplex Faceplate/Blank Faceplate | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. | [20 empty] | 3
0 | F72-FOB-004A/B | Reagents 415V Switchroom RIO Circuit Fibre Optic Breakout Ring 1 Tray #1 | 1 | 2 X 12C SMOF Capacity FOBOT C/W Splice hardware & 1-6 LC Duplex Faceplate (LHS) + 1-6 LC Duplex Faceplate (RHS) | AFL Global | FRE Sliding | Switchroom/MCC Vendor | Switchroom/MCC Vendor | To be supplied "fully loaded" including all splice gear in a kit inside the FOBOT. One FOBOT with two 12C faceplates. Vendor to label each side as per equipment number and name. | [20 empty] | 3
0 | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | 1 | Custom Built Panel. Indoor, Mild Steel. Contains DCS hardware, power supply, MCBs and marshalling terminals. | Fabricated Panel | Custom | Primero | Switchroom/MCC Vendor | [21 empty] | 3
0 | F72SR001-LCS | Reagents 415V Switchroom Emergency Shutdown | 1 | Switchroom Emergency Shutdown C/w shroud or lift-up flap and labelling | Fabricated Panel | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | With E34 Red 40mm Mushroom pushbutton (P/N E34LB2), and 2 off 2 N/O Contact Blocks (10250T2). Refer 2000-F00-STS-EL-10011 Section 4.19. | [20 empty] | 3
0 | F72-FIP-001 | Reagents 415V Switchroom Fire Indicator Panel | 1 | Fire Indicator Panel c/w full installation, wiring, certification, testing and commissioning. HVAC trip upon alarm. FIP shall include SMOF modems for connection to site-wide fire system network. | Wormald | Vigilant 8 Zone F3200 Conventional SHCIE FIP | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Rated to operate in 50C ambience temperature | [20 empty] | 3
0 | F72FIP001-XE1 | Reagents 415V Switchroom VESDA Panel | 1 | VESDA Panel c/w full installation, wiring, certification, testing and commissioning.Alarm and fault signals to fire panel. | Xtralis | VESDA LaserPlus Scanner 12 relay VLS300 ASD system | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Rated to operate in 50C ambience temperature | [20 empty] | 3
0 | F72FIP001-XE2 | Reagents 415V Switchroom Manual Call Points | VTA | Fire system Manual Call points (internal and external) as required by Australian Standards | Wormald | Manual Call Points | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Manual call points shall be tagged in sequential order | [20 empty] | 3
0 | F72FIP001-XE3 | Reagents 415V Switchroom Smoke Detector | VTA | Fire system smoke detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order | [20 empty] | 3
0 | F72FIP001-XE4 | Reagents 415V Switchroom Heat Detector | VTA | Fire system heat detectors as required by Australian Standards | Wormald | Addressable Optical | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Detectors shall be tagged in sequential order | [20 empty] | 3
0 | F72FIP001-UA | Reagents 415V Switchroom External Alarm Bells | VTA | Fire system alarm bells as required by Australian Standards | Wormald | External Sounder / Red Strobe | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Alarm sirens shall be tagged in sequential order | [20 empty] | 3
0 | F72FIP001-XE5 | Reagents 415V Switchroom Gas Suppression System (Inergen) | 1 | Inergen gas suppression system incl. all valves and pipework, gas cylinders placed inside switchroom, refer to Switchroom General Arrangement | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 3
0 | - | Reagents 415V Switchroom Fire Extinguishers | VTA | 5kg dry powder fire extinguishers complete with wall mount and signage. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 3
0 | - | Reagents 415V Switchroom Automatic External Defibrillator | 1 | Automatic external defibrillator complete with wall-mounted cabinet. | Physio Control | Lifepak Defibrillator CR2 Fully Automatic | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 3
0 | - | Reagents 415V Switchroom LV Rescue Kit | 1 | To be suitably located by Vendor. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 3
0 | - | Reagents 415V Switchroom HVAC controller | VTA | Wall mounted Air Conditioner Controller, with relay contacts for Faulty & Healthy | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | One wall mounted controller to control all A/C's per room (One per transformer room, LV room, HV room). | [20 empty] | 3
0 | F72-AC-1XX | Reagents 415V Switchroom Air Conditioners | VTA | High Wall split system, single phase, MULTIPLE (N+1 reqd) with drip trays if necessary | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. AC units shall be tagged in numerical order (e.g. F72-AC-101, F12-AC-102 etc) | [20 empty] | 3
0 | F72AC1XX-ISL | Reagents 415V Switchroom Air Conditioner Isolators | 1 lot | Field isolator, one per split system Air Conditioner | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Isolators shall be tagged with the respective AC equipment number (e.g. F72AC101-ISL etc) | [20 empty] | 3
0 | - | Reagents 415V Switchroom Normal Light Fittings | 1 lot | Lighting to meet National Construction Code | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | [20 empty] | 3
0 | - | Reagents 415V Switchroom Emergency Light Fittings | 1 lot | Lighting to meet National Construction Code; C/w built in battery pack. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | Sizing / qtys are the responsibility of the Switchroom Vendor. Fittings shall be tagged and labelled as per L&SP circuit. | [20 empty] | 3
0 | UT72035 | F72-SR-072 Reagents 415V Switchroom Temperature/Humidity Transmitter | 1 | 415V Switchroom Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | [20 empty] | 4
0 | UT72036 | F72-TR-072 Reagents 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | 1 | Transformer Room Temperature/Humidity Transmitter | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | 4-20mA Combined Temperature/Humidity Transmitter for DCS Switchroom Monitoring - 1 per switching room & transformer room. Not required in airlock. Vendor to position | [20 empty] | 4
0 | F72-PE-001 | Reagents 415V Switchroom Photo-electric cell | 1 | Switchroom Photo-electric cell | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | PE Cell - 1 per building. Vendor to position | [20 empty] | 4
0 | F72SW072-LCS | Reagents 415V Switchroom Remote Switching Panel | 1 | LV MCC Incomer Remote Switching Panel | NHP | TemRack LCS | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 4
0 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | 1 | External to Room: 50 x 6.3mm Tinned Flat Copper Bus bar mounted on insulated standoffs under switchroom floor. Drilled/punch 12mm diameter holes suitable for connection of all internal equipment earth cables to meet requirements of cable schedule. To have spare capacity for connection of an additional 4 x 120mm2 conductors and 4 x 70mm2 conductors, as a minimum. | GVK or similar |  | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 4
0 | F72TR072-EB01 | Reagents 415V MCC Transformer Earth Bar | 1 | 50 x 6.3mm Tinned Flat Copper Bus bar mounted on insulated standoffs on Transformer. | Generic |  | Transformer Vendor | Transformer Vendor | [21 empty] | 4
0 | F72SW072-EB01 | Reagents 415V MCC Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on insulated standoffs inside MCC. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 4
0 | F72SW172-EB01 | Reagents Emergency 415V MCC Earth Bar | 1 | Tinned Flat Copper Bus bar mounted on insulated standoffs inside MCC. | VTA | VTA | Switchroom/MCC Vendor | Switchroom/MCC Vendor | [21 empty] | 4
[7 empty] | Switchroom Vendor | Switchroom Vendor | Earth bonding conductors shall be equal to the larger of 16mm2 or equipment phase conductor size, but no greater than 120mm2. | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | Multiple | Each UPS, DB, switching panel, or other electrical panels. | Reagents 415V Switchroom | Note 6. | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 0 | [6 empty] | 9
[7 empty] | Switchroom Vendor | Switchroom Vendor | Ladder to be bonded to earth bar in two places and bonded across each fish plate. | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | Multiple | Subfloor cable ladder. | Reagents 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 0 | [6 empty] | 9
[7 empty] | Switchroom Vendor | Switchroom Vendor | Switchroom subframe to be bonded to switchroom earth bar. Earth bonds to be at two opposing corners. | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | Multiple | Switchroom subframe. | Reagents 415V Switchroom | 70 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | 0 | [6 empty] | 9
[5 empty] | Allen-Bradley | Frame 2 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 1.5kW | 415V Switchrooms | 500 x 134 x 212 | 8 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 2 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 4kW | 415V Switchrooms | 500 x 134 x 212 | 8 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 2 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 5.5kW | 415V Switchrooms | 500 x 134 x 212 | 8 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 2 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 7.5kW | 415V Switchrooms | 500 x 134 x 212 | 8 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 3 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 11kW | 415V Switchrooms | 531 x 190 x 223.1 | 11 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 3 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 15kW | 415V Switchrooms | 531 x 190 x 223.1 | 11 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 4 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 30kW | 415V Switchrooms | 565.2 x 222 x 222.7 | 16 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 5 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 37kW | 415V Switchrooms | 666.1 x 270 x 222.7 | 24 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 5 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 45kW | 415V Switchrooms | 666.1 x 270 x 222.7 | 24 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 5 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 45kW AFE | 415V Switchrooms | 1127 x 334 x 357 | 125 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 6 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 55kW | 415V Switchrooms | 945.1 x 308 x 346.7 | 39 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 6 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 55kW AFE | 415V Switchrooms | 1876 x 405 x 432 | 145 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 6 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 75kW | 415V Switchrooms | 945.1 x 308 x 346.7 | 39 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 6 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 90kW | 415V Switchrooms | 945.1 x 308 x 346.7 | 39 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 7 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 132kW | 415V Switchrooms | 1271 x 430 x 561 | 106 | Wall Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 8 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 250kW | 415V Switchrooms | 2453 x 600 x 600 | 644 | Floor Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 8 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 250kW AFE | 415V Switchrooms | 2132 x 1200 x 676 | 900 | Floor Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 8 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 315kW | 415V Switchrooms | 2453 x 600 x 600 | 644 | Floor Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 8 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 355kW | 415V Switchrooms | 2453 x 600 x 600 | 644 | Floor Mount | Bottom Entry | 10
[5 empty] | Allen-Bradley | Frame 9 | Primero | Switchroom Vendor | [15 empty] | LV VSD - 500kW | 415V Switchrooms | 2453 x 1200 x 600 | 1287 | Floor Mount | Bottom Entry | 10
[5 empty] | Fabricated Panel | Custom | Primero | Switchroom Vendor | Top entry for communication wiring, bottom entry for power and control. | [14 empty] | Switchroom DCS Panel | 415V Switchrooms | 2000x800x400 | 400kg est. | Floor Mount | Top & Bottom Entry | 10
[5 empty] | Fabricated Panel | Custom | Primero | Switchroom Vendor | Top entry for communication wiring, bottom entry for power and control. | [14 empty] | Switchroom Remote I/O Panel | F00-SR-001, F16-SR-001 | 2000x800x400 | 400kg est. | Floor Mount | Top & Bottom Entry | 10
[5 empty] | Siemens | 11/0.433kV 2500kVA | Primero | Switchroom Vendor | Installed on rails to roll transformer in/out. Refer 2000-EL004-B02- 10001 | [14 empty] | 415V Transformer 11/0.433kV 2500kVA | F12-SR-002 | 1968 x 1280 x 2400 | 5100 | Floor Mount | Bottom Entry | 10
[5 empty] | Siemens | 33/0.433kV 2500kVA | Primero | Switchroom Vendor | Installed on rails to roll transformer in/out. Refer 2000-EL004-B02- 10001 | [14 empty] | 415V Transformer 33/0.433kV 2500kVA | 415V Switchrooms | 2248 x 1280 x 2760 | 6300 | Floor Mount | Bottom Entry | 10
[5 empty] | Siemens | 11/0.433kV 630kVA | Primero | Switchroom Vendor | Installed on rails to roll transformer in/out. Refer 2000-EL004-B02- 10001 | [14 empty] | 415V Transformer 11/0.433kV 630kVA | F16-SR-002 | 1408 x 820 x 1850 | 1950 | Floor Mount | Bottom Entry | 10
[5 empty] | Siemens | 33/0.433kV 1000kVA | Primero | Switchroom Vendor | Installed on rails to roll transformer in/out. Refer 2000-EL004-B02- 10001 | [14 empty] | 415V Transformer 33/0.433kV 1000kVA | F23-SR-002, F28-SR-002 | 1828 x 990 x 2350 | 3420 | Floor Mount | Bottom Entry | 10
[5 empty] | ABB | ZX2 | Primero | Switchroom Vendor | HV Cables - Bottom Entry 48VDC/Control/Comms - Top Entry (to rear of each control compartment) | [14 empty] | 33kV Switchboard Incomer Panel | F00-SR-001 | 800mm W x 1860mm D x 2600mm H | 2000 | Floor Mount | Bottom & Top Entry | 10
[5 empty] | ABB | ZX2 | Primero | Switchroom Vendor | HV Cables - Bottom Entry 48VDC/Control/Comms - Top Entry (to rear of each control compartment) | [14 empty] | 33kV Switchboard Feeder Panel | F00-SR-001 | 600mm W x 1860mm D x 2600mm H | 1400 | Floor Mount | Bottom & Top Entry | 10
[5 empty] | ABB | ZX2 | Primero | Switchroom Vendor | HV Cables - Bottom Entry 48VDC/Control/Comms - Top Entry (to rear of each control compartment) | [14 empty] | 33kV Switchboard Bus Tie Panel | F00-SR-001 | 800mm W x 1860mm D x 2600mm H | 2400 | Floor Mount | Bottom & Top Entry | 10
[5 empty] | ABB | ZS1 | Primero | Switchroom Vendor | HV Cables - Bottom Entry 48VDC/Control/Comms - Top Entry (to rear of each control compartment) | [14 empty] | 11kV Switchboard Incomer Panel | 11kV Switchrooms | 650mm W x 1340mm D x 2533mm H | 850 | Floor Mount | Bottom & Top Entry | 10
[5 empty] | ABB | ZS1 | Primero | Switchroom Vendor | HV Cables - Bottom Entry 48VDC/Control/Comms - Top Entry (to rear of each control compartment) | [14 empty] | 11kV Switchboard Feeder Panel | 11kV Switchrooms | 650mm W x 1340mm D x 2533mm H | 850 | Floor Mount | Bottom & Top Entry | 10
[5 empty] | ABB | ZS1 | Primero | Switchroom Vendor | HV Cables - Bottom Entry 48VDC/Control/Comms - Top Entry (to rear of each control compartment) | [14 empty] | 11kV Switchboard VT Panel | 11kV Switchrooms | 650mm W x 1340mm D x 2533mm H | 850 | Floor Mount | Bottom & Top Entry | 10
[5 empty] | Siemens | SINAMICS Pefect Harmony GH180 6SR55020NE380BH0-Z | Primero | Switchroom Vendor | [15 empty] | 800kVA, 200A HV VSD (Heavy Duty) | F16-SR-001, F23-SR-001 | H=2223mm, W=2905mm, D=1143mm | 3100 | Floor Mount | Bottom Entry | 10
[5 empty] | Siemens | SINAMICS Pefect Harmony GH180 6SR55020NF412BH0-Z | Primero | Switchroom Vendor | [15 empty] | 1250kVA, 260A HV VSD (Heavy Duty) | F16-SR-001, F23-SR-001 | H=2223mm, W=2905mm, D=1143mm | 4950 | Floor Mount | Bottom Entry | 10
[5 empty] | Siemens | SINAMICS Pefect Harmony GH180 6SR55020NG412BH0-Z | Primero | Switchroom Vendor | [15 empty] | 1250kVA, 340A HV VSD (Heavy Duty) | F12-SR-001 | H=2380mm, W=3400mm, D=1230mm | 4141.6 | Floor Mount | Bottom Entry | 10

## Cable schedule
Cable Number | From Equip. Number | From Equipment Name | From Location | To Equip. Number | To Equipment Name | To Location | Conductor Size (mm2) | Insulation (kV) | No. of Cores / Pairs | Conductor | Construction | Sheath (Preferred Colour) | Installation | Supplied By | Installed By | Revision | Comments | Page
F72SW072-P1-R | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-P1-W | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-P1-B | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-P2-R | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-P2-W | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-P2-B | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-P3-R | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-P3-W | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-P3-B | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-P4-R | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-P4-W | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-P4-B | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-N1 | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-N2 | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-N3 | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW072-N4 | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 300 | 0.6/1 | 1C | Cu | XLPE-110/PVC Flex | Orange | Ladder - Trefoil | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW172-P1-R | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | 150 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW172-P1-W | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | 150 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW172-P1-B | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | 150 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW172-P2-R | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | 150 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW172-P2-W | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | 150 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW172-P2-B | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | 150 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW172-N1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | 150 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72SW172-N2 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | 150 | 0.6/1 | 1C | Cu | XLPE-H-110/PVC Flexible | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72MB411AVS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB411A-VS | Lime Mill 1 Motor 1 LV VSD | Reagents 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72MB411BVS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB411B-VS | Lime Mill 1 Motor 2 LV VSD | Reagents 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72MB411CVS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB411C-VS | Lime Mill 1 Motor 3 LV VSD | Reagents 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72MB411DVS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB411D-VS | Lime Mill 1 Motor 4 LV VSD | Reagents 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72MB411EVS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB411E-VS | Lime Mill 1 Motor 5 LV VSD | Reagents 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72MB411FVS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB411F-VS | Lime Mill 1 Motor 6 LV VSD | Reagents 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72MB412AVS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB412A-VS | Lime Mill 2 Motor 1 LV VSD | Reagents 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72MB412BVS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB412B-VS | Lime Mill 2 Motor 2 LV VSD | Reagents 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72MB412CVS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB412C-VS | Lime Mill 2 Motor 3 LV VSD | Reagents 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72MB412DVS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB412D-VS | Lime Mill 2 Motor 4 LV VSD | Reagents 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72MB412EVS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB412E-VS | Lime Mill 2 Motor 5 LV VSD | Reagents 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72MB412FVS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB412F-VS | Lime Mill 2 Motor 6 LV VSD | Reagents 415V Switchroom | 70 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72PP658VS-P1 | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | F72PP658-VS | Slaked Lime Transfer Pump 1 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72PP659VS-P1 | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | F72PP659-VS | Slaked Lime Transfer Pump 2 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72PP681VS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72PP681-VS | Lead Nitrate Dosing Pump 1 LV VSD | Reagents 415V Switchroom | 2.5 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72PP682VS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72PP682-VS | Lead Nitrate Dosing Pump 2 LV VSD | Reagents 415V Switchroom | 2.5 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 5
F72VR411VS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72VR411-VS | Lime Silo 1 Rotary Valve LV VSD | Reagents 415V Switchroom | 2.5 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72VR412VS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72VR412-VS | Lime Silo 2 Rotary Valve LV VSD | Reagents 415V Switchroom | 2.5 | 0.6/1 | 3C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72BW412VS-P1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72BW412-VS | Lime Delivery Blower LV VSD | Reagents 415V Switchroom | 95 | 0.6/1 | 3C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 6
F72DB001-P1 | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | F72-DB-001 | Reagents 415V Switchroom L&SP Distribution Board | Reagents 415V Switchroom | 150 | 0.6/1 | 4C+E | Cu | XLPE/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Flexible cable | 6
F72UPS001ISL-P1 | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | F72UPS001-ISL | Reagents 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Reagents 415V Switchroom | 16 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72UPS001-P1 | F72UPS001-ISL | Reagents 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Reagents 415V Switchroom | F72-UPS-001 | Reagents 415V Switchroom 240VAC UPS | Reagents 415V Switchroom | 6 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72UPS001ISL-P2 | F72-UPS-001 | Reagents 415V Switchroom 240VAC UPS | Reagents 415V Switchroom | F72UPS001-ISL | Reagents 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Reagents 415V Switchroom | 10 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72BA001-P1 | F72-UPS-001 | Reagents 415V Switchroom 240VAC UPS | Reagents 415V Switchroom | F72-BA-001 | Reagents 415V Switchroom 240VAC UPS Battery Bank | Reagents 415V Switchroom | 50 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72DB201-P1 | F72UPS001-ISL | Reagents 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Reagents 415V Switchroom | F72-DB-201 | Reagents 415V Switchroom 240V UPS Distribution Board | Reagents 415V Switchroom | 16 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72DCS413-P1 | F72-DB-201 | Reagents 415V Switchroom 240V UPS Distribution Board | Reagents 415V Switchroom | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72COM001-P1 | F72-DB-201 | Reagents 415V Switchroom 240V UPS Distribution Board | Reagents 415V Switchroom | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | PDU | 6
F72SW072-P5 | F72-DB-201 | Reagents 415V Switchroom 240V UPS Distribution Board | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC PSU 1 | 6
F72SW072-P6 | F72-DB-201 | Reagents 415V Switchroom 240V UPS Distribution Board | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC PSU 2 | 6
F72SW172-P3 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | 10 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 24VDC Supply to Emergency Board | 6
F72TR072-P2 | F72-DB-001 | Reagents 415V Switchroom L&SP Distribution Board | Reagents 415V Switchroom | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | 4 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 240V for transformer cooling fans | 6
F72FIP001-P1 | F72-DB-001 | Reagents 415V Switchroom L&SP Distribution Board | Reagents 415V Switchroom | F72-FIP-001 | Reagents 415V Switchroom Fire Indicator Panel | Reagents 415V Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72FIP001XE1-P1 | F72-FIP-001 | Reagents 415V Switchroom Fire Indicator Panel | Reagents 415V Switchroom | F72FIP001-XE1 | Reagents 415V Switchroom VESDA Panel | Reagents 415V Switchroom | 2.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Orange | Ladder | Switchroom Vendor | Switchroom Vendor | 0 | VESDA Panel Power. | 6
F72SW072-C1 | F72SR001-LCS | Reagents 415V Switchroom Emergency Shutdown | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Emerg/ Shutdown Circuit. E-stop to trip incomer / Marshall trip to upstream 11kV Feeder. | 6
F72SW172-C1 | F72SR001-LCS | Reagents 415V Switchroom Emergency Shutdown | Reagents 415V Switchroom | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Emerg/ Shutdown Circuit. E-stop to trip incomer | 6
F72SR001LCS-C1 | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | F72SR001-LCS | Reagents 415V Switchroom Emergency Shutdown | Reagents 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Orange | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 24VDC supply to PILZ relay in Switchroom E-shut, plus feedback | 6
F72TR072-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Transformer Signals to MCC | 6
F72MB411AVS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB411A-VS | Lime Mill 1 Motor 1 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72MB411BVS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB411B-VS | Lime Mill 1 Motor 2 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72MB411CVS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB411C-VS | Lime Mill 1 Motor 3 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72MB411DVS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB411D-VS | Lime Mill 1 Motor 4 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72MB411EVS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB411E-VS | Lime Mill 1 Motor 5 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72MB411FVS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB411F-VS | Lime Mill 1 Motor 6 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72MB412AVS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB412A-VS | Lime Mill 2 Motor 1 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72MB412BVS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB412B-VS | Lime Mill 2 Motor 2 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72MB412CVS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB412C-VS | Lime Mill 2 Motor 3 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72MB412DVS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB412D-VS | Lime Mill 2 Motor 4 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72MB412EVS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB412E-VS | Lime Mill 2 Motor 5 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72MB412FVS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72MB412F-VS | Lime Mill 2 Motor 6 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72PP658VS-C1 | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | F72PP658-VS | Slaked Lime Transfer Pump 1 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72PP659VS-C1 | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | F72PP659-VS | Slaked Lime Transfer Pump 2 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72PP681VS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72PP681-VS | Lead Nitrate Dosing Pump 1 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 6
F72PP682VS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72PP682-VS | Lead Nitrate Dosing Pump 2 LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72VR411VS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72VR411-VS | Lime Silo 1 Rotary Valve LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72VR412VS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72VR412-VS | Lime Silo 2 Rotary Valve LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72BW412VS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72BW412-VS | Lime Delivery Blower LV VSD | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 1 |  | 7
F72SW072-C2 | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 1.5 | 0.6/1 | 15C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Incomer Signals to DCS | 7
F72SW172-C2 | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | MCC Incomer Signals to DCS | 7
F72DB001-C1 | F72-FIP-001 | Reagents 415V Switchroom Fire Indicator Panel | Reagents 415V Switchroom | F72-DB-001 | Reagents 415V Switchroom L&SP Distribution Board | Reagents 415V Switchroom | 1.5 | 0.6/1 | 2C+E | Cu | PVC/PVC | Black | Ladder | Switchroom Vendor | Switchroom Vendor | 0 | HVAC trip. | 7
F72FIP001-C1 | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | F72-FIP-001 | Reagents 415V Switchroom Fire Indicator Panel | Reagents 415V Switchroom | 1.5 | 0.6/1 | 10C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72DCS413-C2 | - | - | Reagents 415V Switchroom | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Healthy/Fault feedback from wall mounted A/C Controller | 7
F72DB001-C2 | F72-PE-001 | Reagents 415V Switchroom Photo-electric cell | Reagents 415V Switchroom | F72-DB-001 | Reagents 415V Switchroom L&SP Distribution Board | Reagents 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | Lighting Control. Via Photocell direct to L&SP DB | 7
UT72035-I1 | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | UT72035 | F72-SR-072 Reagents 415V Switchroom Temperature/Humidity Transmitter | Reagents 415V Switchroom | 1.5 | 0.15 | 2pr | Cu | PVC/OSCN/PVC | Black | Ladder | Switchroom Vendor | Switchroom Vendor | 0 | Cable changed to Overall Screen | 7
UT72036-I1 | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | UT72036 | F72-TR-072 Reagents 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | Reagents 415V Switchroom | 1.5 | 0.15 | 2pr | Cu | PVC/OSCN/PVC | Black | Ladder | Switchroom Vendor | Switchroom Vendor | 0 | Cable changed to Overall Screen | 7
ZSC72034-I1 | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | ZSC72034 | F72-TR-072 Reagents 415V MCC Transformer Enclosure Door Position Switch Closed | Reagents 415V Switchroom | 1.5 | 0.15 | 2pr | Cu | PVC/OSCN/PVC | Black | Ladder | Switchroom Vendor | Switchroom Vendor | 0 | Transformer Enclosure Door feedback Cable changed to Overall Screen | 7
F72UPS001-C2 | F72UPS001-ISL | Reagents 415V Switchroom 240VAC UPS Maintenance Bypass Switch | Reagents 415V Switchroom | F72-UPS-001 | Reagents 415V Switchroom 240VAC UPS | Reagents 415V Switchroom | 1.5 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder | Switchroom Vendor | Switchroom Vendor | 0 | By pass | 7
F72SW072LCS-C1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72SW072-LCS | Reagents 415V Switchroom Remote Switching Panel | Reagents 415V Switchroom | 1.5 | 0.6/1 | 20C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72SW072-C5 | F72-TR-072 | Reagents 415V MCC Transformer | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 6 | 0.6/1 | 6C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | AFD CT Cable | 7
F72SW072-C3 | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 24VDC PSU monitoring | 7
F72SW072-C4 | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | 1.5 | 0.6/1 | 4C+E | Cu | PVC/PVC | Black | Ladder - Subframe | Switchroom Vendor | Switchroom Vendor | 0 | 24VDC PSU monitoring | 7
F72FIP001-FO1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-FIP-001 | Reagents 415V Switchroom Fire Indicator Panel | Reagents 415V Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Site-Wide Fire network - patch to FIP. | 7
F72FIP001-F02 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-FIP-001 | Reagents 415V Switchroom Fire Indicator Panel | Reagents 415V Switchroom | N/A | N/A | 2C | Fibre | LC-ST Patch (SMFO) | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | Site-Wide Fire network - patch to FIP. | 7
F72UPS001-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-UPS-001 | Reagents 415V Switchroom 240VAC UPS | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72SW172-D1 | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | VAMP CAN Bus Cable. | 7
F72SW172-D11 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-SW-172 | Reagents Emergency 415V MCC | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | Connected to F72-ETH-026 Emergency MCC ethernet switch. Tag Updated | 7
F72MB411AVS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72MB411A-VS | Lime Mill 1 Motor 1 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72MB411BVS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72MB411B-VS | Lime Mill 1 Motor 2 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72MB411CVS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72MB411C-VS | Lime Mill 1 Motor 3 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72MB411DVS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72MB411D-VS | Lime Mill 1 Motor 4 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72MB411EVS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72MB411E-VS | Lime Mill 1 Motor 5 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72MB411FVS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72MB411F-VS | Lime Mill 1 Motor 6 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72MB412AVS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72MB412A-VS | Lime Mill 2 Motor 1 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72MB412BVS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72MB412B-VS | Lime Mill 2 Motor 2 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72MB412CVS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72MB412C-VS | Lime Mill 2 Motor 3 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72MB412DVS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72MB412D-VS | Lime Mill 2 Motor 4 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72MB412EVS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72MB412E-VS | Lime Mill 2 Motor 5 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72MB412FVS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72MB412F-VS | Lime Mill 2 Motor 6 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 7
F72PP658VS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72PP658-VS | Slaked Lime Transfer Pump 1 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72PP659VS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72PP659-VS | Slaked Lime Transfer Pump 2 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72PP681VS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72PP681-VS | Lead Nitrate Dosing Pump 1 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72PP682VS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72PP682-VS | Lead Nitrate Dosing Pump 2 LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72VR411VS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72VR411-VS | Lime Silo 1 Rotary Valve LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72VR412VS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72VR412-VS | Lime Silo 2 Rotary Valve LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72BW412VS-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72BW412-VS | Lime Delivery Blower LV VSD | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 |  | 8
F72SW072-D11 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | Connected to F72-ETH-021 MCC ethernet switch. Tag Updated | 8
F72SW072-D12 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | Connected to F72-ETH-022 MCC ethernet switch. Tag Updated | 8
F72SW072-D13 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | Connected to F72-ETH-023 MCC ethernet switch. Tag Updated | 8
F72SW072-D14 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | Connected to F72-ETH-024 MCC ethernet switch. Tag Updated | 8
F72SW072-D15 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-SW-072 | Reagents 415V MCC | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 1 | Connected to F72-ETH-025 MCC ethernet switch. Tag Updated | 8
F72DCS413-D1 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Orange | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 1 PRIMARY | 8
F72DCS413-D2 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Orange | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 1 SECONDARY | 8
F72DCS413-D3 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Purple | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 2 PRIMARY | 8
F72DCS413-D4 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Purple | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - CPU 2 SECONDARY | 8
F72DCS413-D5 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - ALE CARD (AS REQUIRED) | 8
F72DCS413-D6 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | N/A | N/A | 4 pr | Cu | CAT6A (Shielded) | Green | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - ALE CARD (AS REQUIRED) | 8
F72DCS413-F01 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED) | 8
F72DCS413-F02 | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | F72-DCS-413 | Reagents 415V Switchroom DCS Panel | Reagents 415V Switchroom | N/A | N/A | 2C | Fibre | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | DCS Comms Allowance - RIO UPLINK (AS REQUIRED) | 8
F72COM001-FOx | F72-COM-001 | Reagents 415V Switchroom Communications Rack | Reagents 415V Switchroom | Multiple | Misc SMOF Patch leads in Panel | Reagents 415V Switchroom | N/A | N/A | 2C |  | OS2 SMOF Fibre Patch Lead | Yellow | Suspended Tray / Duct on wall | Switchroom Vendor | Switchroom Vendor | 0 | 1 lot; Qty TBC | 8
F72TR072EB01-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72TR072-EB01 | Reagents 415V MCC Transformer Earth Bar | Reagents 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72TR072EB01-E2 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72TR072-EB01 | Reagents 415V MCC Transformer Earth Bar | Reagents 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72SW072EB01-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72SW072-EB01 | Reagents 415V MCC Earth Bar | Reagents 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72SW072EB01-E2 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72SW072-EB01 | Reagents 415V MCC Earth Bar | Reagents 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72SW172EB01-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72SW172-EB01 | Reagents Emergency 415V MCC Earth Bar | Reagents 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72SW172EB01-E2 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72SW172-EB01 | Reagents Emergency 415V MCC Earth Bar | Reagents 415V Switchroom | 120 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72MB411AVS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72MB411A-VS | Lime Mill 1 Motor 1 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72MB411BVS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72MB411B-VS | Lime Mill 1 Motor 2 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72MB411CVS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72MB411C-VS | Lime Mill 1 Motor 3 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72MB411DVS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72MB411D-VS | Lime Mill 1 Motor 4 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72MB411EVS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72MB411E-VS | Lime Mill 1 Motor 5 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72MB411FVS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72MB411F-VS | Lime Mill 1 Motor 6 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72MB412AVS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72MB412A-VS | Lime Mill 2 Motor 1 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72MB412BVS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72MB412B-VS | Lime Mill 2 Motor 2 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72MB412CVS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72MB412C-VS | Lime Mill 2 Motor 3 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72MB412DVS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72MB412D-VS | Lime Mill 2 Motor 4 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72MB412EVS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72MB412E-VS | Lime Mill 2 Motor 5 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72MB412FVS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72MB412F-VS | Lime Mill 2 Motor 6 LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 8
F72PP658VS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72PP658-VS | Slaked Lime Transfer Pump 1 LV VSD | Reagents 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F72PP659VS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72PP659-VS | Slaked Lime Transfer Pump 2 LV VSD | Reagents 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F72PP681VS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72PP681-VS | Lead Nitrate Dosing Pump 1 LV VSD | Reagents 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F72PP682VS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72PP682-VS | Lead Nitrate Dosing Pump 2 LV VSD | Reagents 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F72VR411VS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72VR411-VS | Lime Silo 1 Rotary Valve LV VSD | Reagents 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F72VR412VS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72VR412-VS | Lime Silo 2 Rotary Valve LV VSD | Reagents 415V Switchroom | 16 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 0 |  | 9
F72BW412VS-E1 | F72SR001-EB01 | Reagents 415V Switchroom Main Earth Bar | Reagents 415V Switchroom | F72BW412-VS | Lime Delivery Blower LV VSD | Reagents 415V Switchroom | 35 | 0.6/1 | 1C | Cu | PVC | Green/Yellow | Ladder | Switchroom Vendor | Switchroom Vendor | 1 |  | 9