## Load list
Nameplate (kW) | Active Power (kW) | Apparent Power (kVA) | Reactive Power (kVAR) | Annual Energy Consumption (MWh) | Equipment Number | Equipment Description | Voltage (V) | Load Type | Duty / Standby | MCC | Motor / Load Efficiency 75% Load | Motor / Load Power Factor 75% Load | Load Factor (LF) | Plant Diversity Factor (PDF) | Annual Run Hours | Schematic Diagram | Data Source | Status | Rev | Page
114 | 91 | 107 | 23 | 349 | [15 empty] | 5
22 | 17 | 19 | 4 | 74 | F75-PS-556 | FIM III Underdrainage Pump 1 | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F75-SW-556 | 0.92 | 0.89 | 0.70 | 0.50 | 1.00 | 2000-F75-SCM-EL-40111 | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
22 | 17 | 19 | 4 | 74 | F75-PS-557 | FIM III Underdrainage Pump 2 | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F75-SW-557 | 0.92 | 0.89 | 0.70 | 0.50 | 1.00 | 2000-F75-SCM-EL-40112 | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
8 | 7 | 8 | 2 | 29 | F75-PS-558 | FIM III Toe Drain Pump | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F75-SW-557 | 0.86 | 0.85 | 0.70 | 0.50 | 1.00 | 2000-F75-SCM-EL-40113 | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
2.2 | 2 | 2 | 1 | 8 | F75-PS-801 | FIM III Seepage Pump 1 | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F75-SW-801 | 0.88 | 0.73 | 0.70 | 0.50 | 1.00 | 2000-F75-SCM-EL-40114 | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
2.2 | 2 | 2 | 1 | 8 | F75-PS-802 | FIM III Seepage Pump 2 | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F75-SW-802 | 0.88 | 0.73 | 0.70 | 0.50 | 1.00 | 2000-F75-SCM-EL-40115 | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
2.2 | 2 | 2 | 1 | 8 | F75-PS-803 | FIM III Seepage Pump 3 | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F75-SW-803 | 0.88 | 0.73 | 0.70 | 0.50 | 1.00 | 2000-F75-SCM-EL-40116 | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
2.2 | 2 | 2 | 1 | 8 | F75-PS-804 | FIM III Seepage Pump 4 | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F75-SW-804 | 0.88 | 0.73 | 0.70 | 0.50 | 1.00 | 2000-F75-SCM-EL-40117 | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
4 | 4 | 5 | 0 | 3 | F75-RTU-329 | FIM III TSF Decant Dam 4 Telemetry Panel | 415 | 240V FEEDER (1 PHASE) | Duty | F75-SW-557 | 0.90 | 0.76 | 0.80 | 0.10 | 1.00 |  | EEL | Confirmed | C | 5
7.5 | 7 | 8 | 0 | 6 | F75-HY-421 | FIM III Valve Station Hydraulic Power Pack | 415 | 415V FEEDER 0.37 TO 110kW | Duty | F75-SW-556 | 0.92 | 0.81 | 0.80 | 0.10 | 1.00 | 2000-PP009-E03-40002 | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
4 | 4 | 5 | 0 | 3 | F75-RTU-421 | FIM III Valve Station RTU Panel | 415 | 240V FEEDER (1 PHASE) | Duty | F75-SW-556 | 0.90 | 0.76 | 0.80 | 0.10 | 1.00 |  | EEL | Confirmed | 0 | 5
22 | 17 | 19 | 4 | 74 | F75-PS-593 | FIM II Cell G Underdrainage Pump | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F75-SW-593 | 0.92 | 0.89 | 0.70 | 0.50 | 1.00 | 2000-F75-SCM-EL-40213 | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
8 | 7 | 8 | 2 | 29 | F75-PS-559 | FIM II Cell G Toe Drain Pump 1 | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F75-SW-593 | 0.86 | 0.85 | 0.70 | 0.50 | 1.00 | 2000-F75-SCM-EL-40211 | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5
8 | 7 | 8 | 2 | 29 | F75-PS-560 | FIM II Cell G Toe Drain Pump 2 | 415 | 415V 0.37 TO 37kW DOL MOTOR | Duty | F75-SW-560 | 0.86 | 0.85 | 0.70 | 0.50 | 1.00 | 2000-F75-SCM-EL-40212 | 2000-F00-LST-ME-40001_0 | Confirmed | 0 | 5