## Cable schedule
Cable Number | Cable Origin Equip. Number | Equipment Name | Cable Destination Equip. Number | Length (m) | Cable Type / Size / Construction | Installation method | Cable Supplier | Cable Installer | Cable Terminator | Schematic / Termination Drawing | Status | Revision | Comments | Page
F75SW560-P1 | F75-TR-560 | FIM II TSF Cell G Transformer 1 | F75-SW-560 | 30 | 4C+E 50mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40214 | Confirmed | 0 |  | 5
F75CP560-P1 | F75-SW-560 | FIM II TSF Cell G Switchboard 1 | F75-CP-560 | 10 | 4C+E 6mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40214 | Confirmed | 0 |  | 5
F75CP560-P2 | F75-SW-560 | FIM II TSF Cell G Switchboard 1 | F75-CP-560 | 10 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40214 | Confirmed | 0 |  | 5
F75PS560DPS-P1 | F75-CP-560 | FIM II Cell G Toe Drain Pump 1 Control Panel | F75PS560-DPS | 15 | 3C+E 6mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40212 | Confirmed | 0 |  | 5
F75PS560DPS-C1 | F75PS560-LCS | FIM II Cell G Toe Drain Pump 1 Local Control Station | F75PS560-DPS | 5 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40212 | Confirmed | 0 |  | 5
F75PS560LCS-C1 | F75-CP-560 | FIM II Cell G Toe Drain Pump 1 Control Panel | F75PS560-LCS | 15 | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40212 | Confirmed | 0 |  | 5
F75PS560-P1 | F75PS560-DPS | FIM II Cell G Toe Drain Pump 1 Decontactor | F75-PS-560 | 5 | 3C+E 6mm² Cu 0.6/1kV PVC/PVC FLEXIBLE | Trailing Cable | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40212 | Confirmed | 0 |  | 5
F75SW560-W12 | F75-SW-560 | FIM II TSF Cell G Switchboard 1 |  | 10 | 3C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit/Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40214 | Confirmed | 0 | Note 10 | 5
F75SW593-P1 | F75-TR-593 | FIM II TSF Cell G Transformer 2 | F75-SW-593 | 30 | 4C+E 150mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40216 | Confirmed | 0 |  | 5
F75CP593-P1 | F75-SW-593 | FIM II TSF Cell G Switchboard 2 | F75-CP-593 | 10 | 4C+E 16mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40216 | Confirmed | 0 |  | 5
F75CP593-P2 | F75-SW-593 | FIM II TSF Cell G Switchboard 2 | F75-CP-593 | 10 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40216 | Confirmed | 0 |  | 5
F75PS593DPS-P1 | F75-CP-593 | FIM II Cell G Underdrainage Pump Control Panel | F75PS593-DPS | 15 | 3C+E 16mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40213 | Confirmed | 0 |  | 5
F75PS593DPS-C1 | F75PS593-LCS | FIM II Cell G Underdrainage Pump Local Control Station | F75PS593-DPS | 5 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40213 | Confirmed | 0 |  | 5
F75PS593LCS-C1 | F75-CP-593 | FIM II Cell G Underdrainage Pump Control Panel | F75PS593-LCS | 15 | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40213 | Confirmed | 0 |  | 5
F75PS593-P1 | F75PS593-DPS | FIM II Cell G Underdrainage Pump Decontactor | F75-PS-593 | 5 | 3C+E 16mm² Cu 0.6/1kV PVC/PVC FLEXIBLE | Trailing Cable | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40213 | Confirmed | 0 |  | 5
F75CP559-P1 | F75-SW-593 | FIM II TSF Cell G Switchboard 2 | F75-CP-559 | 30 | 4C+E 6mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40216 | Confirmed | 0 |  | 5
F75CP559-P2 | F75-SW-593 | FIM II TSF Cell G Switchboard 2 | F75-CP-559 | 30 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40216 | Confirmed | 0 |  | 5
F75PS559DPS-P1 | F75-CP-559 | FIM II Cell G Toe Drain Pump 2 Control Panel | F75PS559-DPS | 15 | 3C+E 6mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40216 | Confirmed | 0 |  | 5
F75PS559DPS-C1 | F75PS559-LCS | FIM II Cell G Underdrainage Pump Local Control Station | F75PS559-DPS | 5 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40211 | Confirmed | 0 |  | 5
F75PS559LCS-C1 | F75-CP-559 | FIM II Cell G Toe Drain Pump 2 Control Panel | F75PS559-LCS | 15 | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40211 | Confirmed | 0 |  | 5
F75PS559-P1 | F75PS559-DPS | FIM II Cell G Toe Drain Pump 2 Decontactor | F75-PS-559 | 5 | 3C+E 6mm² Cu 0.6/1kV PVC/PVC FLEXIBLE | Trailing Cable | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40211 | Confirmed | 0 |  | 5
F75SW593-W12 | F75-SW-593 | FIM II TSF Cell G Switchboard 2 |  | 15 | 3C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40213 | Confirmed | 0 | Note 10 | 5
F75SW556-P1 | F75-TR-556 | FIM III TSF Transformer | F75-SW-556 | 50 | 4C+E 150mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40118 | Confirmed | 0 | Please note this is the same cable that is in the FIM III Booster Station cable schedule | 5
F75CP556-P1 | F75-SW-556 | FIM III TSF Switchboard 1 | F75-CP-556 | 10 | 4C+E 25mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40118 | Confirmed | 0 |  | 5
F75CP556-P2 | F75-SW-556 | FIM III TSF Switchboard 1 | F75-CP-556 | 10 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40118 | Confirmed | 0 |  | 5
F75PS556DPS-P1 | F75-CP-556 | FIM III Underdrainage Pump 1 Control Panel | F75PS556-DPS | 15 | 3C+E 16mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40111 | Confirmed | 0 |  | 5
F75PS556DPS-C1 | F75PS556-LCS | FIM II Cell G Underdrainage Pump Local Control Station | F75PS556-DPS | 5 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40111 | Confirmed | 0 |  | 5
F75PS556LCS-C1 | F75-CP-556 | FIM III Underdrainage Pump 1 Control Panel | F75PS556-LCS | 15 | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40111 | Confirmed | 0 |  | 5
F75PS556-P1 | F75PS556-DPS | FIM III Underdrainage Pump 1 Decontactor | F75-PS-556 | 5 | 3C+E 16mm² Cu 0.6/1kV PVC/PVC FLEXIBLE | Trailing Cable | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40111 | Confirmed | 0 |  | 5
F23RTU421-P1 | F75-SW-556 | FIM III TSF Switchboard 1 | F23-RTU-421 | 140 | 2C+E 16mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40118 | Confirmed | 0 |  | 5
F23HY421-P1 | F75-SW-556 | FIM III TSF Switchboard 1 | F23-HY-421 | 140 | 4C+E 16mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40118 2000-PP009-D02-40002 | Confirmed | 0 |  | 5
F75SW556-W12 | F75-SW-556 | FIM III TSF Switchboard 1 |  | 15 | 3C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40118 | Confirmed | 0 | Note 10 | 5
F75SW556-B12 | F75-SW-556 | FIM III TSF Switchboard 1 |  | 160 | 3C+E 6mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40118 | Confirmed | 0 | Note 10 | 5
F75SW557-P1 | F23-SW-602 | FIM III Booster Station LV Motor Control Centre | F75-SW-557 | 170 | 4C+E 150mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40120 | Confirmed | 0 |  | 5
F75CP557-P1 | F75-SW-557 | FIM III TSF Switchboard 2 | F75-CP-557 | 15 | 4C+E 25mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40120 | Confirmed | 0 |  | 5
F75CP557-P2 | F75-SW-557 | FIM III TSF Switchboard 2 | F75-CP-557 | 15 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40120 | Confirmed | 0 |  | 5
F75PS557DPS-P1 | F75-CP-557 | FIM III Underdrainage Pump 2 Control Panel | F75PS557-DPS | 15 | 3C+E 16mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40112 | Confirmed | 0 |  | 5
F75PS557DPS-C1 | F75PS557-LCS | FIM III Underdrainage Pump 2 Local Control Station | F75PS557-DPS | 5 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40112 | Confirmed | 0 |  | 5
F75PS557LCS-C1 | F75-CP-557 | FIM III Underdrainage Pump 2 Control Panel | F75PS557-LCS | 15 | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40112 | Confirmed | 0 |  | 5
F75PS557-P1 | F75PS557-DPS | FIM III Underdrainage Pump 2 Decontactor | F75-PS-557 | 5 | 3C+E 16mm² Cu 0.6/1kV PVC/PVC FLEXIBLE | Trailing Cable | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40112 | Confirmed | 0 |  | 5
F75SW557-W12 | F75-SW-557 | FIM III TSF Switchboard 2 |  | 15 | 3C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit/Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40213 | Confirmed | 0 | Note 10 | 5
F75CP558-P1 | F75-SW-557 | FIM III TSF Switchboard 2 | F75-CP-558 | 10 | 4C+E 6mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40120 | Confirmed | 0 |  | 5
F75CP558-P2 | F75-SW-557 | FIM III TSF Switchboard 2 | F75-CP-558 | 10 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40120 | Confirmed | 0 |  | 5
F75PS558DPS-P1 | F75-CP-558 | FIM III Toe Drain Pump 1 Control Panel | F75PS558-DPS | 20 | 3C+E 6mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40113 | Confirmed | 0 |  | 5
F75PS558DPS-C1 | F75PS558-LCS | FIM III Toe Drain Pump 1 Local Control Station | F75PS558-DPS | 5 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40113 | Confirmed | 0 |  | 5
F75PS558LCS-C1 | F75-CP-558 | FIM III Toe Drain Pump 1 Control Panel | F75PS558-LCS | 20 | 10C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40113 | Confirmed | 0 |  | 5
F75PS558-P1 | F75PS558-DPS | FIM III Toe Drain Pump 1 Decontactor | F75-PS-558 | 5 | 3C+E 6mm² Cu 0.6/1kV PVC/PVC FLEXIBLE | Trailing Cable | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40113 | Confirmed | 0 |  | 5
F75SW801-P1 | F75-TR-801 | FIM III TSF Transformer | F75-SW-801 | 30 | 4C+E 50mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40122 | Confirmed | 0 |  | 5
F75CP801-P1 | F75-SW-801 | FIM III TSF Switchboard 3 | F75-CP-801 | 15 | 4C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40122 | Confirmed | 0 |  | 5
Client: Project: | NORTHERN STAR RESOURCES KCGM |  | FIM II CELL G & FIM III TAILINGS STORAGE FACILITIES CABLE SCHEDULE | [10 empty] | 6
Document Number: Revision: | 2000-F75-LST-EL-40003 0 | [12 empty] | 6
F75CP801-P2 | F75-SW-801 | FIM III TSF Switchboard 3 | F75-CP-801 | 15 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40122 | Confirmed | 0 |  | 6
F75PS801-P1 | F75PS801-DPS | FIM III Seepage Pump 1 Decontactor | F75-PS-801 | 10 | 3C+E 4mm² Cu 0.6/1kV PVC/PVC FLEXIBLE | Trailing Cable | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40114 | Confirmed | 0 |  | 6
F75SW801-W12 | F75-SW-801 | FIM III TSF Switchboard 3 |  | 10 | 3C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40122 | Confirmed | 0 |  | 6
F75SW802-P1 | F75-TR-802 | FIM III TSF Transformer | F75-SW-802 | 30 | 4C+E 50mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40124 | Confirmed | 0 |  | 6
F75CP802-P1 | F75-SW-802 | FIM III TSF Switchboard 4 | F75-CP-802 | 15 | 4C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40124 | Confirmed | 0 |  | 6
F75CP802-P2 | F75-SW-802 | FIM III TSF Switchboard 4 | F75-CP-802 | 15 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40124 | Confirmed | 0 |  | 6
F75PS802-P1 | F75PS802-DPS | FIM III Seepage Pump 2 Decontactor | F75-PS-802 | 10 | 3C+E 4mm² Cu 0.6/1kV PVC/PVC FLEXIBLE | Trailing Cable | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40115 | Confirmed | 0 |  | 6
F75SW802-W12 | F75-SW-802 | FIM III TSF Switchboard 4 |  | 10 | 3C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40124 | Confirmed | 0 |  | 6
F75SW803-P1 | F75-TR-803 | FIM III TSF Transformer | F75-SW-803 | 30 | 4C+E 50mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40126 | Confirmed | 0 |  | 6
F75CP803-P1 | F75-SW-803 | FIM III TSF Switchboard 5 | F75-CP-803 | 15 | 4C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40126 | Confirmed | 0 |  | 6
F75CP803-P2 | F75-SW-803 | FIM III TSF Switchboard 5 | F75-CP-803 | 15 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40126 | Confirmed | 0 |  | 6
F75PS803-P1 | F75PS803-DPS | FIM III Seepage Pump 3 Decontactor | F75-PS-803 | 10 | 3C+E 4mm² Cu 0.6/1kV PVC/PVC FLEXIBLE | Trailing Cable | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40116 | Confirmed | 0 |  | 6
F75SW803-W12 | F75-SW-803 | FIM III TSF Switchboard 5 |  | 10 | 3C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40126 | Confirmed | 0 |  | 6
F75SW804-P1 | F75-TR-804 | FIM III TSF Transformer | F75-SW-804 | 30 | 4C+E 50mm² Cu 0.6/1kV XLPE/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40128 | Confirmed | 0 |  | 6
F75CP804-P1 | F75-SW-804 | FIM III TSF Switchboard 6 | F75-CP-804 | 15 | 4C+E 4mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40128 | Confirmed | 0 |  | 6
F75CP804-P2 | F75-SW-804 | FIM III TSF Switchboard 6 | F75-CP-804 | 15 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40128 | Confirmed | 0 |  | 6
F75PS804-P1 | F75PS804-DPS | FIM III Seepage Pump 4 Decontactor | F75-PS-804 | 10 | 3C+E 4mm² Cu 0.6/1kV PVC/PVC FLEXIBLE | Trailing Cable | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40117 | Confirmed | 0 |  | 6
F75SW804-W12 | F75-SW-804 | FIM III TSF Switchboard 6 |  | 10 | 3C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40128 | Confirmed | 0 |  | 6
F23HY421-P1 | F75-SW-556 | FIM III TSF Switchboard 1 | F23-HY-421 | 150 | 4C+E 16mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-SCM-EL-40118 | Confirmed | 0 | Neutral required for panel anti-con heater. | 6
F75RTU329-P1 | F75-SW-557 | FIM III TSF Switchboard 2 | F75-RTU-329 | 200 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Underground Conduit | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 6
Client: | NORTHERN STAR RESOURCES |  | FIM II CELL G & FIM III TAILINGS STORAGE FACILITIES C ABLE SCHEDULE | [10 empty] | 7
Project: Document Number: | KCGM 2000-F75-LST-EL-40003 | [12 empty] | 7
Revision: | 0 | [12 empty] | 7
F75SW560-N1 | F75-RTU-560 | FIM II TSF Cell G Remote Telemetry Unit 1 ACE 3600 Serial Port 1 | F75-RTU-560_Radio | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75SS560A-C1 | F75-RTU-560_Radio | FIM II TSF Cell G Remote Telemetry Unit 1 Data Radio | F75-SS-560A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SS560A-C2 | F75-SS-560A | FIM II TSF Cell G Remote Telemetry Unit 1 Surge Supressor 1 | F75-ANT-560A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SW560-N2 | F75-RTU-560 | FIM II TSF Cell G Remote Telemetry Unit 1 ACE 3600 Serial Port 2 | F75-RTU-560_Modem | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75SS560B-C1 | F75-RTU-560_Modem | FIM II TSF Cell G Remote Telemetry Unit 1 Radio Modem 4G | F75-SS-560B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SS560B-C2 | F75-SS-560B | FIM II TSF Cell G Remote Telemetry Unit 1 Surge Supressor 2 | F75-ANT-560B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SW560-N3 | F75-RTU-560 | FIM II TSF Cell G Remote Telemetry Unit 1 ACE 3600 Ethernet Port 1 | F75-RTU-560_ETHSW | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 7
F75SW560-N4 | F75-RTU-560_ETHSW | FIM II TSF Cell G Remote Telemetry Unit 1 Network Switch | F75-RTU-560_EMP700 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 7
F75SW593-N1 | F75-RTU-593 | FIM II TSF Cell G Remote Telemetry Unit 2 ACE 3600 Serial Port 1 | F75-RTU-593_Radio | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75SS593A-C1 | F75-RTU-593_Radio | FIM II TSF Cell G Remote Telemetry Unit 2 Data Radio | F75-SS-593A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SS593A-C2 | F75-SS-593A | FIM II TSF Cell G Remote Telemetry Unit 2 Surge Supressor 1 | F75-ANT-593A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SW593-N2 | F75-RTU-593 | FIM II TSF Cell G Remote Telemetry Unit 2 ACE 3600 Serial Port 2 | F75-RTU-593_Modem | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75SS593B-C1 | F75-RTU-593_Modem | FIM II TSF Cell G Remote Telemetry Unit 2 Radio Modem 4G | F75-SS-593B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SS593B-C2 | F75-SS-593B | FIM II TSF Cell G Remote Telemetry Unit 2 Surge Supressor 2 | F75-ANT-593B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SW593-N3 | F75-RTU-593 | FIM II TSF Cell G Remote Telemetry Unit 2 ACE 3600 Ethernet Port 1 | F75-RTU-593_ETHSW | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 7
F75SW593-N4 | F75-RTU-593_ETHSW | FIM II TSF Cell G Remote Telemetry Unit 2 Network Switch | F75-RTU-593_EMP700 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 7
F75RTU600-N1 | F75-RTU-600 | FIM III Decant Pump Cell 1 Telemetry Panel ACE 3600 Serial Port 1 | F75-RTU-600_Radio | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75RTU600A-C1 | F75-RTU-600_Radio | FIM III Decant Pump Cell 1 Telemetry Panel Data Radio | F75-SS-600A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU600A-C2 | F75-SS-600A | FIM III Decant Pump Cell 1 Telemetry Panel Surge Supressor 1 | F75-ANT-600A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU600-N2 | F75-RTU-600 | FIM III Decant Pump Cell 1 Telemetry Panel ACE 3600 Serial Port 2 | F75-RTU-600_Modem | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75RTU600B-C1 | F75-RTU-600_Modem | FIM III Decant Pump Cell 1 Telemetry Panel Radio Modem 4G | F75-SS-600B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU600B-C2 | F75-SS-600B | FIM III Decant Pump Cell 1 Telemetry Panel Surge Supressor 2 | F75-ANT-600B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU601-N1 | F75-RTU-601 | FIM III Decant Pump Cell 2 Telemetry Panel ACE 3600 Serial Port 1 | F75-RTU-601_Radio | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75RTU601A-C1 | F75-RTU-601_Radio | FIM III Decant Pump Cell 2 Telemetry Panel Data Radio | F75-SS-601A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU601A-C2 | F75-SS-601A | FIM III Decant Pump Cell 2 Telemetry Panel Surge Supressor 1 | F75-ANT-601A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU601-N2 | F75-RTU-601 | FIM III Decant Pump Cell 2 Telemetry Panel ACE 3600 Serial Port 2 | F75-RTU-601_Modem | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75RTU601B-C1 | F75-RTU-601_Modem | FIM III Decant Pump Cell 2 Telemetry Panel Radio Modem 4G | F75-SS-601B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU601B-C2 | F75-SS-601B | FIM III Decant Pump Cell 2 Telemetry Panel Surge Supressor 2 | F75-ANT-601B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU602-N1 | F75-RTU-602 | FIM III Decant Pump Cell 3 Telemetry Panel ACE 3600 Serial Port 1 | F75-RTU-602_Radio | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75RTU602A-C1 | F75-RTU-602_Radio | FIM III Decant Pump Cell 3 Telemetry Panel Data Radio | F75-SS-602A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU602A-C2 | F75-SS-602A | FIM III Decant Pump Cell 3 Telemetry Panel Surge Supressor 1 | F75-ANT-602A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU602-N2 | F75-RTU-602 | FIM III Decant Pump Cell 3 Telemetry Panel ACE 3600 Port 2 | F75-RTU-602_Modem | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75RTU602B-C1 | F75-RTU-602_Modem | FIM III Decant Pump Cell 3 Telemetry Panel Radio Modem 4G | F75-SS-602B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU602B-C2 | F75-SS-602B | FIM III Decant Pump Cell 3 Telemetry Panel Surge Supressor 2 | F75-ANT-602B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU556-N1 | F75-RTU-556 | FIM III TSF Switchboard 1 Telemetry Panel ACE 3600 Serial Port 1 | F75-RTU-556_Radio | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75RTU556A-C1 | F75-RTU-556_Radio | FIM III TSF Switchboard 1 Telemetry Panel ACE 3600 Data Radio | F75-SS-556A | Note 8 | CNT-400 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU556A-C2 | F75-SS-556A | FIM III TSF Switchboard 1 Telemetry Panel Surge Supressor 1 | F75-ANT-556A | Note 8 | CNT-400 | Switchroom | EL006 | EL006 | EL006 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SW556-N2 | F75-RTU-556 | FIM III TSF Switchboard 1 Telemetry Panel ACE 3600 Serial Port 1 | F75-RTU-556_Modem | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75SS556B-C1 | F75-RTU-556_Modem | FIM III TSF Switchboard 1 Radio Modem 4G | F75-SS-556B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SS556B-C2 | F75-SS-556B | FIM III TSF Switchboard 1 Surge Supressor 2 | F75-ANT-556B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SW556-N3 | F75-RTU-556 | FIM III TSF Switchboard 1 ACE 3600 Ethernet Port 1 | F75-RTU-556_ETHSW | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 7
F75SW556-N4 | F75-RTU-556_ETHSW | FIM III TSF Switchboard 1 Network Switch | F75-RTU-556_EMP700 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 7
F75SW557-N1 | F75-RTU-557 | FIM III TSF Switchboard 2 ACE 3600 Ethernet Port 1 | F75-RTU-557_ETHSW | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 7
F75SW557-N2 | F75-RTU-557_ETHSW | FIM III TSF Switchboard 2 Network Switch | F75-RTU-557_EMP700 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 7
F75RTU801-N1 | F75-RTU-801 | FIM III Cel 1 - Bore 8 Telemetry Panel ACE 3600 Serial Port 1 | F75-RTU-801_Radio | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75RTU801A-C1 | F75-RTU-801_Radio | FIM III Cel 1 - Bore 8 Telemetry Panel ACE 3600 Data Radio | F75-SS-801A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75RTU801A-C2 | F75-SS-801A | FIM III Cel 1 - Bore 8 Telemetry Panel Surge Supressor 1 | F75-ANT-801A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SW801-N2 | F75-RTU-801 | FIM III Cel 1 - Bore 8 Telemetry Panel ACE 3600 Serial Port 2 | F75-RTU-801_Modem | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
F75SS801B-C1 | F75-RTU-801_Modem | FIM III Cel 1 - Bore 8 Telemetry Panel Radio Modem 4G | F75-SS-801B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SS801B-C2 | F75-SS-801B | FIM III Cel 1 - Bore 8 Telemetry Panel Surge Supressor 2 | F75-ANT-801B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 7
F75SW801-N3 | F75-RTU-801 | FIM III Cel 1 - Bore 8 Telemetry Panel ACE 3600 Ethernet Port 1 | F75-RTU-801_ETHSW | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 7
F75SW801-N4 | F75-RTU-801_ETHSW | FIM III Cel 1 - Bore 8 Telemetry Panel Network Switch | F75-RTU-801_EMP700 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 7
F75RTU802-N1 | F75-RTU-802 | FIM III Cel 1 - Bore 9 Telemetry Panel ACE 3600 Serial Port 1 | F75-RTU-802_Radio | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 7
Client: | NORTHERN STAR RESOURCES |  | FIM II CELL G & FIM III TAILINGS STORAGE FACILITIES C ABLE SCHEDULE | [10 empty] | 8
Project: Document Number: | KCGM 2000-F75-LST-EL-40003 | [12 empty] | 8
Revision: | 0 | [12 empty] | 8
F75RTU802A-C1 | F75-RTU-802_Radio | FIM III Cel 1 - Bore 9 Telemetry Panel ACE 3600 Data Radio | F75-SS-802A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75RTU802A-C2 | F75-SS-802A | FIM III Cel 1 - Bore 9 Telemetry Panel Surge Supressor 1 | F75-ANT-802A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75SW802-N2 | F75-RTU-802 | FIM III Cel 1 - Bore 9 Telemetry Panel ACE 3600 Serial Port 2 | F75-RTU-802_Modem | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 8
F75SS802B-C1 | F75-RTU-802_Modem | FIM III Cel 1 - Bore 9 Telemetry Panel Radio Modem 4G | F75-SS-802B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75SS802B-C2 | F75-SS-802B | FIM III Cel 1 - Bore 9 Telemetry Panel Surge Supressor 2 | F75-ANT-802B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75SW802-N3 | F75-RTU-802 | FIM III Cel 1 - Bore 9 Telemetry Panel ACE 3600 Ethernet Port 1 | F75-RTU-802_ETHSW | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 8
F75SW802-N4 | F75-RTU-802_ETHSW | FIM III Cel 1 - Bore 9 Telemetry Panel Network Switch | F75-RTU-802_EMP700 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 8
F75RTU803-N1 | F75-RTU-803 | FIM III Cel 1 - Bore 11 Telemetry Panel ACE 3600 Serial Port 1 | F75-RTU-803_Radio | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 8
F75RTU803A-C1 | F75-RTU-803_Radio | FIM III Cel 1 - Bore 11 Telemetry Panel ACE 3600 Data Radio | F75-SS-803A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75RTU803A-C2 | F75-SS-803A | FIM III Cel 1 - Bore 11 Telemetry Panel Surge Supressor 1 | F75-ANT-803A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75SW803-N2 | F75-RTU-803 | FIM III Cel 1 - Bore 11 Telemetry Panel ACE 3600 Serial Port 2 | F75-RTU-803_Modem | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 8
F75SS803B-C1 | F75-RTU-803_Modem | FIM III Cel 1 - Bore 11 Telemetry Panel Radio Modem 4G | F75-SS-803B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75SS803B-C2 | F75-SS-803B | FIM III Cel 1 - Bore 11 Telemetry Panel Surge Supressor 2 | F75-ANT-803B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75SW803-N3 | F75-RTU-803 | FIM III Cel 1 - Bore 11 Telemetry Panel ACE 3600 Ethernet Port 1 | F75-RTU-803_ETHSW | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 8
F75SW803-N4 | F75-RTU-803_ETHSW | FIM III Cel 1 - Bore 11 Telemetry Panel Network Switch | F75-RTU-803_EMP700 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 8
F75RTU804-N1 | F75-RTU-804 | FIM III Cel 1 - Bore 12 Telemetry Panel ACE 3600 Serial Port 1 | F75-RTU-804_Radio | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 8
F75RTU804A-C1 | F75-RTU-804_Radio | FIM III Cel 1 - Bore 12 Telemetry Panel ACE 3600 Data Radio | F75-SS-804A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75RTU804A-C2 | F75-SS-804A | FIM III Cel 1 - Bore 12 Telemetry Panel Surge Supressor 1 | F75-ANT-804A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75SW804-N2 | F75-RTU-804 | FIM III Cel 1 - Bore 12 Telemetry Panel ACE 3600 Serial Port 2 | F75-RTU-804_Modem | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 8
F75SS804B-C1 | F75-RTU-804_Modem | FIM III Cel 1 - Bore 12 Telemetry Panel Radio Modem 4G | F75-SS-804B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75SS804B-C2 | F75-SS-804B | FIM III Cel 1 - Bore 12 Telemetry Panel Surge Supressor 2 | F75-ANT-804B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75SW804-N3 | F75-RTU-804 | FIM III Cel 1 - Bore 12 Telemetry Panel ACE 3600 Ethernet Port 1 | F75-RTU-804_ETHSW | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 8
F75SW804-N4 | F75-RTU-804_ETHSW | FIM III Cel 1 - Bore 12 Telemetry Panel Network Switch | F75-RTU-804_EMP700 | Note 8 | 4Pr Cu Cat6 SF/UTP | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 |  | 8
F75RTU329-N1 | F75-RTU-329 | FIM III TSF Decant Dam 4 Telemetry Panel ACE 3600 Serial Port 1 | F75-RTU-329_Radio | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 8
F75RTU329A-C1 | F75-RTU-329_Radio | FIM III TSF Decant Dam 4 Telemetry Panel ACE 3600 Data Radio | F75-SS-329A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75RTU329A-C2 | F75-SS-329A | FIM III TSF Decant Dam 4 Telemetry Panel Surge Supressor 1 | F75-ANT-329A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75RTU329-N2 | F75-RTU-329 | FIM III TSF Decant Dam 4 Telemetry Panel | F75-RTU-6329_Modem | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 8
F75RTU329B-C1 | F75-RTU-329_Modem | FIM III TSF Decant Dam 4 Telemetry Panel Radio Modem 4G | F75-SS-329B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F75RTU329B-C2 | F75-SS-329B | FIM III TSF Decant Dam 4 Telemetry Panel Surge Supressor 2 | F75-ANT-329B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 |  | Confirmed | 0 | Low Loss 5ohm Cable | 8
F23RTU421-N1 | F23-RTU-421 | FIM III Valve Station RTU Panel ACE 3600 Serial Port 1 | F23-RTU-421_Radio | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 | 2000-F23-SCM-IC-40020 | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 8
F23RTU421A-C1 | F23-RTU-421_Radio | FIM III Valve Station RTU Panel ACE 3600 Data Radio | F23-SS-421A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 | 2000-F23-SCM-IC-40020 | Confirmed | 0 | Low Loss 5ohm Cable | 8
F23RTU421A-C2 | F23-SS-421A | FIM III Valve Station RTU Panel Surge Supressor 1 | F23-ANT-421A | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 | 2000-F23-SCM-IC-40020 | Confirmed | 0 | Low Loss 5ohm Cable | 8
F23RTU421-N2 | F23-RTU-421 | FIM III Valve Station RTU Panel | F23-RTU-6421_Modem | Note 8 | RS232 c/w 9 pin and RJ45 Plug | Switchroom | EL008 | EL008 | EL008 | 2000-F23-SCM-IC-40020 | Confirmed | 0 | Cable on DCS Equipment List, 2000- F75-LST-IC-40003 | 8
F23RTU421B-C1 | F23-RTU-421_Modem | FIM III Valve Station RTU Panel Radio Modem 4G | F23-SS-421B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 | 2000-F23-SCM-IC-40020 | Confirmed | 0 | Low Loss 5ohm Cable | 8
F23RTU421B-C2 | F23-SS-421B | FIM III Valve Station RTU Panel Surge Supressor 2 | F23-ANT-421B | Note 8 | CNT-400 | Switchroom | EL008 | EL008 | EL008 | 2000-F23-SCM-IC-40020 | Confirmed | 0 | Low Loss 5ohm Cable | 8
F23HY421-D1 | F75-RTU-421 | FIM III Valve Station RTU Panel | F23-HY-421 | 25 | 4Pr Cu Cat6 SF/UTP | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F23-SCM-IC-40020 2000-EL006-D02-40002 | Confirmed | 0 | Cable to be suited for outdoor installation | 8
Client: | NORTHERN STAR RESOURCES |  | FIM II CELL G & FIM III TAILINGS STORAGE FACILITIES C ABLE SCHEDULE | [10 empty] | 9
Project: Document Number: | KCGM 2000-F75-LST-EL-40003 | [12 empty] | 9
Revision: | 0 | [12 empty] | 9
FIT23592-I1 | F23-RTU-421 | FIM III Valve Station RTU Panel | FIT-23592 | 110 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 9
FIT23592-P1 | F23-RTU-421 | FIM III Valve Station RTU Panel | FIT-23592 | 110 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 9
FIT23593-I1 | F23-RTU-421 | FIM III Valve Station RTU Panel | FIT-23593 | 110 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 9
FIT23593-P1 | F23-RTU-421 | FIM III Valve Station RTU Panel | FIT-23593 | 110 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 9
FIT23596-I1 | F23-RTU-421 | FIM III Valve Station RTU Panel | FIT-23596 | 110 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 9
FIT23596-P1 | F23-RTU-421 | FIM III Valve Station RTU Panel | FIT-23596 | 110 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 9
FIT23597-I1 | F23-RTU-421 | FIM III Valve Station RTU Panel | FIT-23597 | 110 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 9
FIT23597-P1 | F23-RTU-421 | FIM III Valve Station RTU Panel | FIT-23597 | 110 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I |  | Confirmed | 0 |  | 9
ZS23700-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23700-JB | 22 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23700-I1 | ZS23700-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 1 Isolation Valve 1 Position Switch Junction Box | ZSO-23700 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23700-I1 | ZS23700-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 1 Isolation Valve 1 Position Switch Junction Box | ZSC-23700 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23701-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23701-JB | 22 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23701-I1 | ZS23701-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 1 Isolation Valve 2 Position Switch Junction Box | ZSO-23701 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23701-I1 | ZS23701-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 1 Isolation Valve 2 Position Switch Junction Box | ZSC-23701 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23702-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23702-JB | 25 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23702-I1 | ZS23702-JB | FIM III Booster Pump 2 to Line D FIM III TSF Cell 1 Isolation Valve Position Switch Junction Box | ZSO-23702 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23702-I1 | ZS23702-JB | FIM III Booster Pump 2 to Line D FIM III TSF Cell 1 Isolation Valve Position Switch Junction Box | ZSC-23702 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23703-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23703-JB | 27 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23703-I1 | ZS23703-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 1 Isolation Valve 1 Position Switch Junction Box | ZSO-23703 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23703-I1 | ZS23703-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 1 Isolation Valve 1 Position Switch Junction Box | ZSC-23703 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23704-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23704-JB | 27 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23704-I1 | ZS23704-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 1 Isolation Valve 2 Position Switch Junction Box | ZSO-23704 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23704-I1 | ZS23704-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 1 Isolation Valve 2 Position Switch Junction Box | ZSC-23704 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23705-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23705-JB | 27 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23705-I1 | ZS23705-JB | Decant Dam 4 to Line D FIM III TSF Cell 1 Isolation Valve Position Switch Junction Box | ZSO-23705 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23705-I1 | ZS23705-JB | Decant Dam 4 to Line D FIM III TSF Cell 1 Isolation Valve Position Switch Junction Box | ZSC-23705 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23706-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23706-JB | 22 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23706-I1 | ZS23706-JB | Decant Dam 4 to Line B FIM III TSF Cell 1 Isolation Valve Position Switch Junction Box | ZSO-23706 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23706-I1 | ZS23706-JB | Decant Dam 4 to Line B FIM III TSF Cell 1 Isolation Valve Position Switch Junction Box | ZSC-23706 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23707-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23707-JB | 30 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23707-I1 | ZS23707-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 2 Isolation Valve 1 Position Switch Junction Box | ZSO-23707 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23707-I1 | ZS23707-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 2 Isolation Valve 1 Position Switch Junction Box | ZSC-23707 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23708-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23708-JB | 30 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23708-I1 | ZS23708-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 2 Isolation Valve 1 Position Switch Junction Box | ZSO-23708 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23708-I1 | ZS23708-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 2 Isolation Valve 1 Position Switch Junction Box | ZSC-23708 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23709-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23709-JB | 20 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23709-I1 | ZS23709-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 2 Isolation Valve 2 Position Switch Junction Box | ZSO-23709 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23709-I1 | ZS23709-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 2 Isolation Valve 2 Position Switch Junction Box | ZSC-23709 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23710-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23710-JB | 10 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23710-I1 | ZS23710-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 2 Isolation Valve 3 Position Switch Junction Box | ZSO-23710 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23710-I1 | ZS23710-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 2 Isolation Valve 3 Position Switch Junction Box | ZSC-23710 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23711-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23711-JB | 12 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23711-I1 | ZS23711-JB | FIM III Booster Pump 2 to Line D FIM III TSF Cell 2 Isolation Valve Position Switch Junction Box | ZSO-23711 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23711-I1 | ZS23711-JB | FIM III Booster Pump 2 to Line D FIM III TSF Cell 2 Isolation Valve Position Switch Junction Box | ZSC-23711 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23712-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23712-JB | 25 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23712-I1 | ZS23712-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 2 Isolation Valve 2 Position Switch Junction Box | ZSO-23712 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23712-I1 | ZS23712-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 2 Isolation Valve 2 Position Switch Junction Box | ZSC-23712 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23713-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23713-JB | 15 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23713-I1 | ZS23713-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 2 Isolation Valve 3 Position Switch Junction Box | ZSO-23713 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23713-I1 | ZS23713-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 2 Isolation Valve 3 Position Switch Junction Box | ZSC-23713 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23714-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23714-JB | 15 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23714-I1 | ZS23714-JB | Decant Dam 4 to Line D FIM III TSF Cell 2 Isolation Valve Position Switch Junction Box | ZSO-23714 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23714-I1 | ZS23714-JB | Decant Dam 4 to Line D FIM III TSF Cell 2 Isolation Valve Position Switch Junction Box | ZSC-23714 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZS23715-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23715-JB | 10 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSO23715-I1 | ZS23715-JB | Decant Dam 4 to Line B FIM III TSF Cell 2 Isolation Valve Position Switch Junction Box | ZSO-23715 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
ZSC23715-I1 | ZS23715-JB | Decant Dam 4 to Line B FIM III TSF Cell 2 Isolation Valve Position Switch Junction Box | ZSC-23715 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 9
Client: | NORTHERN STAR RESOURCES |  | FIM II CELL G & FIM III TAILINGS STORAGE FACILITIES C ABLE SCHEDULE | [10 empty] | 10
Project: Document Number: | KCGM 2000-F75-LST-EL-40003 | [12 empty] | 10
Revision: | 0 | [12 empty] | 10
ZS23716-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23716-JB | 17 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSO23716-I1 | ZS23716-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 3 Isolation Valve 1 Position Switch Junction Box | ZSO-23716 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSC23716-I1 | ZS23716-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 3 Isolation Valve 1 Position Switch Junction Box | ZSC-23716 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZS23717-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23717-JB | 17 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSO23717-I1 | ZS23717-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 3 Isolation Valve 2 Position Switch Junction Box | ZSO-23717 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSC23717-I1 | ZS23717-JB | FIM III Booster Pump 2 to Line B FIM III TSF Cell 3 Isolation Valve 2 Position Switch Junction Box | ZSC-23717 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZS23718-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23718-JB | 20 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSO23718-I1 | ZS23718-JB | FIM III Booster Pump 2 to Line D FIM III TSF Cell 3 Isolation Valve Position Switch Junction Box | ZSO-23718 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSC23718-I1 | ZS23718-JB | FIM III Booster Pump 2 to Line D FIM III TSF Cell 3 Isolation Valve Position Switch Junction Box | ZSC-23718 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZS23719-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23719-JB | 20 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSO23719-I1 | ZS23719-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 3 Isolation Valve 1 Position Switch Junction Box | ZSO-23719 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSC23719-I1 | ZS23719-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 3 Isolation Valve 1 Position Switch Junction Box | ZSC-23719 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZS23720-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23720-JB | 20 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSO23720-I1 | ZS23720-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 3 Isolation Valve 2 Position Switch Junction Box | ZSO-23720 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSC23720-I1 | ZS23720-JB | FIM III Booster Pump 1 to Line D FIM III TSF Cell 3 Isolation Valve 2 Position Switch Junction Box | ZSC-23720 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZS23721-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23721-JB | 20 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSO23721-I1 | ZS23721-JB | Decant Dam 4 to Line D FIM III TSF Cell 3 Isolation Valve Position Switch Junction Box | ZSO-23721 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSC23721-I1 | ZS23721-JB | Decant Dam 4 to Line D FIM III TSF Cell 3 Isolation Valve Position Switch Junction Box | ZSC-23721 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZS23722-I1 | F23-HY-421 | FIM III Valve Station Hydraulic Power Pack Control Panel | ZS23722-JB | 17 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit / Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSO23722-I1 | ZS23722-JB | Decant Dam 4 to Line B FIM III TSF Cell 3 Isolation Valve Position Switch Junction Box | ZSO-23722 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
ZSC23722-I1 | ZS23722-JB | Decant Dam 4 to Line B FIM III TSF Cell 3 Isolation Valve Position Switch Junction Box | ZSC-23722 | 2 | 2PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 2000-PP009-D02-40002 | Confirmed | 0 |  | 10
LIT75318-I1 | F75-RTU-600 | FIM III Decant Pump Cell 1 Telemetry Panel | LIT-75318 | 20 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40102 | Confirmed | 0 |  | 10
LIT75318-P1 | F75-RTU-600 | FIM III Decant Pump Cell 1 Telemetry Panel | LIT-75318 | 20 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40102 | Confirmed | 0 |  | 10
FIT75319-P1 | F75-RTU-600 | FIM III Decant Pump Cell 1 Telemetry Panel | FIT-75319 | 15 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40102 | Confirmed | 0 |  | 10
FIT75319-I1 | F75-RTU-600 | FIM III Decant Pump Cell 1 Telemetry Panel | FIT-75319 | 15 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40101 2000-F75-TER-IC-40102 | Confirmed | 0 |  | 10
F75PW600-I1 | F75-RTU-600 | FIM III Decant Pump Cell 1 Telemetry Panel | F75-PW-600 | 15 | 8PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40101 | Confirmed | 0 |  | 10
LIT75324-I1 | F75-RTU-600 | FIM III Decant Pump Cell 1 Telemetry Panel | LIT-75324 | 15 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40102 | Confirmed | 0 |  | 10
FIT75329-P1 | F75-RTU-329 | Decant Dam 4 Telemetry Panel | FIT-75329 | 20 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40021 | Confirmed | 0 | Located Decant dam 4 | 10
FIT75329-I1 | F75-RTU-329 | Decant Dam 4 Telemetry Panel | FIT-75329 | 20 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40020 2000-F75-TER-IC-40021 | Confirmed | 0 | Located Decant dam 4 | 10
LIT75325-I1 | F75-RTU-601 | FIM III Decant Pump Cell 2 Telemetry Panel | LIT-75325 | 20 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40104 | Confirmed | 0 |  | 10
LIT75325-P1 | F75-RTU-601 | FIM III Decant Pump Cell 2 Telemetry Panel | LIT-75325 | 20 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40104 | Confirmed | 0 |  | 10
FIT75326-P1 | F75-RTU-601 | FIM III Decant Pump Cell 2 Telemetry Panel | FIT-75326 | 15 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40104 | Confirmed | 0 |  | 10
FIT75326-I1 | F75-RTU-601 | FIM III Decant Pump Cell 2 Telemetry Panel | FIT-75326 | 15 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40103 2000-F75-TER-IC-40104 | Confirmed | 0 |  | 10
F75PW601-I1 | F75-RTU-601 | FIM III Decant Pump Cell 2 Telemetry Panel | F75-PW-601 | 15 | 8PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40103 | Confirmed | 0 |  | 10
LIT75342-I1 | F75-RTU-601 | FIM III Decant Pump Cell 2 Telemetry Panel | LIT-75342 | 15 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40104 | Confirmed | 0 |  | 10
LIT75327-I1 | F75-RTU-602 | FIM III Decant Pump Cell 3 Telemetry Panel | LIT-75327 | 20 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40106 | Confirmed | 0 |  | 10
LIT75327-P1 | F75-RTU-602 | FIM III Decant Pump Cell 3 Telemetry Panel | LIT-75327 | 20 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40106 | Confirmed | 0 |  | 10
FIT75328-P1 | F75-RTU-602 | FIM III Decant Pump Cell 3 Telemetry Panel | FIT-75328 | 15 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40106 | Confirmed | 0 |  | 10
FIT75328-I1 | F75-RTU-602 | FIM III Decant Pump Cell 3 Telemetry Panel | FIT-75328 | 15 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40105 2000-F75-TER-IC-40106 | Confirmed | 0 |  | 10
F75PW602-I1 | F75-RTU-602 | FIM III Decant Pump Cell 3 Telemetry Panel | F75-PW-602 | 15 | 8PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40105 | Confirmed | 0 |  | 10
LIT75343-I1 | F75-RTU-602 | FIM III Decant Pump Cell 3 Telemetry Panel | LIT-75343 | 15 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40106 | Confirmed | 0 |  | 10
FIT75730-P1 | F75-SW-801 | FIM III TSF Switchboard 3 | FIT-75730 | 20 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40133 | Confirmed | 0 |  | 10
FIT75730-I1 | F75-RTU-801 | FIM III TSF Switchboard 3 Remote Telemetry Unit | FIT-75730 | 20 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40132 2000-F75-TER-IC-40133 | Confirmed | 0 |  | 10
PIT75730-I1 | F75-RTU-801 | FIM III TSF Switchboard 3 Remote Telemetry Unit | PIT-75730 | 20 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40133 | Confirmed | 0 |  | 10
F75CP801-I1 | F75-SW-801 | FIM III TSF Switchboard 3 | F75-CP-801 | 10 | 12PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40132 | Confirmed | 0 |  | 10
FIT75731-P1 | F75-SW-802 | FIM III TSF Switchboard 4 | FIT-75731 | 20 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40134 | Confirmed | 0 |  | 10
FIT75731-I1 | F75-RTU-802 | FIM III TSF Switchboard 4 Remote Telemetry Unit | FIT-75731 | 20 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40134 2000-F75-TER-IC-40135 | Confirmed | 0 |  | 10
PIT75731-I1 | F75-RTU-802 | FIM III TSF Switchboard 4 Remote Telemetry Unit | PIT-75731 | 20 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40135 | Confirmed | 0 |  | 10
F75CP802-I1 | F75-SW-802 | FIM III TSF Switchboard 4 | F75-CP-802 | 10 | 12PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40134 | Confirmed | 0 |  | 10
FIT75732-P1 | F75-SW-803 | FIM III TSF Switchboard 5 | FIT-75732 | 20 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40137 | Confirmed | 0 |  | 10
FIT75732-I1 | F75-RTU-803 | FIM III TSF Switchboard 5 Remote Telemetry Unit | FIT-75732 | 20 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40136 2000-F75-TER-IC-40137 | Confirmed | 0 |  | 10
PIT75732-I1 | F75-RTU-803 | FIM III TSF Switchboard 5 Remote Telemetry Unit | PIT-75732 | 20 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40137 | Confirmed | 0 |  | 10
F75CP803-I1 | F75-SW-803 | FIM III TSF Switchboard 5 | F75-CP-803 | 10 | 12PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40136 | Confirmed | 0 |  | 10
FIT75733-P1 | F75-SW-804 | FIM III TSF Switchboard 6 | FIT-75733 | 20 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40139 | Confirmed | 0 |  | 10
FIT75733-I1 | F75-RTU-804 | FIM III TSF Switchboard 6 Remote Telemetry Unit | FIT-75733 | 20 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40138 2000-F75-TER-IC-40139 | Confirmed | 0 |  | 10
PIT75733-I1 | F75-RTU-804 | FIM III TSF Switchboard 6 Remote Telemetry Unit | PIT-75733 | 20 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40139 | Confirmed | 0 |  | 10
Client: | NORTHERN STAR RESOURCES |  | FIM II CELL G & FIM III TAILINGS STORAGE FACILITIES C ABLE SCHEDULE | [10 empty] | 11
Project: Document Number: | KCGM 2000-F75-LST-EL-40003 | [12 empty] | 11
Revision: | 0 | [12 empty] | 11
F75CP804-I1 | F75-SW-804 | FIM III TSF Switchboard 6 | F75-CP-804 | 10 | 12PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40138 | Confirmed | 0 |  | 11
FIT75793-P1 | F75-IJB-606 | Decant Dam 4 Instrument Junction Box | FIT-75793 | 30 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40012 | Confirmed | 0 |  | 11
FIT75793-I1 | F75-IJB-606 | Decant Dam 4 Instrument Junction Box | FIT-75793 | 30 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40012 | Confirmed | 0 |  | 11
LIT75785-I2 | LIT75785-JB | FIM III Toe Drain Pump 1 Level Transmitter Junction Box | LIT-75785 | 5 | Vendor Cable Pre-Terminated one side | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40129 | Confirmed | 0 |  | 11
LIT75785-I1 | F75-RTU-557 | FIM III TSF Switchboard 2 Remote Telemetry Unit | LIT75785-JB | 20 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40129 | Confirmed | 0 |  | 11
FIT75785-P1 | F75-SW-557 | FIM III TSF Switchboard 2 | FIT-75785 | 20 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40129 | Confirmed | 0 |  | 11
FIT75785-I1 | F75-RTU-557 | FIM III TSF Switchboard 2 Remote Telemetry Unit | FIT-75785 | 20 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40128 2000-F75-TER-IC-40129 | Confirmed | 0 |  | 11
LIT75790-I2 | LIT75790-JB | FIM III Underdrainage Pump 2 Level Transmitter Junction Box | LIT-75790 | 5 | Vendor Cable Pre-Terminated one side | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40127 | Confirmed | 0 |  | 11
LIT75790-I1 | F75-RTU-557 | FIM III TSF Switchboard 2 Remote Telemetry Unit | LIT75790-JB | 20 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40127 | Confirmed | 0 |  | 11
FIT75790-P1 | F75-SW-557 | FIM III TSF Switchboard 2 | FIT-75790 | 20 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40127 | Confirmed | 0 |  | 11
FIT75790-I1 | F75-RTU-557 | FIM III TSF Switchboard 2 Remote Telemetry Unit | FIT-75790 | 20 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40126 2000-F75-TER-IC-40127 | Confirmed | 0 |  | 11
XV75796-I1 | F75-RTU-557 | FIM III TSF Switchboard 2 Remote Telemetry Unit | XV-75796 | 25 | 6PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40126 2000-F75-TER-IC-40127 | Confirmed | 0 |  | 11
XV75796-P1 | F75-SW-557 | FIM III TSF Switchboard 2 | XV-75796 | 25 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40127 | Confirmed | 0 |  | 11
XV75798-I1 | F75-RTU-557 | FIM III TSF Switchboard 2 Remote Telemetry Unit | XV-75798 | 25 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40126 2000-F75-TER-IC-40127 | Confirmed | 0 |  | 11
XV75798-P1 | F75-SW-557 | FIM III TSF Switchboard 2 | XV-75798 | 25 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40127 | Confirmed | 0 |  | 11
F75CP557-I1 | F75-SW-557 | FIM III TSF Switchboard 2 | F75-CP-557 | 10 | 12PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40126 2000-F75-TER-IC-40127 | Confirmed | 0 |  | 11
F75CP558-I1 | F75-SW-557 | FIM III TSF Switchboard 2 | F75-CP-558 | 10 | 12PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40128 2000-F75-TER-IC-40129 | Confirmed | 0 |  | 11
LIT75789-I2 | LIT75789-JB | FIM III Underdrainage Pump 1 Level Transmitter Junction Box | LIT-75789 | 5 | Vendor Cable Pre-Terminated one side | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40121 | Confirmed | 0 |  | 11
LIT75789-I1 | F75-RTU-556 | FIM III TSF Switchboard 1 Remote Telemetry Unit | LIT75789-JB | 20 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40121 | Confirmed | 0 |  | 11
FIT75789-P1 | F75-SW-556 | FIM III TSF Switchboard 1 | FIT-75789 | 20 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40120 2000-F75-TER-IC-40121 | Confirmed | 0 |  | 11
FIT75789-I1 | F75-RTU-556 | FIM III TSF Switchboard 1 Remote Telemetry Unit | FIT-75789 | 20 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40121 | Confirmed | 0 |  | 11
XV75795-I1 | F75-RTU-556 | FIM III TSF Switchboard 1 Remote Telemetry Unit | XV-75795 | 25 | 6PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40120 2000-F75-TER-IC-40121 | Confirmed | 0 |  | 11
XV75795-P1 | F75-SW-556 | FIM III TSF Switchboard 1 | XV-75795 | 25 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40121 | Confirmed | 0 |  | 11
XV75797-I1 | F75-RTU-556 | FIM III TSF Switchboard 1 Remote Telemetry Unit | XV-75797 | 25 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40120 2000-F75-TER-IC-40121 | Confirmed | 0 |  | 11
XV75797-P1 | F75-SW-556 | FIM III TSF Switchboard 1 | XV-75797 | 25 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40121 | Confirmed | 0 |  | 11
F75CP556-I1 | F75-SW-556 | FIM III TSF Switchboard 1 | F75-CP-556 | 20 | 12PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40120 2000-F75-TER-IC-40121 | Confirmed | 0 |  | 11
FIT75792-P1 | F75-RTU-329 | FIM III TSF Decant Dam 4 Telemetry Panel | FIT-75792 | 20 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40021 | Confirmed | 0 | Located Decant dam 4 | 11
FIT75792-I1 | F75-RTU-329 | FIM III TSF Decant Dam 4 Telemetry Panel | FIT-75792 | 20 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40020 2000-F75-TER-IC-40021 | Confirmed | 0 | Located Decant dam 4 | 11
FIT75794-P1 | SEBDT01SW | Eastern Borefield Dam Switchboard | FIT-75794 | 30 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 175\E\3045-002 175\E\3038_5 | Estimated t | 0 | Not on model Contractor to provide, install and wire a 2A (DTCB6202D) circuit breaker into the existing SEBDT01DB01A distribution board. The flow transmitter power cable will be wired to this circui breaker. | 11
FIT75794-I1 | SEBDT01SW | Eastern Borefield Dam Switchboard | FIT-75794 | 30 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Final Run | CN037-E&I | CN037-E&I | CN037-E&I | 175\E\3045-002 175\E\3043-002 | Estimated | 0 | Not on model Contractor to provide, install and wire in a new IO Module Card (Slot 4 -V562) c/w 52 terminals (weidmuller -W2 wC il_l 4 b_eD wT i) r, e dw h toic oh . the FIT signals | 11
LIT75265-I2 | LIT75265-JB | FIM II Cell G Underdrainage Pump Level Transmitter Junction Box | LIT-75265 | 5 | Vendor Cable Pre-Terminated one side | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40214 | Confirmed | 0 |  | 11
LIT75265-I1 | F75-RTU-593 | FIM II TSF Cell G Remote Telemetry Unit 2 | LIT75265-JB | 20 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40214 | Confirmed | 0 |  | 11
FIT75265-P1 | F75-SW-593 | FIM II TSF Cell G Switchboard 2 | FIT-75265 | 20 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40214 | Confirmed | 0 |  | 11
FIT75265-I1 | F75-RTU-593 | FIM II TSF Cell G Remote Telemetry Unit 2 | FIT-75265 | 20 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40213 2000-F75-TER-IC-40214 | Confirmed | 0 |  | 11
XV75283-I1 | F75-RTU-593 | FIM II TSF Cell G Remote Telemetry Unit 2 | XV-75283 | 20 | 6PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40213 2000-F75-TER-IC-40214 | Confirmed | 0 |  | 11
XV75283-P1 | F75-SW-593 | FIM II TSF Cell G Switchboard 2 | XV-75283 | 20 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40214 | Confirmed | 0 |  | 11
XV75284-I1 | F75-RTU-593 | FIM II TSF Cell G Remote Telemetry Unit 2 | XV-75284 | 20 | 4PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40213 2000-F75-TER-IC-40214 | Confirmed | 0 |  | 11
XV75284-P1 | F75-SW-593 | FIM II TSF Cell G Switchboard 2 | XV-75284 | 20 | 2C+E 2.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40214 | Confirmed | 0 |  | 11
LIT75264-I2 | LIT75264-JB | FIM II Cell G Toe Drain Pump 1 Level Transmitter Junction Box | LIT-75264 | 5 | Vendor Cable Pre-Terminated one side | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40216 | Confirmed | 0 |  | 11
LIT75264-I1 | F75-RTU-593 | FIM II TSF Cell G Remote Telemetry Unit 2 | LIT75264-JB | 20 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40216 | Confirmed | 0 |  | 11
FIT75264-P1 | F75-SW-593 | FIM II TSF Cell G Switchboard 2 | FIT-75264 | 30 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40216 | Confirmed | 0 |  | 11
FIT75264-I1 | F75-RTU-593 | FIM II TSF Cell G Remote Telemetry Unit 2 | FIT-75264 | 30 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40215 2000-F75-TER-IC-40216 | Confirmed | 0 |  | 11
F75CP559-I1 | F75-SW-593 | FIM II TSF Cell G Switchboard 2 | F75-CP-559 | 10 | 12PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40215 2000-F75-TER-IC-40216 | Confirmed | 0 |  | 11
F75CP593-I1 | F75-SW-593 | FIM II TSF Cell G Switchboard 2 | F75-CP-593 | 10 | 12PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40213 2000-F75-TER-IC-40214 | Confirmed | 0 |  | 11
LIT75365-I2 | LIT75365-JB | FIM II Cell G Toe Drain Pump 2 Level Transmitter Junction Box | LIT-75365 | 5 | Vendor Cable Pre-Terminated one side | Conduit | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40212 | Confirmed | 0 |  | 11
LIT75365-I1 | F75-RTU-560 | FIM II TSF Cell G Remote Telemetry Unit 1 | LIT75365-JB | 30 | 1PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Ladder/ Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40212 | Confirmed | 0 |  | 11
F75CP560-I1 | F75-SW-560 | FIM II TSF Cell G Switchboard 1 | F75-CP-560 | 30 | 12PR 1.5mm² Cu 0.11kV PVC/OSCN/PVC | Underground | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40211 2000-F75-TER-IC-40212 | Confirmed | 0 |  | 11
FIT75365-P1 | F75-SW-560 | FIM II TSF Cell G Switchboard 1 | FIT-75365 | 35 | 2C+E 1.5mm² Cu 0.6/1kV PVC/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40212 | Confirmed | 0 |  | 11
FIT75365-I1 | F75-RTU-560 | FIM II TSF Cell G Remote Telemetry Unit 1 | FIT-75365 | 35 | 2PR 1.5mm² Cu 0.11kV PVC/IOSCN/PVC | Ladder | CN037-E&I | CN037-E&I | CN037-E&I | 2000-F75-TER-IC-40211 2000-F75-TER-IC-40212 | Confirmed | 0 |  | 11