## Revisions
PROCESS CONTROL TABLES
REVISION HISTORY
KCGM GROWTH PROJECT
2000-F23-LST-PR-10001
NORTHERN STAR RESOURCES LIMITED
Revision | Document Changes | Date
Issued for Internal Review | - Vendor Data TBC highlighted or red-text
2024-05-24
Issued for Client Review | - Vendor/Third Party Data TBC highlighted or red-text
2024-07-18
Issued for Design | - Vendor/Third Party Data TBC highlighted or red-text
| - Final Tails Pumps removed (already included in KCGM FIM TSF Project scope) | 2025-02-13
Post-FAT updates | - Changes highlighted orange
| - Strikethrough indicates removed from design | 2025-10-17
Prepared for SAT | -Highlighting and strikethough tect removed

## 1. Analogue Input
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FINAL TAILINGS HANDLING AND STORAGE
2000-F23-LST-PR-10001
ANALOGUE INSTRUMENTS (AI)
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [10 empty] | C1 Sign Off |  | C2 Sign Off |  | C1 Comments
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date
|  |  |  | AIT23406 | AI23406 | 2000-F23-PID-PR-10001 | F23-TK-404 Final Tails Tank HCN Gas Monitor Analyser Indicating Transmitter | F23TK404 Air HCN Con | 1 | 0 | 25 | ppm | [16 empty] | 5 | 5 | 10 | 0 |  |  | 3 |  |  |  |  | MOC-585 to change range alarm set points and alarm priorities SC 3/6/26 | Removed alarm as HH switch alarm already present HH alarm put back. Switch not used. MOC 712. AP 15/07/2026
|  |  |  | F23AG404AIS | F23AG404AI | 2000-F23-PID-PR-10001 | F23-AG-404 Fibnal Tails Tank Agitator Current | F23AG404 Current | 1 | 0 | 76.6 | A | [14 empty] | 38.3 | 0 | 61.2 | 0 |  |  | F24-AG-404 Not Running | Soft Tag Alarm setpoints to be confirmed during commissioning Allow 60 seconds alarm masking delay for agitator start-up | 1 |  |  |  |  | 2025-07-25 | KAN-2097
|  |  |  | UT23500 | UI23500 | N/A | F23-SR-001 Final Tails Pumps 11kV Switchroom Temperature/Humidity Transmitter | 572 | 1 | 0 | 50 | °C | [16 empty] | 30 | 300 |  |  |  | A_Hi = Alarm. Nominal 24C. Alarm setpoint to be confirmed during commissioning. | 0 |  |  |  |  | jwho - change A_Hi delay to match alarm database from 5sec to 300sec
|  |  |  | UT23501 | UI23501 | N/A | F23-SR-002 Final Tails Pumps 415V Switchroom Temperature/Humidity Transmitter | F23SR002 415V SR Temp | 1 | 0 | 50 | °C | [16 empty] | 30 | 300 |  |  |  | A_Hi = Alarm. Nominal 24C. Alarm setpoint to be confirmed during commissioning. | 0 |  |  |  |  | jwho - change A_Hi delay to match alarm database from 5sec to 300sec
|  |  |  | UT23502 | UI23502 | N/A | F23-SR-002 Final Tails Pumps 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | F23SR002 415V SR TF Temp | 1 | 0 | 50 | °C | [16 empty] | 30 | 300 |  |  |  | A_Hi = Alarm. Nominal 24C. Alarm setpoint to be confirmed during commissioning. | 0 |  |  |  |  | jwho - change A_Hi delay to match alarm database from 5sec to 300sec
|  |  |  | TT23470 | TI23470 |  |  | F23PP466 Gearbox Temp | 1 | -50 | 150 | °C | [16 empty] | 85 | 5 | 90 | 5 |  | Hi --> Warning, Hi-Hi --> Trip | 1 |  |  |  |  | has simiar tag in final tails PCT F00
|  |  |  | TT23472 | TI23472 |  |  | F23PP467 Gearbox Temp | 1 | -50 | 150 | °C | [16 empty] | 85 | 5 | 90 | 5 |  | Hi --> Warning, Hi-Hi --> Trip | 1 |  |  |  |  | has simiar tag in final tails PCT F00
|  |  |  | TT23474 | TI23474 |  |  | F23PP468 Gearbox Temp | 1 | -50 | 150 | °C | [16 empty] | 85 | 5 | 90 | 5 |  | Hi --> Warning, Hi-Hi --> Trip | 1 |  |  |  |  | has simiar tag in final tails PCT F00
|  |  |  | TT23476 | TI23476 |  |  | F23PP469 Gearbox Temp | 1 | -50 | 150 | °C | [16 empty] | 85 | 5 | 90 | 5 |  | Hi --> Warning, Hi-Hi --> Trip | 1 |  |  |  |  | has simiar tag in final tails PCT F00
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 5 | 5

## 2. Analogue Output
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FINAL TAILINGS HANDLING AND STORAGE
2000-F23-LST-PR-10001
ANALOGUE INSTRUMENTS (AO)
Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  |  |  | C1 Sign Off |  | C2 Sign Off
[5 empty] | Trend (sec) | Min | Max | Unit | Comments | Rev | OK | Date | OK | Date
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
0 | 0

## 3. Digital Input
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FINAL TAILINGS HANDLING AND STORAGE |  |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)*
2000-F23-LST-PR-10001
DIGITAL INSTRUMENTS (DI)
[13 empty] | C1 Sign Off |  | C2 Sign Off |  |  | C1 comments
Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Source | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date
F23DCS409PS1 | 23DCS409_PS1 | N/A | F23-DCS-409 PS1 24VDC HEALTHY | F23DCS409 PS1 24VDC OK | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23DCS409PS2 | 23DCS409_PS2 | N/A | F23-DCS-409 PS2 24VDC HEALTHY | F23DCS409 PS2 24VDC OK | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23SW023PS | F23SW023_PS | N/A | F23-SW-023 ACB SHUNT TRIP 24VDC OK | F23SW023 ACBSHUNT 24V OK | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 1 |  |  |  |  | 23/10/2025
F23SW023AF | F23SW023_AF | N/A | F23-SW-023 ARC FLASH DETECTION SYSTEM ALARM | F23SW023 ARC FLASH | Alarm | Normal | Alarm | Hardwired | 0 |  | MOC-125 VG 27/02/2026 | 0
F23SW023OP | F23SW023_OP | N/A | F23-SW-023 CIRCUIT BREAKER OPENED | F23SW023 BREAKER OPEN | Inactive | Active |  | Hardwired | 0 |  |  | 0
F23SW023CL | F23SW023_CL | N/A | F23-SW-023 CIRCUIT BREAKER CLOSED | F23SW023 BREAKER CLOSE | Inactive | Active |  | Hardwired | 0 |  |  | 0
F23SW023TRP | F23SW023_TRP | N/A | F23-SW-023 CIRCUIT BREAKER TRIPPED | F23SW023 BREAKER TRIP | Normal | Alarm | Alarm | Hardwired | 0 |  | MOC-125 VG 27/02/2026 | 0
F23SW023SD | F23SW023_SD | N/A | F23-SW-023 INCOMER SURGE DIVERTER OK | F23SW023 IncSurgeDiv OK | Alarm | Normal | Alarm | Hardwired | 0 |  | MOC-125 VG 27/02/2026 | 0
F23SR001ESTP | 23SR001_ESTP | N/A | F23-SR-001 SWITCHROOM EMERGENCY SHUTDOWN DCS INPUT | F23SR001 SR E Shut | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23SW023PS1 | F23SW023_PS1 | N/A | F23-SW-023 PS1 24VDC HEALTHY | F23SW023 PS1 24VDC OK | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23SW023PS2 | F23SW023_PS2 | N/A | F23-SW-023 PS2 24VDC HEALTHY | F23SW023 PS2 24VDC OK | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23BC001FL1 | F23BC001_FL1 | N/A | F23-BC-001 48VDC Charger Mains Fail | F23BC001 48VDC Main Fail | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23BC001FL2 | F23BC001_FL2 | N/A | F23-BC-001 48VDC Charger Battery Fail | F23BC001 48VDC Batt Fail | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23BC001FL3 | F23BC001_FL3 | N/A | F23-BC-001 48VDC Charger Charger Fail | F23BC001 48VDC Chrg Fail | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23FIP001ALM | 23FIP001_ALM | N/A | F23-FIP-001 Alarm | F23FIP001 Alarm | Normal | Alarm | Alarm | Hardwired | 0 |  | 20/02/2026 MOC103 | 0
F23FIP001ISL | 23FIP001_ISL | N/A | F23-FIP-001 Isolated | F23FIP001 Isolated | Normal | Alarm | Alarm | Hardwired | 0 |  | 20/02/2026 MOC103 | 0
F23FIP001FLT | 23FIP001_FLT | N/A | F23-FIP-001 Fault | F23FIP001 Fault | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23SW123SD | F23SW123_SD | N/A | F23-SW-123 Surge Diverter Ok | F23SW123 SurgeDiv OK | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23SW123Q1CL | 23SW123_Q1CL | N/A | F23-SW-123 Mains Supply CB Closed | F23SW123 MainCB Closed | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23SW123Q1OP | 23SW123Q1_OP | N/A | F23-SW-123 Mains Supply CB Tripped | F23SW123 MainCB Open | Inactive | Active |  | Hardwired | 0 |  |  | 1 |  |  |  |  | 22/09/2025 | CR-029
F23SW123Q2CL | 23SW123_Q2CL | N/A | F23-SW-123 Generator Supply CB Closed | F23SW123 GenCB Closed | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23SW123Q2OP | 23SW123Q2_OP | N/A | F23-SW-123 Generator Supply CB Tripped | F23SW123 GenCB Open | Inactive | Active |  | Hardwired | 0 |  |  | 1 |  |  |  |  | 22/09/2025 | CR-029
LSHH23503 | LAHH23503 | N/A | F23-GE-123 Final Tails Pumps Emergency Supply 415V Generator Fuel Level Switch High High | [13 empty] | 24/06/2025 | Removed, does not exist
LSH23503 | LAH23503 | N/A | F23-GE-123 Final Tails Pumps Emergency Supply 415V Generator Fuel Level Switch High | F23SW123 EPS Gen. Fuel | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
LSL23503 | LAL23503 | N/A | F23-GE-123 Final Tails Pumps Emergency Supply 415V Generator Fuel Level Switch Low | F23SW123 EPS Gen. Fuel | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23RIO001PS1 | 23RIO001_PS1 | N/A | F23-RIO-001 PS1 24VDC HEALTHY | F23RIO001 PS1 24VDC OK | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23RIO001PS2 | 23RIO001_PS2 | N/A | F23-RIO-001 PS2 24VDC HEALTHY | F23RIO001 PS2 24VDC OK | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23SW016HTY | F23SW016_HTY | N/A | F23-SW-016 Fuse Healthy | F23SW016 Fuse Healthy | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
F23SW016ESCL | 23SW016_ESCL | N/A | F23-SW-016 Earth Switch Closed | F23SW016 ES Closed | Inactive | Active | - | Hardwired | 0 |  |  | 0
F23SW016ESOP | 23SW016_ESOP | N/A | F23-SW-016 Earth Switch Opened | F23SW016 ES Open | Inactive | Active | - | Hardwired | 0 |  |  | 0
ZSC23504 | ZAC23504 | N/A | F23-TR-023 FINAL TAILS PUMPS 415V MCC TRANSFORMER Enclosure Door Position Switch Closed | F23TR023 415VMCC Door | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 0
FSH23505 | FAH23505 | 2000-F24-PID-PR-10005 |  | F23SE429 Alarm | Alarm | Normal | Alarm | Hardwired | 30 |  |  | 1 |  |  |  |  | 26/06/2025 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FSH23506 | FAH23506 | 2000-F24-PID-PR-10005 | F23-TR-023 FINAL TAILS PUMPS 415V MCC TRANSFORMER Enclosure Door Position Switch Closed | F23SE452 Alarm | Alarm | Normal | Alarm | Hardwired | 30 |  |  | 1 |  |  |  |  | 26/06/2025 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
F23TR023WTH | F23TR023_WTH | - | F23-TR-023 TRANSFORMER WINDING TEMPERATURE HIGH ALARM | F23TR023 Temp Hi | Alarm | Normal | Alarm | Hardwired to DCS | 0 |  |  | 1 |  |  |  |  | 19/08/2025 | CR-034/ MOC-240
PSL23471 | PAL23471 |  |  | F23PP466 Gearbox Pres Lo | Alarm | Normal | Alarm | Hardwired | 30 | Mask when pump not running | Warning | 1 |  |  |  |  | 27/10/2025 | pump not available to test alarms
PSL23473 | PAL23473 |  |  | F23PP467 Gearbox Pres Lo | Alarm | Normal | Alarm | Hardwired | 30 | Mask when pump not running | Warning | 1 |  |  |  |  | 27/10/2025
PSL23475 | PAL23475 |  |  | F23PP468 Gearbox Pres Lo | Alarm | Normal | Alarm | Hardwired | 30 | Mask when pump not running | Warning | 1 |  |  |  |  | 27/10/2025
PSL23477 | PAL23477 |  |  | F23PP469 Gearbox Pres Lo | Alarm | Normal | Alarm | Hardwired | 30 | Mask when pump not running | Warning | 1 |  |  |  |  | 27/10/2025 | pump not available to test alarms
F23GE123CBTRP | 23GE123CBTRP |  | F23-GE-123 FINAL TAILS PUMPS EMERGENCY SUPPLY 415V GENERATOR CB TRIPPED | F23-GE-123 GEN CB TRP | Alarm | Normal | Alarm | Hardwired to DCS | 0 | [8 empty] | added to graphics?
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
34 | 34

## 4. Digital Output
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FINAL TAILINGS HANDLING AND STORAGE |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)*
2000-F23-LST-PR-10001
DIGITAL INSTRUMENTS (DO)
[12 empty] | C1 Sign Off |  | C2 Sign Off
Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date | Change Date | Change Reference
YY23407 | YA23407 | 2000-F23-PID-PR-10001 | F23-TK-404 Final Tails Tank HCN Gas Monitor Warning Beacon | F23TK404 HCN Beacn & Srn | Normal | Activated | Activated | 0 |  | Activate if AI23406_HH = Alarm Deactivate if AI23406_HH= Normal and alarm is reset. | 3 | [5 empty] | MOC - 712. AP 15/07/2026
YY23408 | YA23408 | 2000-F23-PID-PR-10001 | Acid Wash Siren and Becaon Alarm 1 | Acid Wash Alarm 1 | Normal | Activated | Activated | 0 |  | Activate when acid wash in the elution columns is started (F22-SEQ-0002 SEQ START) OR (KV65702 is OPEN OR KV65802 is OPEN) Deactivate when F22-SEQ-0002 is COMPLETED and reset AND (KV65702 is CLOSED AND KV65802 is CLOSED) | 1 |  |  |  |  | 15/05/2025 | Updated to include Acid Rinse from existing elution circuit, as per M3 design reivew 14/05/2025
YY23409 | YA23409 | 2000-F23-PID-PR-10001 | Acid Wash Siren and Becaon Alarm 2 | Acid Wash Alarm 2 | Normal | Activated | Activated | 0 |  | Activate when acid wash in the elution columns is started (F22-SEQ-0002 SEQ START) OR (KV65702 is OPEN OR KV65802 is OPEN) Deactivate when F22-SEQ-0002 is COMPLETED and reset AND (KV65702 is CLOSED AND KV65802 is CLOSED) | 1 |  |  |  |  | 15/05/2025 | Updated to include Acid Rinse from existing elution circuit, as per M3 design reivew 14/05/2025
F23SW016OP | F23SW016_OP |  | Final Tails Pumps 11kV Switchboard Remote Switching Panel Open Breaker | F23SW016 Breaker Opened | Normal | Activated | Activated | 0 |  |  | 0 |  |  |  |  | 28/02/2026 LR
F23SW016CL | F23SW016_CL |  | Final Tails Pumps 11kV Switchboard Remote Switching Panel Close Breaker | F23SW016 Breaker Closed | Normal | Activated | Activated | 0 |  |  | 0 |  |  |  |  | 28/02/2026 LR
YY23410 | YY23410 | 2000-F23-PID-PR-10001 | F23-TK-404 Final Tails Tank HCN Gas Monitor Reset | F23TK404 HCN Reset | Normal | Activated | Activated | 0 |  | When the HCN levels drop below 10ppm for 10 minutes the DCS will reset the alarm via the new digital output. | 3 | [5 empty] | MOC - 712. AP 15/07/2026
YY23406 | YY23410 | 2000-F23-PID-PR-10001 | F23-TK-404 Final Tails Tank HCN Gas Monitor Reset | F23TK404 HCN Reset | Normal | Activated | Activated | 0 |  | When the HCN levels drop below 10ppm for 10 minutes the DCS will reset the alarm via the new digital output. | 3 | [5 empty] | MOC-736 DE 08/08/.2026 To retest logic
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
5 | 5
.

## 5. Totalisers
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FINAL TAILINGS HANDLING AND STORAGE
2000-F23-LST-PR-10001
TOTALISERS
[7 empty] | Reset Period |  |  |  |  | C1 Sign Off |  | C2 Sign Off
Tag Source | Tag Name | Type | P&ID | Description | Abbreviated Description (Faceplate) | Units | Shift | Day | Cont | Comments | Rev | OK | Date | OK | Date
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
0 | 0

## 6. OnOff Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FINAL TAILINGS HANDLING AND STORAGE
2000-F23-LST-PR-10001
OPEN-CLOSE VALVES
[10 empty] | Permissives and Trips | [12 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position (Loss of Power) | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (Faceplate) | Delay On | Delay Off | Open Permissive | Close Permissive | Open Interlock | Close Interlock | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date | C1 Comments
XV23411 | 2000-F23-PID-PR-10002 | F23-PP-466 Final Tails Pump 1 Suction Valve | F23PP466 Suction | Detail 4 | FC | X | X | F23-SEQ-10001 | F23-SEQ-10002 F23-SEQ-10003 | [11 empty] | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 0 |  |  |  |  | Could not green mark the related interlocks to pump due to PCT not available for SP2 yet.
XV23424 | 2000-F23-PID-PR-10002 | F23-PP-467 Final Tails Pump 2 Suction Valve | F23PP467 Suction | Detail 4 | FC | X | X | F23-SEQ-10004 | F23-SEQ-10005 F23-SEQ-10006 | [11 empty] | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 0 |  |  |  |  | Could not green mark the related interlocks at 23PP467 due to PCT not available for SP2 yet.
XV23435 | 2000-F23-PID-PR-10002 | F23-PP-468 Final Tails Pump 3 Suction Valve | F23PP468 Suction | Detail 4 | FC | X | X | F23-SEQ-10007 | F23-SEQ-10008 F23-SEQ-10009 | [11 empty] | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 0 |  |  |  |  | Could not green mark the related interlocks to pump due to PCT not available for SP2 yet.
XV23446 | 2000-F23-PID-PR-10002 | F23-PP-469 Final Tails Pump 4 Suction Valve | F23PP469 Suction | Detail 4 | FC | X | X | F23-SEQ-10010 | F23-SEQ-10011 F23-SEQ-10012 | [11 empty] | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 0 |  |  |  |  | Could not green mark the related interlocks to pump due to PCT not available for SP2 yet.
XV23412 | 2000-F23-PID-PR-10002 | F23-PP-466 Final Tails Pump 1 Suction Flushing Water Valve | F23PP466 Suction Flush | Detail 4 | FC | X | X | F23-SEQ-10003 | F23-SEQ-10001 F23-SEQ-10002 | [11 empty] | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 0 |  |  |  |  | Could not green mark the related interlocks to pump due to PCT not available for SP2 yet.
XV23425 | 2000-F23-PID-PR-10002 | F23-PP-467 Final Tails Pump 2 Suction Flushing Water Valve | F23PP467 Suction Flush | Detail 4 | FC | X | X | F23-SEQ-10006 | F23-SEQ-10004 F23-SEQ-10005 | [11 empty] | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 0
XV23436 | 2000-F23-PID-PR-10002 | F23-PP-468 Final Tails Pump 3 Suction Flushing Water Valve | F23PP468 Suction Flush | Detail 4 | FC | X | X | F23-SEQ-10009 | F23-SEQ-10007 F23-SEQ-10008 | [11 empty] | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 0
XV23447 | 2000-F23-PID-PR-10002 | F23-PP-469 Final Tails Pump 4 Suction Flushing Water Valve | F23PP469 Suction Flush | Detail 4 | FC | X | X | F23-SEQ-10012 | F23-SEQ-10010 F23-SEQ-10011 | [11 empty] | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 0 |  |  |  |  | Could not green mark the related interlocks to pump due to PCT not available for SP2 yet.
XV23413 | 2000-F23-PID-PR-10002 | F23-PP-466 Final Tails Pump 1 Suction Drain Valve | F23PP466 Suction Drain | Detail 4 | FO | X | X | F23-SEQ-10002 | F23-SEQ-10001 F23-SEQ-10003 | OT1 | XV23411 CLOSED AND XV23412 OPEN AND F23-PP-466 TRIPS (ONESHOT) | FLUSHING PUMP TRIP | 1 |  |  |  | X |  | X |  | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 0 |  |  |  |  | Could not green mark the related interlocks to pump due to PCT not available for SP2 yet. FC 4/7/26: INTERLOCK ADDED AS PART OF MOC682
XV23426 | 2000-F23-PID-PR-10002 | F23-PP-467 Final Tails Pump 2 Suction Drain Valve | F23PP467 Suction Drain | Detail 4 | FO | X | X | F23-SEQ-10005 | F23-SEQ-10004 F23-SEQ-10006 | OT1 | XV23424 CLOSED AND XV23425 OPEN AND F23-PP-467 TRIPS (ONESHOT) | FLUSHING PUMP TRIP | 1 |  |  |  | X |  | X |  | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 0 |  |  |  |  | Could not green mark the related interlocks at 23PP467 due to PCT not available for SP2 yet. Could not green mark the related interlocks to pump due to PCT not available for SP2 yet. FC 4/7/26: INTERLOCK ADDED AS PART OF MOC682
XV23437 | 2000-F23-PID-PR-10002 | F23-PP-468 Final Tails Pump 3 Suction Drain Valve | F23PP468 Suction Drain | Detail 4 | FO | X | X | F23-SEQ-10008 | F23-SEQ-10007 F23-SEQ-10009 | OT1 | XV23435 CLOSED AND XV23436 OPEN AND F23-PP-468 TRIPS (ONESHOT) | FLUSHING PUMP TRIP | 1 |  |  |  | X |  | X |  | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 0 |  |  |  |  | Could not green mark the related interlocks to pump due to PCT not available for SP2 yet. Could not green mark the related interlocks to pump due to PCT not available for SP2 yet. FC 4/7/26: INTERLOCK ADDED AS PART OF MOC682
XV23448 | 2000-F23-PID-PR-10002 | F23-PP-469 Final Tails Pump 4 Suction Drain Valve | F23PP469 Suction Drain | Detail 4 | FO | X | X | F23-SEQ-100011 | F23-SEQ-10010 F23-SEQ-10012 | OT1 | XV23446 CLOSED AND XV23447 OPEN AND F23-PP-469 TRIPS (ONESHOT) | FLUSHING PUMP TRIP | 1 |  |  |  | X |  | X |  | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 0 |  |  |  |  | Could not green mark the related interlocks to pump due to PCT not available for SP2 yet. Could not green mark the related interlocks to pump due to PCT not available for SP2 yet. FC 4/7/26: INTERLOCK ADDED AS PART OF MOC682
SV23480 | 2000-F24-PID-PR-10004 | F23-PP-466 Final Tails Pump 1 Gland Water Solenoid Valve | F23PP466 Gland Supply | Detail 11 | FO | X | X | F23-SEQ-10001 OR F23-PP-466 START | F23-SEQ-10002 F23-SEQ-10003 | [11 empty] | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 1
SV23484 | 2000-F24-PID-PR-10004 | F23-PP-467 Final Tails Pump 2 Gland Water Solenoid Valve | F23PP467 Gland Supply | Detail 11 | FO | X | X | F23-SEQ-10004 OR F23-PP-467 START | F23-SEQ-10005 F23-SEQ-10006 | [11 empty] | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 1
SV23488 | 2000-F24-PID-PR-10004 | F23-PP-468 Final Tails Pump 3 Gland Water Solenoid Valve | F23PP468 Gland Supply | Detail 11 | FO | X | X | F23-SEQ-10007 OR F23-PP-468 START | F23-SEQ-10008 F23-SEQ-10009 | [11 empty] | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 1
SV23492 | 2000-F24-PID-PR-10004 | F23-PP-469 Final Tails Pump 4 Gland Water Solenoid Valve | F23PP469 Gland Supply | Detail 11 | FO | X | X | F23-SEQ-10010 OR F23-PP-469 START | F23-SEQ-10011 F23-SEQ-10012 | [11 empty] | Refer to DRA document 2000-F00-LST-PR-40001 Tailings Sequence Flowcharts | 1
XV23402 | 2000-F23-PID-PR-10001 | F23-TK-404 Final Tails Tank Drain Valve | F23TK404 Drain Valve | Detail 3 | FL | X | [15 empty] | 0 |  |  |  |  | Should Auto button be visible if no auto mode?
XV23457 | 2000-F23-PID-PR-10002 | FIM 1 Valve Station Feed Valve 1 | FIM1 HP Water Vlv 1 | Detail 4 | FC | X | X | [14 empty] | 1
XV23458 | 2000-F23-PID-PR-10002 | FIM 1 Valve Station Feed Valve 2 | FIM1 HP Water Vlv 2 | Detail 4 | FC | X | X | [14 empty] | 1
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
19 | 19

## 7. Control Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FINAL TAILINGS HANDLING AND STORAGE
2000-F23-LST-PR-10001
CONTROL VALVES
[10 empty] | Permissive and Trips | [12 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open Interlock | Close Interlock | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date
FCV23405 | 2000-F23-PID-PR-10001 | F23-TK-404 Final Tails Tank Saline Water Feed Flow Control Valve | F23TK404 Saline Water | Detail 1 | FC | X | X | [14 empty] | 0
FCV23456 | 2000-F23-PID-PR-10002 | FIM 1 Valve Station Feed Flow Control Valve | FIM1 HP Flush Water | Detail 1 | FC | X | X | [14 empty] | 1
PCV23410 | 2000-F23-PID-PR-10002 | F23-PP-466 Final Tails Pump 1 Suction Flushing Water Pressure Control Valve | F23PP466 Saline Water | Detail 1 | FC | X | X | [14 empty] | 0
PCV23423 | 2000-F23-PID-PR-10002 | F23-PP-467 Final Tails Pump 2 Suction Flushing Water Pressure Control Valve | F23PP467 Saline Water | Detail 1 | FC | X | X | [14 empty] | 0
PCV23434 | 2000-F23-PID-PR-10002 | F23-PP-468 Final Tails Pump 3 Suction Flushing Water Pressure Control Valve | F23PP468 Saline Water | Detail 1 | FC | X | X | [14 empty] | 0
PCV23445 | 2000-F23-PID-PR-10002 | F23-PP-469 Final Tails Pump 4 Suction Flushing Water Pressure Control Valve | F23PP469 Saline Water | Detail 1 | FC | X | X | [14 empty] | 0
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
6

## 8. PID Cont
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FINAL TAILINGS HANDLING AND STORAGE
2000-F23-LST-PR-10001
PID Controllers
[6 empty] | Modes |  |  |  | Setpoint |  |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [8 empty] | Controlled/Manipulated Variable | [12 empty] | C1 Sign Off |  | C2 Sign Off
Tag Source | Tag Name | P&ID | Controller Description | Abbreviated Description (Faceplate) | Normal Operating Mode | Manual | Auto | Cascade | Process Value Tag | Min | Max | Unit | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Range Min | Range Max | Lower Limit | Upper Limit | Unit | Destination Description | Destination (Output) Tag | Direct / Reverse Acting | P | I | D | Comment | Rev | OK | Date | OK | Date
FIT23405 | FIC23405 | 2000-F23-PID-PR-10001 | F23-TK-404 Final Tails Tank Saline Water Feed Flow Indicating Transmitter | F23TK404 Water Ctrl | Cascade | X | X | X | FIT23405 | 0 | 2200 | m3/h | 0 | 3800 | m3/h | [21 empty] | 0 | 100 | 0 | 100 | % Open | F23TK404 Top-up Saline Water FCV | FCV23405 | Reverse |  |  |  | When in Cascade, Final Tails Tank LIT-23401 (Master) controls Saline water addition through FIC-23405 (Slave) which maintains level via FCV-23405. Nominal values and alarm set points to be confirmed during commissioning (expected maximum flowrate 1300 m3/hr). | 0
LT23401 | LIC23401A | 2000-F23-PID-PR-10001 | F23-TK-404 Final Tails Tank Level Indicating Transmitter | F23TK404 Water Add Ctrl | Cascade | X | X | X | LT23401 | 0 | 100 | % | 0 | 100 | % | [12 empty] | 10 | 10 | 25 | 30 | 90 | 5 | 95 | 5 |  | 0 | 1500 | 0 | 1500 | m3/hr | F23TK404 Top-Up Saline Water FIC | FIC23405 | Reverse |  |  |  | Final Tails Tank level is maintained through FIC-23405 (Saline water addition control), A_Hi = Warning A_Lo = Trip F23-AG-404 A_LL = Trip F23-PP-466/467/468/469 (This is an interface with DRA Scope) Nominal values and alarm set points to be confirmed during commissioning. See F23TK404_LVL in Misc Tab for the control loop switches as per the level process value Refer to F28CALC10001 for the calculated set point of the controller | 1 |  |  |  |  | 15/07/2025 15/10/2025 | Updated as per KAN-2082 https://pastech-2955.atlassian.net/browse/KAN-2490
LT23401 | LIC23401B | 2000-F23-PID-PR-10001 | F23-TK-404 Final Tails Tank Level Indicating Transmitter | F23TK404 PP Ctrl | Automatic | X | X |  | LT23401 | 50 | 85 | % | 0 | 100 | % | [21 empty] | 0 | 6000 | 0 | 4500 | m3/hr | Final Tails Pumps FIC (DRA Scope) | FIC23417, FIC23430, FIC23441, FIC23452 via Calc Block (DRA Scope) | Direct |  |  |  | LIC23401 is Primero Scope. The Final Tails Tank Level can be maintained through Cascade control of the Final Tails Pumps Flow Indicator Controllers. LIC23401B would be the master controller and could input into a ratio calculation block to provide the inputs to the Final Tails Pumps Flow Indicator Controllers MV Range estimated from 2000-F00-CAL-PR-10001 Max Case = 3869m3/hr. LIC23401B setpoint is always higher than the LIC23401A setpoint See 2000-F00-PHL-PR-40001 KCGM FIM TSF Control Philosophy Table for the Final Tails Pumps Flow Indicator Controllers details. | 1 |  |  |  |  | 2025-07-30 | Updated during FAT to match calc limits
FIT23456 | FIC23456 | 2000-F23-PID-PR-10002 | #N/A | FIM 1 VLV FW Ctrl | Automatic | X | X |  | FIT23456 | 0 | 800 | m3/h | 0 | 1500 | m3/h | [21 empty] | 0 | 100 | 0 | 100 | % Open | FIM I Valve Station Water FCV | FCV23456 | Reverse |  |  |  |  | 1
PIT23410 | PIC23410 | 2000-F23-PID-PR-10002 | F23-PP-466 Final Tails Pump 1 Suction Flushing Water Pressure Indicating Transmitter | F23PP466 Suction FW Ctrl | Automatic | X | X |  | PIT23410 | 0 | 1000 | kPa | 0 | 1000 | kPa | [21 empty] | 0 | 100 | 0 | 100 | % Open | F23PP466 Suction Flushing Water PCV | PCV23410 | Reverse |  |  |  |  | 0
PIT23423 | PIC23423 | 2000-F23-PID-PR-10002 | F23-PP-467 Final Tails Pump 2 Suction Flushing Water Pressure Indicating Transmitter | F23PP467 Suction FW Ctrl | Automatic | X | X |  | PIT23423 | 0 | 1000 | kPa | 0 | 1000 | kPa | [21 empty] | 0 | 100 | 0 | 100 | % Open | F23PP467 Suction Flushing Water PCV | PCV23423 | Reverse |  |  |  |  | 0
PIT23434 | PIC23434 | 2000-F23-PID-PR-10002 | F23-PP-468 Final Tails Pump 3 Suction Flushing Water Pressure Indicating Transmitter | F23PP468 Suction FW Ctrl | Automatic | X | X |  | PIT23434 | 0 | 1000 | kPa | 0 | 1000 | kPa | [21 empty] | 0 | 100 | 0 | 100 | % Open | F23PP468 Suction Flushing Water PCV | PCV23434 | Reverse |  |  |  |  | 0
PIT23445 | PIC23445 | 2000-F23-PID-PR-10002 | F23-PP-469 Final Tails Pump 4 Suction Flushing Water Pressure Indicating Transmitter | F23PP469 Suction FW Ctrl | Automatic | X | X |  | PIT23445 | 0 | 1000 | kPa | 0 | 1000 | kPa | [21 empty] | 0 | 100 | 0 | 100 | % Open | F23PP469 Suction Flushing Water PCV | PCV23445 | Reverse |  |  |  |  | 0
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
8 | 8

## 9. Drives
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FINAL TAILINGS HANDLING AND STORAGE
2000-F23-LST-PR-10001
DRIVE INTERLOCKS AND CONTROL
[15 empty] | Description (Unhealthy Interlocks) |  |  |  | Interlocks | [6 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Name | Drive Type | Speed Min | Speed Max | Speed Units | SP Lower Limit | SP Upper Limit | Current Max | Manual | Auto | Start Condition (Auto Mode) | Stop Condition (Auto Mode) | # |  | Delay On | Delay Off | Start Permissive | Process | Critical | Hardwired to Drive | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date
F23-AG-404 | 2000-F23-PID-PR-10001 | Final Tails Tank Agitator | VSD | 0 | 100 | % | 40 | 100 | 76.6 77 | X | X | F23AG404_ES | [11 empty] | VSD is used for agitator protection only in start-up with settled solids, maximum start-up torque limited to 80% of full load torque. Include low and high current alarms for F23-AG-404, available from the DCS. FLC Current changed to match nameplate. LR 23/03/2026 | 2
[14 empty] | 1 | F23-AG-404 Comms Failure | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 2 | F23-AG-404 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 0 |  |  |  |  | Desktop Review - Inherent Behaviour
[14 empty] | 3 | F23-AG-404 Drive Fault | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 4 | F23-AG-404 E-Stop | 0 |  |  |  | X | X |  |  |  | 0
[14 empty] | 5 | F23-AG-404 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 6 | F23-AG-404 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | A
[14 empty] | 7 | F23-AG-404 Drive Ready | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 8 | LIC23401A < A_Lo | 5 |  |  | X |  |  | X |  | Trip agitator if Final Tails Tank level < A_Lo | B
1

## 10. Sequence
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FINAL TAILINGS HANDLING AND STORAGE
2000-F23-LST-PR-10001
SEQUENCES
Seq No. | Seq Description | Step | Action | Tag / Item | Description | Next Step Delay (s) | Step Advance Condition | Comments | Rev | Equipment Permissives | Recovery Seq. No if Step Faults
SEQUENCE FLOWCHART DELIVERABLE DOCUMENTS BY OTHERS (2000-F00-LST-PR-40001)
0

## 11. Calculation
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FINAL TAILINGS HANDLING AND STORAGE
2000-F23-LST-PR-10001
CALCULATIONS
|  |  | Unit | Inputs |  |  |  | Operator Input | Calc. Value | Manual Input | [5 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Description (Software Tag Only) |  | # | Tag | Unit | Description |  |  | Nom | Min | Max | Calculation | Comments | Rev | OK | Date | OK | Date
F23CALC10001 | 2000-F23-PID-PR-10001 | F23TK404 Lvl SP |  | 1 | LIC23401B.SV | % | LIC23401B Set Point | X |  | 65 | 50 | 85 | LIC23401A.SV = LIC23401B.SV - F23TK404_Parameter_1 | Min/Max values can be adjusted | 0
|  |  |  | 2 | F23TK404_Parameter_1 | % | Set Point Difference | X |  | 10 | 5 | 20 |  | Allowable set point difference between LIC23401B and LIC23401A Can be adjusted. Cannot be zero or negative | 0
|  |  |  | 3 | LIC23401A.SV | % | LIC23401A Set Point |  | X | [5 empty] | 0
1 | 1

## 12. Misc
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FINAL TAILINGS HANDLING AND STORAGE
2000-F23-LST-PR-10001
MISC. INSTRUMENTS AND CONTROLLERS
[11 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Description | Normal State | Alarm State | Hardwired (y/n) | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date
F24TK404_LVL | 2000-F23-PID-PR-10001 | F23TK404 LVL CTRL | Active |  | N |  |  |  | F24-TK-404 Level Control Conditions: IF LIC23401B.SV > LIC23401.PV > LIC23401A.SV OR LIC23401A.SV > LIC23401.PV THEN USE LIC23401A Control Loop to maintain tank level IF LIC23401B.SV < LIC23401.PV, THEN USE LIC23401B Control Loop to maintain tank level Refer to F28CALC10001 for the control loops' setpoint values | 0 | [6 empty] | MSH: Tag not found in current or offline project
F23AG404_ES | 2000-F23-PID-PR-10001 | F23AG404 Emergency Start | Logic |  | N |  |  |  | if F23-GE-123 = running and F23SW123Q2CL = active pulse F23AG404 to auto and pulse start F23AG404 | 2 |  |  |  |  | 2025-10-02 | CR-010 | MSH: verified logic in drawings, couldn't simulate
F23FN466_ES | 2000-F23-PID-PR-10001 | F23FN466 Emergency Start | Logic |  | N |  |  |  | if F23-GE-123 = running and F23SW123Q2CL = active pulse F23FN466 to auto and pulse start F23FN466 | 2 |  |  |  |  | 2025-10-02 | CR-010 | MSH: verified logic in drawings, couldn't simulate
F23FN467_ES | 2000-F23-PID-PR-10001 | F23FN467 Emergency Start | Logic |  | N |  |  |  | if F23-GE-123 = running and F23SW123Q2CL = active pulse F23FN467 to auto and pulse start F23FN467 | 2 |  |  |  |  | 2025-10-02 | CR-010 | MSH: verified logic in drawings, couldn't simulate
F23FN468_ES | 2000-F23-PID-PR-10001 | F23FN468 Emergency Start | Logic |  | N |  |  |  | if F23-GE-123 = running and F23SW123Q2CL = active pulse F23FN468 to auto and pulse start F23FN468 | 2 |  |  |  |  | 2025-10-02 | CR-010 | MSH: verified logic in drawings, couldn't simulate
F23FN469_ES | 2000-F23-PID-PR-10001 | F23FN469 Emergency Start | Logic |  | N |  |  |  | if F23-GE-123 = running and F23SW123Q2CL = active pulse F23FN469 to auto and pulse start F23FN469 | 2 |  |  |  |  | 2025-10-02 | CR-010 | MSH: verified logic in drawings, couldn't simulate
6

## 13. Alarm Database
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - FINAL TAILINGS HANDLING AND STORAGE
2000-F23-LST-PR-10001
ALARM DATABASE
[14 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Abbreviated Description (Faceplate) | Type | Alarm State | Alarm Value | Alarm Units | On Delay (sec) | Alarm Masking Condition | Impact | Urgency | Priority | Operator Response | Rev | OK | Date | OK | Date
F23AG404AI | 2000-F23-PID-PR-10001 | F23AG404 Current | Analogue | A_Hi | 61.2 | A |  |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Final Tails Tank for high density. Add saline water. Else, Advise Field Operator / Maintenance to investigate. NOTE: HAZOP Action 102 (2000-F00-LST-GE-10010), do not remove. | 1 |  |  |  |  | 2025-07-25 | KAN-2097
F23AG404AI | 2000-F23-PID-PR-10001 | F23AG404 Current | Analogue | A_Lo | 38.3 | A |  | F23AG404 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check Final Tails Tank for low density. Check saline water addition. Else, Advise Field Operator / Maintenance to investigate. NOTE: HAZOP Action 102 (2000-F00-LST-GE-10010), do not remove. | 1 |  |  |  |  | 2025-07-25 | KAN-2097
AI23406 | 2000-F23-PID-PR-10001 | F23TK404 Air HCN Con | Analogue | A_H | 5 | ppm | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Rapid (>5 to <15 minutes) | Low | Radio to prepare to evacuate area | 1 |  |  |  |  | MOC 585 SC 3/6/26
AI23406 | 2000-F23-PID-PR-10001 | F23TK404 Air HCN Con | Analogue | A_HH | 10 | ppm | 5 |  | Personnel1: First Aid Injury, Reversible health effects | Immediate (<5 minutes) | High | Radio to prepare to evacuate area. | 3 |  |  |  |  | MOC-712 AP 15/07/2026
LIC23401A | 2000-F23-PID-PR-10001 | F23TK404 Water Add Ctrl | Analogue | A_LL | 10 | % | 10 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | F23-PP-466,467,468, 469 and F23-AG-404 tripped. Check Saline Water top up is in cascade and operating as intended. Check Tails Pumps are in cascade and operating as intended. | 0
LIC23401A | 2000-F23-PID-PR-10001 | F23TK404 Water Add Ctrl | Analogue | A_Lo | 25 | % | 30 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Check Saline Water top up is in cascade and operating as intended. Check Tails Pumps are in cascade and operating as intended. | 0
LIC23401A | 2000-F23-PID-PR-10001 | F23TK404 Water Add Ctrl | Analogue | A_Hi | 90 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Plant Tripped | Logging | . Check Tails Pumps are in cascade and operating as intended. | 1 |  |  |  |  | 2025-07-31 | Updated as per PL-377
LIC23401A | 2000-F23-PID-PR-10001 | F23TK404 Water Add Ctrl | Analogue | A_HH | 95 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Plant Tripped | Logging | Check Tails Pumps are in cascade and operating as intended. | 1 |  |  |  |  | 2025-07-31 | Updated as per PL-377
23DCS409_PS1 | N/A | F23DCS409 PS1 24VDC OK | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Operator to get electrician to inspect unit for potential failure | 0
23DCS409_PS2 | N/A | F23DCS409 PS2 24VDC OK | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Operator to get electrician to inspect unit for potential failure | 0
F23SW023_PS | N/A | F23SW023 ACBSHUNT 24V OK | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 1 |  |  |  |  | 2025-10-23
F23SW023_AF | N/A | F23SW023 ARC FLASH | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate in-field. | 0
F23SW023_TRP | N/A | F23SW023 BREAKER TRIP | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate in-field. | 0
F23SW023_SD | N/A | F23SW023 IncSurgeDiv OK | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 0
23SR001_ESTP | N/A | F23SR001 SR E Shut | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 0
F23SW023_PS1 | N/A | F23SW023 PS1 24VDC OK | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Operator to get electrician to inspect unit for potential failure | 0
F23SW023_PS2 | N/A | F23SW023 PS2 24VDC OK | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Operator to get electrician to inspect unit for potential failure | 0
F23BC001_FL1 | N/A | F23BC001 48VDC Main Fail | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Operator to get electrician to inspect unit for potential failure | 0
F23BC001_FL2 | N/A | F23BC001 48VDC Batt Fail | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Operator to get electrician to inspect unit for potential failure | 0
F23BC001_FL3 | N/A | F23BC001 48VDC Chrg Fail | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Operator to get electrician to inspect unit for potential failure | 0 | [7 empty] | 1
F23BC001_FL4 | N/A | F23BC001 48VDC Earth Flt | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Operator to get electrician to inspect unit for potential failure | 0
23RIO001_PS1 | N/A | F23RIO001 PS1 24VDC OK | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Operator to get electrician to inspect unit for potential failure | 0
23RIO001_PS2 | N/A | F23RIO001 PS2 24VDC OK | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Not Urgent (>30 minutes) | Low \ Review the alarm for urgency | Operator to get electrician to inspect unit for potential failure | 0
23FIP001_ALM | N/A | F23FIP001 Alarm | Digital | Alarm |  |  | 0 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm. Follow site specific Fire Emergency Plan. | 0
23FIP001_ISL | N/A | F23FIP001 Isolated | Digital | Alarm |  |  | 0 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm. Follow site specific Fire Emergency Plan. | 0
23FIP001_FLT | N/A | F23FIP001 Fault | Digital | Alarm |  |  | 0 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm. Follow site specific Fire Emergency Plan. | 0
F23SW123_SD | N/A | F23SW123 SurgeDiv OK | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 0
F23SW123_Q1CL | N/A | F23SW123 MainCB Closed | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 0
F23SW123_Q2CL | N/A | F23SW123 GenCB Closed | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 0
LAH23503 | N/A | F23SW123 EPS Gen. Fuel | Digital | Alarm |  |  | 0 |  | None | Rapid (>5 to <15 minutes) | No Alarm | High fuel level in generator fuel reservoir. Operator to radio local field operator to cease re-fuelling. | 0
LAL23503 | N/A | F23SW123 EPS Gen. Fuel | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operational risk for backup power. Operator to organise re-fuelling. | 0
ZAC23504 | N/A | F23TR023 415VMCC Door | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Restricted work area potential safety breach/issue | 0
AAHH23406 | 2000-F23-PID-PR-10001 | F23TK404 HCN Gas HH | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Field personel to evacuate Final Tails Tank area | 1 |  |  |  |  | 2025-07-25 | KAN-2087
UI23500 | N/A | F23SR001 11kV SR Temp | Analogue | A_Hi | 30 | °C | 300 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate air conditioning and cause of high room temperatures. | 0
UI23501 | N/A | F23SR002 415V SR Temp | Analogue | A_Hi | 30 | °C | 300 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate air conditioning and cause of high room temperatures. | 0
UI23502 | N/A | F23SR002 415V SR TF Temp | Analogue | A_Hi | 30 | °C | 300 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate air conditioning and cause of high room temperatures. | 0
FAH23505 | 2000-F24-PID-PR-10005 | F23SE429 Alarm | Digital | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 |  |  |  |  | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
FAH23506 | 2000-F24-PID-PR-10005 | F23SE452 Alarm | Digital | Alarm |  |  | 30 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Dispatch field check immediately and notify supervisor. | 1 |  |  |  |  | 2025-06-26 | Addition to design as per Client request (2000-F24-TQY-PR-20001)
F23TR023_WTH | - | F23TR023 Temp Hi | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Advise electrican to investigate high transformer winding temperature alarm | 1 |  |  |  |  | 2025-08-19 | CR-034 | jwho - fixed in CAMS
PAL23471 |  | F23PP466 Gearbox Pres Lo | Digital | Alarm |  |  | 30 | Mask when pump not running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate in field. Consider swapping Duty/Standby until investigation complete | 1 |  |  |  |  | 2025-10-27
PAL23473 |  | F23PP467 Gearbox Pres Lo | Digital | Alarm |  |  | 30 | Mask when pump not running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate in field. Consider swapping Duty/Standby until investigation complete | 1 |  |  |  |  | 2025-10-27
PAL23475 |  | F23PP468 Gearbox Pres Lo | Digital | Alarm |  |  | 30 | Mask when pump not running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate in field. Consider swapping Duty/Standby until investigation complete | 1 |  |  |  |  | 2025-10-27
PAL23477 |  | F23PP469 Gearbox Pres Lo | Digital | Alarm |  |  | 30 | Mask when pump not running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate in field. Consider swapping Duty/Standby until investigation complete | 1 |  |  |  |  | 2025-10-27
TI23470 |  | F23PP466 Temperature | Analogue | A_Hi | 85 | °C | 5 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Operator to investigate in field. Consider swapping Duty/Standby until investigation complete | 1 |  |  |  |  | 2025-10-27
TI23470 |  | F23PP466 Temperature | Analogue | A_HH | 90 | °C | 5 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Pump tripped. Operator to take action to prevent tailings tank from overflowing (tank may contain acid). Field check to be dispatched once overflow hazard resolved | 1 |  |  |  |  | 2025-10-27
TI23472 |  | F23PP467 Temperature | Analogue | A_Hi | 85 | °C | 5 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Operator to investigate in field. Consider swapping Duty/Standby until investigation complete | 1 |  |  |  |  | 2025-10-27
TI23472 |  | F23PP467 Temperature | Analogue | A_HH | 90 | °C | 5 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Pump tripped. Operator to take action to prevent tailings tank from overflowing (tank may contain acid). Field check to be dispatched once overflow hazard resolved | 1 |  |  |  |  | 2025-10-27
TI23474 |  | F23PP468 Temperature | Analogue | A_Hi | 85 | °C | 5 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Operator to investigate in field. Consider swapping Duty/Standby until investigation complete | 1 |  |  |  |  | 2025-10-27
TI23474 |  | F23PP468 Temperature | Analogue | A_HH | 90 | °C | 5 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Pump tripped. Operator to take action to prevent tailings tank from overflowing (tank may contain acid). Field check to be dispatched once overflow hazard resolved | 1 |  |  |  |  | 2025-10-27
TI23476 |  | F23PP469 Temperature | Analogue | A_Hi | 85 | °C | 5 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Operator to investigate in field. Consider swapping Duty/Standby until investigation complete | 1 |  |  |  |  | 2025-10-27
TI23476 |  | F23PP469 Temperature | Analogue | A_HH | 90 | °C | 5 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Pump tripped. Operator to take action to prevent tailings tank from overflowing (tank may contain acid). Field check to be dispatched once overflow hazard resolved | 1 |  |  |  |  | 2025-10-27
F23GE123CBTRP | - | F23-GE-123 GEN CB TRP | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to manually change over generator | 1

## RiskMatrix
Consequence | None | Personnel1: First Aid Injury, Reversible health effects | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Environmental2: Minor on-site environmental impact, reportable to regulators. | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness. | Environmental3: Moderate environmental impacts, extends beyond site boundary or regulatory violations with fines. | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k
Not Urgent (>30 minutes) | No Alarm | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Logging \ Review the alarm for urgency (Incorrect Alarm Ranking) | Low \ Review the alarm for urgency | Low \ Review the alarm for urgency | Low \ Review the alarm for urgency | High \ Review the alarm for urgency | High \ Review the alarm for urgency | High \ Review the alarm for urgency
Prompt (>15 to <30 minutes) | No Alarm | Low | Low | Low | Low | Low | Low | High | High | High
Rapid (>5 to <15 minutes) | No Alarm | Low | Low | Low | High | High | High | Urgent | Urgent | Urgent
Immediate (<5 minutes) | No Alarm | High | High | High | Urgent | Urgent | Urgent | Invalid | Invalid | Invalid
Plant Tripped | Logging \ Review the alarm priority (Invalid Alarm Ranking) | Logging | Logging | Logging | Logging | Logging | Logging | Logging | Logging | Logging
|  | Priority | Description
|  | Low | Indicates that the process in no longer within nominal operational limits and a prompt operator intervention is required before the process becomes unrecoverable, resulting in minor safety, environmental or financial impacts.
|  | High | Indicates that the process is no longer within nominal operational limits and a rapid operator intervention is required before the process becomes unrecoverable resulting in serious safety, environmental or financial impacts.
|  | Urgent | Indicates that the process is no longer within nominal operational limits and a immediate operator intervention is required before the process becomes unrecoverable resulting in catastrophic safety, environmental or financial impacts.
|  | Logging | Indicates that the process or equipment has reached a unrecoverable or inoperable state and has been stopped. Logging alarms are for post event investigation and are not to enunciate to the operator.
|  | No Alarm | This condition does not meet the minimum requirements required under ISA 18.2 for a alarm to be generated. Including being a abnormal event\condition, requiring an operator response, undertaking a defined action within a defined time limit and having a defined consequences of no action is taken.
|  | Invalid | This senario is likely to be already unrecovreable and as such is unacceptable. Additional solutions such as automated repsonses, re-engeering or modifications the the process \ equipment is required.

## ReferenceList
Consequences
None
Personnel1: First Aid Injury, Reversible health effects
Environmental1: Localised environmental impact, contained, with no regulatory reporting
Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000
Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment.
Environmental2: Minor on-site environmental impact, reportable to regulators.
Financial3: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k.
Personnel3: Lost Time Injury > 48hrs. Severe, reversible health effects with potential to result in a lost time injury/illness.
Environmental3: Moderate environmental impacts, extends beyond site boundary or regulatory violations with fines.
Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k
Type
Analogue
Digital
Alarm State
High-High
High
Low
Low-Low
Active