## Revisions
PROCESS CONTROL TABLES
REVISION HISTORY
KCGM GROWTH PROJECT
2000-F30-LST-PR-10001
NORTHERN STAR RESOURCES LIMITED
Revision | Document Changes | Date
A for Sequence Flowchart Review Only | - Vendor data TBC highlighted or red-text | 2023-12-12
- Does not include the remainder of the Process Control Tables
B for Internal Review | - Vendor data TBC highlighted yellow | 2024-04-04
C for Client Review | Yellow highlight indicates TBC
2024-04-22
0 Issued for Design | - Updated with Client Comments
| - General Updates (character limits) | 2024-06-19
- Yellow highlight indicates TBC
1 Re-issued for Design | - Updates highlighted in orange
| - Deletions are struck out | 2025-02-03
2 Post Software FAT Updates | - Updates highlighted in orange
| - Deletions are struck out | 2026-03-18

## 1. Analogue Input
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CONCENTRATE PRE-LEACH THICKENING, CIL2/3 & CONCENTRATE THICKENING (F30)
2000-F30-LST-PR-10001
ANALOGUE INSTRUMENTS
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [12 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Comments | Rev |  |  | OK | Date | OK | Date
|  |  |  | DIT30455 | DI30455 | 2000-F30-PID-PR-10002 |  | F30PP417/18 Thcknr Dens | 1 | 0 | 2.03 | t/m3 | [21 empty] | The output from DIT30455 inputs into F30-CALC-0001 to calculate DNI30455 | 2 | 2025-03-18 | PCT algnment action register (calc DIT/DNIC tagging)
|  |  |  | F30CALC0002 | WI30455 | 2000-F30-PID-PR-10002 | 30-PP-417/18 Cons Thickener Underflow Pump Density Indicating Transmitter | F30PP417/418 Dry Tonnes | 1 | 0 | 120 | t/h | [22 empty] | 1 | 2025-03-18 | PCT algnment action register (calc DIT/DNIC tagging)
|  |  |  | FIT30456 | FI30456 | 2000-F30-PID-PR-10002 | 30-PP-417/18 Cons Thickener Underflow Pump Discharge Flow Transmitter | F30PP417/418 Flowrate | 1 | 0 | 100 | m3/h | [12 empty] | 5 | 5 | 25 | 5 | 95 | 5 | 100 | 5 | F30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Min = 26.57, Nom = 66.19 and Max = 92.95 m3/hr. A_LL < Trip F30-PP-417/418 Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | PT30459 | PI30459 | 2000-F30-PID-PR-10002 | 30-PP-417/18 Cons Thickener Underflow Pump Discharge Pressure Transmitter | F30PP417/418 Pressure | 1 | 0 | 1000 | kPa | [12 empty] | 250 | 5 | 350 | 5 | 800 | 5 | 850 | 5 | F30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Nominal pressure of 700kPa and maximum pressure of 1000kPa sourced from 2000-F00-DSH-11104 A_HH > Trip F30-PP-417/18 Trip | 1
|  |  |  | FIT30599 | FI30599 | 2000-F30-PID-PR-10001 | F30-TH-61 CONCENTRATE THICKENER FLOCCULANT WATER ADDITION FLOW INDICATING TRANSMITTER | F30TH61 Flocc Dilution | 1 | 0 | 50 | m3/h | [14 empty] | 5 | 5 | 35 | 5 |  |  | F18-PP-407 AND F18-PP-408 NOT RUNNING for > 20 minutes Enable 10s delay for pump start-up | Refer to F72 Stage 2 Misc tab for HS30616B | 2 | 2025-08-14 | New flowmeters to be installed. Existing flowmeters decommissioned
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 5 | 5
WIP | 1 | Re-issued for Design | E. Wilmot
2025-02-03

## 2. Analogue Output
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CONCENTRATE PRE-LEACH THICKENING, CIL2/3 & CONCENTRATE THICKENING (F30)
2000-F30-LST-PR-10001
ANALOGUE OUTPUT
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  |  |  | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | Comments | Rev | OK | Date | OK | Date
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 0 | 0
WIP | 1 | Re-issued for Design | E. Wilmot
2025-02-03

## 3. Digital Input
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - CONCENTRATE PRE-LEACH THICKENING, CIL2/3 & CONCENTRATE THICKENING (F30) | [7 empty] | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)*
2000-F30-LST-PR-10001
DIGITAL INSTRUMENTS (DI)
[19 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Source | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev |  |  | OK | Date | OK | Date
|  |  |  | ZSO30444 | ZIO30444 | 2000-F30-PID-PR-10001 | XV30444 Open Limit Switch | HV30444 Open | N_Open | Open | Nil | Hardwired | 0 |  | No alarm, indication only | 1
|  |  |  | ZSC30444 | ZIC30444 | 2000-F30-PID-PR-10001 | XV30444 Close Limit Switch | HV30444 Close | N_Closed | Closed | Nil | Hardwired | 0 |  | No alarm, indication only | 1
|  |  |  | ZSO30443 | ZIO30443 | 2000-F30-PID-PR-10001 | XV30443 Open Limit Switch | HV30443 Open | N_Open | Open | Nil | Hardwired | 0 |  | No alarm, indication only | 1
|  |  |  | ZSC30443 | ZIC30443 | 2000-F30-PID-PR-10001 | XV30443 Close Limit Switch | HV30443 Close | N_Closed | Closed | Nil | Hardwired | 0 |  | No alarm, indication only | 1
|  |  |  | F30RIO401PS1 | F30RIO401_PS1 | N/A | Substation 68 N-IO Panel Power Supply 1 Healthy | Sub68N-IO Power Supply 1 | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 1
|  |  |  | F30RIO401PS2 | F30RIO401_PS2 | N/A | Substation 68 N-IO Panel Power Supply 2 Healthy | Sub68N-IO Power Supply 2 | Alarm | Normal | Alarm | Hardwired | 0 |  |  | 1
|  |  |  | FSL30448 | FAL30448 | 2000-F24-PID-PR-10003 | F30PP417 Gland Low Flow Switch | F30PP417 Gland | Alarm | Normal | Alarm | Hardwired | 3 | F30-PP-417 NOT RUNNING | Enable 10 second delay on start-up to allow flow from LP Gland Seal Water Pump. | 2 | 18/03/2025 18/8/25 | PCT alignment action register (corrected switches states and associated interlock) https://pastech-2955.atlassian.net/browse/KAN-2155
|  |  |  | FSL30453 | FAL30453 | 2000-F24-PID-PR-10003 | F30PP418 Gland Low Flow Switch | F30PP418 Gland | Alarm | Normal | Alarm | Hardwired | 3 | F30-PP-418 NOT RUNNING | Enable 10 second delay on start-up to allow flow from LP Gland Seal Water Pump. | 2 | 18/03/2025 18/8/25 | PCT alignment action register (corrected switches states and associated interlock) https://pastech-2955.atlassian.net/browse/KAN-2155
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 7 | 7

## 4. Digital Output
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - CONCENTRATE PRE-LEACH THICKENING, CIL2/3 & CONCENTRATE THICKENING (F30) |  |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)*
2000-F30-LST-PR-10001
DIGITAL INSTRUMENTS (DO)
[16 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev | OK | Date | OK | Date
F30-PP-417/418 Concentrate Thickener Underflow Pump 1/2 Recirculation Drain Valve Solenoid Close
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 0 | 0
WIP | 1 | Re-issued for Design | E. Wilmot
2025-02-03

## 5. Totalisers
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CONCENTRATE PRE-LEACH THICKENING, CIL2/3 & CONCENTRATE THICKENING (F30)
2000-F30-LST-PR-10001
TOTALISERS
[11 empty] | Reset Period |  |  |  |  | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | Type | P&ID | Description | Abbreviated Description (Faceplate) | Units | Shift | Day | Cont | Comments | Rev | OK | Date | OK | Date
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 0 | 0
0

## 6. OnOff Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CONCENTRATE PRE-LEACH THICKENING, CIL2/3 & CONCENTRATE THICKENING (F30)
2000-F30-LST-PR-10001
OPEN-CLOSE VALVES
[14 empty] | Permissives and Trips | [14 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open Interlock | Close Interlock | Bypass | Reset Required | Comments | Rev |  |  | OK | Date | OK | Date
|  |  |  | FV30608A | 2000-F30-PID-PR-10001 | F30-PP-417 Suction Drain Valve | F30PP417 Inlet Valve | Existing | FC | X | X | F30-SEQ-0001 | F30-SEQ-0002 | CT1 | FV30608B Open | F30PP418 Inlet Valve Open | 3 |  |  |  |  | X | X |  | FV30608A is existing equipment. | 1
|  |  |  | FV30608B | 2000-F30-PID-PR-10001 |  | F30PP418 Inlet Valve | Existing | FC | X | X | F30-SEQ-0001 | F30-SEQ-0002 | CT1 | FV30608A Open | F30PP417 Inlet Valve Open | 3 |  |  |  |  | X | X |  | FV30608B is existing equipment. | 1
|  |  |  | XV30445 | 2000-F30-PID-PR-10002 | F30-PP-417 Suction Drain Valve | F30PP417 Suction Drain | Detail 4 | FO | X | X | F30-SEQ-0002 | F30-SEQ-0001 | CT1 | F30PP417 RUNNING | F30PP417 Running | 3 |  |  |  |  | X | X |  |  | 1
|  |  |  | XV30446 | 2000-F30-PID-PR-10002 | F30-PP-417 Discharge Valve | F30PP417 Discharge Valve | Detail 3 | FL | X | X | F30-SEQ-0001 | F30-SEQ-0002 | CT1 | F30PP418 RUNNING | F30PP418 Running | 3 |  |  |  |  | X | X |  |  | 1
|  |  |  | XV30450 | 2000-F30-PID-PR-10002 | F30-PP-418 Suction Drain Valve | F30PP418 Suction Drain | Detail 4 | FO | X | X | F30-SEQ-0002 | F30-SEQ-0001 | CT1 | F30PP418 RUNNING | F30PP418 Running | 3 |  |  |  |  | X | X |  |  | 1
|  |  |  | XV30451 | 2000-F30-PID-PR-10002 | F30-PP-418 Discharge Valve | F30PP418 Discharge Valve | Detail 3 | FL | X | X | F30-SEQ-0001 | F30-SEQ-0002 | CT1 | F30PP417 RUNNING | F30PP417 Running | 3 |  |  |  |  | X | X |  |  | 1
|  |  |  | XV30457 | 2000-F30-PID-PR-10002 | F30-PP-417/18 Recirc Valve to Cons Thickener | F30PP417/18 Recirc Valve | Detail 3 | FL | X | X | F30-SEQ-0001 | F30-SEQ-0001 | OT1 | F30PP417/418 RUNNING AND F35TK01A LIT3502 > A_HH OR F35TK01B LIT3503 > A_HH for 120 secs | Pumps Running And LI3502/03 >A_HH | 120 |  |  |  | X |  | X |  | Cons Thickener Underflow Pump 1 OR 2 is running and Filter Feed Tanks 01A/01B level > A_HH for 120 secs | 0
|  |  |  | XV30458 | 2000-F30-PID-PR-10002 | F30-PP-417/18 Forward Valve | F30PP417/18 Fwd Valve | Detail 3 | FL | X | X | F30-SEQ-0001 | F30-SEQ-0001 | CT1 | F30PP417/418 RUNNING AND F35TK01A LIT3502 > A_HH OR F35TK01B LIT3503 > A_HH AND XV30457 OPEN | Pumps Running And LI3502/03 >A_HH | 3 |  |  |  |  | X | X |  | Forward valve closes when the Recirc valve has opened due to the high high alarm level setpoint being reach on the downstream Filter Feed Tanks for 120 secs | 1
|  |  |  | XV30475 | 2000-F30-PID-PR-10002 | F30-PP-417/18 Forward Drain Valve | F30PP417/18 Fwd Drain | Detail 4 | FO | X | X |  | F30-SEQ-0001 | [12 empty] | C
|  |  |  | XV30476 | 2000-F30-PID-PR-10002 | F30-PP-417/18 Recirc Drain Valve | F30PP417/18 Recirc Drain | Detail 4 | FO | X | X |  | F30-SEQ-0001 | [12 empty] | C
|  |  |  | XV30477 | 2000-F30-PID-PR-10002 |  | F30PP417 Suction Flush | Detail 3 | FL | X | X | F30-SEQ-0002 | F30-SEQ-0002 | CT1 | XV30445 CLOSED | F30PP417 Suction Drain Closed | 3 |  |  |  |  | X | X |  |  | 2 | 2026-02-20 | https://pastech-2955.atlassian.net/browse/PL-701
|  |  |  | XV30478 | 2000-F30-PID-PR-10002 |  | F30PP418 Suction Flush | Detail 3 | FL | X | X | F30-SEQ-0002 | F30-SEQ-0002 | CT1 | XV30450 CLOSED | F30PP418 Suction Drain Closed | 3 |  |  |  |  | X | X |  |  | 2 | 2026-02-20 | https://pastech-2955.atlassian.net/browse/PL-701
|  |  |  | SV30447 | 2000-F24-PID-PR-10003 |  | F30PP417 Gland Supply | Detail 11 | FO | X | X | F30-SEQ-0001 OR F30-PP-417 START | F30-SEQ-0002 | OT1 | F30PP417 Running | F30PP417 Running | 3 | - | - | - | X | - | X | - |  | 2 |  | https://pastech-2955.atlassian.net/browse/KAN-2155
|  |  |  | SV30452 | 2000-F24-PID-PR-10003 |  | F30PP418 Gland Supply | Detail 11 | FO | X | X | F30-SEQ-0001 OR F30-PP-418 START | F30-SEQ-0002 | OT1 | F30PP418 Running | F30PP418 Running | 3 | - | - | - | X | - | X | - |  | 2 |  | https://pastech-2955.atlassian.net/browse/KAN-2155
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
14
1

## 7. Control Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CONCENTRATE PRE-LEACH THICKENING, CIL2/3 & CONCENTRATE THICKENING (F30)
2000-F30-LST-PR-10001
CONTROL VALVES
[14 empty] | Permissive and Trips | [12 empty] | C1 Sign Off |  | C2 Sign Off
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open | Close | Bypass | Reset Required | Comments | Rev | OK | Date | OK | Date
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
0

## 8. PID Cont
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - CONCENTRATE PRE-LEACH THICKENING, CIL2/3 & CONCENTRATE THICKENING (F30) | [56 empty] | 0
|  |  |  | 2000-F30-LST-PR-10001 | [56 empty] | 0
|  |  |  | PID Controllers | [55 empty] | C1 Sign Off |  | C2 Sign Off
[10 empty] | Modes |  |  |  | Setpoint |  |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [7 empty] | Alarm Priority |  |  |  |  | Controlled/Manipulated Variable | [10 empty] | Comment | Rev |  |  | OK | Date | OK | Date
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Controller Description | Abbreviated Description (Faceplate) | Normal Operating Mode | Manual | Auto | Cascade | Process Value Tag | Min | Max | Unit | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | A_LL | A_Lo | A_Hi | A_HH | Alarm Masking Conditions | Range Min | Range Max | Lower Limit | Upper Limit | Unit | Destination Description | Destination (Output) Tag | Direct / Reverse Acting | P | I | D
|  |  |  | LT30606 | LIC30606 | 2000-F30-PID-PR-10001 | 30-TH-61 Concentrate Thickener Interface Level Controller | F30TH61 Thcknr Bed Lvl | Auto | X | X |  | LT30606 | 0 | 100 | % | 0 | 100 | % | [12 empty] | 15 | 5 | 25 | 5 | 75 | 5 | 90 | 5 | [5 empty] | 0 | use existing | 0 | 10 | m3/hr | Flowrate setpoint to FIC30598 via HS30616A OFF | FIC30598_SV | Direct |  |  |  | Repurposed thickener. LT30606 is existing equipment. FE30616 is existing equipment so existing instrument range is to be applied. LI30606 alarm setpoints to be confirmed during commissioning. | 2 | 18/03/2025 11/02/2025 | updated to include the handswitch condition for the cascade KAN-2649 updated the destination output to FIC30598.
|  |  |  | FT30616 | FIC30616 | 2000-F30-PID-PR-10001 | 30-TH-61 Concentrate Thickener Interface Flocculant Flow Controller | F30TH61 Floc Dose | Cascade | X | X | X | FT30616 | 0 | 10 | m3/h | 0 | use existing | m3/h | [14 empty] | 1 | 5 | 6 | 5 | [6 empty] | F72-PP-694 VSD / F72-PP-696 Not Running Enable 10s delay for pump start-up | 0 | 100 | 40 | 100 | % VSD Speed | Concentrate Thickener Flocculant Dosing Pump VSD / Thickeners Standby Flocculant Dosing Pump VSD via HS30616 | F72-PP-694 VSD/F72-PP-696 | Reverse |  |  |  | FE30616 is existing equipment so existing instrument range is to be applied. FIC30616 is existing. FIC30616 setpoint ranges and alarm setpoints to be confirmed during commissioning Cascade set value from LIC30606 or F30CALC0003 based on HS306161A selection | 2 | 2025-08-14 | New flowmeters to be installed. Existing flowmeters decommissioned
|  |  |  | PT30607 | PIC30607 | 2000-F30-PID-PR-10001 | 30-PP-417/18 Cons Thickener Bed Pressure Controller | F30TH61 Thcknr Bed Press | Auto | X | X |  | PT30607 | 0 | 100 | % | 0 | 100 | % | [14 empty] | 30 | 5 | 90 | 5 | 95 | 5 | [5 empty] | 0 | 100 | 40 | 100 | % VSD Speed | Concentrate Thickener Underflow Pump 1/2 VSD via HS30607 | F30-PP-417/418 VSD | Direct |  |  |  | Repurposed thickener. PT30607 is existing equipment. PIC30607 setpoint ranges and alarm setpoints to be confirmed during commissioning. Thickener pump speed can only be controlled by one PID controller at a time (refer to HS30607). | C
|  |  |  | F30CALC0001 | DNIC30455 | 2000-F30-PID-PR-10002 | 30-PP-417/18 Cons Thickener Underflow Pump Density Controller | F30PP417/18 Thcknr Dens | Auto | X | X |  | F30CALC0001 | 57 | 63 | % | 0 | 100 | % solids | [12 empty] | 53 | 5 | 55 | 5 | 65 | 5 | 67 | 5 |  |  |  |  | F30-PP-417/418 is Not Running Enable 10s delay for pump start-up | 0 | 100 | 40 | 100 | % VSD Speed | Concentrate Thickener Underflow Pump 1/2 VSD via HS30607 | F30-PP-417/418 VSD | Direct |  |  |  | Thickener pump speed can only be controlled by one PID controller at a time (refer to HS30607). Alarm setpoints to be confirmed during commissioning. | 2 | 2025-03-18 | PCT alignment action register (DI to DNI/DNIC)
|  |  |  | FIT30598 | FIC30598 | 2000-F30-PID-PR-10001 | F30-TH-61 CONCENTRATE THICKENER FLOCCULANT WATER ADDITION FLOW INDICATING TRANSMITTER | F30TH61 Flocc Ctrl | Cascade | X | X | X | FIT30598 | 0 | 10 | % | 0 | 10 | m3/h | [14 empty] | 0.25 | 5 | 4 | 5 | [6 empty] | Mask if 70-PP-20A not running and (70-PP-20B not running and selected for 30-TH-61 duty) F72-PP-694 Not Running and (F72-PP-696 Not Running if selected on HS30616B) Enable 10s delay for pump start-up | 0 | 100 | 40 | 100 | % VSD Speed | Flocculant Distribution Pump A and (Flocculant Distribution Pump B if selected for Concentrate Thickener duty) Concentrate Thickener Flocculant Dosing Pump and (Thickeners Standby Flocculant Dosing Pump if selected on HS30616B) | 70-PP-20A and (F72-PP-20B if selected for 30-TH-61 duty) F72-PP-694 and (F72-PP-696 if selected on HS30616B) VSD | Reverse |  |  |  | Refer to F72 Stage 2 Misc tab for HS30616B | 2 | 14/08/2025 11/02/2026 | New flowmeters to be installed. Existing flowmeters decommissioned https://pastech-2955.atlassian.net/browse/KAN-2651
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 5 | 5

## 9. Drives
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CONCENTRATE PRE-LEACH THICKENING, CIL2/3 & CONCENTRATE THICKENING (F30)
2000-F30-LST-PR-10001
DRIVE INTERLOCKS AND CONTROL
[15 empty] | Description (Unhealthy Interlocks) |  |  |  | Interlocks | [8 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Name | Drive Type | Speed Min | Speed Max | Speed Units | SP Lower Limit | SP Upper Limit | Current Max | Manual | Auto | Start Condition (Auto Mode) | Stop Condition (Auto Mode) | # |  | Delay On | Delay Off | Start Permissive | Process | Critical | Hardwired to Drive | Bypass | Reset Required | Comments | Rev |  |  | OK | Date | OK | Date
F30-PP-417 | 2000-F30-PID-PR-10002 | CONCENTRATE THICKENER U/F PUMP 1 | VSD | 0 | 100 | % | 40 | 100 | 51.4 | X | X | F30-SEQ-0001 | F30-SEQ-0002 | [11 empty] | 1
[14 empty] | 1 | F30-PP-417 Communications Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F30-PP-417 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 3 | F30-PP-417 Drive Fault | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 4 | F30-PP-417 E-Stop | 0 |  |  |  | X | X |  |  |  | 1
[14 empty] | 5 | F30-PP-417 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F30-PP-417 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F30-PP-417 Drive Ready | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 8 | SV30447 Auto or Open | 3 |  | X |  |  |  | X |  | Gland water valve is in Auto or Open | 1
[14 empty] | 9 | FV30608A AND XV30477 is Closed | 3 |  |  | X |  |  | X |  | Pump suction valve should be open and can be bypassed when flushing water is applied to pump | 2 | 2026-02-06 | https://pastech-2955.atlassian.net/browse/KAN-2653
[14 empty] | 10 | XV30445 is Open | 3 |  |  | X |  |  | X |  | Pump suction drain valve should be closed and can be bypassed for unbogging | 1
[14 empty] | 11 | XV30446 is Closed | 3 |  |  | X |  |  | X |  | Pump discharge valve should be open but can be bypassed for unbogging | 1
[14 empty] | 12 | XV30458 AND XV30457 Closed | 3 |  |  | X |  |  | X |  | Trip when both the forward and recirc valves (downstream) are closed | 1
[14 empty] | 13 | FSL30448 Inactive AND F72-PP-417 RUN | 25 |  |  | X |  |  | X |  | Prevent start-up or trip pump if Gland Water is low flow | 2 | 2025-03-18 | PCT alignment action register (corrected switches states and associated interlock)
[14 empty] | 14 | FI30456 < A_LL AND F30-PP-417 RUN | 15 |  |  | X |  |  | X |  | Trip pump if discharge flowrate reaches the low low alarm setpoint. Bypass if instrument faulty or for maintenance purposes. | 2 | 2025-03-18 | Removed alarm delay in comments
[14 empty] | 15 | PI30459 > A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure reaches the high high alarm setpoint. Bypass if instrument faulty or for maintenance purposes. | 2 | 2025-03-18 | Removed alarm delay in comments
F30-PP-418 | 2000-F30-PID-PR-10002 | CONCENTRATE THICKENER U/F PUMP 2 | VSD | 0 | 100 | % | 40 | 100 | 51.4 | X | X | F30-SEQ-0001 | F30-SEQ-0002 | [11 empty] | 1
[14 empty] | 1 | F30-PP-418 Communications Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F30-PP-418 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 3 | F30-PP-418 Drive Fault | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 4 | F30-PP-418 E-Stop | 0 |  |  |  | X | X |  |  |  | 1
[14 empty] | 5 | F30-PP-418 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F30-PP-418 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F30-PP-418 Drive Ready | 0 |  |  |  | X |  |  |  |  | 1
[14 empty] | 8 | SV30452 Auto or Open | 3 |  | X |  |  |  | X |  | Gland water valve is in Auto or Open | 1
[14 empty] | 9 | FV30608B AND XV30478 is Closed | 3 |  |  | X |  |  | X |  | Pump suction valve should be open and can be bypassed when flushing water is applied to pump | 2 | 2026-02-06 | https://pastech-2955.atlassian.net/browse/KAN-2653
[14 empty] | 10 | XV30450 is Open | 3 |  |  | X |  |  | X |  | Pump suction drain valve should be closed and can be bypassed for unbogging | 1
[14 empty] | 11 | XV30451 is Closed | 3 |  |  | X |  |  | X |  | Pump discharge valve should be open but can be bypassed for unbogging | 1
[14 empty] | 12 | XV30458 AND XV30457 are Closed | 3 |  |  | X |  |  | X |  | Trip when both the forward and recirc valves (downstream) are closed | 1
[14 empty] | 13 | FSL30453 Inactive AND F30-PP-418 RUN | 25 |  |  | X |  |  | X |  | Prevent start-up or trip pump if Gland Water Low flow switch is activated. | 2 | 2025-03-18 | PCT alignment action register (corrected switches states and associated interlock)
[14 empty] | 14 | FI30456 < A_LL AND F30-PP-418 RUN | 15 |  |  | X |  |  | X |  | Trip pump if discharge flowrate reaches the low low alarm setpoint. Bypass if instrument faulty or for maintenance purposes. | 2 | 2025-03-18 | Removed alarm delay in comments
[14 empty] | 15 | PI30459 > A_HH | 15 |  |  | X |  |  | X |  | Trip pump if discharge pressure reaches the high high alarm setpoint. Bypass if instrument faulty or for maintenance purposes. | 2 | 2025-03-18 | Removed alarm delay in comments
2

## 11. Calculation
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CONCENTRATE PRE-LEACH THICKENING, CIL2/3 & CONCENTRATE THICKENING (F30)
2000-F30-LST-PR-10001
CALCULATIONS
|  |  | Unit | Inputs |  |  |  | Operator Input | Calc. Value | Manual Input | [7 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Description (Software Tag Only) |  | # | Tag | Unit | Description |  |  | Nom | Min | Max | Calculation | Comments | Rev |  |  | OK | Date | OK | Date
F30CALC0001 | 2000-F30-PID-PR-10002 | F30PP417/18 Thcknr Dens | % solids | 1 | DI30455 | t/m3 | F30PP417/418 Disch SG | [5 empty] | DNIC30455 =[[(F30PP417_P1 * F30PP417_P2)-(DI30455 * F30PP417_P1)] / [DI30455 * (F30PP417_P2 - F30PP417_P1)]] * 100 |  | 2 | 2025-03-18 | PCT algnment action register (calc DIT/DNIC tagging)
|  |  |  | 2 | F30PP417_P1 | t/m3 | Dry Solids SG | X |  | 3.99 | 3 | 4.5 |  | Engineer Input | 2
|  |  |  | 3 | F30PP417_P2 | t/m3 | Liquid SG | X |  | 1.07 | 0.9 | 1.2 |  | Engineer Input | 2
|  |  |  | 4 | DNIC30455 | % Solids | F30PP417/418 Disch %Sol |  | X | [5 empty] | 2
F30CALC0002 | 2000-F30-PID-PR-10002 | F30PP417/418 Dry Tonnes | t/h | 1 | DI30455 | t/m3 | F30PP417/418 Disch SG | [5 empty] | WI30455 = DNIC30455/100 * DI30455.PV * FI30456.PV FI30456 / ((1/F30PP417_P1) + (1/(DI30455/100) - F30PP417_P2)) |  | 2 | 2025-03-18 | PCT algnment action register (calc DIT/DNIC tagging)
|  |  |  | 2 | DNIC30455 | % Solids | F30PP417/418 Disch %Sol |  | X | [5 empty] | 2
|  |  |  | 3 | FI30456 | m3/h | F30PP417/418 Disch flow | [7 empty] | 2
|  |  |  | 4 | WI30455 | t/h | F30PP417/418 Dry Tonnes |  | X | [5 empty] | 2
|  |  |  | 3 | F30PP417_P1 | t/m3 | Dry Solids SG | X |  | 3.99 | 3 | 4.5 |  | Engineer Input | 2
|  |  |  | 4 | F30PP417_P2 | t/m3 | Liquid SG | X |  | 1.07 | 0.9 | 1.2 |  | Engineer Input | 2
F30CALC0003 | 2000-F30-PID-PR-10002 | F30TH61 Floc Dose SP | m3/h | 1 | FIC30598.SV | m3/h | Cascade pump flow SP |  | X |  |  |  | FIC30598.SV = (FIC30598_P1 * WI18027.PV) / (FIC30598_P2 * 10000) |  | 2 | 2025-03-18 | PCT algnment action register (calc DIT/DNIC tagging)
|  |  |  | 2 | WI18027.PV | t/h | F18PP407/408 Dry Tonnes |  | X | [5 empty] | 2
|  |  |  | 3 | FIC30598_P1 | g/t | Flocculant Dose Rate | X |  | 70 | 60 | 140 |  | Engineer Input | 2
|  |  |  | 4 | FIC30598_P2 | % w/v | Flocculant Concentration | X |  | 0.3 | 0.25 | 0.35 |  | Engineer Input | 2
3 | 3

## 12. Misc
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CONCENTRATE PRE-LEACH THICKENING, CIL2/3 & CONCENTRATE THICKENING (F30)
2000-F30-LST-PR-10001
MISC. INSTRUMENTS AND CONTROLLERS
[13 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Description | Normal State | Alarm State | Hardwired (y/n) | Alarm Priority | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev |  |  | OK | Date | OK | Date
HS30616A | 2000-F30-PID-PR-10001 | F30TH61 Floc Control | Operator Selection |  | N |  |  |  | HS30616A Toggle Switch to select between two modes of Cascade control for FIC30598: ON = Input from F30CALC0003 for FIC30598 with manually entered g/t ratio OFF = Cascade input for FIC30598 from bed level input LIC30606 Refer to Calculation F30CALC0003 for further details. CRO Selects FIC30598 cascade setvalue source: ON = Cascade SV from F30CALC0003 OFF = Cascade SV from LIC30606 | 2 | 18/03/2025 11/02/2026 | Design change - need another handswitch tag for the cascade control mode selection for the flocculant flowrate addition in the thickener https://pastech-2955.atlassian.net/browse/KAN-2651
HS30607 | 2000-F30-PID-PR-10002 | F30PP417/418 Control | Operator Selection |  | N |  |  |  | Handswtich for selection of controller to be used for Auto control of F30PP417/418 VSD Faceplate Selection: • ON = DIC30455 OR • OFF = PIC30607 | 2 | 2025-03-18 | Design change - need another handswitch tag for the duty pump selection
HS30607B | 2000-F30-PID-PR-10002 | F30PP417/418 Duty | Operator Selection |  | N |  |  |  | Handswtich for selection of duty pump between F30PP417/418: Faceplate Selection: • ON = F30PP417 DUTY AND F30PP418 STANDBY • OFF = F30PP418 DUTY AND F30PP417 STANDBY | 2 | 2025-08-14 | Not required
F30PP4178STT | 2000-F30-PID-PR-10002 | F30PP417/418 Startup | Setpoint |  | N |  |  |  | Operator-adjustable start-up VSD speed for the Concentrate Thickener Underflow Pumps. F30PP4178STT [=] % Speed (Engineering Units). Configurable Range: 40 - 100% Used in F30-SEQ-0001 START. This will set the MV of DIC30455 AND PIC30607 when it is changed to manual. Value and configurable range to be confirmed during commissioning. | 1
F30PP4178_T1 | 2000-F30-PID-PR-10002 | F30PP417/418 Start Timer | Setpoint |  | N |  |  |  | Timer Duration: 30 seconds (Default) Operator Configurable Range: 0 - 120 seconds. Timer to count-down from nominated duration. Used in F30-SEQ-0001 START. | 1
F30PP4178_T2 | 2000-F30-PID-PR-10002 | F30PP417/418 Flush Timer | Setpoint |  | N |  |  |  | Timer Duration: 120 seconds (Default) Operator Configurable Range: 0 - 600 seconds. Timer to count-down from nominated duration. Used in F30-SEQ-0001 STOP. | 1
HS30607A | 2000-F30-PID-PR-10002 | F30PP417/418 Control | Operator Selection |  | N |  |  |  | Handswitch for selection of controller to be used for Auto control of F30PP417/418 VSD Faceplate Selection: • ON = DIC30455 OR • OFF = PIC30607 | 2 | 2025-08-14 | Duplicate
7

## 13. Alarm Database
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CONCENTRATE PRE-LEACH THICKENING, CIL2/3 & CONCENTRATE THICKENING (F30)
2000-F30-LST-PR-10001
ALARM DATABASE
[16 empty] | C1 Sign Off |  | C2 Sign Off
Tag Name | P&ID | Abbreviated Description (Faceplate) | Type | Alarm State | Alarm Value | Alarm Units | On Delay (sec) | Alarm Masking Condition | Impact | Urgency | Priority | Operator Response | Rev |  |  | OK | Date | OK | Date
DNIC30455 | 2000-F30-PID-PR-10002 | F30PP417/18 Thcknr Dens | Analogue | LL | 53 | % | 5 | 30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | CRO to evaluate thickener bed level and floc dosing and determine whether to switch to to RECIRC mode or make adjustments to setpoints | 2
DNIC30455 | 2000-F30-PID-PR-10002 | F30PP417/18 Thcknr Dens | Analogue | Lo | 55 | % | 5 | 30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Field operator to perform a manual density check to confirm value and then evaluate pump health and speed | 2
DNIC30455 | 2000-F30-PID-PR-10002 | F30PP417/18 Thcknr Dens | Analogue | Hi | 65 | % | 5 | 30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Field operator to perform manual density check to confirm value and then evaluate pump health and speed | 2
DNIC30455 | 2000-F30-PID-PR-10002 | F30PP417/18 Thcknr Dens | Analogue | HH | 67 | % | 5 | 30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | CRO to check pump controller, floc dosing and status of the bed pressure and rake torque in the thickener. Decide if thickener operation needs to be adjusted or pump speed increased. | 2
LIC30606 | 2000-F30-PID-PR-10001 | F30TH61 Thcknr Bed Lvl | Analogue | LL | 15 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | CRO to review flocculant flow controller and floc dosing, and adjust to a lower setpoint if required. | 1
LIC30606 | 2000-F30-PID-PR-10001 | F30TH61 Thcknr Bed Lvl | Analogue | Lo | 25 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Field operator to check for flocculant delivery to thickener from pipe. | 1
LIC30606 | 2000-F30-PID-PR-10001 | F30TH61 Thcknr Bed Lvl | Analogue | Hi | 75 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Field operator to check for flocculant delivery to thickener from pipe and to visually inspect the overflow for turbidity. | 1
LIC30606 | 2000-F30-PID-PR-10001 | F30TH61 Thcknr Bed Lvl | Analogue | HH | 90 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | CRO to review flocculant flow controller and adjust setpoint. CRO to also review thickener underflow pump speed. | 1
FIC30598 | 2000-F30-PID-PR-10001 | F30TH61 Floc Dose | Analogue | Lo | 1 | m3/h | 5 | F72-PP-694 VSD / F72-PP-696 Not Running Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Field operator to inspect flocculant flow into thickener from pipe and inspect flocculant dosing pump. | 2 | 2026-02-11 | https://pastech-2955.atlassian.net/browse/KAN-2651
FIC30598 | 2000-F30-PID-PR-10001 | F30TH61 Floc Dose | Analogue | Hi | 6 | m3/h | 5 | F72-PP-694 VSD / F72-PP-696 Not Running Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | CRO to check bed level instrumentation feedback, bed level controller setpoints and adjust. | 2 | 2026-02-11 | https://pastech-2955.atlassian.net/browse/KAN-2651
PIC30607 | 2000-F30-PID-PR-10002 | F30TH61 Thcknr Bed Press | Analogue | Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review thickener discharge mode, density and underflow pump flowrate then adjust setpoint or set to Recirc mode | 1
PIC30607 | 2000-F30-PID-PR-10002 | F30TH61 Thcknr Bed Press | Analogue | Hi | 90 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review thickener discharge mode, density and underflow pump flowrate, then adjust setpoint | 1
PIC30607 | 2000-F30-PID-PR-10002 | F30TH61 Thcknr Bed Press | Analogue | HH | 95 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review thickener discharge mode, pump controller, rake height, density and underflow pump flowrate, floc addition and make adjustments to control mode and setpoints | 1
PI30459 | 2000-F30-PID-PR-10002 | F30PP417/18 Pressure | Analogue | LL | 250 | kPa | 5 | 30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to check discharge line flow if healthy. Check the discharge density and flowrates. Put pump to manual and increase speed to increase pressure. Stop the duty pump and swap to the next pump if pump needs checking | 0
PI30459 | 2000-F30-PID-PR-10002 | F30PP417/18 Pressure | Analogue | Lo | 350 | kPa | 5 | 30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to review pump operation, discharge density and flowrates. If operating lower than normal, observe and check trend | 1
PI30459 | 2000-F30-PID-PR-10002 | F30PP417/18 Pressure | Analogue | Hi | 800 | kPa | 5 | 30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to review pump operation, discharge density and flowrates. If operating higher than normal, observe and check trend | 1
PI30459 | 2000-F30-PID-PR-10002 | F30PP417/18 Pressure | Analogue | HH | 850 | kPa | 5 | 30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Duty concentrate thickener underflow pump trips. Operator to check discharge line flow if healthy. Check the discharge density and flowrates. Open flush water valve to reduce line pressure. Swap to the next pump if line needs unbogging | 1
FI30456 | 2000-F30-PID-PR-10001 | F30PP417/18 Flowrate | Analogue | LL | 5 | m3/h | 5 | 30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to change to other pump. | 1
FI30456 | 2000-F30-PID-PR-10001 | F30PP417/18 Flowrate | Analogue | Lo | 25 | m3/h | 5 | 30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to review pump setpoint and speed, and discharge density. Check trend and observe | 1
FI30456 | 2000-F30-PID-PR-10002 | F30PP417/418 Flowrate | Analogue | A_Hi | 95 | m3/h | 5 | F30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check underflow pump control | 2 | 2025-08-14 | Missing from alarm DB
FI30456 | 2000-F30-PID-PR-10002 | F30PP417/418 Flowrate | Analogue | A_HH | 100 | m3/h | 5 | F30-PP-417/418 NOT RUNNING Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Check underflow pump control | 2 | 2025-08-14 | Missing from alarm DB
F30RIO401_PS1 | N/A | Sub68N-IO Power Supply 1 | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to inspect power supply to panel | 1
F30RIO401_PS2 | N/A | Sub68N-IO Power Supply 2 | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Electrician to inspect power supply to panel | 1
FAL30448 | 2000-F24-PID-PR-10003 | F30PP417 Gland | Digital | Active |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect pump gland and gland water supply | 2 | 2025-08-15 | https://pastech-2955.atlassian.net/browse/KAN-2155
FAL30453 | 2000-F24-PID-PR-10003 | F30PP418 Gland | Digital | Active |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect pump gland and gland water supply | 2 | 2025-08-15 | https://pastech-2955.atlassian.net/browse/KAN-2155
FI30599 | 2000-F30-PID-PR-10001 | F30TH61 Flocc Dilution | Analogue | A_Lo | 5 | m3/h | 5 | F18-PP-407 AND F18-PP-408 NOT RUNNING for > 20 minutes Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check flocc dilution manual valves | 2 | 2025-08-14 | New flowmeters to be installed. Existing flowmeters decommissioned
FI30599 | 2000-F30-PID-PR-10001 | F30TH61 Flocc Dilution | Analogue | A_Hi | 35 | m3/h | 5 | F18-PP-407 AND F18-PP-408 NOT RUNNING for > 20 minutes Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check flocc dilution manual valves | 2 | 2025-08-14 | New flowmeters to be installed. Existing flowmeters decommissioned
FIC30598 | 2000-F30-PID-PR-10001 | F30TH61 Flocc Ctrl | Analogue PID | A_Lo | 0.25 | m3/h | 5 | F72-PP-694 Not Running and (F72-PP-696 Not Running if selected on HS30616B) Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check flocc control | 2 | 2025-08-14 | New flowmeters to be installed. Existing flowmeters decommissioned
FIC30598 | 2000-F30-PID-PR-10001 | F30TH61 Flocc Ctrl | Analogue PID | A_Hi | 4 | m3/h | 5 | F72-PP-694 Not Running and (F72-PP-696 Not Running if selected on HS30616B) Enable 10s delay for pump start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Check flocc control | 2 | 2025-08-14 | New flowmeters to be installed. Existing flowmeters decommissioned
24